## UDPoints20190321
标签名 | 标签ID | 描述 | 单位 | 类型
FW.#1CLBY | 1 | Ovation Control Builder |  | digital
FW.#1CLQG | 2 | #1超滤设备全关 |  | digital
FW.#1EDI_AUTOM | 3 | #1EDI装置启停步序自动 |  | digital
FW.#1EDI_DONE | 4 | #1EDI装置启停步序结束 |  | digital
FW.#1EDI_FB1 | 5 | #1EDI装置启停步序反馈1 |  | digital
FW.#1EDI_FB1TIME | 6 | #1EDI装置启停步序反馈1时间 |  | float32
FW.#1EDI_FB1TIMESPO | 7 | Ovation Control Builder |  | float32
FW.#1EDI_FB2 | 8 | #1EDI装置启停步序反馈2 |  | digital
FW.#1EDI_FB2TIME | 9 | #1EDI装置启停步序反馈2时间 |  | float32
FW.#1EDI_FB2TIMESPO | 10 | Ovation Control Builder |  | float32
FW.#1EDI_FB3 | 11 | #1EDI装置启停步序反馈3 |  | digital
FW.#1EDI_FB3TIME | 12 | #1EDI装置启停步序反馈3时间 |  | float32
FW.#1EDI_FB3TIMESPO | 13 | Ovation Control Builder |  | float32
FW.#1EDI_FB4 | 14 | #1EDI装置启停步序反馈4 |  | digital
FW.#1EDI_FB4TIME | 15 | #1EDI装置启停步序反馈4时间 |  | float32
FW.#1EDI_FB4TIMESPO | 16 | Ovation Control Builder |  | float32
FW.#1EDI_LP | 17 | #1EDI装置启停步序状态点 |  | int32
FW.#1EDI_MANM | 18 | #1EDI装置启停步序手动 |  | digital
FW.#1EDI_READY | 19 | Ovation Control Builder |  | digital
FW.#1EDI_SEQ1 | 20 | #1EDI装置启停STEP1 |  | digital
FW.#1EDI_SEQ2 | 21 | #1EDI装置启停STEP2 |  | digital
FW.#1EDI_SEQ3 | 22 | #1EDI装置启停STEP3 |  | digital
FW.#1EDI_SEQ4 | 23 | #1EDI装置启停STEP4 |  | digital
FW.#1EDI_SEQGO | 24 | #1EDI装置启停步序启动 |  | digital
FW.#1EDI_SEQNUM | 25 | #1EDI装置启停当前步序 |  | float32
FW.#2CLBY | 26 | Ovation Control Builder |  | digital
FW.#2CLQG | 27 | #2超滤设备全关 |  | digital
FW.#2EDI_AUTOM | 28 | #2EDI装置启停步序自动 |  | digital
FW.#2EDI_DONE | 29 | #2EDI装置启停步序结束 |  | digital
FW.#2EDI_FB1 | 30 | #2EDI装置启停步序反馈1 |  | digital
FW.#2EDI_FB1TIME | 31 | #2EDI装置启停步序反馈1时间 |  | float32
FW.#2EDI_FB1TIMESPO | 32 | Ovation Control Builder |  | float32
FW.#2EDI_FB2 | 33 | #2EDI装置启停步序反馈2 |  | digital
FW.#2EDI_FB2TIME | 34 | #2EDI装置启停步序反馈2时间 |  | float32
FW.#2EDI_FB2TIMESPO | 35 | Ovation Control Builder |  | float32
FW.#2EDI_FB3 | 36 | #2EDI装置启停步序反馈3 |  | digital
FW.#2EDI_FB3TIME | 37 | #2EDI装置启停步序反馈3时间 |  | float32
FW.#2EDI_FB3TIMESPO | 38 | Ovation Control Builder |  | float32
FW.#2EDI_FB4 | 39 | #2EDI装置启停步序反馈4 |  | digital
FW.#2EDI_FB4TIME | 40 | #2EDI装置启停步序反馈4时间 |  | float32
FW.#2EDI_FB4TIMESPO | 41 | Ovation Control Builder |  | float32
FW.#2EDI_LP | 42 | #2EDI装置启停步序状态点 |  | int32
FW.#2EDI_MANM | 43 | #2EDI装置启停步序手动 |  | digital
FW.#2EDI_READY | 44 | Ovation Control Builder |  | digital
FW.#2EDI_SEQ1 | 45 | #2EDI装置启停STEP1 |  | digital
FW.#2EDI_SEQ2 | 46 | #2EDI装置启停STEP2 |  | digital
FW.#2EDI_SEQ3 | 47 | #2EDI装置启停STEP3 |  | digital
FW.#2EDI_SEQ4 | 48 | #2EDI装置启停STEP4 |  | digital
FW.#2EDI_SEQGO | 49 | #2EDI装置启停步序启动 |  | digital
FW.#2EDI_SEQNUM | 50 | #2EDI装置启停当前步序 |  | float32
FW.#3CLBY | 51 | Ovation Control Builder |  | digital
FW.#3CLQG | 52 | #3超滤设备全关 |  | digital
FW.#3EDI_AUTOM | 53 | #3EDI装置启停步序自动 |  | digital
FW.#3EDI_DONE | 54 | #3EDI装置启停步序结束 |  | digital
FW.#3EDI_FB1 | 55 | #3EDI装置启停步序反馈1 |  | digital
FW.#3EDI_FB1TIME | 56 | #3EDI装置启停步序反馈1时间 |  | float32
FW.#3EDI_FB1TIMESPO | 57 | Ovation Control Builder |  | float32
FW.#3EDI_FB2 | 58 | #3EDI装置启停步序反馈2 |  | digital
FW.#3EDI_FB2TIME | 59 | #3EDI装置启停步序反馈2时间 |  | float32
FW.#3EDI_FB2TIMESPO | 60 | Ovation Control Builder |  | float32
FW.#3EDI_FB3 | 61 | #3EDI装置启停步序反馈3 |  | digital
FW.#3EDI_FB3TIME | 62 | #3EDI装置启停步序反馈3时间 |  | float32
FW.#3EDI_FB3TIMESPO | 63 | Ovation Control Builder |  | float32
FW.#3EDI_FB4 | 64 | #3EDI装置启停步序反馈4 |  | digital
FW.#3EDI_FB4TIME | 65 | #3EDI装置启停步序反馈4时间 |  | float32
FW.#3EDI_FB4TIMESPO | 66 | Ovation Control Builder |  | float32
FW.#3EDI_LP | 67 | #3EDI装置启停步序状态点 |  | int32
FW.#3EDI_MANM | 68 | #3EDI装置启停步序手动 |  | digital
FW.#3EDI_READY | 69 | Ovation Control Builder |  | digital
FW.#3EDI_SEQ1 | 70 | #3EDI装置启停STEP1 |  | digital
FW.#3EDI_SEQ2 | 71 | #3EDI装置启停STEP2 |  | digital
FW.#3EDI_SEQ3 | 72 | #3EDI装置启停STEP3 |  | digital
FW.#3EDI_SEQ4 | 73 | #3EDI装置启停STEP4 |  | digital
FW.#3EDI_SEQGO | 74 | #3EDI装置启停步序启动 |  | digital
FW.#3EDI_SEQNUM | 75 | #3EDI装置启停当前步序 |  | float32
FW.#4CLBY | 76 | Ovation Control Builder |  | digital
FW.#4CLQG | 77 | #4超滤设备全关 |  | digital
FW.#4EDI_AUTOM | 78 | #4EDI装置启停步序自动 |  | digital
FW.#4EDI_DONE | 79 | #4EDI装置启停步序结束 |  | digital
FW.#4EDI_FB1 | 80 | #4EDI装置启停步序反馈1 |  | digital
FW.#4EDI_FB1TIME | 81 | #4EDI装置启停步序反馈1时间 |  | float32
FW.#4EDI_FB1TIMESPO | 82 | Ovation Control Builder |  | float32
FW.#4EDI_FB2 | 83 | #4EDI装置启停步序反馈2 |  | digital
FW.#4EDI_FB2TIME | 84 | #4EDI装置启停步序反馈2时间 |  | float32
FW.#4EDI_FB2TIMESPO | 85 | Ovation Control Builder |  | float32
FW.#4EDI_FB3 | 86 | #4EDI装置启停步序反馈3 |  | digital
FW.#4EDI_FB3TIME | 87 | #4EDI装置启停步序反馈3时间 |  | float32
FW.#4EDI_FB3TIMESPO | 88 | Ovation Control Builder |  | float32
FW.#4EDI_FB4 | 89 | #4EDI装置启停步序反馈4 |  | digital
FW.#4EDI_FB4TIME | 90 | #4EDI装置启停步序反馈4时间 |  | float32
FW.#4EDI_FB4TIMESPO | 91 | Ovation Control Builder |  | float32
FW.#4EDI_LP | 92 | #4EDI装置启停步序状态点 |  | int32
FW.#4EDI_MANM | 93 | #4EDI装置启停步序手动 |  | digital
FW.#4EDI_READY | 94 | Ovation Control Builder |  | digital
FW.#4EDI_SEQ1 | 95 | #4EDI装置启停STEP1 |  | digital
FW.#4EDI_SEQ2 | 96 | #4EDI装置启停STEP2 |  | digital
FW.#4EDI_SEQ3 | 97 | #4EDI装置启停STEP3 |  | digital
FW.#4EDI_SEQ4 | 98 | #4EDI装置启停STEP4 |  | digital
FW.#4EDI_SEQGO | 99 | #4EDI装置启停步序启动 |  | digital
FW.#4EDI_SEQNUM | 100 | #4EDI装置启停当前步序 |  | float32
FW.0ALARM | 101 | Ovation Control Builder |  | digital
FW.0JJ | 102 | 不使用加碱泵 |  | digital
FW.0REALARM | 103 | Ovation Control Builder |  | digital
FW.0ZG/HY | 104 | 不使用阻垢/还原泵 |  | digital
FW.1 | 105 | Ovation Control Builder |  | digital
FW.10ALARM | 106 | Ovation Control Builder |  | digital
FW.10ALARM1 | 107 | Ovation Control Builder |  | digital
FW.10REALARM | 108 | Ovation Control Builder |  | digital
FW.11ALARM | 109 | Ovation Control Builder |  | digital
FW.11ALARM1 | 110 | Ovation Control Builder |  | digital
FW.11REALARM | 111 | Ovation Control Builder |  | digital
FW.12ALARM | 112 | Ovation Control Builder |  | digital
FW.12ALARM1 | 113 | Ovation Control Builder |  | digital
FW.12REALARM | 114 | Ovation Control Builder |  | digital
FW.13ALARM | 115 | Ovation Control Builder |  | digital
FW.13ALARM1 | 116 | Ovation Control Builder |  | digital
FW.13REALARM | 117 | Ovation Control Builder |  | digital
FW.14ALARM | 118 | Ovation Control Builder |  | digital
FW.14ALARM1 | 119 | Ovation Control Builder |  | digital
FW.14REALARM | 120 | Ovation Control Builder |  | digital
FW.15ALARM | 121 | Ovation Control Builder |  | digital
FW.15ALARM1 | 122 | Ovation Control Builder |  | digital
FW.15REALARM | 123 | Ovation Control Builder |  | digital
FW.16ALARM | 124 | Ovation Control Builder |  | digital
FW.16ALARM1 | 125 | Ovation Control Builder |  | digital
FW.16REALARM | 126 | Ovation Control Builder |  | digital
FW.17ALARM | 127 | Ovation Control Builder |  | digital
FW.17ALARM1 | 128 | Ovation Control Builder |  | digital
FW.17REALARM | 129 | Ovation Control Builder |  | digital
FW.18ALARM | 130 | Ovation Control Builder |  | digital
FW.18ALARM1 | 131 | Ovation Control Builder |  | digital
FW.18REALARM | 132 | Ovation Control Builder |  | digital
FW.19ALARM | 133 | Ovation Control Builder |  | digital
FW.19ALARM1 | 134 | Ovation Control Builder |  | digital
FW.19REALARM | 135 | Ovation Control Builder |  | digital
FW.1ALARM | 136 | Ovation Control Builder |  | digital
FW.1ALARM1 | 137 | Ovation Control Builder |  | digital
FW.1ALARM10 | 138 | Ovation Control Builder |  | digital
FW.1ALARM11 | 139 | Ovation Control Builder |  | digital
FW.1ALARM12 | 140 | Ovation Control Builder |  | digital
FW.1ALARM13 | 141 | Ovation Control Builder |  | digital
FW.1ALARM14 | 142 | Ovation Control Builder |  | digital
FW.1ALARM15 | 143 | Ovation Control Builder |  | digital
FW.1ALARM2 | 144 | Ovation Control Builder |  | digital
FW.1ALARM3 | 145 | Ovation Control Builder |  | digital
FW.1ALARM4 | 146 | Ovation Control Builder |  | digital
FW.1ALARM5 | 147 | Ovation Control Builder |  | digital
FW.1ALARM6 | 148 | Ovation Control Builder |  | digital
FW.1ALARM7 | 149 | Ovation Control Builder |  | digital
FW.1ALARM8 | 150 | Ovation Control Builder |  | digital
FW.1ALARM9 | 151 | Ovation Control Builder |  | digital
FW.1ALSTR | 152 | 1A号雨水提升泵联锁投入 |  | digital
FW.1BLSTR | 153 | 1B号雨水提升泵联锁投入 |  | digital
FW.1CLBQG | 154 | #1超滤泵全关 |  | digital
FW.1CLBXBY | 155 | #1超滤步延 |  | digital
FW.1CLFX_CS | 156 | #1超滤已运行次数 |  | float32
FW.1CLFX_CSSDSPO | 157 | Ovation Control Builder |  | float32
FW.1CLFX_PD | 158 | #1超滤反洗排队 |  | digital
FW.1CLYX_AUTOM | 159 | #1超滤运行步序自动 |  | digital
FW.1CLYX_DONE | 160 | #1超滤运行步序结束 |  | digital
FW.1CLYX_FB1 | 161 | #1超滤运行步序反馈1 |  | digital
FW.1CLYX_FB10 | 162 | #1超滤运行步序反馈10 |  | digital
FW.1CLYX_FB11 | 163 | #1超滤运行步序反馈11 |  | digital
FW.1CLYX_FB2 | 164 | #1超滤运行步序反馈2 |  | digital
FW.1CLYX_FB3 | 165 | #1超滤运行步序反馈3 |  | digital
FW.1CLYX_FB4 | 166 | #1超滤运行步序反馈4 |  | digital
FW.1CLYX_FB5 | 167 | #1超滤运行步序反馈5 |  | digital
FW.1CLYX_FB6 | 168 | #1超滤运行步序反馈6 |  | digital
FW.1CLYX_FB7 | 169 | #1超滤运行步序反馈7 |  | digital
FW.1CLYX_FB8 | 170 | #1超滤运行步序反馈8 |  | digital
FW.1CLYX_FB9 | 171 | #1超滤运行步序反馈9 |  | digital
FW.1CLYX_JT | 172 | #1超滤急停 |  | digital
FW.1CLYX_JTXD | 173 | Ovation Control Builder |  | digital
FW.1CLYX_LP | 174 | #1超滤运行步序状态点 |  | int32
FW.1CLYX_MANM | 175 | #1超滤运行步序手动 |  | digital
FW.1CLYX_READY | 176 | Ovation Control Builder |  | digital
FW.1CLYX_SEQ1 | 177 | #1超滤运行步序STEP1 |  | digital
FW.1CLYX_SEQ10 | 178 | #1超滤运行步序STEP10 |  | digital
FW.1CLYX_SEQ11 | 179 | #1超滤运行步序STEP11 |  | digital
FW.1CLYX_SEQ2 | 180 | #1超滤运行步序STEP2 |  | digital
FW.1CLYX_SEQ3 | 181 | #1超滤运行步序STEP3 |  | digital
FW.1CLYX_SEQ4 | 182 | #1超滤运行步序STEP4 |  | digital
FW.1CLYX_SEQ5 | 183 | #1超滤运行步序STEP5 |  | digital
FW.1CLYX_SEQ6 | 184 | #1超滤运行步序STEP6 |  | digital
FW.1CLYX_SEQ7 | 185 | #1超滤运行步序STEP7 |  | digital
FW.1CLYX_SEQ8 | 186 | #1超滤运行步序STEP8 |  | digital
FW.1CLYX_SEQ9 | 187 | #1超滤运行步序STEP9 |  | digital
FW.1CLYX_SEQGO | 188 | #1超滤运行步序启动 |  | digital
FW.1CLYX_SEQNUM | 189 | #1超滤运行当前步序 |  | float32
FW.1CLYX_STOP | 190 | #1超滤运行步序停止 |  | digital
FW.1CLYX_TZXD | 191 | Ovation Control Builder |  | digital
FW.1CLYXBY | 192 | #1超滤运行步延 |  | digital
FW.1CLYXBYTIME | 193 | #1超滤运行步延时间 |  | float32
FW.1CLYXFB10TIME | 194 | #1超滤运行步序10时间 |  | float32
FW.1CLYXFB10TIMESPO | 195 | Ovation Control Builder |  | float32
FW.1CLYXFB11TIME | 196 | #1超滤运行步序11时间 |  | float32
FW.1CLYXFB11TIMESPO | 197 | Ovation Control Builder |  | float32
FW.1CLYXFB1TIME | 198 | #1超滤运行步序1时间 |  | float32
FW.1CLYXFB1TIMESPO | 199 | Ovation Control Builder |  | float32
FW.1CLYXFB2TIME | 200 | #1超滤运行步序2时间 |  | float32
FW.1CLYXFB2TIMESPO | 201 | Ovation Control Builder |  | float32
FW.1CLYXFB3TIME | 202 | #1超滤运行步序3时间 |  | float32
FW.1CLYXFB3TIMESPO | 203 | Ovation Control Builder |  | float32
FW.1CLYXFB4TIME | 204 | #1超滤运行步序4时间 |  | float32
FW.1CLYXFB4TIMESPO | 205 | Ovation Control Builder |  | float32
FW.1CLYXFB5TIME | 206 | #1超滤运行步序5时间 |  | float32
FW.1CLYXFB5TIMESPO | 207 | Ovation Control Builder |  | float32
FW.1CLYXFB6TIME | 208 | #1超滤运行步序6时间 |  | float32
FW.1CLYXFB6TIMESPO | 209 | Ovation Control Builder |  | float32
FW.1CLYXFB7TIME | 210 | #1超滤运行步序7时间 |  | float32
FW.1CLYXFB7TIMESPO | 211 | Ovation Control Builder |  | float32
FW.1CLYXFB8TIME | 212 | #1超滤运行步序8时间 |  | float32
FW.1CLYXFB8TIMESPO | 213 | Ovation Control Builder |  | float32
FW.1CLYXFB9TIME | 214 | #1超滤运行步序9时间 |  | float32
FW.1CLYXFB9TIMESPO | 215 | Ovation Control Builder |  | float32
FW.1CLZQ_J0GCB11AA005_CLOSE | 216 | #1超滤增强反洗进水门顺控关 |  | digital
FW.1CLZQ_J0GCB11AA005_OPEN | 217 | #1超滤增强反洗进水门顺控开 |  | digital
FW.1CLZQ_J0GCB11AA006_CLOSE | 218 | #1超滤增强反洗进气门顺控关 |  | digital
FW.1CLZQ_J0GCB11AA006_OPEN | 219 | #1超滤增强反洗进气门顺控开 |  | digital
FW.1CLZQ_J0GCB11AA402_CLOSE | 220 | #1超滤增强反洗上排门顺控关 |  | digital
FW.1CLZQ_J0GCB11AA402_OPEN | 221 | #1超滤增强反洗上排门顺控开 |  | digital
FW.1CLZQ_J0GCB11AA403_CLOSE | 222 | #1超滤增强反洗药洗排水门关 |  | digital
FW.1CLZQ_J0GCB11AA403_OPEN | 223 | #1超滤增强反洗药洗排水门开 |  | digital
FW.1CLZQ_J0GCQ11AP001_CLOSE | 224 | 超滤增强反洗加次氯酸泵停 |  | digital
FW.1CLZQ_J0GCQ11AP001_OPEN | 225 | 超滤增强反洗加次氯酸泵启 |  | digital
FW.1CLZQ_J0GCQ21AP001_CLOSE | 226 | 超滤增强反洗加酸泵顺控停 |  | digital
FW.1CLZQ_J0GCQ21AP001_OPEN | 227 | 超滤增强反洗加酸泵顺控启 |  | digital
FW.1CLZQ_J0GCQ51AP001_CLOSE | 228 | 超滤增强反洗加碱泵顺控停 |  | digital
FW.1CLZQ_J0GCQ51AP001_OPEN | 229 | 超滤增强反洗加碱泵顺控启 |  | digital
FW.1CLZQ_JJL_CLOSE | 230 | 超滤增强反洗加碱氯停 |  | digital
FW.1CLZQ_JJL_OPEN | 231 | 超滤增强反洗加碱氯启 |  | digital
FW.1CLZQBY | 232 | #1超滤增强步延 |  | digital
FW.1CLZQFX_AUTOM | 233 | #1超滤增强反洗步序自动 |  | digital
FW.1CLZQFX_DONE | 234 | #1超滤增强反洗步序结束 |  | digital
FW.1CLZQFX_FB1 | 235 | #1超滤增强反洗步序反馈1 |  | digital
FW.1CLZQFX_FB1TIME | 236 | #1超滤增强反洗步序1时间 |  | float32
FW.1CLZQFX_FB1TIMESPO | 237 | Ovation Control Builder |  | float32
FW.1CLZQFX_FB2 | 238 | #1超滤增强反洗步序反馈2 |  | digital
FW.1CLZQFX_FB2TIME | 239 | #1超滤增强反洗步序2时间 |  | float32
FW.1CLZQFX_FB2TIMESPO | 240 | Ovation Control Builder |  | float32
FW.1CLZQFX_FB3 | 241 | #1超滤增强反洗步序反馈3 |  | digital
FW.1CLZQFX_FB3TIME | 242 | #1超滤增强反洗步序3时间 |  | float32
FW.1CLZQFX_FB3TIMESPO | 243 | Ovation Control Builder |  | float32
FW.1CLZQFX_FB4 | 244 | #1超滤增强反洗步序反馈4 |  | digital
FW.1CLZQFX_FB4TIME | 245 | #1超滤增强反洗步序4时间 |  | float32
FW.1CLZQFX_FB4TIMESPO | 246 | Ovation Control Builder |  | float32
FW.1CLZQFX_FB5 | 247 | #1超滤增强反洗步序反馈5 |  | digital
FW.1CLZQFX_FB5TIME | 248 | #1超滤增强反洗步序5时间 |  | float32
FW.1CLZQFX_FB5TIMESPO | 249 | Ovation Control Builder |  | float32
FW.1CLZQFX_FB6 | 250 | #1超滤增强反洗步序反馈6 |  | digital
FW.1CLZQFX_FB6TIME | 251 | #1超滤增强反洗步序6时间 |  | float32
FW.1CLZQFX_FB6TIMESPO | 252 | Ovation Control Builder |  | float32
FW.1CLZQFX_JL | 253 | #1超滤增强反洗加碱氯 |  | digital
FW.1CLZQFX_JS | 254 | #1超滤增强反洗加酸 |  | digital
FW.1CLZQFX_LP | 255 | #1超滤增强反洗步序状态点 |  | int32
FW.1CLZQFX_MANM | 256 | #1超滤增强反洗步序手动 |  | digital
FW.1CLZQFX_PD | 257 | #1超滤增强反洗步序排队 |  | digital
FW.1CLZQFX_QD | 258 | 启动#1超滤增强反洗步序 |  | digital
FW.1CLZQFX_READY | 259 | Ovation Control Builder |  | digital
FW.1CLZQFX_SEQ1 | 260 | #1超滤增强反洗步序STEP1 |  | digital
FW.1CLZQFX_SEQ2 | 261 | #1超滤增强反洗步序STEP2 |  | digital
FW.1CLZQFX_SEQ3 | 262 | #1超滤增强反洗步序STEP3 |  | digital
FW.1CLZQFX_SEQ4 | 263 | #1超滤增强反洗步序STEP4 |  | digital
FW.1CLZQFX_SEQ5 | 264 | #1超滤增强反洗步序STEP5 |  | digital
FW.1CLZQFX_SEQ6 | 265 | #1超滤增强反洗步序STEP6 |  | digital
FW.1CLZQFX_SEQGO | 266 | #1超滤增强反洗步序启动 |  | digital
FW.1CLZQFX_SEQNUM | 267 | #1超滤增强反洗当前步序 |  | float32
FW.1CLZQFX_STOP | 268 | #1超滤增强反洗步序停止 |  | digital
FW.1CLZQFXBY | 269 | #1超滤增强反洗步延 |  | digital
FW.1CLZQFXBYTIME | 270 | #1超滤增强反洗步延时间 |  | float32
FW.1EDI_JT | 271 | #1EDI急停 |  | digital
FW.1EDI_JTXD | 272 | Ovation Control Builder |  | digital
FW.1EDI_TZ | 273 | #1EDI运行停止 |  | digital
FW.1EDI_TZXD | 274 | Ovation Control Builder |  | digital
FW.1EDIBXBY | 275 | #1EDI步延 |  | digital
FW.1EDIGF | 276 | #1EDI急停关阀指令 |  | digital
FW.1EDIQG | 277 | #1EDI设备全关 |  | digital
FW.1EDIYXBY | 278 | #1EDI运行步延 |  | digital
FW.1EDIYXBYTIME | 279 | #1EDI运行步延时间 |  | float32
FW.1EIFSTBQG | 280 | Ovation Control Builder |  | digital
FW.1EJFST_AUTOM | 281 | #1二级反渗透运行步序自动 |  | digital
FW.1EJFST_BYCX | 282 | Ovation Control Builder |  | digital
FW.1EJFST_DONE | 283 | #1二级反渗透运行步序结束 |  | digital
FW.1EJFST_FB1 | 284 | #1二级反渗透运行步序反馈1 |  | digital
FW.1EJFST_FB1TIME | 285 | #1二级反渗透运行步序1时间 |  | float32
FW.1EJFST_FB1TIMESPO | 286 | Ovation Control Builder |  | float32
FW.1EJFST_FB2 | 287 | #1二级反渗透运行步序反馈2 |  | digital
FW.1EJFST_FB2TIME | 288 | #1二级反渗透运行步序2时间 |  | float32
FW.1EJFST_FB2TIMESPO | 289 | Ovation Control Builder |  | float32
FW.1EJFST_FB3 | 290 | #1二级反渗透运行步序反馈3 |  | digital
FW.1EJFST_FB3TIME | 291 | #1二级反渗透运行步序3时间 |  | float32
FW.1EJFST_FB3TIMESPO | 292 | Ovation Control Builder |  | float32
FW.1EJFST_FB4 | 293 | #1二级反渗透运行步序反馈4 |  | digital
FW.1EJFST_FB4TIME | 294 | #1二级反渗透运行步序4时间 |  | float32
FW.1EJFST_FB4TIMESPO | 295 | Ovation Control Builder |  | float32
FW.1EJFST_FB5 | 296 | #1二级反渗透运行步序反馈5 |  | digital
FW.1EJFST_FB5TIME | 297 | #1二级反渗透运行步序5时间 |  | float32
FW.1EJFST_FB5TIMESPO | 298 | Ovation Control Builder |  | float32
FW.1EJFST_J0GCF41AA005CP | 299 | #1二级反渗透冲洗水门顺控关 |  | digital
FW.1EJFST_J0GCF41AA005OP | 300 | #1二级反渗透冲洗水门顺控开 |  | digital
FW.1EJFST_J0GCF41AA401CP | 301 | #1二级反渗透产水排放门顺控关 |  | digital
FW.1EJFST_J0GCF41AA401OP | 302 | #1二级反渗透产水排放门顺控开 |  | digital
FW.1EJFST_J0GCF41AA402CP | 303 | #1二级反渗透浓水排放门顺控关 |  | digital
FW.1EJFST_J0GCF41AA402OP | 304 | #1二级反渗透浓水排放门顺控开 |  | digital
FW.1EJFST_J0GCK41AA003CP | 305 | #1二级反渗透高压泵出水门关 |  | digital
FW.1EJFST_J0GCK41AA003OP | 306 | #1二级反渗透高压泵出水门开 |  | digital
FW.1EJFST_J0GCK41AP001CP | 307 | #1二级反渗透高压泵顺控停 |  | digital
FW.1EJFST_J0GCK41AP001OP | 308 | #1二级反渗透高压泵顺控启 |  | digital
FW.1EJFST_JT | 309 | #1二级反渗透急停 |  | digital
FW.1EJFST_JTXD | 310 | Ovation Control Builder |  | digital
FW.1EJFST_LP | 311 | #1二级反渗透运行步序状态点 |  | int32
FW.1EJFST_MANM | 312 | #1二级反渗透运行步序手动 |  | digital
FW.1EJFST_READY | 313 | Ovation Control Builder |  | digital
FW.1EJFST_SEQ1 | 314 | #1二级反渗透运行步序STEP1 |  | digital
FW.1EJFST_SEQ2 | 315 | #1二级反渗透运行步序STEP2 |  | digital
FW.1EJFST_SEQ3 | 316 | #1二级反渗透运行步序STEP3 |  | digital
FW.1EJFST_SEQ4 | 317 | #1二级反渗透运行步序STEP4 |  | digital
FW.1EJFST_SEQ5 | 318 | #1二级反渗透运行步序STEP5 |  | digital
FW.1EJFST_SEQGO | 319 | #1二级反渗透运行步序启动 |  | digital
FW.1EJFST_SEQNUM | 320 | #1二级反渗透运行当前步序 |  | float32
FW.1EJFST_STOP | 321 | #1二级反渗透冲洗停止 |  | digital
FW.1EJFST_TZ | 322 | #1二级反渗透停止 |  | digital
FW.1EJFST_TZXD | 323 | Ovation Control Builder |  | digital
FW.1EJFST_YLKGDZ | 324 | #1二级反渗透压力动作 |  | digital
FW.1EJFSTBXBY | 325 | #1二级反渗透步延 |  | digital
FW.1EJFSTFX_PD | 326 | #1二级反渗透冲洗排队 |  | digital
FW.1EJFSTQG | 327 | #1二级反渗透设备全关 |  | digital
FW.1EJFSTYXBY | 328 | #1二级反渗透运行步延 |  | digital
FW.1EJFSTYXBYTIME | 329 | #1二级反渗透运行步延时间 |  | float32
FW.1FK1 | 330 | Ovation Control Builder |  | digital
FW.1JFYHSJJ_AUTOM | 331 | #1加非氧化性杀菌剂步序自动 |  | digital
FW.1JFYHSJJ_BQG | 332 | Ovation Control Builder |  | digital
FW.1JFYHSJJ_DONE | 333 | #1加非氧化性杀菌剂步序结束 |  | digital
FW.1JFYHSJJ_FB1 | 334 | #1加非氧化性杀菌剂步序反馈1 |  | digital
FW.1JFYHSJJ_FB1TIME | 335 | 加非氧化性杀菌剂步序反馈1时间 |  | float32
FW.1JFYHSJJ_FB1TIMESPO | 336 | Ovation Control Builder |  | float32
FW.1JFYHSJJ_FB2 | 337 | #1加非氧化性杀菌剂步序反馈2 |  | digital
FW.1JFYHSJJ_FB2TIME | 338 | 加非氧化性杀菌剂步序反馈2时间 |  | float32
FW.1JFYHSJJ_FB2TIMESPO | 339 | Ovation Control Builder |  | float32
FW.1JFYHSJJ_FB3 | 340 | #1加非氧化性杀菌剂步序反馈3 |  | digital
FW.1JFYHSJJ_FB3TIME | 341 | 加非氧化性杀菌剂步序反馈3时间 |  | float32
FW.1JFYHSJJ_FB3TIMESPO | 342 | Ovation Control Builder |  | float32
FW.1JFYHSJJ_FB4 | 343 | #1加非氧化性杀菌剂步序反馈4 |  | digital
FW.1JFYHSJJ_FB4TIME | 344 | 加非氧化性杀菌剂步序反馈4时间 |  | float32
FW.1JFYHSJJ_FB4TIMESPO | 345 | Ovation Control Builder |  | float32
FW.1JFYHSJJ_FB5 | 346 | #1加非氧化性杀菌剂步序反馈5 |  | digital
FW.1JFYHSJJ_FB5TIME | 347 | 加非氧化性杀菌剂步序反馈5时间 |  | float32
FW.1JFYHSJJ_FB5TIMESPO | 348 | Ovation Control Builder |  | float32
FW.1JFYHSJJ_FB6 | 349 | #1加非氧化性杀菌剂步序反馈6 |  | digital
FW.1JFYHSJJ_FB6TIME | 350 | Ovation Control Builder |  | float32
FW.1JFYHSJJ_FB6TIMESPO | 351 | Ovation Control Builder |  | float32
FW.1JFYHSJJ_JT | 352 | #1加非氧化性杀菌剂急停 |  | digital
FW.1JFYHSJJ_JTXD | 353 | Ovation Control Builder |  | digital
FW.1JFYHSJJ_LP | 354 | #1加非氧化性杀菌剂步序状态点 |  | int32
FW.1JFYHSJJ_MANM | 355 | #1加非氧化性杀菌剂步序手动 |  | digital
FW.1JFYHSJJ_READY | 356 | Ovation Control Builder |  | digital
FW.1JFYHSJJ_SEQ1 | 357 | #1加非氧化性杀菌剂Step1 |  | digital
FW.1JFYHSJJ_SEQ2 | 358 | #1加非氧化性杀菌剂Step2 |  | digital
FW.1JFYHSJJ_SEQ3 | 359 | #1加非氧化性杀菌剂Step3 |  | digital
FW.1JFYHSJJ_SEQ4 | 360 | #1加非氧化性杀菌剂Step4 |  | digital
FW.1JFYHSJJ_SEQ5 | 361 | #1加非氧化性杀菌剂Step5 |  | digital
FW.1JFYHSJJ_SEQ6 | 362 | Ovation Control Builder |  | digital
FW.1JFYHSJJ_SEQGO | 363 | #1加非氧化性杀菌剂步序启动 |  | digital
FW.1JFYHSJJ_SEQNUM | 364 | #1加非氧化性杀菌剂当前步序 |  | float32
FW.1JFYHSJJ_STOP | 365 | #1加非氧化性杀菌剂步序停止 |  | digital
FW.1JFYHSJJBY | 366 | #1加非氧化杀菌剂步延 |  | digital
FW.1JFYHSJJFX_PD | 367 | #1加非氧化性杀菌剂步序排队 |  | digital
FW.1JFYHSJJQG | 368 | #1加非氧化性杀菌剂全关 |  | digital
FW.1JFYHSJJYXBY | 369 | #1加非氧化杀菌剂运行步延 |  | digital
FW.1JFYHSJJYXBYTIME | 370 | #1加非氧化杀菌剂步延时间 |  | float32
FW.1JJ | 371 | 1套设备使用加碱泵 |  | digital
FW.1JSKPWB_LSTR | 372 | #1集水坑排污泵连锁投入 |  | digital
FW.1KQCXZLLC_AUTOM | 373 | #1空气擦洗重力滤池步序自动 |  | digital
FW.1KQCXZLLC_DONE | 374 | #1空气擦洗重力滤池步序结束 |  | digital
FW.1KQCXZLLC_FB1 | 375 | #1空气擦洗重力滤池反馈1 |  | digital
FW.1KQCXZLLC_FB1TIME | 376 | #1空气擦洗重力滤池反馈1时间 |  | float32
FW.1KQCXZLLC_FB1TIMESPO | 377 | Ovation Control Builder |  | float32
FW.1KQCXZLLC_FB2 | 378 | #1空气擦洗重力滤池反馈2 |  | digital
FW.1KQCXZLLC_FB2TIME | 379 | #1空气擦洗重力滤池反馈2时间 |  | float32
FW.1KQCXZLLC_FB2TIMESPO | 380 | Ovation Control Builder |  | float32
FW.1KQCXZLLC_FB3 | 381 | #1空气擦洗重力滤池反馈3 |  | digital
FW.1KQCXZLLC_FB3TIME | 382 | #1空气擦洗重力滤池反馈3时间 |  | float32
FW.1KQCXZLLC_FB3TIMESPO | 383 | Ovation Control Builder |  | float32
FW.1KQCXZLLC_FB4 | 384 | #1空气擦洗重力滤池反馈4 |  | digital
FW.1KQCXZLLC_FB4TIME | 385 | #1空气擦洗重力滤池反馈4时间 |  | float32
FW.1KQCXZLLC_FB4TIMESPO | 386 | Ovation Control Builder |  | float32
FW.1KQCXZLLC_FB5 | 387 | #1空气擦洗重力滤池反馈5 |  | digital
FW.1KQCXZLLC_FB5TIME | 388 | #1空气擦洗重力滤池反馈5时间 |  | float32
FW.1KQCXZLLC_FB5TIMESPO | 389 | Ovation Control Builder |  | float32
FW.1KQCXZLLC_FB6 | 390 | #1空气擦洗重力滤池反馈6 |  | digital
FW.1KQCXZLLC_FB6TIME | 391 | #1空气擦洗重力滤池反馈6时间 |  | float32
FW.1KQCXZLLC_FB6TIMESPO | 392 | Ovation Control Builder |  | float32
FW.1KQCXZLLC_LP | 393 | #1空气擦洗重力滤池状态点 |  | int32
FW.1KQCXZLLC_MANM | 394 | #1空气擦洗重力滤池步序手动 |  | digital
FW.1KQCXZLLC_PD | 395 | #1空气擦洗重力滤池排队 |  | digital
FW.1KQCXZLLC_READY | 396 | Ovation Control Builder |  | digital
FW.1KQCXZLLC_SEQ1 | 397 | #1空气擦洗重力滤池step1 |  | digital
FW.1KQCXZLLC_SEQ2 | 398 | #1空气擦洗重力滤池step2 |  | digital
FW.1KQCXZLLC_SEQ2A | 399 | Ovation Control Builder |  | digital
FW.1KQCXZLLC_SEQ3 | 400 | #1空气擦洗重力滤池step3 |  | digital
FW.1KQCXZLLC_SEQ3A | 401 | Ovation Control Builder |  | digital
FW.1KQCXZLLC_SEQ4 | 402 | #1空气擦洗重力滤池step4 |  | digital
FW.1KQCXZLLC_SEQ5 | 403 | #1空气擦洗重力滤池step5 |  | digital
FW.1KQCXZLLC_SEQ6 | 404 | #1空气擦洗重力滤池step6 |  | digital
FW.1KQCXZLLC_SEQGO | 405 | #1空气擦洗重力滤池步序启动 |  | digital
FW.1KQCXZLLC_SEQNUM | 406 | #1空气擦洗重力滤池当前步序 |  | float32
FW.1KQCXZLLCTIME | 407 | #1空气擦洗重力滤池排队时间 |  | float32
FW.1KQCXZLLCYX2 | 408 | #2空气擦洗重力滤池排队优先 |  | digital
FW.1KQCXZLLCYX3 | 409 | #3空气擦洗重力滤池排队优先 |  | digital
FW.1REALARM | 410 | Ovation Control Builder |  | digital
FW.1XNCPNTIME | 411 | Ovation Control Builder |  | float32
FW.1XNCPNTIMESPO | 412 | Ovation Control Builder |  | float32
FW.1XZLVDJ_LSTR | 413 | #1旋转滤网电机连锁投入 |  | digital
FW.1YB | 414 | #1一级反渗透在运行 |  | digital
FW.1YIFSTBQG | 415 | #1一级反渗透泵全关 |  | digital
FW.1YJFST_AUTOM | 416 | #1一级反渗透运行步序自动 |  | digital
FW.1YJFST_BYCX | 417 | Ovation Control Builder |  | digital
FW.1YJFST_DONE | 418 | #1一级反渗透运行步序结束 |  | digital
FW.1YJFST_FB1 | 419 | #1一级反渗透运行步序反馈1 |  | digital
FW.1YJFST_FB1TIME | 420 | #1一级反渗透运行步序1时间 |  | float32
FW.1YJFST_FB1TIMESPO | 421 | Ovation Control Builder |  | float32
FW.1YJFST_FB2 | 422 | #1一级反渗透运行步序反馈2 |  | digital
FW.1YJFST_FB2TIME | 423 | #1一级反渗透运行步序2时间 |  | float32
FW.1YJFST_FB2TIMESPO | 424 | Ovation Control Builder |  | float32
FW.1YJFST_FB3 | 425 | #1一级反渗透运行步序反馈3 |  | digital
FW.1YJFST_FB3TIME | 426 | #1一级反渗透运行步序3时间 |  | float32
FW.1YJFST_FB3TIMESPO | 427 | Ovation Control Builder |  | float32
FW.1YJFST_FB4 | 428 | #1一级反渗透运行步序反馈4 |  | digital
FW.1YJFST_FB4TIME | 429 | #1一级反渗透运行步序4时间 |  | float32
FW.1YJFST_FB4TIMESPO | 430 | Ovation Control Builder |  | float32
FW.1YJFST_FB5 | 431 | #1一级反渗透运行步序反馈5 |  | digital
FW.1YJFST_FB5TIME | 432 | #1一级反渗透运行步序5时间 |  | float32
FW.1YJFST_FB5TIMESPO | 433 | Ovation Control Builder |  | float32
FW.1YJFST_FB6 | 434 | #1一级反渗透运行步序反馈6 |  | digital
FW.1YJFST_FB6TIME | 435 | Ovation Control Builder |  | float32
FW.1YJFST_FB6TIMESPO | 436 | Ovation Control Builder |  | float32
FW.1YJFST_JT | 437 | #1一级反渗透急停 |  | digital
FW.1YJFST_JTXD | 438 | Ovation Control Builder |  | digital
FW.1YJFST_LP | 439 | #1一级反渗透运行步序状态点 |  | int32
FW.1YJFST_MANM | 440 | #1一级反渗透运行步序手动 |  | digital
FW.1YJFST_READY | 441 | Ovation Control Builder |  | digital
FW.1YJFST_SEQ1 | 442 | #1一级反渗透运行步序STEP1 |  | digital
FW.1YJFST_SEQ2 | 443 | #1一级反渗透运行步序STEP2 |  | digital
FW.1YJFST_SEQ3 | 444 | #1一级反渗透运行步序STEP3 |  | digital
FW.1YJFST_SEQ4 | 445 | #1一级反渗透运行步序STEP4 |  | digital
FW.1YJFST_SEQ5 | 446 | #1一级反渗透运行步序STEP5 |  | digital
FW.1YJFST_SEQ6 | 447 | #1一级反渗透运行步序STEP6 |  | digital
FW.1YJFST_SEQGO | 448 | #1一级反渗透运行步序启动 |  | digital
FW.1YJFST_SEQNUM | 449 | #1一级反渗透运行当前步序 |  | float32
FW.1YJFST_STOP | 450 | #1一级反渗透运行步序停止 |  | digital
FW.1YJFST_TZ | 451 | #1一级反渗透运行停止 |  | digital
FW.1YJFST_TZXD | 452 | Ovation Control Builder |  | digital
FW.1YJFST_YLKGDZ | 453 | #1一级反渗透压力开关动作 |  | digital
FW.1YJFSTBXBY | 454 | #1一级反渗透步延 |  | digital
FW.1YJFSTFX_PD | 455 | #1一级反渗透冲洗排队 |  | digital
FW.1YJFSTQG | 456 | #1一级反渗透全关 |  | digital
FW.1YJFSTYXBY | 457 | #1一级反渗透运行步延 |  | digital
FW.1YJFSTYXBYTIME | 458 | #1一级反渗透运行步延时间 |  | float32
FW.1ZDLSQJKM_LSTR | 459 | #1自动滤水器进口门联锁投入 |  | digital
FW.1ZG/HY | 460 | 1套设备使用阻垢/还原泵 |  | digital
FW.2 | 461 | Ovation Control Builder |  | digital
FW.20ALARM | 462 | Ovation Control Builder |  | digital
FW.20ALARM1 | 463 | Ovation Control Builder |  | digital
FW.20REALARM | 464 | Ovation Control Builder |  | digital
FW.21ALARM | 465 | Ovation Control Builder |  | digital
FW.21ALARM1 | 466 | Ovation Control Builder |  | digital
FW.21REALARM | 467 | Ovation Control Builder |  | digital
FW.21XNCPNTIME | 468 | Ovation Control Builder |  | float32
FW.21XNCPNTIMESPO | 469 | Ovation Control Builder |  | float32
FW.22ALARM | 470 | Ovation Control Builder |  | digital
FW.22ALARM1 | 471 | Ovation Control Builder |  | digital
FW.22REALARM | 472 | Ovation Control Builder |  | digital
FW.22XNCPNTIME | 473 | Ovation Control Builder |  | float32
FW.22XNCPNTIMESPO | 474 | Ovation Control Builder |  | float32
FW.23ALARM | 475 | Ovation Control Builder |  | digital
FW.23ALARM1 | 476 | Ovation Control Builder |  | digital
FW.23REALARM | 477 | Ovation Control Builder |  | digital
FW.23XNCPNTIME | 478 | Ovation Control Builder |  | float32
FW.23XNCPNTIMESPO | 479 | Ovation Control Builder |  | float32
FW.24ALARM | 480 | Ovation Control Builder |  | digital
FW.24ALARM1 | 481 | Ovation Control Builder |  | digital
FW.24REALARM | 482 | Ovation Control Builder |  | digital
FW.24XNCPNTIME | 483 | Ovation Control Builder |  | float32
FW.24XNCPNTIMESPO | 484 | Ovation Control Builder |  | float32
FW.25ALARM | 485 | Ovation Control Builder |  | digital
FW.25ALARM1 | 486 | Ovation Control Builder |  | digital
FW.25REALARM | 487 | Ovation Control Builder |  | digital
FW.25XNCDPNTIME | 488 | Ovation Control Builder |  | float32
FW.25XNCDPNTIMESPO | 489 | Ovation Control Builder |  | float32
FW.25XNCPNTIME | 490 | Ovation Control Builder |  | float32
FW.25XNCPNTIMESPO | 491 | Ovation Control Builder |  | float32
FW.26ALARM | 492 | Ovation Control Builder |  | digital
FW.26ALARM1 | 493 | Ovation Control Builder |  | digital
FW.26REALARM | 494 | Ovation Control Builder |  | digital
FW.26XNCDPNTIME | 495 | Ovation Control Builder |  | float32
FW.26XNCDPNTIMESPO | 496 | Ovation Control Builder |  | float32
FW.26XNCPNTIME | 497 | Ovation Control Builder |  | float32
FW.26XNCPNTIMESPO | 498 | Ovation Control Builder |  | float32
FW.27ALARM | 499 | Ovation Control Builder |  | digital
FW.27ALARM1 | 500 | Ovation Control Builder |  | digital
FW.27REALARM | 501 | Ovation Control Builder |  | digital
FW.27XNCDPNTIME | 502 | Ovation Control Builder |  | float32
FW.27XNCDPNTIMESPO | 503 | Ovation Control Builder |  | float32
FW.27XNCPNTIME | 504 | Ovation Control Builder |  | float32
FW.27XNCPNTIMESPO | 505 | Ovation Control Builder |  | float32
FW.28ALARM | 506 | Ovation Control Builder |  | digital
FW.28ALARM1 | 507 | Ovation Control Builder |  | digital
FW.28REALARM | 508 | Ovation Control Builder |  | digital
FW.28XNCDPNTIME | 509 | Ovation Control Builder |  | float32
FW.28XNCDPNTIMESPO | 510 | Ovation Control Builder |  | float32
FW.28XNCPNTIME | 511 | Ovation Control Builder |  | float32
FW.28XNCPNTIMESPO | 512 | Ovation Control Builder |  | float32
FW.29ALARM | 513 | Ovation Control Builder |  | digital
FW.29ALARM1 | 514 | Ovation Control Builder |  | digital
FW.29REALARM | 515 | Ovation Control Builder |  | digital
FW.2ALARM | 516 | Ovation Control Builder |  | digital
FW.2ALARM1 | 517 | Ovation Control Builder |  | digital
FW.2ALSTR | 518 | 2A号雨水提升泵联锁投入 |  | digital
FW.2BLSTR | 519 | 2B号雨水提升泵联锁投入 |  | digital
FW.2CLBQG | 520 | #2超滤泵全关 |  | digital
FW.2CLBXBY | 521 | #2超滤步延 |  | digital
FW.2CLFX_CS | 522 | #2超滤已运行次数 |  | float32
FW.2CLFX_CSSDSPO | 523 | Ovation Control Builder |  | float32
FW.2CLFX_PD | 524 | #2超滤反洗排队 |  | digital
FW.2CLYX_AUTOM | 525 | #2超滤运行步序自动 |  | digital
FW.2CLYX_DONE | 526 | #2超滤运行步序结束 |  | digital
FW.2CLYX_FB1 | 527 | #2超滤运行步序反馈1 |  | digital
FW.2CLYX_FB10 | 528 | #2超滤运行步序反馈10 |  | digital
FW.2CLYX_FB11 | 529 | #2超滤运行步序反馈11 |  | digital
FW.2CLYX_FB2 | 530 | #2超滤运行步序反馈2 |  | digital
FW.2CLYX_FB3 | 531 | #2超滤运行步序反馈3 |  | digital
FW.2CLYX_FB4 | 532 | #2超滤运行步序反馈4 |  | digital
FW.2CLYX_FB5 | 533 | #2超滤运行步序反馈5 |  | digital
FW.2CLYX_FB6 | 534 | #2超滤运行步序反馈6 |  | digital
FW.2CLYX_FB7 | 535 | #2超滤运行步序反馈7 |  | digital
FW.2CLYX_FB8 | 536 | #2超滤运行步序反馈8 |  | digital
FW.2CLYX_FB9 | 537 | #2超滤运行步序反馈9 |  | digital
FW.2CLYX_JT | 538 | #2超滤急停 |  | digital
FW.2CLYX_JTXD | 539 | Ovation Control Builder |  | digital
FW.2CLYX_LP | 540 | #2超滤运行步序状态点 |  | int32
FW.2CLYX_MANM | 541 | #2超滤运行步序手动 |  | digital
FW.2CLYX_READY | 542 | Ovation Control Builder |  | digital
FW.2CLYX_SEQ1 | 543 | #2超滤运行步序STEP1 |  | digital
FW.2CLYX_SEQ10 | 544 | #2超滤运行步序STEP10 |  | digital
FW.2CLYX_SEQ11 | 545 | #2超滤运行步序STEP11 |  | digital
FW.2CLYX_SEQ2 | 546 | #2超滤运行步序STEP2 |  | digital
FW.2CLYX_SEQ3 | 547 | #2超滤运行步序STEP3 |  | digital
FW.2CLYX_SEQ4 | 548 | #2超滤运行步序STEP4 |  | digital
FW.2CLYX_SEQ5 | 549 | #2超滤运行步序STEP5 |  | digital
FW.2CLYX_SEQ6 | 550 | #2超滤运行步序STEP6 |  | digital
FW.2CLYX_SEQ7 | 551 | #2超滤运行步序STEP7 |  | digital
FW.2CLYX_SEQ8 | 552 | #2超滤运行步序STEP8 |  | digital
FW.2CLYX_SEQ9 | 553 | #2超滤运行步序STEP9 |  | digital
FW.2CLYX_SEQGO | 554 | #2超滤运行步序启动 |  | digital
FW.2CLYX_SEQNUM | 555 | #2超滤运行当前步序 |  | float32
FW.2CLYX_STOP | 556 | #2超滤运行步序停止 |  | digital
FW.2CLYX_TZXD | 557 | Ovation Control Builder |  | digital
FW.2CLYXBY | 558 | #2超滤运行步延 |  | digital
FW.2CLYXBYTIME | 559 | #2超滤运行步延时间 |  | float32
FW.2CLYXFB10TIME | 560 | #2超滤运行步序10时间 |  | float32
FW.2CLYXFB10TIMESPO | 561 | Ovation Control Builder |  | float32
FW.2CLYXFB11TIME | 562 | #2超滤运行步序11时间 |  | float32
FW.2CLYXFB11TIMESPO | 563 | Ovation Control Builder |  | float32
FW.2CLYXFB1TIME | 564 | #2超滤运行步序1时间 |  | float32
FW.2CLYXFB1TIMESPO | 565 | Ovation Control Builder |  | float32
FW.2CLYXFB2TIME | 566 | #2超滤运行步序2时间 |  | float32
FW.2CLYXFB2TIMESPO | 567 | Ovation Control Builder |  | float32
FW.2CLYXFB3TIME | 568 | #2超滤运行步序3时间 |  | float32
FW.2CLYXFB3TIMESPO | 569 | Ovation Control Builder |  | float32
FW.2CLYXFB4TIME | 570 | #2超滤运行步序4时间 |  | float32
FW.2CLYXFB4TIMESPO | 571 | Ovation Control Builder |  | float32
FW.2CLYXFB5TIME | 572 | #2超滤运行步序5时间 |  | float32
FW.2CLYXFB5TIMESPO | 573 | Ovation Control Builder |  | float32
FW.2CLYXFB6TIME | 574 | #2超滤运行步序6时间 |  | float32
FW.2CLYXFB6TIMESPO | 575 | Ovation Control Builder |  | float32
FW.2CLYXFB7TIME | 576 | #2超滤运行步序7时间 |  | float32
FW.2CLYXFB7TIMESPO | 577 | Ovation Control Builder |  | float32
FW.2CLYXFB8TIME | 578 | #2超滤运行步序8时间 |  | float32
FW.2CLYXFB8TIMESPO | 579 | Ovation Control Builder |  | float32
FW.2CLYXFB9TIME | 580 | #2超滤运行步序9时间 |  | float32
FW.2CLYXFB9TIMESPO | 581 | Ovation Control Builder |  | float32
FW.2CLZQ_J0GCB12AA005_CLOSE | 582 | #2超滤增强反洗进水门顺控关 |  | digital
FW.2CLZQ_J0GCB12AA005_OPEN | 583 | #2超滤增强反洗进水门顺控开 |  | digital
FW.2CLZQ_J0GCB12AA006_CLOSE | 584 | #2超滤增强反洗进气门顺控关 |  | digital
FW.2CLZQ_J0GCB12AA006_OPEN | 585 | #2超滤增强反洗进气门顺控开 |  | digital
FW.2CLZQ_J0GCB12AA402_CLOSE | 586 | #2超滤增强反洗上排门顺控关 |  | digital
FW.2CLZQ_J0GCB12AA402_OPEN | 587 | #2超滤增强反洗上排门顺控开 |  | digital
FW.2CLZQ_J0GCB12AA403_CLOSE | 588 | #2超滤增强反洗药洗排水门关 |  | digital
FW.2CLZQ_J0GCB12AA403_OPEN | 589 | #2超滤增强反洗药洗排水门开 |  | digital
FW.2CLZQBY | 590 | #2超滤增强步延 |  | digital
FW.2CLZQFX_AUTOM | 591 | #2超滤增强反洗步序自动 |  | digital
FW.2CLZQFX_DONE | 592 | #2超滤增强反洗步序结束 |  | digital
FW.2CLZQFX_FB1 | 593 | #2超滤增强反洗步序反馈1 |  | digital
FW.2CLZQFX_FB1TIME | 594 | #2超滤增强反洗步序1时间 |  | float32
FW.2CLZQFX_FB1TIMESPO | 595 | Ovation Control Builder |  | float32
FW.2CLZQFX_FB2 | 596 | #2超滤增强反洗步序反馈2 |  | digital
FW.2CLZQFX_FB2TIME | 597 | #2超滤增强反洗步序2时间 |  | float32
FW.2CLZQFX_FB2TIMESPO | 598 | Ovation Control Builder |  | float32
FW.2CLZQFX_FB3 | 599 | #2超滤增强反洗步序反馈3 |  | digital
FW.2CLZQFX_FB3TIME | 600 | #2超滤增强反洗步序3时间 |  | float32
FW.2CLZQFX_FB3TIMESPO | 601 | Ovation Control Builder |  | float32
FW.2CLZQFX_FB4 | 602 | #2超滤增强反洗步序反馈4 |  | digital
FW.2CLZQFX_FB4TIME | 603 | #2超滤增强反洗步序4时间 |  | float32
FW.2CLZQFX_FB4TIMESPO | 604 | Ovation Control Builder |  | float32
FW.2CLZQFX_FB5 | 605 | #2超滤增强反洗步序反馈5 |  | digital
FW.2CLZQFX_FB5TIME | 606 | #2超滤增强反洗步序5时间 |  | float32
FW.2CLZQFX_FB5TIMESPO | 607 | Ovation Control Builder |  | float32
FW.2CLZQFX_FB6 | 608 | #2超滤增强反洗步序反馈6 |  | digital
FW.2CLZQFX_FB6TIME | 609 | #2超滤增强反洗步序6时间 |  | float32
FW.2CLZQFX_FB6TIMESPO | 610 | Ovation Control Builder |  | float32
FW.2CLZQFX_JL | 611 | #2超滤增强反洗加碱氯 |  | digital
FW.2CLZQFX_JS | 612 | #2超滤增强反洗加酸 |  | digital
FW.2CLZQFX_LP | 613 | #2超滤增强反洗步序状态点 |  | int32
FW.2CLZQFX_MANM | 614 | #2超滤增强反洗步序手动 |  | digital
FW.2CLZQFX_PD | 615 | #2超滤增强反洗步序排队 |  | digital
FW.2CLZQFX_QD | 616 | 启动#2超滤增强反洗步序 |  | digital
FW.2CLZQFX_READY | 617 | Ovation Control Builder |  | digital
FW.2CLZQFX_SEQ1 | 618 | #2超滤增强反洗步序STEP1 |  | digital
FW.2CLZQFX_SEQ2 | 619 | #2超滤增强反洗步序STEP2 |  | digital
FW.2CLZQFX_SEQ3 | 620 | #2超滤增强反洗步序STEP3 |  | digital
FW.2CLZQFX_SEQ4 | 621 | #2超滤增强反洗步序STEP4 |  | digital
FW.2CLZQFX_SEQ5 | 622 | #2超滤增强反洗步序STEP5 |  | digital
FW.2CLZQFX_SEQ6 | 623 | #2超滤增强反洗步序STEP6 |  | digital
FW.2CLZQFX_SEQGO | 624 | #2超滤增强反洗步序启动 |  | digital
FW.2CLZQFX_SEQNUM | 625 | #2超滤增强反洗当前步序 |  | float32
FW.2CLZQFX_STOP | 626 | #2超滤增强反洗步序停止 |  | digital
FW.2CLZQFXBY | 627 | #2超滤增强反洗步延 |  | digital
FW.2CLZQFXBYTIME | 628 | #2超滤增强反洗步延时间 |  | float32
FW.2EDI_JT | 629 | #2EDI急停 |  | digital
FW.2EDI_JTXD | 630 | Ovation Control Builder |  | digital
FW.2EDI_TZ | 631 | #2EDI运行停止 |  | digital
FW.2EDI_TZXD | 632 | Ovation Control Builder |  | digital
FW.2EDIBXBY | 633 | #2EDI步延 |  | digital
FW.2EDIGF | 634 | #2EDI急停关阀指令 |  | digital
FW.2EDIQG | 635 | #2EDI设备全关 |  | digital
FW.2EDIYXBY | 636 | #2EDI运行步延 |  | digital
FW.2EDIYXBYTIME | 637 | #2EDI运行步延时间 |  | float32
FW.2EIFSTBQG | 638 | Ovation Control Builder |  | digital
FW.2EJFST_AUTOM | 639 | #2二级反渗透运行步序自动 |  | digital
FW.2EJFST_BYCX | 640 | Ovation Control Builder |  | digital
FW.2EJFST_DONE | 641 | #2二级反渗透运行步序结束 |  | digital
FW.2EJFST_FB1 | 642 | #2二级反渗透运行步序反馈1 |  | digital
FW.2EJFST_FB1TIME | 643 | #2二级反渗透运行步序1时间 |  | float32
FW.2EJFST_FB1TIMESPO | 644 | Ovation Control Builder |  | float32
FW.2EJFST_FB2 | 645 | #2二级反渗透运行步序反馈2 |  | digital
FW.2EJFST_FB2TIME | 646 | #2二级反渗透运行步序2时间 |  | float32
FW.2EJFST_FB2TIMESPO | 647 | Ovation Control Builder |  | float32
FW.2EJFST_FB3 | 648 | #2二级反渗透运行步序反馈3 |  | digital
FW.2EJFST_FB3TIME | 649 | #2二级反渗透运行步序3时间 |  | float32
FW.2EJFST_FB3TIMESPO | 650 | Ovation Control Builder |  | float32
FW.2EJFST_FB4 | 651 | #2二级反渗透运行步序反馈4 |  | digital
FW.2EJFST_FB4TIME | 652 | #2二级反渗透运行步序4时间 |  | float32
FW.2EJFST_FB4TIMESPO | 653 | Ovation Control Builder |  | float32
FW.2EJFST_FB5 | 654 | #2二级反渗透运行步序反馈5 |  | digital
FW.2EJFST_FB5TIME | 655 | #2二级反渗透运行步序5时间 |  | float32
FW.2EJFST_FB5TIMESPO | 656 | Ovation Control Builder |  | float32
FW.2EJFST_J0GCF42AA005CP | 657 | #2二级反渗透冲洗水门顺控关 |  | digital
FW.2EJFST_J0GCF42AA005OP | 658 | #2二级反渗透冲洗水门顺控开 |  | digital
FW.2EJFST_J0GCF42AA401CP | 659 | #2二级反渗透产水排放门顺控关 |  | digital
FW.2EJFST_J0GCF42AA401OP | 660 | #2二级反渗透产水排放门顺控开 |  | digital
FW.2EJFST_J0GCF42AA402CP | 661 | #2二级反渗透浓水排放门顺控关 |  | digital
FW.2EJFST_J0GCF42AA402OP | 662 | #2二级反渗透浓水排放门顺控开 |  | digital
FW.2EJFST_J0GCK42AA003CP | 663 | #2二级反渗透高压泵出水门关 |  | digital
FW.2EJFST_J0GCK42AA003OP | 664 | #2二级反渗透高压泵出水门开 |  | digital
FW.2EJFST_J0GCK42AP001CP | 665 | #2二级反渗透高压泵顺控停 |  | digital
FW.2EJFST_J0GCK42AP001OP | 666 | #2二级反渗透高压泵顺控启 |  | digital
FW.2EJFST_JT | 667 | #2二级反渗透急停 |  | digital
FW.2EJFST_JTXD | 668 | Ovation Control Builder |  | digital
FW.2EJFST_LP | 669 | #2二级反渗透运行步序状态点 |  | int32
FW.2EJFST_MANM | 670 | #2二级反渗透运行步序手动 |  | digital
FW.2EJFST_READY | 671 | Ovation Control Builder |  | digital
FW.2EJFST_SEQ1 | 672 | #2二级反渗透运行步序STEP1 |  | digital
FW.2EJFST_SEQ2 | 673 | #2二级反渗透运行步序STEP2 |  | digital
FW.2EJFST_SEQ3 | 674 | #2二级反渗透运行步序STEP3 |  | digital
FW.2EJFST_SEQ4 | 675 | #2二级反渗透运行步序STEP4 |  | digital
FW.2EJFST_SEQ5 | 676 | #2二级反渗透运行步序STEP5 |  | digital
FW.2EJFST_SEQGO | 677 | #2二级反渗透运行步序启动 |  | digital
FW.2EJFST_SEQNUM | 678 | #2二级反渗透运行当前步序 |  | float32
FW.2EJFST_STOP | 679 | #2二级反渗透冲洗停止 |  | digital
FW.2EJFST_TZ | 680 | #2二级反渗透停止 |  | digital
FW.2EJFST_TZXD | 681 | Ovation Control Builder |  | digital
FW.2EJFST_YLKGDZ | 682 | #2二级反渗透压力动作 |  | digital
FW.2EJFSTBXBY | 683 | #2二级反渗透步延 |  | digital
FW.2EJFSTFX_PD | 684 | #2二级反渗透冲洗排队 |  | digital
FW.2EJFSTQG | 685 | #2二级反渗透设备全关 |  | digital
FW.2EJFSTYXBY | 686 | #2二级反渗透运行步延 |  | digital
FW.2EJFSTYXBYTIME | 687 | #2二级反渗透运行步延时间 |  | float32
FW.2FK1 | 688 | Ovation Control Builder |  | digital
FW.2JFYHSJJ_AUTOM | 689 | #2加非氧化性杀菌剂步序自动 |  | digital
FW.2JFYHSJJ_BQG | 690 | Ovation Control Builder |  | digital
FW.2JFYHSJJ_DONE | 691 | #2加非氧化性杀菌剂步序结束 |  | digital
FW.2JFYHSJJ_FB1 | 692 | #2加非氧化性杀菌剂步序反馈1 |  | digital
FW.2JFYHSJJ_FB1TIME | 693 | 加非氧化性杀菌剂步序反馈1时间 |  | float32
FW.2JFYHSJJ_FB1TIMESPO | 694 | Ovation Control Builder |  | float32
FW.2JFYHSJJ_FB2 | 695 | #2加非氧化性杀菌剂步序反馈2 |  | digital
FW.2JFYHSJJ_FB2TIME | 696 | 加非氧化性杀菌剂步序反馈2时间 |  | float32
FW.2JFYHSJJ_FB2TIMESPO | 697 | Ovation Control Builder |  | float32
FW.2JFYHSJJ_FB3 | 698 | #2加非氧化性杀菌剂步序反馈3 |  | digital
FW.2JFYHSJJ_FB3TIME | 699 | 加非氧化性杀菌剂步序反馈3时间 |  | float32
FW.2JFYHSJJ_FB3TIMESPO | 700 | Ovation Control Builder |  | float32
FW.2JFYHSJJ_FB4 | 701 | #2加非氧化性杀菌剂步序反馈4 |  | digital
FW.2JFYHSJJ_FB4TIME | 702 | 加非氧化性杀菌剂步序反馈4时间 |  | float32
FW.2JFYHSJJ_FB4TIMESPO | 703 | Ovation Control Builder |  | float32
FW.2JFYHSJJ_FB5 | 704 | #2加非氧化性杀菌剂步序反馈5 |  | digital
FW.2JFYHSJJ_FB5TIME | 705 | 加非氧化性杀菌剂步序反馈5时间 |  | float32
FW.2JFYHSJJ_FB5TIMESPO | 706 | Ovation Control Builder |  | float32
FW.2JFYHSJJ_FB6 | 707 | Ovation Control Builder |  | digital
FW.2JFYHSJJ_FB6TIME | 708 | Ovation Control Builder |  | float32
FW.2JFYHSJJ_FB6TIMESPO | 709 | Ovation Control Builder |  | float32
FW.2JFYHSJJ_JT | 710 | #2加非氧化性杀菌剂急停 |  | digital
FW.2JFYHSJJ_JTXD | 711 | Ovation Control Builder |  | digital
FW.2JFYHSJJ_LP | 712 | #2加非氧化性杀菌剂步序状态点 |  | int32
FW.2JFYHSJJ_MANM | 713 | #2加非氧化性杀菌剂步序手动 |  | digital
FW.2JFYHSJJ_READY | 714 | Ovation Control Builder |  | digital
FW.2JFYHSJJ_SEQ1 | 715 | #2加非氧化性杀菌剂Step1 |  | digital
FW.2JFYHSJJ_SEQ2 | 716 | #2加非氧化性杀菌剂Step2 |  | digital
FW.2JFYHSJJ_SEQ3 | 717 | #2加非氧化性杀菌剂Step3 |  | digital
FW.2JFYHSJJ_SEQ4 | 718 | #2加非氧化性杀菌剂Step4 |  | digital
FW.2JFYHSJJ_SEQ5 | 719 | #2加非氧化性杀菌剂Step5 |  | digital
FW.2JFYHSJJ_SEQ6 | 720 | Ovation Control Builder |  | digital
FW.2JFYHSJJ_SEQGO | 721 | #2加非氧化性杀菌剂步序启动 |  | digital
FW.2JFYHSJJ_SEQNUM | 722 | #2加非氧化性杀菌剂当前步序 |  | float32
FW.2JFYHSJJ_STOP | 723 | #2加非氧化性杀菌剂步序停止 |  | digital
FW.2JFYHSJJBY | 724 | #2加非氧化杀菌剂步延 |  | digital
FW.2JFYHSJJFX_PD | 725 | #2加非氧化性杀菌剂步序排队 |  | digital
FW.2JFYHSJJQG | 726 | #2加非氧化性杀菌剂全关 |  | digital
FW.2JFYHSJJYXBY | 727 | #2加非氧化杀菌剂运行步延 |  | digital
FW.2JFYHSJJYXBYTIME | 728 | #2加非氧化杀菌剂步延时间 |  | float32
FW.2JJ | 729 | 2套设备使用加碱泵 |  | digital
FW.2JSKPWB_LSTR | 730 | #2集水坑排污泵连锁投入 |  | digital
FW.2KQCXZLLC_AUTOM | 731 | #2空气擦洗重力滤池步序自动 |  | digital
FW.2KQCXZLLC_DONE | 732 | #2空气擦洗重力滤池步序结束 |  | digital
FW.2KQCXZLLC_FB1 | 733 | #2空气擦洗重力滤池反馈1 |  | digital
FW.2KQCXZLLC_FB1TIME | 734 | #2空气擦洗重力滤池反馈1时间 |  | float32
FW.2KQCXZLLC_FB1TIMESPO | 735 | Ovation Control Builder |  | float32
FW.2KQCXZLLC_FB2 | 736 | #2空气擦洗重力滤池反馈2 |  | digital
FW.2KQCXZLLC_FB2TIME | 737 | #2空气擦洗重力滤池反馈2时间 |  | float32
FW.2KQCXZLLC_FB2TIMESPO | 738 | Ovation Control Builder |  | float32
FW.2KQCXZLLC_FB3 | 739 | #2空气擦洗重力滤池反馈3 |  | digital
FW.2KQCXZLLC_FB3TIME | 740 | #2空气擦洗重力滤池反馈3时间 |  | float32
FW.2KQCXZLLC_FB3TIMESPO | 741 | Ovation Control Builder |  | float32
FW.2KQCXZLLC_FB4 | 742 | #2空气擦洗重力滤池反馈4 |  | digital
FW.2KQCXZLLC_FB4TIME | 743 | #2空气擦洗重力滤池反馈4时间 |  | float32
FW.2KQCXZLLC_FB4TIMESPO | 744 | Ovation Control Builder |  | float32
FW.2KQCXZLLC_FB5 | 745 | #2空气擦洗重力滤池反馈5 |  | digital
FW.2KQCXZLLC_FB5TIME | 746 | #2空气擦洗重力滤池反馈5时间 |  | float32
FW.2KQCXZLLC_FB5TIMESPO | 747 | Ovation Control Builder |  | float32
FW.2KQCXZLLC_FB6 | 748 | #2空气擦洗重力滤池反馈6 |  | digital
FW.2KQCXZLLC_FB6TIME | 749 | #2空气擦洗重力滤池反馈6时间 |  | float32
FW.2KQCXZLLC_FB6TIMESPO | 750 | Ovation Control Builder |  | float32
FW.2KQCXZLLC_LP | 751 | #2空气擦洗重力滤池步序状态点 |  | int32
FW.2KQCXZLLC_MANM | 752 | #2空气擦洗重力滤池步序手动 |  | digital
FW.2KQCXZLLC_PD | 753 | #2空气擦洗重力滤池排队 |  | digital
FW.2KQCXZLLC_READY | 754 | Ovation Control Builder |  | digital
FW.2KQCXZLLC_SEQ1 | 755 | #2空气擦洗重力滤池step1 |  | digital
FW.2KQCXZLLC_SEQ2 | 756 | #2空气擦洗重力滤池step2 |  | digital
FW.2KQCXZLLC_SEQ2A | 757 | Ovation Control Builder |  | digital
FW.2KQCXZLLC_SEQ3 | 758 | #2空气擦洗重力滤池step3 |  | digital
FW.2KQCXZLLC_SEQ3A | 759 | Ovation Control Builder |  | digital
FW.2KQCXZLLC_SEQ4 | 760 | #2空气擦洗重力滤池step4 |  | digital
FW.2KQCXZLLC_SEQ5 | 761 | #2空气擦洗重力滤池step5 |  | digital
FW.2KQCXZLLC_SEQ6 | 762 | #2空气擦洗重力滤池step6 |  | digital
FW.2KQCXZLLC_SEQGO | 763 | #2空气擦洗重力滤池步序启动 |  | digital
FW.2KQCXZLLC_SEQNUM | 764 | #2空气擦洗重力滤池当前步序 |  | float32
FW.2KQCXZLLCTIME | 765 | #2空气擦洗重力滤池排队时间 |  | float32
FW.2REALARM | 766 | Ovation Control Builder |  | digital
FW.2XNCDC_DPN | 767 | #2絮凝池排泥大排泥 |  | digital
FW.2XNCDC_DPNFW | 768 | #2絮凝池排泥大排泥复位 |  | digital
FW.2XNCDC_DPNTZ | 769 | #2絮凝池排泥大排泥停止 |  | digital
FW.2XNCDC_DPNZFW | 770 | Ovation Control Builder |  | digital
FW.2XNCDC_QD | 771 | #2絮凝池排泥排泥启动 |  | digital
FW.2XNCDC_QDTZ | 772 | #2絮凝池排泥排泥停止 |  | digital
FW.2XNCDC_QDTZFW | 773 | #2絮凝池排泥排泥停止复位 |  | digital
FW.2XNCPNTIME | 774 | Ovation Control Builder |  | float32
FW.2XNCPNTIMESPO | 775 | Ovation Control Builder |  | float32
FW.2XZLVDJ_LSTR | 776 | #2旋转滤网连锁投入 |  | digital
FW.2YB | 777 | #2一级反渗透在运行 |  | digital
FW.2YIFSTBQG | 778 | #2一级反渗透泵全关 |  | digital
FW.2YJFST_AUTOM | 779 | #2一级反渗透运行步序自动 |  | digital
FW.2YJFST_BYCX | 780 | Ovation Control Builder |  | digital
FW.2YJFST_DONE | 781 | #2一级反渗透运行步序结束 |  | digital
FW.2YJFST_FB1 | 782 | #2一级反渗透运行步序反馈1 |  | digital
FW.2YJFST_FB1TIME | 783 | #2一级反渗透运行步序1时间 |  | float32
FW.2YJFST_FB1TIMESPO | 784 | Ovation Control Builder |  | float32
FW.2YJFST_FB2 | 785 | #2一级反渗透运行步序反馈2 |  | digital
FW.2YJFST_FB2TIME | 786 | #2一级反渗透运行步序2时间 |  | float32
FW.2YJFST_FB2TIMESPO | 787 | Ovation Control Builder |  | float32
FW.2YJFST_FB3 | 788 | #2一级反渗透运行步序反馈3 |  | digital
FW.2YJFST_FB3TIME | 789 | #2一级反渗透运行步序3时间 |  | float32
FW.2YJFST_FB3TIMESPO | 790 | Ovation Control Builder |  | float32
FW.2YJFST_FB4 | 791 | #2一级反渗透运行步序反馈4 |  | digital
FW.2YJFST_FB4TIME | 792 | #2一级反渗透运行步序4时间 |  | float32
FW.2YJFST_FB4TIMESPO | 793 | Ovation Control Builder |  | float32
FW.2YJFST_FB5 | 794 | #2一级反渗透运行步序反馈5 |  | digital
FW.2YJFST_FB5TIME | 795 | #2一级反渗透运行步序5时间 |  | float32
FW.2YJFST_FB5TIMESPO | 796 | Ovation Control Builder |  | float32
FW.2YJFST_FB6 | 797 | Ovation Control Builder |  | digital
FW.2YJFST_FB6TIME | 798 | Ovation Control Builder |  | float32
FW.2YJFST_FB6TIMESPO | 799 | Ovation Control Builder |  | float32
FW.2YJFST_JT | 800 | #2一级反渗透急停 |  | digital
FW.2YJFST_JTXD | 801 | Ovation Control Builder |  | digital
FW.2YJFST_LP | 802 | #2一级反渗透运行步序状态点 |  | int32
FW.2YJFST_MANM | 803 | #2一级反渗透运行步序手动 |  | digital
FW.2YJFST_READY | 804 | Ovation Control Builder |  | digital
FW.2YJFST_SEQ1 | 805 | #2一级反渗透运行步序STEP1 |  | digital
FW.2YJFST_SEQ2 | 806 | #2一级反渗透运行步序STEP2 |  | digital
FW.2YJFST_SEQ3 | 807 | #2一级反渗透运行步序STEP3 |  | digital
FW.2YJFST_SEQ4 | 808 | #2一级反渗透运行步序STEP4 |  | digital
FW.2YJFST_SEQ5 | 809 | #2一级反渗透运行步序STEP5 |  | digital
FW.2YJFST_SEQ6 | 810 | Ovation Control Builder |  | digital
FW.2YJFST_SEQGO | 811 | #2一级反渗透运行步序启动 |  | digital
FW.2YJFST_SEQNUM | 812 | #2一级反渗透运行当前步序 |  | float32
FW.2YJFST_STOP | 813 | #2一级反渗透运行步序停止 |  | digital
FW.2YJFST_TZ | 814 | #2一级反渗透运行停止 |  | digital
FW.2YJFST_TZXD | 815 | Ovation Control Builder |  | digital
FW.2YJFST_YLKGDZ | 816 | #2一级反渗透压力开关动作 |  | digital
FW.2YJFSTBXBY | 817 | #2一级反渗透步延 |  | digital
FW.2YJFSTFX_PD | 818 | #2一级反渗透冲洗排队 |  | digital
FW.2YJFSTQG | 819 | #2一级反渗透全关 |  | digital
FW.2YJFSTYXBY | 820 | #2一级反渗透运行步延 |  | digital
FW.2YJFSTYXBYTIME | 821 | #2一级反渗透运行步延时间 |  | float32
FW.2ZDLSQJKM_LSTR | 822 | #2自动滤水器进口门联锁投入 |  | digital
FW.2ZG/HY | 823 | 2套设备使用阻垢/还原泵 |  | digital
FW.3 | 824 | Ovation Control Builder |  | digital
FW.30ALARM | 825 | Ovation Control Builder |  | digital
FW.30ALARM1 | 826 | Ovation Control Builder |  | digital
FW.30REALARM | 827 | Ovation Control Builder |  | digital
FW.31ALARM | 828 | Ovation Control Builder |  | digital
FW.31ALARM1 | 829 | Ovation Control Builder |  | digital
FW.31REALARM | 830 | Ovation Control Builder |  | digital
FW.32ALARM | 831 | Ovation Control Builder |  | digital
FW.32ALARM1 | 832 | Ovation Control Builder |  | digital
FW.32REALARM | 833 | Ovation Control Builder |  | digital
FW.33ALARM | 834 | Ovation Control Builder |  | digital
FW.33ALARM1 | 835 | Ovation Control Builder |  | digital
FW.33REALARM | 836 | Ovation Control Builder |  | digital
FW.34ALARM | 837 | Ovation Control Builder |  | digital
FW.34ALARM1 | 838 | Ovation Control Builder |  | digital
FW.34REALARM | 839 | Ovation Control Builder |  | digital
FW.35ALARM | 840 | Ovation Control Builder |  | digital
FW.35ALARM1 | 841 | Ovation Control Builder |  | digital
FW.35REALARM | 842 | Ovation Control Builder |  | digital
FW.36ALARM | 843 | Ovation Control Builder |  | digital
FW.36ALARM1 | 844 | Ovation Control Builder |  | digital
FW.36REALARM | 845 | Ovation Control Builder |  | digital
FW.37ALARM | 846 | Ovation Control Builder |  | digital
FW.37ALARM1 | 847 | Ovation Control Builder |  | digital
FW.37REALARM | 848 | Ovation Control Builder |  | digital
FW.38ALARM | 849 | Ovation Control Builder |  | digital
FW.38ALARM1 | 850 | Ovation Control Builder |  | digital
FW.38REALARM | 851 | Ovation Control Builder |  | digital
FW.39ALARM | 852 | Ovation Control Builder |  | digital
FW.39ALARM1 | 853 | Ovation Control Builder |  | digital
FW.39REALARM | 854 | Ovation Control Builder |  | digital
FW.3ALARM | 855 | Ovation Control Builder |  | digital
FW.3ALARM1 | 856 | Ovation Control Builder |  | digital
FW.3CLBQG | 857 | #3超滤泵全关 |  | digital
FW.3CLBXBY | 858 | #3超滤步延 |  | digital
FW.3CLFX_CS | 859 | #3超滤已运行次数 |  | float32
FW.3CLFX_CSSDSPO | 860 | Ovation Control Builder |  | float32
FW.3CLFX_PD | 861 | #3超滤反洗排队 |  | digital
FW.3CLYX_AUTOM | 862 | #3超滤运行步序自动 |  | digital
FW.3CLYX_DONE | 863 | #3超滤运行步序结束 |  | digital
FW.3CLYX_FB1 | 864 | #3超滤运行步序反馈1 |  | digital
FW.3CLYX_FB10 | 865 | #3超滤运行步序反馈10 |  | digital
FW.3CLYX_FB11 | 866 | #3超滤运行步序反馈11 |  | digital
FW.3CLYX_FB2 | 867 | #3超滤运行步序反馈2 |  | digital
FW.3CLYX_FB3 | 868 | #3超滤运行步序反馈3 |  | digital
FW.3CLYX_FB4 | 869 | #3超滤运行步序反馈4 |  | digital
FW.3CLYX_FB5 | 870 | #3超滤运行步序反馈5 |  | digital
FW.3CLYX_FB6 | 871 | #3超滤运行步序反馈6 |  | digital
FW.3CLYX_FB7 | 872 | #3超滤运行步序反馈7 |  | digital
FW.3CLYX_FB8 | 873 | #3超滤运行步序反馈8 |  | digital
FW.3CLYX_FB9 | 874 | #3超滤运行步序反馈9 |  | digital
FW.3CLYX_JT | 875 | #3超滤急停 |  | digital
FW.3CLYX_JTXD | 876 | Ovation Control Builder |  | digital
FW.3CLYX_LP | 877 | #3超滤运行步序状态点 |  | int32
FW.3CLYX_MANM | 878 | #3超滤运行步序手动 |  | digital
FW.3CLYX_READY | 879 | Ovation Control Builder |  | digital
FW.3CLYX_SEQ1 | 880 | #3超滤运行步序STEP1 |  | digital
FW.3CLYX_SEQ10 | 881 | #3超滤运行步序STEP10 |  | digital
FW.3CLYX_SEQ11 | 882 | #3超滤运行步序STEP11 |  | digital
FW.3CLYX_SEQ2 | 883 | #3超滤运行步序STEP2 |  | digital
FW.3CLYX_SEQ3 | 884 | #3超滤运行步序STEP3 |  | digital
FW.3CLYX_SEQ4 | 885 | #3超滤运行步序STEP4 |  | digital
FW.3CLYX_SEQ5 | 886 | #3超滤运行步序STEP5 |  | digital
FW.3CLYX_SEQ6 | 887 | #3超滤运行步序STEP6 |  | digital
FW.3CLYX_SEQ7 | 888 | #3超滤运行步序STEP7 |  | digital
FW.3CLYX_SEQ8 | 889 | #3超滤运行步序STEP8 |  | digital
FW.3CLYX_SEQ9 | 890 | #3超滤运行步序STEP9 |  | digital
FW.3CLYX_SEQGO | 891 | #3超滤运行步序启动 |  | digital
FW.3CLYX_SEQNUM | 892 | #3超滤运行当前步序 |  | float32
FW.3CLYX_STOP | 893 | #3超滤运行步序停止 |  | digital
FW.3CLYX_TZXD | 894 | Ovation Control Builder |  | digital
FW.3CLYXBY | 895 | #3超滤运行步延 |  | digital
FW.3CLYXBYTIME | 896 | #3超滤运行步延时间 |  | float32
FW.3CLYXFB10TIME | 897 | #3超滤运行步序10时间 |  | float32
FW.3CLYXFB10TIMESPO | 898 | Ovation Control Builder |  | float32
FW.3CLYXFB11TIME | 899 | #3超滤运行步序11时间 |  | float32
FW.3CLYXFB11TIMESPO | 900 | Ovation Control Builder |  | float32
FW.3CLYXFB1TIME | 901 | #3超滤运行步序1时间 |  | float32
FW.3CLYXFB1TIMESPO | 902 | Ovation Control Builder |  | float32
FW.3CLYXFB2TIME | 903 | #3超滤运行步序2时间 |  | float32
FW.3CLYXFB2TIMESPO | 904 | Ovation Control Builder |  | float32
FW.3CLYXFB3TIME | 905 | #3超滤运行步序3时间 |  | float32
FW.3CLYXFB3TIMESPO | 906 | Ovation Control Builder |  | float32
FW.3CLYXFB4TIME | 907 | #3超滤运行步序4时间 |  | float32
FW.3CLYXFB4TIMESPO | 908 | Ovation Control Builder |  | float32
FW.3CLYXFB5TIME | 909 | #3超滤运行步序5时间 |  | float32
FW.3CLYXFB5TIMESPO | 910 | Ovation Control Builder |  | float32
FW.3CLYXFB6TIME | 911 | #3超滤运行步序6时间 |  | float32
FW.3CLYXFB6TIMESPO | 912 | Ovation Control Builder |  | float32
FW.3CLYXFB7TIME | 913 | #3超滤运行步序7时间 |  | float32
FW.3CLYXFB7TIMESPO | 914 | Ovation Control Builder |  | float32
FW.3CLYXFB8TIME | 915 | #3超滤运行步序8时间 |  | float32
FW.3CLYXFB8TIMESPO | 916 | Ovation Control Builder |  | float32
FW.3CLYXFB9TIME | 917 | #3超滤运行步序9时间 |  | float32
FW.3CLYXFB9TIMESPO | 918 | Ovation Control Builder |  | float32
FW.3CLZQ_J0GCB13AA005_CLOSE | 919 | #3超滤增强反洗进水门顺控关 |  | digital
FW.3CLZQ_J0GCB13AA005_OPEN | 920 | #3超滤增强反洗进水门顺控开 |  | digital
FW.3CLZQ_J0GCB13AA006_CLOSE | 921 | #3超滤增强反洗进气门顺控关 |  | digital
FW.3CLZQ_J0GCB13AA006_OPEN | 922 | #3超滤增强反洗进气门顺控开 |  | digital
FW.3CLZQ_J0GCB13AA402_CLOSE | 923 | #3超滤增强反洗上排门顺控关 |  | digital
FW.3CLZQ_J0GCB13AA402_OPEN | 924 | #3超滤增强反洗上排门顺控开 |  | digital
FW.3CLZQ_J0GCB13AA403_CLOSE | 925 | #3超滤增强反洗药洗排水门关 |  | digital
FW.3CLZQ_J0GCB13AA403_OPEN | 926 | #3超滤增强反洗药洗排水门开 |  | digital
FW.3CLZQBY | 927 | #3超滤增强步延 |  | digital
FW.3CLZQFX_AUTOM | 928 | #3超滤增强反洗步序自动 |  | digital
FW.3CLZQFX_DONE | 929 | #3超滤增强反洗步序结束 |  | digital
FW.3CLZQFX_FB1 | 930 | #3超滤增强反洗步序反馈1 |  | digital
FW.3CLZQFX_FB1TIME | 931 | #3超滤增强反洗步序1时间 |  | float32
FW.3CLZQFX_FB1TIMESPO | 932 | Ovation Control Builder |  | float32
FW.3CLZQFX_FB2 | 933 | #3超滤增强反洗步序反馈2 |  | digital
FW.3CLZQFX_FB2TIME | 934 | #3超滤增强反洗步序2时间 |  | float32
FW.3CLZQFX_FB2TIMESPO | 935 | Ovation Control Builder |  | float32
FW.3CLZQFX_FB3 | 936 | #3超滤增强反洗步序反馈3 |  | digital
FW.3CLZQFX_FB3TIME | 937 | #3超滤增强反洗步序3时间 |  | float32
FW.3CLZQFX_FB3TIMESPO | 938 | Ovation Control Builder |  | float32
FW.3CLZQFX_FB4 | 939 | #3超滤增强反洗步序反馈4 |  | digital
FW.3CLZQFX_FB4TIME | 940 | #3超滤增强反洗步序4时间 |  | float32
FW.3CLZQFX_FB4TIMESPO | 941 | Ovation Control Builder |  | float32
FW.3CLZQFX_FB5 | 942 | #3超滤增强反洗步序反馈5 |  | digital
FW.3CLZQFX_FB5TIME | 943 | #3超滤增强反洗步序5时间 |  | float32
FW.3CLZQFX_FB5TIMESPO | 944 | Ovation Control Builder |  | float32
FW.3CLZQFX_FB6 | 945 | #3超滤增强反洗步序反馈6 |  | digital
FW.3CLZQFX_FB6TIME | 946 | #3超滤增强反洗步序6时间 |  | float32
FW.3CLZQFX_FB6TIMESPO | 947 | Ovation Control Builder |  | float32
FW.3CLZQFX_JL | 948 | #3超滤增强反洗加碱氯 |  | digital
FW.3CLZQFX_JS | 949 | #3超滤增强反洗加酸 |  | digital
FW.3CLZQFX_LP | 950 | #3超滤增强反洗步序状态点 |  | int32
FW.3CLZQFX_MANM | 951 | #3超滤增强反洗步序手动 |  | digital
FW.3CLZQFX_PD | 952 | #3超滤增强反洗步序排队 |  | digital
FW.3CLZQFX_QD | 953 | 启动#3超滤增强反洗步序 |  | digital
FW.3CLZQFX_READY | 954 | Ovation Control Builder |  | digital
FW.3CLZQFX_SEQ1 | 955 | #3超滤增强反洗步序STEP1 |  | digital
FW.3CLZQFX_SEQ2 | 956 | #3超滤增强反洗步序STEP2 |  | digital
FW.3CLZQFX_SEQ3 | 957 | #3超滤增强反洗步序STEP3 |  | digital
FW.3CLZQFX_SEQ4 | 958 | #3超滤增强反洗步序STEP4 |  | digital
FW.3CLZQFX_SEQ5 | 959 | #3超滤增强反洗步序STEP5 |  | digital
FW.3CLZQFX_SEQ6 | 960 | #3超滤增强反洗步序STEP6 |  | digital
FW.3CLZQFX_SEQGO | 961 | #3超滤增强反洗步序启动 |  | digital
FW.3CLZQFX_SEQNUM | 962 | #3超滤增强反洗当前步序 |  | float32
FW.3CLZQFX_STOP | 963 | #3超滤增强反洗步序停止 |  | digital
FW.3CLZQFXBY | 964 | #3超滤增强反洗步延 |  | digital
FW.3CLZQFXBYTIME | 965 | #3超滤增强反洗步延时间 |  | float32
FW.3EDI_JT | 966 | #3EDI急停 |  | digital
FW.3EDI_JTXD | 967 | Ovation Control Builder |  | digital
FW.3EDI_TZ | 968 | #3EDI运行停止 |  | digital
FW.3EDI_TZXD | 969 | Ovation Control Builder |  | digital
FW.3EDIBXBY | 970 | #3EDI步延 |  | digital
FW.3EDIGF | 971 | #3EDI急停关阀指令 |  | digital
FW.3EDIQG | 972 | #3EDI设备全关 |  | digital
FW.3EDIYXBY | 973 | #3EDI运行步延 |  | digital
FW.3EDIYXBYTIME | 974 | #3EDI运行步延时间 |  | float32
FW.3EIFSTBQG | 975 | Ovation Control Builder |  | digital
FW.3EJFST_AUTOM | 976 | #3二级反渗透运行步序自动 |  | digital
FW.3EJFST_BYCX | 977 | Ovation Control Builder |  | digital
FW.3EJFST_DONE | 978 | #3二级反渗透运行步序结束 |  | digital
FW.3EJFST_FB1 | 979 | #3二级反渗透运行步序反馈1 |  | digital
FW.3EJFST_FB1TIME | 980 | #3二级反渗透运行步序1时间 |  | float32
FW.3EJFST_FB1TIMESPO | 981 | Ovation Control Builder |  | float32
FW.3EJFST_FB2 | 982 | #3二级反渗透运行步序反馈2 |  | digital
FW.3EJFST_FB2TIME | 983 | #3二级反渗透运行步序2时间 |  | float32
FW.3EJFST_FB2TIMESPO | 984 | Ovation Control Builder |  | float32
FW.3EJFST_FB3 | 985 | #3二级反渗透运行步序反馈3 |  | digital
FW.3EJFST_FB3TIME | 986 | #3二级反渗透运行步序3时间 |  | float32
FW.3EJFST_FB3TIMESPO | 987 | Ovation Control Builder |  | float32
FW.3EJFST_FB4 | 988 | #3二级反渗透运行步序反馈4 |  | digital
FW.3EJFST_FB4TIME | 989 | #3二级反渗透运行步序4时间 |  | float32
FW.3EJFST_FB4TIMESPO | 990 | Ovation Control Builder |  | float32
FW.3EJFST_FB5 | 991 | #3二级反渗透运行步序反馈5 |  | digital
FW.3EJFST_FB5TIME | 992 | #3二级反渗透运行步序5时间 |  | float32
FW.3EJFST_FB5TIMESPO | 993 | Ovation Control Builder |  | float32
FW.3EJFST_J0GCF43AA005CP | 994 | #3二级反渗透冲洗水门顺控关 |  | digital
FW.3EJFST_J0GCF43AA005OP | 995 | #3二级反渗透冲洗水门顺控开 |  | digital
FW.3EJFST_J0GCF43AA401CP | 996 | #3二级反渗透产水排放门顺控关 |  | digital
FW.3EJFST_J0GCF43AA401OP | 997 | #3二级反渗透产水排放门顺控开 |  | digital
FW.3EJFST_J0GCF43AA402CP | 998 | #3二级反渗透浓水排放门顺控关 |  | digital
FW.3EJFST_J0GCF43AA402OP | 999 | #3二级反渗透浓水排放门顺控开 |  | digital
FW.3EJFST_J0GCK43AA003CP | 1000 | #3二级反渗透高压泵出水门关 |  | digital
FW.3EJFST_J0GCK43AA003OP | 1001 | #3二级反渗透高压泵出水门开 |  | digital
FW.3EJFST_J0GCK43AP001CP | 1002 | #3二级反渗透高压泵顺控停 |  | digital
FW.3EJFST_J0GCK43AP001OP | 1003 | #3二级反渗透高压泵顺控启 |  | digital
FW.3EJFST_JT | 1004 | #3二级反渗透急停 |  | digital
FW.3EJFST_JTXD | 1005 | Ovation Control Builder |  | digital
FW.3EJFST_LP | 1006 | #3二级反渗透运行步序状态点 |  | int32
FW.3EJFST_MANM | 1007 | #3二级反渗透运行步序手动 |  | digital
FW.3EJFST_READY | 1008 | Ovation Control Builder |  | digital
FW.3EJFST_SEQ1 | 1009 | #3二级反渗透运行步序STEP1 |  | digital
FW.3EJFST_SEQ2 | 1010 | #3二级反渗透运行步序STEP2 |  | digital
FW.3EJFST_SEQ3 | 1011 | #3二级反渗透运行步序STEP3 |  | digital
FW.3EJFST_SEQ4 | 1012 | #3二级反渗透运行步序STEP4 |  | digital
FW.3EJFST_SEQ5 | 1013 | #3二级反渗透运行步序STEP5 |  | digital
FW.3EJFST_SEQGO | 1014 | #3二级反渗透运行步序启动 |  | digital
FW.3EJFST_SEQNUM | 1015 | #3二级反渗透运行当前步序 |  | float32
FW.3EJFST_STOP | 1016 | #3二级反渗透冲洗停止 |  | digital
FW.3EJFST_TZ | 1017 | #3二级反渗透停止 |  | digital
FW.3EJFST_TZXD | 1018 | Ovation Control Builder |  | digital
FW.3EJFST_YLKGDZ | 1019 | #3二级反渗透压力动作 |  | digital
FW.3EJFSTBXBY | 1020 | #3二级反渗透步延 |  | digital
FW.3EJFSTFX_PD | 1021 | #3二级反渗透冲洗排队 |  | digital
FW.3EJFSTQG | 1022 | #3二级反渗透设备全关 |  | digital
FW.3EJFSTYXBY | 1023 | #3二级反渗透运行步延 |  | digital
FW.3EJFSTYXBYTIME | 1024 | #3二级反渗透运行步延时间 |  | float32
FW.3FK1 | 1025 | Ovation Control Builder |  | digital
FW.3JFYHSJJ_AUTOM | 1026 | #3加非氧化性杀菌剂步序自动 |  | digital
FW.3JFYHSJJ_BQG | 1027 | Ovation Control Builder |  | digital
FW.3JFYHSJJ_DONE | 1028 | #3加非氧化性杀菌剂步序结束 |  | digital
FW.3JFYHSJJ_FB1 | 1029 | #3加非氧化性杀菌剂步序反馈1 |  | digital
FW.3JFYHSJJ_FB1TIME | 1030 | 加非氧化性杀菌剂步序反馈1时间 |  | float32
FW.3JFYHSJJ_FB1TIMESPO | 1031 | Ovation Control Builder |  | float32
FW.3JFYHSJJ_FB2 | 1032 | #3加非氧化性杀菌剂步序反馈2 |  | digital
FW.3JFYHSJJ_FB2TIME | 1033 | 加非氧化性杀菌剂步序反馈2时间 |  | float32
FW.3JFYHSJJ_FB2TIMESPO | 1034 | Ovation Control Builder |  | float32
FW.3JFYHSJJ_FB3 | 1035 | #3加非氧化性杀菌剂步序反馈3 |  | digital
FW.3JFYHSJJ_FB3TIME | 1036 | 加非氧化性杀菌剂步序反馈3时间 |  | float32
FW.3JFYHSJJ_FB3TIMESPO | 1037 | Ovation Control Builder |  | float32
FW.3JFYHSJJ_FB4 | 1038 | #3加非氧化性杀菌剂步序反馈4 |  | digital
FW.3JFYHSJJ_FB4TIME | 1039 | 加非氧化性杀菌剂步序反馈4时间 |  | float32
FW.3JFYHSJJ_FB4TIMESPO | 1040 | Ovation Control Builder |  | float32
FW.3JFYHSJJ_FB5 | 1041 | #3加非氧化性杀菌剂步序反馈5 |  | digital
FW.3JFYHSJJ_FB5TIME | 1042 | 加非氧化性杀菌剂步序反馈5时间 |  | float32
FW.3JFYHSJJ_FB5TIMESPO | 1043 | Ovation Control Builder |  | float32
FW.3JFYHSJJ_FB6 | 1044 | Ovation Control Builder |  | digital
FW.3JFYHSJJ_FB6TIME | 1045 | Ovation Control Builder |  | float32
FW.3JFYHSJJ_FB6TIMESPO | 1046 | Ovation Control Builder |  | float32
FW.3JFYHSJJ_JT | 1047 | #3加非氧化性杀菌剂急停 |  | digital
FW.3JFYHSJJ_JTXD | 1048 | Ovation Control Builder |  | digital
FW.3JFYHSJJ_LP | 1049 | #3加非氧化性杀菌剂步序状态点 |  | int32
FW.3JFYHSJJ_MANM | 1050 | #3加非氧化性杀菌剂步序手动 |  | digital
FW.3JFYHSJJ_READY | 1051 | Ovation Control Builder |  | digital
FW.3JFYHSJJ_SEQ1 | 1052 | #3加非氧化性杀菌剂Step1 |  | digital
FW.3JFYHSJJ_SEQ2 | 1053 | #3加非氧化性杀菌剂Step2 |  | digital
FW.3JFYHSJJ_SEQ3 | 1054 | #3加非氧化性杀菌剂Step3 |  | digital
FW.3JFYHSJJ_SEQ4 | 1055 | #3加非氧化性杀菌剂Step4 |  | digital
FW.3JFYHSJJ_SEQ5 | 1056 | #3加非氧化性杀菌剂Step5 |  | digital
FW.3JFYHSJJ_SEQ6 | 1057 | #3加非氧化性杀菌剂Step6 |  | digital
FW.3JFYHSJJ_SEQGO | 1058 | #3加非氧化性杀菌剂步序启动 |  | digital
FW.3JFYHSJJ_SEQNUM | 1059 | #3加非氧化性杀菌剂当前步序 |  | float32
FW.3JFYHSJJ_STOP | 1060 | #3加非氧化性杀菌剂步序停止 |  | digital
FW.3JFYHSJJBY | 1061 | #3加非氧化杀菌剂步延 |  | digital
FW.3JFYHSJJFX_PD | 1062 | #3加非氧化性杀菌剂步序排队 |  | digital
FW.3JFYHSJJQG | 1063 | #3加非氧化性杀菌剂全关 |  | digital
FW.3JFYHSJJYXBY | 1064 | #3加非氧化杀菌剂运行步延 |  | digital
FW.3JFYHSJJYXBYTIME | 1065 | #3加非氧化杀菌剂步延时间 |  | float32
FW.3JJ | 1066 | 3套设备使用加碱泵 |  | digital
FW.3KQCXZLLC_AUTOM | 1067 | #3空气擦洗重力滤池步序自动 |  | digital
FW.3KQCXZLLC_DONE | 1068 | #3空气擦洗重力滤池步序结束 |  | digital
FW.3KQCXZLLC_FB1 | 1069 | #3空气擦洗重力滤池反馈1 |  | digital
FW.3KQCXZLLC_FB1TIME | 1070 | #3空气擦洗重力滤池反馈1时间 |  | float32
FW.3KQCXZLLC_FB1TIMESPO | 1071 | Ovation Control Builder |  | float32
FW.3KQCXZLLC_FB2 | 1072 | #3空气擦洗重力滤池反馈2 |  | digital
FW.3KQCXZLLC_FB2TIME | 1073 | #3空气擦洗重力滤池反馈2时间 |  | float32
FW.3KQCXZLLC_FB2TIMESPO | 1074 | Ovation Control Builder |  | float32
FW.3KQCXZLLC_FB3 | 1075 | #3空气擦洗重力滤池反馈3 |  | digital
FW.3KQCXZLLC_FB3TIME | 1076 | #3空气擦洗重力滤池反馈3时间 |  | float32
FW.3KQCXZLLC_FB3TIMESPO | 1077 | Ovation Control Builder |  | float32
FW.3KQCXZLLC_FB4 | 1078 | #3空气擦洗重力滤池反馈4 |  | digital
FW.3KQCXZLLC_FB4TIME | 1079 | #3空气擦洗重力滤池反馈4时间 |  | float32
FW.3KQCXZLLC_FB4TIMESPO | 1080 | Ovation Control Builder |  | float32
FW.3KQCXZLLC_FB5 | 1081 | #3空气擦洗重力滤池反馈5 |  | digital
FW.3KQCXZLLC_FB5TIME | 1082 | #3空气擦洗重力滤池反馈5时间 |  | float32
FW.3KQCXZLLC_FB5TIMESPO | 1083 | Ovation Control Builder |  | float32
FW.3KQCXZLLC_FB6 | 1084 | #3空气擦洗重力滤池反馈6 |  | digital
FW.3KQCXZLLC_FB6TIME | 1085 | #3空气擦洗重力滤池反馈6时间 |  | float32
FW.3KQCXZLLC_FB6TIMESPO | 1086 | Ovation Control Builder |  | float32
FW.3KQCXZLLC_LP | 1087 | #3空气擦洗重力滤池步序状态点 |  | int32
FW.3KQCXZLLC_MANM | 1088 | #2空气擦洗重力滤池步序手动 |  | digital
FW.3KQCXZLLC_PD | 1089 | #3空气擦洗重力滤池排队 |  | digital
FW.3KQCXZLLC_READY | 1090 | Ovation Control Builder |  | digital
FW.3KQCXZLLC_SEQ1 | 1091 | #3空气擦洗重力滤池step1 |  | digital
FW.3KQCXZLLC_SEQ2 | 1092 | #3空气擦洗重力滤池step2 |  | digital
FW.3KQCXZLLC_SEQ2A | 1093 | Ovation Control Builder |  | digital
FW.3KQCXZLLC_SEQ3 | 1094 | #3空气擦洗重力滤池step3 |  | digital
FW.3KQCXZLLC_SEQ3A | 1095 | Ovation Control Builder |  | digital
FW.3KQCXZLLC_SEQ4 | 1096 | #3空气擦洗重力滤池step4 |  | digital
FW.3KQCXZLLC_SEQ5 | 1097 | #3空气擦洗重力滤池step5 |  | digital
FW.3KQCXZLLC_SEQ6 | 1098 | #3空气擦洗重力滤池step6 |  | digital
FW.3KQCXZLLC_SEQGO | 1099 | #3空气擦洗重力滤池步序启动 |  | digital
FW.3KQCXZLLC_SEQNUM | 1100 | #3空气擦洗重力滤池当前步序 |  | float32
FW.3KQCXZLLCTIME | 1101 | #3空气擦洗重力滤池排队时间 |  | float32
FW.3REALARM | 1102 | Ovation Control Builder |  | digital
FW.3XNCPNTIME | 1103 | Ovation Control Builder |  | float32
FW.3XNCPNTIMESPO | 1104 | Ovation Control Builder |  | float32
FW.3YB | 1105 | #3一级反渗透在运行 |  | digital
FW.3YIFSTBQG | 1106 | #3一级反渗透泵全关 |  | digital
FW.3YJFST_AUTOM | 1107 | #3一级反渗透运行步序自动 |  | digital
FW.3YJFST_BYCX | 1108 | Ovation Control Builder |  | digital
FW.3YJFST_DONE | 1109 | #3一级反渗透运行步序结束 |  | digital
FW.3YJFST_FB1 | 1110 | #3一级反渗透运行步序反馈1 |  | digital
FW.3YJFST_FB1TIME | 1111 | #3一级反渗透运行步序1时间 |  | float32
FW.3YJFST_FB1TIMESPO | 1112 | Ovation Control Builder |  | float32
FW.3YJFST_FB2 | 1113 | #3一级反渗透运行步序反馈2 |  | digital
FW.3YJFST_FB2TIME | 1114 | #3一级反渗透运行步序2时间 |  | float32
FW.3YJFST_FB2TIMESPO | 1115 | Ovation Control Builder |  | float32
FW.3YJFST_FB3 | 1116 | #3一级反渗透运行步序反馈3 |  | digital
FW.3YJFST_FB3TIME | 1117 | #3一级反渗透运行步序3时间 |  | float32
FW.3YJFST_FB3TIMESPO | 1118 | Ovation Control Builder |  | float32
FW.3YJFST_FB4 | 1119 | #3一级反渗透运行步序反馈4 |  | digital
FW.3YJFST_FB4TIME | 1120 | #3一级反渗透运行步序4时间 |  | float32
FW.3YJFST_FB4TIMESPO | 1121 | Ovation Control Builder |  | float32
FW.3YJFST_FB5 | 1122 | #3一级反渗透运行步序反馈5 |  | digital
FW.3YJFST_FB5TIME | 1123 | #3一级反渗透运行步序5时间 |  | float32
FW.3YJFST_FB5TIMESPO | 1124 | Ovation Control Builder |  | float32
FW.3YJFST_FB6 | 1125 | Ovation Control Builder |  | digital
FW.3YJFST_FB6TIME | 1126 | Ovation Control Builder |  | float32
FW.3YJFST_FB6TIMESPO | 1127 | Ovation Control Builder |  | float32
FW.3YJFST_JT | 1128 | #3一级反渗透急停 |  | digital
FW.3YJFST_JTXD | 1129 | Ovation Control Builder |  | digital
FW.3YJFST_LP | 1130 | #3一级反渗透运行步序状态点 |  | int32
FW.3YJFST_MANM | 1131 | #3一级反渗透运行步序手动 |  | digital
FW.3YJFST_READY | 1132 | Ovation Control Builder |  | digital
FW.3YJFST_SEQ1 | 1133 | #3一级反渗透运行步序STEP1 |  | digital
FW.3YJFST_SEQ2 | 1134 | #3一级反渗透运行步序STEP2 |  | digital
FW.3YJFST_SEQ3 | 1135 | #3一级反渗透运行步序STEP3 |  | digital
FW.3YJFST_SEQ4 | 1136 | #3一级反渗透运行步序STEP4 |  | digital
FW.3YJFST_SEQ5 | 1137 | #3一级反渗透运行步序STEP5 |  | digital
FW.3YJFST_SEQ6 | 1138 | Ovation Control Builder |  | digital
FW.3YJFST_SEQGO | 1139 | #3一级反渗透运行步序启动 |  | digital
FW.3YJFST_SEQNUM | 1140 | #3一级反渗透运行当前步序 |  | float32
FW.3YJFST_STOP | 1141 | #3一级反渗透运行步序停止 |  | digital
FW.3YJFST_TZ | 1142 | #3一级反渗透运行停止 |  | digital
FW.3YJFST_TZXD | 1143 | Ovation Control Builder |  | digital
FW.3YJFST_YLKGDZ | 1144 | #3一级反渗透压力开关动作 |  | digital
FW.3YJFSTBXBY | 1145 | #3一级反渗透步延 |  | digital
FW.3YJFSTFX_PD | 1146 | #3一级反渗透冲洗排队 |  | digital
FW.3YJFSTQG | 1147 | #3一级反渗透全关 |  | digital
FW.3YJFSTYXBY | 1148 | #3一级反渗透运行步延 |  | digital
FW.3YJFSTYXBYTIME | 1149 | #3一级反渗透运行步延时间 |  | float32
FW.3ZG/HY | 1150 | 3套设备使用阻垢/还原泵 |  | digital
FW.4 | 1151 | Ovation Control Builder |  | digital
FW.40ALARM | 1152 | Ovation Control Builder |  | digital
FW.40ALARM1 | 1153 | Ovation Control Builder |  | digital
FW.40REALARM | 1154 | Ovation Control Builder |  | digital
FW.41ALARM | 1155 | Ovation Control Builder |  | digital
FW.41ALARM1 | 1156 | Ovation Control Builder |  | digital
FW.41REALARM | 1157 | Ovation Control Builder |  | digital
FW.42ALARM | 1158 | Ovation Control Builder |  | digital
FW.42ALARM1 | 1159 | #1超滤水箱液位高 |  | digital
FW.42ALARM2 | 1160 | #2超滤水箱液位高 |  | digital
FW.42ALARM3 | 1161 | #1超滤水箱液位低 |  | digital
FW.42ALARM4 | 1162 | #2超滤水箱液位低 |  | digital
FW.42REALARM | 1163 | Ovation Control Builder |  | digital
FW.43ALARM | 1164 | Ovation Control Builder |  | digital
FW.43ALARM1 | 1165 | #1一级反渗透产水箱液位高 |  | digital
FW.43ALARM2 | 1166 | #2一级反渗透产水箱液位高 |  | digital
FW.43ALARM3 | 1167 | #1一级反渗透产水箱液位低 |  | digital
FW.43ALARM4 | 1168 | #2一级反渗透产水箱液位低 |  | digital
FW.43REALARM | 1169 | Ovation Control Builder |  | digital
FW.44ALARM | 1170 | Ovation Control Builder |  | digital
FW.44ALARM1 | 1171 | #1二级反渗透产水箱液位高 |  | digital
FW.44ALARM2 | 1172 | #2二级反渗透产水箱液位高 |  | digital
FW.44ALARM3 | 1173 | #1二级反渗透产水箱液位低 |  | digital
FW.44ALARM4 | 1174 | #2二级反渗透产水箱液位低 |  | digital
FW.44REALARM | 1175 | Ovation Control Builder |  | digital
FW.45ALARM | 1176 | Ovation Control Builder |  | digital
FW.45ALARM1 | 1177 | #1除盐水箱液位高 |  | digital
FW.45ALARM2 | 1178 | #2除盐水箱液位高 |  | digital
FW.45ALARM3 | 1179 | #1除盐水箱液位低 |  | digital
FW.45ALARM4 | 1180 | #2除盐水箱液位低 |  | digital
FW.45REALARM | 1181 | Ovation Control Builder |  | digital
FW.46ALARM | 1182 | Ovation Control Builder |  | digital
FW.46ALARM1 | 1183 | #1回收水池液位高 |  | digital
FW.46ALARM2 | 1184 | #2回收水池液位高 |  | digital
FW.46ALARM3 | 1185 | #1回收水池液位低 |  | digital
FW.46ALARM4 | 1186 | #2回收水池液位低 |  | digital
FW.46REALARM | 1187 | Ovation Control Builder |  | digital
FW.47ALARM | 1188 | Ovation Control Builder |  | digital
FW.47ALARM1 | 1189 | 超滤反洗气罐出口母管压力高 |  | digital
FW.47ALARM2 | 1190 | 仪表及控制用气罐出口母管压力高 |  | digital
FW.47ALARM3 | 1191 | 仪表及控制用气罐出口母管压力低 |  | digital
FW.47REALARM | 1192 | Ovation Control Builder |  | digital
FW.48ALARM | 1193 | Ovation Control Builder |  | digital
FW.48ALARM1 | 1194 | #1阻垢剂溶液箱液位低 |  | digital
FW.48ALARM2 | 1195 | #2阻垢剂溶液箱液位低 |  | digital
FW.48ALARM3 | 1196 | #1还原剂溶液箱液位低 |  | digital
FW.48ALARM4 | 1197 | #2还原剂溶液箱液位低 |  | digital
FW.48ALARM5 | 1198 | #1超滤反洗碱溶液箱液位低 |  | digital
FW.48ALARM6 | 1199 | #2超滤反洗碱溶液箱液位低 |  | digital
FW.48ALARM7 | 1200 | 次酸溶液箱液位低 |  | digital
FW.48ALARM8 | 1201 | 次氯酸钠溶液箱液位低 |  | digital
FW.48REALARM | 1202 | Ovation Control Builder |  | digital
FW.49ALARM | 1203 | Ovation Control Builder |  | digital
FW.49ALARM1 | 1204 | #1超滤装置出水浊度高 |  | digital
FW.49ALARM2 | 1205 | #2超滤装置出水浊度高 |  | digital
FW.49ALARM3 | 1206 | #3超滤装置出水浊度高 |  | digital
FW.49ALARM4 | 1207 | #4超滤装置出水浊度高 |  | digital
FW.49REALARM | 1208 | Ovation Control Builder |  | digital
FW.4ALARM | 1209 | Ovation Control Builder |  | digital
FW.4ALARM1 | 1210 | Ovation Control Builder |  | digital
FW.4CLBQG | 1211 | #4超滤泵全关 |  | digital
FW.4CLBXBY | 1212 | #4超滤步延 |  | digital
FW.4CLFX_CS | 1213 | #4超滤已运行次数 |  | float32
FW.4CLFX_CSSDSPO | 1214 | Ovation Control Builder |  | float32
FW.4CLFX_PD | 1215 | #4超滤反洗排队 |  | digital
FW.4CLYX_AUTOM | 1216 | #4超滤运行步序自动 |  | digital
FW.4CLYX_DONE | 1217 | #4超滤运行步序结束 |  | digital
FW.4CLYX_FB1 | 1218 | #4超滤运行步序反馈1 |  | digital
FW.4CLYX_FB10 | 1219 | #4超滤运行步序反馈10 |  | digital
FW.4CLYX_FB11 | 1220 | #4超滤运行步序反馈11 |  | digital
FW.4CLYX_FB2 | 1221 | #4超滤运行步序反馈2 |  | digital
FW.4CLYX_FB3 | 1222 | #4超滤运行步序反馈3 |  | digital
FW.4CLYX_FB4 | 1223 | #4超滤运行步序反馈4 |  | digital
FW.4CLYX_FB5 | 1224 | #4超滤运行步序反馈5 |  | digital
FW.4CLYX_FB6 | 1225 | #4超滤运行步序反馈6 |  | digital
FW.4CLYX_FB7 | 1226 | #4超滤运行步序反馈7 |  | digital
FW.4CLYX_FB8 | 1227 | #4超滤运行步序反馈8 |  | digital
FW.4CLYX_FB9 | 1228 | #4超滤运行步序反馈9 |  | digital
FW.4CLYX_JT | 1229 | #4超滤急停 |  | digital
FW.4CLYX_JTXD | 1230 | Ovation Control Builder |  | digital
FW.4CLYX_LP | 1231 | #4超滤运行步序状态点 |  | int32
FW.4CLYX_MANM | 1232 | #4超滤运行步序手动 |  | digital
FW.4CLYX_READY | 1233 | Ovation Control Builder |  | digital
FW.4CLYX_SEQ1 | 1234 | #4超滤运行步序STEP1 |  | digital
FW.4CLYX_SEQ10 | 1235 | #4超滤运行步序STEP10 |  | digital
FW.4CLYX_SEQ11 | 1236 | #4超滤运行步序STEP11 |  | digital
FW.4CLYX_SEQ2 | 1237 | #4超滤运行步序STEP2 |  | digital
FW.4CLYX_SEQ3 | 1238 | #4超滤运行步序STEP3 |  | digital
FW.4CLYX_SEQ4 | 1239 | #4超滤运行步序STEP4 |  | digital
FW.4CLYX_SEQ5 | 1240 | #4超滤运行步序STEP5 |  | digital
FW.4CLYX_SEQ6 | 1241 | #4超滤运行步序STEP6 |  | digital
FW.4CLYX_SEQ7 | 1242 | #4超滤运行步序STEP7 |  | digital
FW.4CLYX_SEQ8 | 1243 | #4超滤运行步序STEP8 |  | digital
FW.4CLYX_SEQ9 | 1244 | #4超滤运行步序STEP9 |  | digital
FW.4CLYX_SEQGO | 1245 | #4超滤运行步序启动 |  | digital
FW.4CLYX_SEQNUM | 1246 | #4超滤运行当前步序 |  | float32
FW.4CLYX_STOP | 1247 | #4超滤运行步序停止 |  | digital
FW.4CLYX_TZXD | 1248 | Ovation Control Builder |  | digital
FW.4CLYXBY | 1249 | #4超滤运行步延 |  | digital
FW.4CLYXBYTIME | 1250 | #4超滤运行步延时间 |  | float32
FW.4CLYXFB10TIME | 1251 | #4超滤运行步序10时间 |  | float32
FW.4CLYXFB10TIMESPO | 1252 | Ovation Control Builder |  | float32
FW.4CLYXFB11TIME | 1253 | #4超滤运行步序11时间 |  | float32
FW.4CLYXFB11TIMESPO | 1254 | Ovation Control Builder |  | float32
FW.4CLYXFB1TIME | 1255 | #4超滤运行步序1时间 |  | float32
FW.4CLYXFB1TIMESPO | 1256 | Ovation Control Builder |  | float32
FW.4CLYXFB2TIME | 1257 | #4超滤运行步序2时间 |  | float32
FW.4CLYXFB2TIMESPO | 1258 | Ovation Control Builder |  | float32
FW.4CLYXFB3TIME | 1259 | #4超滤运行步序3时间 |  | float32
FW.4CLYXFB3TIMESPO | 1260 | Ovation Control Builder |  | float32
FW.4CLYXFB4TIME | 1261 | #4超滤运行步序4时间 |  | float32
FW.4CLYXFB4TIMESPO | 1262 | Ovation Control Builder |  | float32
FW.4CLYXFB5TIME | 1263 | #4超滤运行步序5时间 |  | float32
FW.4CLYXFB5TIMESPO | 1264 | Ovation Control Builder |  | float32
FW.4CLYXFB6TIME | 1265 | #4超滤运行步序6时间 |  | float32
FW.4CLYXFB6TIMESPO | 1266 | Ovation Control Builder |  | float32
FW.4CLYXFB7TIME | 1267 | #4超滤运行步序7时间 |  | float32
FW.4CLYXFB7TIMESPO | 1268 | Ovation Control Builder |  | float32
FW.4CLYXFB8TIME | 1269 | #4超滤运行步序8时间 |  | float32
FW.4CLYXFB8TIMESPO | 1270 | Ovation Control Builder |  | float32
FW.4CLYXFB9TIME | 1271 | #4超滤运行步序9时间 |  | float32
FW.4CLYXFB9TIMESPO | 1272 | Ovation Control Builder |  | float32
FW.4CLZQ_J0GCB14AA005_CLOSE | 1273 | #4超滤增强反洗进水门顺控关 |  | digital
FW.4CLZQ_J0GCB14AA005_OPEN | 1274 | #4超滤增强反洗进水门顺控开 |  | digital
FW.4CLZQ_J0GCB14AA006_CLOSE | 1275 | #4超滤增强反洗进气门顺控关 |  | digital
FW.4CLZQ_J0GCB14AA006_OPEN | 1276 | #4超滤增强反洗进气门顺控开 |  | digital
FW.4CLZQ_J0GCB14AA402_CLOSE | 1277 | #4超滤增强反洗上排门顺控关 |  | digital
FW.4CLZQ_J0GCB14AA402_OPEN | 1278 | #4超滤增强反洗上排门顺控开 |  | digital
FW.4CLZQ_J0GCB14AA403_CLOSE | 1279 | #4超滤增强反洗药洗排水门关 |  | digital
FW.4CLZQ_J0GCB14AA403_OPEN | 1280 | #4超滤增强反洗药洗排水门开 |  | digital
FW.4CLZQBY | 1281 | #4超滤增强步延 |  | digital
FW.4CLZQFX_AUTOM | 1282 | #4超滤增强反洗步序自动 |  | digital
FW.4CLZQFX_DONE | 1283 | #4超滤增强反洗步序结束 |  | digital
FW.4CLZQFX_FB1 | 1284 | #4超滤增强反洗步序反馈1 |  | digital
FW.4CLZQFX_FB1TIME | 1285 | #4超滤增强反洗步序1时间 |  | float32
FW.4CLZQFX_FB1TIMESPO | 1286 | Ovation Control Builder |  | float32
FW.4CLZQFX_FB2 | 1287 | #4超滤增强反洗步序反馈2 |  | digital
FW.4CLZQFX_FB2TIME | 1288 | #4超滤增强反洗步序2时间 |  | float32
FW.4CLZQFX_FB2TIMESPO | 1289 | Ovation Control Builder |  | float32
FW.4CLZQFX_FB3 | 1290 | #4超滤增强反洗步序反馈3 |  | digital
FW.4CLZQFX_FB3TIME | 1291 | #4超滤增强反洗步序3时间 |  | float32
FW.4CLZQFX_FB3TIMESPO | 1292 | Ovation Control Builder |  | float32
FW.4CLZQFX_FB4 | 1293 | #4超滤增强反洗步序反馈4 |  | digital
FW.4CLZQFX_FB4TIME | 1294 | #4超滤增强反洗步序4时间 |  | float32
FW.4CLZQFX_FB4TIMESPO | 1295 | Ovation Control Builder |  | float32
FW.4CLZQFX_FB5 | 1296 | #4超滤增强反洗步序反馈5 |  | digital
FW.4CLZQFX_FB5TIME | 1297 | #4超滤增强反洗步序5时间 |  | float32
FW.4CLZQFX_FB5TIMESPO | 1298 | Ovation Control Builder |  | float32
FW.4CLZQFX_FB6 | 1299 | #4超滤增强反洗步序反馈6 |  | digital
FW.4CLZQFX_FB6TIME | 1300 | #4超滤增强反洗步序6时间 |  | float32
FW.4CLZQFX_FB6TIMESPO | 1301 | Ovation Control Builder |  | float32
FW.4CLZQFX_JL | 1302 | #4超滤增强反洗加碱氯 |  | digital
FW.4CLZQFX_JS | 1303 | #4超滤增强反洗加酸 |  | digital
FW.4CLZQFX_LP | 1304 | #4超滤增强反洗步序状态点 |  | int32
FW.4CLZQFX_MANM | 1305 | #4超滤增强反洗步序手动 |  | digital
FW.4CLZQFX_PD | 1306 | #4超滤增强反洗步序排队 |  | digital
FW.4CLZQFX_QD | 1307 | 启动#4超滤增强反洗步序 |  | digital
FW.4CLZQFX_READY | 1308 | Ovation Control Builder |  | digital
FW.4CLZQFX_SEQ1 | 1309 | #4超滤增强反洗步序STEP1 |  | digital
FW.4CLZQFX_SEQ2 | 1310 | #4超滤增强反洗步序STEP2 |  | digital
FW.4CLZQFX_SEQ3 | 1311 | #4超滤增强反洗步序STEP3 |  | digital
FW.4CLZQFX_SEQ4 | 1312 | #4超滤增强反洗步序STEP4 |  | digital
FW.4CLZQFX_SEQ5 | 1313 | #4超滤增强反洗步序STEP5 |  | digital
FW.4CLZQFX_SEQ6 | 1314 | #4超滤增强反洗步序STEP6 |  | digital
FW.4CLZQFX_SEQGO | 1315 | #4超滤增强反洗步序启动 |  | digital
FW.4CLZQFX_SEQNUM | 1316 | #4超滤增强反洗当前步序 |  | float32
FW.4CLZQFX_STOP | 1317 | #4超滤增强反洗步序停止 |  | digital
FW.4CLZQFXBY | 1318 | #4超滤增强反洗步延 |  | digital
FW.4CLZQFXBYTIME | 1319 | #4超滤增强反洗步延时间 |  | float32
FW.4EDI_JT | 1320 | #4EDI急停 |  | digital
FW.4EDI_JTXD | 1321 | Ovation Control Builder |  | digital
FW.4EDI_TZ | 1322 | #4EDI运行停止 |  | digital
FW.4EDI_TZXD | 1323 | Ovation Control Builder |  | digital
FW.4EDIBXBY | 1324 | #4EDI步延 |  | digital
FW.4EDIGF | 1325 | #4EDI急停关阀指令 |  | digital
FW.4EDIQG | 1326 | #4EDI设备全关 |  | digital
FW.4EDIYXBY | 1327 | #4EDI运行步延 |  | digital
FW.4EDIYXBYTIME | 1328 | #4EDI运行步延时间 |  | float32
FW.4EIFSTBQG | 1329 | Ovation Control Builder |  | digital
FW.4EJFST_AUTOM | 1330 | #4二级反渗透运行步序自动 |  | digital
FW.4EJFST_BYCX | 1331 | Ovation Control Builder |  | digital
FW.4EJFST_DONE | 1332 | #4二级反渗透运行步序结束 |  | digital
FW.4EJFST_FB1 | 1333 | #4二级反渗透运行步序反馈1 |  | digital
FW.4EJFST_FB1TIME | 1334 | #4二级反渗透运行步序1时间 |  | float32
FW.4EJFST_FB1TIMESPO | 1335 | Ovation Control Builder |  | float32
FW.4EJFST_FB2 | 1336 | #4二级反渗透运行步序反馈2 |  | digital
FW.4EJFST_FB2TIME | 1337 | #4二级反渗透运行步序2时间 |  | float32
FW.4EJFST_FB2TIMESPO | 1338 | Ovation Control Builder |  | float32
FW.4EJFST_FB3 | 1339 | #4二级反渗透运行步序反馈3 |  | digital
FW.4EJFST_FB3TIME | 1340 | #4二级反渗透运行步序3时间 |  | float32
FW.4EJFST_FB3TIMESPO | 1341 | Ovation Control Builder |  | float32
FW.4EJFST_FB4 | 1342 | #4二级反渗透运行步序反馈4 |  | digital
FW.4EJFST_FB4TIME | 1343 | #4二级反渗透运行步序4时间 |  | float32
FW.4EJFST_FB4TIMESPO | 1344 | Ovation Control Builder |  | float32
FW.4EJFST_FB5 | 1345 | #4二级反渗透运行步序反馈5 |  | digital
FW.4EJFST_FB5TIME | 1346 | #4二级反渗透运行步序5时间 |  | float32
FW.4EJFST_FB5TIMESPO | 1347 | Ovation Control Builder |  | float32
FW.4EJFST_J0GCF44AA005CP | 1348 | #4二级反渗透冲洗水门顺控关 |  | digital
FW.4EJFST_J0GCF44AA005OP | 1349 | #4二级反渗透冲洗水门顺控开 |  | digital
FW.4EJFST_J0GCF44AA401CP | 1350 | #4二级反渗透产水排放门顺控关 |  | digital
FW.4EJFST_J0GCF44AA401OP | 1351 | #4二级反渗透产水排放门顺控开 |  | digital
FW.4EJFST_J0GCF44AA402CP | 1352 | #4二级反渗透浓水排放门顺控关 |  | digital
FW.4EJFST_J0GCF44AA402OP | 1353 | #4二级反渗透浓水排放门顺控开 |  | digital
FW.4EJFST_J0GCK44AA003CP | 1354 | #4二级反渗透高压泵出水门关 |  | digital
FW.4EJFST_J0GCK44AA003OP | 1355 | #4二级反渗透高压泵出水门开 |  | digital
FW.4EJFST_J0GCK44AP001CP | 1356 | #4二级反渗透高压泵顺控停 |  | digital
FW.4EJFST_J0GCK44AP001OP | 1357 | #4二级反渗透高压泵顺控启 |  | digital
FW.4EJFST_JT | 1358 | #4二级反渗透急停 |  | digital
FW.4EJFST_JTXD | 1359 | Ovation Control Builder |  | digital
FW.4EJFST_LP | 1360 | #4二级反渗透运行步序状态点 |  | int32
FW.4EJFST_MANM | 1361 | #4二级反渗透运行步序手动 |  | digital
FW.4EJFST_READY | 1362 | Ovation Control Builder |  | digital
FW.4EJFST_SEQ1 | 1363 | #4二级反渗透运行步序STEP1 |  | digital
FW.4EJFST_SEQ2 | 1364 | #4二级反渗透运行步序STEP2 |  | digital
FW.4EJFST_SEQ3 | 1365 | #4二级反渗透运行步序STEP3 |  | digital
FW.4EJFST_SEQ4 | 1366 | #4二级反渗透运行步序STEP4 |  | digital
FW.4EJFST_SEQ5 | 1367 | #4二级反渗透运行步序STEP5 |  | digital
FW.4EJFST_SEQGO | 1368 | #4二级反渗透运行步序启动 |  | digital
FW.4EJFST_SEQNUM | 1369 | #4二级反渗透运行当前步序 |  | float32
FW.4EJFST_STOP | 1370 | #4二级反渗透冲洗停止 |  | digital
FW.4EJFST_TZ | 1371 | #4二级反渗透停止 |  | digital
FW.4EJFST_TZXD | 1372 | Ovation Control Builder |  | digital
FW.4EJFST_YLKGDZ | 1373 | #4二级反渗透口压力动作 |  | digital
FW.4EJFSTBXBY | 1374 | #4二级反渗透步延 |  | digital
FW.4EJFSTFX_PD | 1375 | #4二级反渗透冲洗排队 |  | digital
FW.4EJFSTQG | 1376 | #4二级反渗透设备全关 |  | digital
FW.4EJFSTYXBY | 1377 | #4二级反渗透运行步延 |  | digital
FW.4EJFSTYXBYTIME | 1378 | #4二级反渗透运行步延时间 |  | float32
FW.4FK1 | 1379 | Ovation Control Builder |  | digital
FW.4JFYHSJJ_AUTOM | 1380 | #4加非氧化性杀菌剂步序自动 |  | digital
FW.4JFYHSJJ_BQG | 1381 | Ovation Control Builder |  | digital
FW.4JFYHSJJ_DONE | 1382 | #4加非氧化性杀菌剂步序结束 |  | digital
FW.4JFYHSJJ_FB1 | 1383 | #4加非氧化性杀菌剂步序反馈1 |  | digital
FW.4JFYHSJJ_FB1TIME | 1384 | 加非氧化性杀菌剂步序反馈1时间 |  | float32
FW.4JFYHSJJ_FB1TIMESPO | 1385 | Ovation Control Builder |  | float32
FW.4JFYHSJJ_FB2 | 1386 | #4加非氧化性杀菌剂步序反馈2 |  | digital
FW.4JFYHSJJ_FB2TIME | 1387 | 加非氧化性杀菌剂步序反馈2时间 |  | float32
FW.4JFYHSJJ_FB2TIMESPO | 1388 | Ovation Control Builder |  | float32
FW.4JFYHSJJ_FB3 | 1389 | #4加非氧化性杀菌剂步序反馈3 |  | digital
FW.4JFYHSJJ_FB3TIME | 1390 | 加非氧化性杀菌剂步序反馈3时间 |  | float32
FW.4JFYHSJJ_FB3TIMESPO | 1391 | Ovation Control Builder |  | float32
FW.4JFYHSJJ_FB4 | 1392 | #4加非氧化性杀菌剂步序反馈4 |  | digital
FW.4JFYHSJJ_FB4TIME | 1393 | 加非氧化性杀菌剂步序反馈4时间 |  | float32
FW.4JFYHSJJ_FB4TIMESPO | 1394 | Ovation Control Builder |  | float32
FW.4JFYHSJJ_FB5 | 1395 | #4加非氧化性杀菌剂步序反馈5 |  | digital
FW.4JFYHSJJ_FB5TIME | 1396 | 加非氧化性杀菌剂步序反馈5时间 |  | float32
FW.4JFYHSJJ_FB5TIMESPO | 1397 | Ovation Control Builder |  | float32
FW.4JFYHSJJ_FB6 | 1398 | Ovation Control Builder |  | digital
FW.4JFYHSJJ_FB6TIME | 1399 | Ovation Control Builder |  | float32
FW.4JFYHSJJ_FB6TIMESPO | 1400 | Ovation Control Builder |  | float32
FW.4JFYHSJJ_JT | 1401 | #4加非氧化性杀菌剂急停 |  | digital
FW.4JFYHSJJ_JTXD | 1402 | Ovation Control Builder |  | digital
FW.4JFYHSJJ_LP | 1403 | #4加非氧化性杀菌剂步序状态点 |  | int32
FW.4JFYHSJJ_MANM | 1404 | #4加非氧化性杀菌剂步序手动 |  | digital
FW.4JFYHSJJ_READY | 1405 | Ovation Control Builder |  | digital
FW.4JFYHSJJ_SEQ1 | 1406 | #4加非氧化性杀菌剂Step1 |  | digital
FW.4JFYHSJJ_SEQ2 | 1407 | #4加非氧化性杀菌剂Step2 |  | digital
FW.4JFYHSJJ_SEQ3 | 1408 | #4加非氧化性杀菌剂Step3 |  | digital
FW.4JFYHSJJ_SEQ4 | 1409 | #4加非氧化性杀菌剂Step4 |  | digital
FW.4JFYHSJJ_SEQ5 | 1410 | #4加非氧化性杀菌剂Step5 |  | digital
FW.4JFYHSJJ_SEQ6 | 1411 | Ovation Control Builder |  | digital
FW.4JFYHSJJ_SEQGO | 1412 | #4加非氧化性杀菌剂步序启动 |  | digital
FW.4JFYHSJJ_SEQNUM | 1413 | #4加非氧化性杀菌剂当前步序 |  | float32
FW.4JFYHSJJ_STOP | 1414 | #4加非氧化性杀菌剂步序停止 |  | digital
FW.4JFYHSJJBY | 1415 | #4加非氧化杀菌剂步延 |  | digital
FW.4JFYHSJJFX_PD | 1416 | #4加非氧化性杀菌剂步序排队 |  | digital
FW.4JFYHSJJQG | 1417 | #4加非氧化性杀菌剂全关 |  | digital
FW.4JFYHSJJYXBY | 1418 | #4加非氧化杀菌剂运行步延 |  | digital
FW.4JFYHSJJYXBYTIME | 1419 | #4加非氧化杀菌剂步延时间 |  | float32
FW.4JJ | 1420 | 4套设备使用加碱泵 |  | digital
FW.4REALARM | 1421 | Ovation Control Builder |  | digital
FW.4XNCPNTIME | 1422 | Ovation Control Builder |  | float32
FW.4XNCPNTIMESPO | 1423 | Ovation Control Builder |  | float32
FW.4YB | 1424 | #4一级反渗透在运行 |  | digital
FW.4YIFSTBQG | 1425 | #4一级反渗透泵全关 |  | digital
FW.4YJFST_AUTOM | 1426 | #4一级反渗透运行步序自动 |  | digital
FW.4YJFST_BYCX | 1427 | Ovation Control Builder |  | digital
FW.4YJFST_DONE | 1428 | #4一级反渗透运行步序结束 |  | digital
FW.4YJFST_FB1 | 1429 | #4一级反渗透运行步序反馈1 |  | digital
FW.4YJFST_FB1TIME | 1430 | #4一级反渗透运行步序1时间 |  | float32
FW.4YJFST_FB1TIMESPO | 1431 | Ovation Control Builder |  | float32
FW.4YJFST_FB2 | 1432 | #4一级反渗透运行步序反馈2 |  | digital
FW.4YJFST_FB2TIME | 1433 | #4一级反渗透运行步序2时间 |  | float32
FW.4YJFST_FB2TIMESPO | 1434 | Ovation Control Builder |  | float32
FW.4YJFST_FB3 | 1435 | #4一级反渗透运行步序反馈3 |  | digital
FW.4YJFST_FB3TIME | 1436 | #4一级反渗透运行步序3时间 |  | float32
FW.4YJFST_FB3TIMESPO | 1437 | Ovation Control Builder |  | float32
FW.4YJFST_FB4 | 1438 | #4一级反渗透运行步序反馈4 |  | digital
FW.4YJFST_FB4TIME | 1439 | #4一级反渗透运行步序4时间 |  | float32
FW.4YJFST_FB4TIMESPO | 1440 | Ovation Control Builder |  | float32
FW.4YJFST_FB5 | 1441 | #4一级反渗透运行步序反馈5 |  | digital
FW.4YJFST_FB5TIME | 1442 | #4一级反渗透运行步序5时间 |  | float32
FW.4YJFST_FB5TIMESPO | 1443 | Ovation Control Builder |  | float32
FW.4YJFST_FB6 | 1444 | Ovation Control Builder |  | digital
FW.4YJFST_FB6TIME | 1445 | Ovation Control Builder |  | float32
FW.4YJFST_FB6TIMESPO | 1446 | Ovation Control Builder |  | float32
FW.4YJFST_JT | 1447 | #4一级反渗透急停 |  | digital
FW.4YJFST_JTXD | 1448 | Ovation Control Builder |  | digital
FW.4YJFST_LP | 1449 | #4一级反渗透运行步序状态点 |  | int32
FW.4YJFST_MANM | 1450 | #4一级反渗透运行步序手动 |  | digital
FW.4YJFST_READY | 1451 | Ovation Control Builder |  | digital
FW.4YJFST_SEQ1 | 1452 | #4一级反渗透运行步序STEP1 |  | digital
FW.4YJFST_SEQ2 | 1453 | #4一级反渗透运行步序STEP2 |  | digital
FW.4YJFST_SEQ3 | 1454 | #4一级反渗透运行步序STEP3 |  | digital
FW.4YJFST_SEQ4 | 1455 | #4一级反渗透运行步序STEP4 |  | digital
FW.4YJFST_SEQ5 | 1456 | #4一级反渗透运行步序STEP5 |  | digital
FW.4YJFST_SEQ6 | 1457 | Ovation Control Builder |  | digital
FW.4YJFST_SEQGO | 1458 | #4一级反渗透运行步序启动 |  | digital
FW.4YJFST_SEQNUM | 1459 | #4一级反渗透运行当前步序 |  | float32
FW.4YJFST_STOP | 1460 | #4一级反渗透运行步序停止 |  | digital
FW.4YJFST_TZ | 1461 | #4一级反渗透运行停止 |  | digital
FW.4YJFST_TZXD | 1462 | Ovation Control Builder |  | digital
FW.4YJFST_YLKGDZ | 1463 | #4一级反渗透压力开关动作 |  | digital
FW.4YJFSTBXBY | 1464 | #4一级反渗透步延 |  | digital
FW.4YJFSTFX_PD | 1465 | #4一级反渗透冲洗排队 |  | digital
FW.4YJFSTQG | 1466 | #4一级反渗透全关 |  | digital
FW.4YJFSTYXBY | 1467 | #4一级反渗透运行步延 |  | digital
FW.4YJFSTYXBYTIME | 1468 | #4一级反渗透运行步延时间 |  | float32
FW.4ZG/HY | 1469 | 4套设备使用阻垢/还原泵 |  | digital
FW.50ALARM | 1470 | Ovation Control Builder |  | digital
FW.50ALARM1 | 1471 | 反渗透保安过滤器进水母管PH表高 |  | digital
FW.50ALARM2 | 1472 | 反渗透保安过滤器进水母管PH表低 |  | digital
FW.50ALARM3 | 1473 | 一级反渗透装置母管PH高 |  | digital
FW.50ALARM4 | 1474 | 一级反渗透装置母管PH低 |  | digital
FW.50REALARM | 1475 | Ovation Control Builder |  | digital
FW.51ALARM | 1476 | Ovation Control Builder |  | digital
FW.51ALARM1 | 1477 | #1一级反渗透装置产水电导率高 |  | digital
FW.51ALARM2 | 1478 | #2一级反渗透装置产水电导率高 |  | digital
FW.51ALARM3 | 1479 | #3一级反渗透装置产水电导率高 |  | digital
FW.51ALARM4 | 1480 | #4一级反渗透装置产水电导率高 |  | digital
FW.51ALARM5 | 1481 | #1二级反渗透装置产水电导率高 |  | digital
FW.51ALARM6 | 1482 | #2二级反渗透装置产水电导率高 |  | digital
FW.51ALARM7 | 1483 | #3二级反渗透装置产水电导率高 |  | digital
FW.51ALARM8 | 1484 | #4二级反渗透装置产水电导率高 |  | digital
FW.51REALARM | 1485 | Ovation Control Builder |  | digital
FW.52ALARM | 1486 | Ovation Control Builder |  | digital
FW.52ALARM1 | 1487 | #1EDI装置产水电导率高 |  | digital
FW.52ALARM2 | 1488 | #2EDI装置产水电导率高 |  | digital
FW.52ALARM3 | 1489 | #3EDI装置产水电导率高 |  | digital
FW.52ALARM4 | 1490 | #4EDI装置产水电导率高 |  | digital
FW.52ALARM5 | 1491 | #1EDI装置产水硅酸根浓度高 |  | digital
FW.52ALARM6 | 1492 | #2EDI装置产水硅酸根浓度高 |  | digital
FW.52ALARM7 | 1493 | #3EDI装置产水硅酸根浓度高 |  | digital
FW.52ALARM8 | 1494 | #4EDI装置产水硅酸根浓度高 |  | digital
FW.52REALARM | 1495 | Ovation Control Builder |  | digital
FW.53ALARM | 1496 | Ovation Control Builder |  | digital
FW.53ALARM1 | 1497 | #1EDI装置产水流量低 |  | digital
FW.53ALARM2 | 1498 | #2EDI装置产水流量低 |  | digital
FW.53ALARM3 | 1499 | #3EDI装置产水流量低 |  | digital
FW.53ALARM4 | 1500 | #4EDI装置产水流量低 |  | digital
FW.53REALARM | 1501 | Ovation Control Builder |  | digital
FW.54ALARM | 1502 | Ovation Control Builder |  | digital
FW.54ALARM1 | 1503 | #1EDI装置浓水流量低 |  | digital
FW.54ALARM2 | 1504 | #2EDI装置浓水流量低 |  | digital
FW.54ALARM3 | 1505 | #3EDI装置浓水流量低 |  | digital
FW.54ALARM4 | 1506 | #4EDI装置浓水流量低 |  | digital
FW.54REALARM | 1507 | Ovation Control Builder |  | digital
FW.55ALARM | 1508 | Ovation Control Builder |  | digital
FW.55ALARM1 | 1509 | #1一级反渗透高压泵进口压力低 |  | digital
FW.55ALARM10 | 1510 | #2二级反渗透高压泵出口压力高 |  | digital
FW.55ALARM11 | 1511 | #3二级反渗透高压泵出口压力高 |  | digital
FW.55ALARM12 | 1512 | #4二级反渗透高压泵出口压力高 |  | digital
FW.55ALARM2 | 1513 | #2一级反渗透高压泵进口压力低 |  | digital
FW.55ALARM3 | 1514 | #3一级反渗透高压泵进口压力低 |  | digital
FW.55ALARM4 | 1515 | #4一级反渗透高压泵进口压力低 |  | digital
FW.55ALARM5 | 1516 | #1一级反渗透高压泵出口压力高 |  | digital
FW.55ALARM6 | 1517 | #2一级反渗透高压泵出口压力高 |  | digital
FW.55ALARM7 | 1518 | #3一级反渗透高压泵出口压力高 |  | digital
FW.55ALARM8 | 1519 | #4一级反渗透高压泵出口压力高 |  | digital
FW.55ALARM9 | 1520 | #1二级反渗透高压泵出口压力高 |  | digital
FW.55REALARM | 1521 | Ovation Control Builder |  | digital
FW.56ALARM | 1522 | Ovation Control Builder |  | digital
FW.56ALARM1 | 1523 | #1超滤装置进水压力高 |  | digital
FW.56ALARM2 | 1524 | #2超滤装置进水压力高 |  | digital
FW.56ALARM3 | 1525 | #3超滤装置进水压力高 |  | digital
FW.56ALARM4 | 1526 | #4超滤装置进水压力高 |  | digital
FW.56REALARM | 1527 | Ovation Control Builder |  | digital
FW.57ALARM | 1528 | Ovation Control Builder |  | digital
FW.57ALARM1 | 1529 | #1自清洗过滤器进出口差压高 |  | digital
FW.57ALARM2 | 1530 | #2自清洗过滤器进出口差压高 |  | digital
FW.57ALARM3 | 1531 | #3自清洗过滤器进出口差压高 |  | digital
FW.57ALARM4 | 1532 | #4自清洗过滤器进出口差压高 |  | digital
FW.57REALARM | 1533 | Ovation Control Builder |  | digital
FW.58ALARM | 1534 | Ovation Control Builder |  | digital
FW.58ALARM1 | 1535 | #1一级RO保安过滤器进出口差压高 |  | digital
FW.58ALARM2 | 1536 | #2一级RO保安过滤器进出口差压高 |  | digital
FW.58ALARM3 | 1537 | #3一级RO保安过滤器进出口差压高 |  | digital
FW.58ALARM4 | 1538 | #4一级RO保安过滤器进出口差压高 |  | digital
FW.58REALARM | 1539 | Ovation Control Builder |  | digital
FW.59ALARM | 1540 | Ovation Control Builder |  | digital
FW.59ALARM1 | 1541 | #1二级RO保安过滤器进出口差压高 |  | digital
FW.59ALARM2 | 1542 | #2二级RO保安过滤器进出口差压高 |  | digital
FW.59ALARM3 | 1543 | #3二级RO保安过滤器进出口差压高 |  | digital
FW.59ALARM4 | 1544 | #4二级RO保安过滤器进出口差压高 |  | digital
FW.59REALARM | 1545 | Ovation Control Builder |  | digital
FW.5ALARM | 1546 | Ovation Control Builder |  | digital
FW.5ALARM1 | 1547 | Ovation Control Builder |  | digital
FW.5REALARM | 1548 | Ovation Control Builder |  | digital
FW.5XNCDPNTIME | 1549 | Ovation Control Builder |  | float32
FW.5XNCDPNTIMESPO | 1550 | Ovation Control Builder |  | float32
FW.5XNCPNTIME | 1551 | Ovation Control Builder |  | float32
FW.5XNCPNTIMESPO | 1552 | Ovation Control Builder |  | float32
FW.60ALARM | 1553 | Ovation Control Builder |  | digital
FW.60ALARM1 | 1554 | #1EDI保安过滤器进出口差压高 |  | digital
FW.60ALARM2 | 1555 | #2EDI保安过滤器进出口差压高 |  | digital
FW.60ALARM3 | 1556 | #3EDI保安过滤器进出口差压高 |  | digital
FW.60ALARM4 | 1557 | #4EDI保安过滤器进出口差压高 |  | digital
FW.60REALARM | 1558 | Ovation Control Builder |  | digital
FW.61ALARM | 1559 | Ovation Control Builder |  | digital
FW.61ALARM1 | 1560 | 生活水泵全停 |  | digital
FW.61REALARM | 1561 | Ovation Control Builder |  | digital
FW.62ALARM | 1562 | Ovation Control Builder |  | digital
FW.62ALARM1 | 1563 | 生活水池液位高 |  | digital
FW.62ALARM2 | 1564 | 生活水池液位低 |  | digital
FW.62REALARM | 1565 | Ovation Control Builder |  | digital
FW.63ALARM | 1566 | Ovation Control Builder |  | digital
FW.63ALARM1 | 1567 | #1化学消防水水池液位高 |  | digital
FW.63ALARM2 | 1568 | #1化学消防水水池液位低 |  | digital
FW.63ALARM3 | 1569 | #2化学消防水水池液位高 |  | digital
FW.63ALARM4 | 1570 | #2化学消防水水池液位低 |  | digital
FW.63REALARM | 1571 | Ovation Control Builder |  | digital
FW.64ALARM | 1572 | Ovation Control Builder |  | digital
FW.64ALARM1 | 1573 | #1絮凝斜板沉淀池出水浊度高 |  | digital
FW.64ALARM2 | 1574 | #2絮凝斜板沉淀池出水浊度高 |  | digital
FW.64REALARM | 1575 | Ovation Control Builder |  | digital
FW.6ALARM | 1576 | Ovation Control Builder |  | digital
FW.6ALARM1 | 1577 | Ovation Control Builder |  | digital
FW.6REALARM | 1578 | Ovation Control Builder |  | digital
FW.6XNCDPNTIME | 1579 | Ovation Control Builder |  | float32
FW.6XNCDPNTIMESPO | 1580 | Ovation Control Builder |  | float32
FW.6XNCPNTIME | 1581 | Ovation Control Builder |  | float32
FW.6XNCPNTIMESPO | 1582 | Ovation Control Builder |  | float32
FW.7ALARM | 1583 | Ovation Control Builder |  | digital
FW.7ALARM1 | 1584 | Ovation Control Builder |  | digital
FW.7REALARM | 1585 | Ovation Control Builder |  | digital
FW.7STOP | 1586 | Ovation Control Builder |  | digital
FW.7XNCDPNTIME | 1587 | Ovation Control Builder |  | float32
FW.7XNCDPNTIMESPO | 1588 | Ovation Control Builder |  | float32
FW.7XNCPNTIME | 1589 | Ovation Control Builder |  | float32
FW.7XNCPNTIMESPO | 1590 | Ovation Control Builder |  | float32
FW.8ALARM | 1591 | Ovation Control Builder |  | digital
FW.8ALARM1 | 1592 | Ovation Control Builder |  | digital
FW.8REALARM | 1593 | Ovation Control Builder |  | digital
FW.8STOP | 1594 | Ovation Control Builder |  | digital
FW.8XNCDPNTIME | 1595 | Ovation Control Builder |  | float32
FW.8XNCDPNTIMESPO | 1596 | Ovation Control Builder |  | float32
FW.8XNCPNTIME | 1597 | Ovation Control Builder |  | float32
FW.8XNCPNTIMESPO | 1598 | Ovation Control Builder |  | float32
FW.9ALARM | 1599 | Ovation Control Builder |  | digital
FW.9ALARM1 | 1600 | Ovation Control Builder |  | digital
FW.9REALARM | 1601 | Ovation Control Builder |  | digital
FW.9STOP | 1602 | Ovation Control Builder |  | digital
FW.A | 1603 | Ovation Control Builder |  | digital
FW.AAA | 1604 |  |  | float32
FW.AAAAA | 1605 | Ovation Control Builder |  | float32
FW.B | 1606 | Ovation Control Builder |  | digital
FW.BQG1 | 1607 | Ovation Control Builder |  | digital
FW.BQG2 | 1608 | Ovation Control Builder |  | digital
FW.BQG3 | 1609 | Ovation Control Builder |  | digital
FW.BQG4 | 1610 | Ovation Control Builder |  | digital
FW.C | 1611 | Ovation Control Builder |  | digital
FW.CL_J0GCB11AA001CLOSE | 1612 | #1超滤进水门自动关 |  | digital
FW.CL_J0GCB11AA001OPEN | 1613 | #1超滤进水门自动开 |  | digital
FW.CL_J0GCB11AA002CLOSE | 1614 | #1超滤出水门自动关 |  | digital
FW.CL_J0GCB11AA002OPEN | 1615 | #1超滤出水门自动开 |  | digital
FW.CL_J0GCB11AA005CLOSE | 1616 | #1超滤反洗进水门自动关 |  | digital
FW.CL_J0GCB11AA005OPEN | 1617 | #1超滤反洗进水门自动开 |  | digital
FW.CL_J0GCB11AA006CLOSE | 1618 | #1超滤进气门自动关 |  | digital
FW.CL_J0GCB11AA006OPEN | 1619 | #1超滤进气门自动开 |  | digital
FW.CL_J0GCB11AA401CLOSE | 1620 | #1超滤反洗下排水门关 |  | digital
FW.CL_J0GCB11AA401OPEN | 1621 | #1超滤反洗下排水门开 |  | digital
FW.CL_J0GCB11AA402CLOSE | 1622 | #1超滤反洗上排水门关 |  | digital
FW.CL_J0GCB11AA402OPEN | 1623 | #1超滤反洗上排水门开 |  | digital
FW.CL_J0GCB12AA001CLOSE | 1624 | #2超滤进水门自动关 |  | digital
FW.CL_J0GCB12AA001OPEN | 1625 | #2超滤进水门自动开 |  | digital
FW.CL_J0GCB12AA002CLOSE | 1626 | #2超滤出水门自动关 |  | digital
FW.CL_J0GCB12AA002OPEN | 1627 | #2超滤出水门自动开 |  | digital
FW.CL_J0GCB12AA005CLOSE | 1628 | #2超滤反洗进水门自动关 |  | digital
FW.CL_J0GCB12AA005OPEN | 1629 | #2超滤反洗进水门自动开 |  | digital
FW.CL_J0GCB12AA006CLOSE | 1630 | #2超滤反洗进气门自动关 |  | digital
FW.CL_J0GCB12AA006OPEN | 1631 | #2超滤反洗进气门自动开 |  | digital
FW.CL_J0GCB12AA401CLOSE | 1632 | #2超滤反洗下排水门关 |  | digital
FW.CL_J0GCB12AA401OPEN | 1633 | #2超滤反洗下排水门开 |  | digital
FW.CL_J0GCB12AA402CLOSE | 1634 | #2超滤反洗上排水门关 |  | digital
FW.CL_J0GCB12AA402OPEN | 1635 | #2超滤反洗上排水门开 |  | digital
FW.CL_J0GCB13AA001CLOSE | 1636 | #3超滤进水门自动关 |  | digital
FW.CL_J0GCB13AA001OPEN | 1637 | #3超滤进水门自动开 |  | digital
FW.CL_J0GCB13AA002CLOSE | 1638 | #3超滤出水门自动关 |  | digital
FW.CL_J0GCB13AA002OPEN | 1639 | #3超滤出水门自动开 |  | digital
FW.CL_J0GCB13AA005CLOSE | 1640 | #3超滤反洗进水门自动关 |  | digital
FW.CL_J0GCB13AA005OPEN | 1641 | #3超滤反洗进水门自动开 |  | digital
FW.CL_J0GCB13AA006CLOSE | 1642 | #3超滤进气门自动关 |  | digital
FW.CL_J0GCB13AA006OPEN | 1643 | #3超滤进气门自动开 |  | digital
FW.CL_J0GCB13AA401CLOSE | 1644 | #3超滤反洗下排水门关 |  | digital
FW.CL_J0GCB13AA401OPEN | 1645 | #3超滤反洗下排水门开 |  | digital
FW.CL_J0GCB13AA402CLOSE | 1646 | #3超滤反洗上排水门关 |  | digital
FW.CL_J0GCB13AA402OPEN | 1647 | #3超滤反洗上排水门开 |  | digital
FW.CL_J0GCB14AA001CLOSE | 1648 | #4超滤进水门自动关 |  | digital
FW.CL_J0GCB14AA001OPEN | 1649 | #4超滤进水门自动开 |  | digital
FW.CL_J0GCB14AA002CLOSE | 1650 | #4超滤出水门自动关 |  | digital
FW.CL_J0GCB14AA002OPEN | 1651 | #4超滤出水门自动开 |  | digital
FW.CL_J0GCB14AA005CLOSE | 1652 | #4超滤反洗进水门自动关 |  | digital
FW.CL_J0GCB14AA005OPEN | 1653 | #4超滤反洗进水门自动开 |  | digital
FW.CL_J0GCB14AA006CLOSE | 1654 | #4超滤进气门自动关 |  | digital
FW.CL_J0GCB14AA006OPEN | 1655 | #4超滤进气门自动开 |  | digital
FW.CL_J0GCB14AA401CLOSE | 1656 | #4超滤反洗下排水门关 |  | digital
FW.CL_J0GCB14AA401OPEN | 1657 | #4超滤反洗下排水门开 |  | digital
FW.CL_J0GCB14AA402CLOSE | 1658 | #4超滤反洗上排水门关 |  | digital
FW.CL_J0GCB14AA402OPEN | 1659 | #4超滤反洗上排水门开 |  | digital
FW.CL_J0GCB21AP001CLOSE | 1660 | #1超滤反洗水泵自动停 |  | digital
FW.CL_J0GCB21AP001OPEN | 1661 | #1超滤反洗水泵自动启 |  | digital
FW.CL_J0GCB22AP001CLOSE | 1662 | #2超滤反洗水泵自动停 |  | digital
FW.CL_J0GCB22AP001OPEN | 1663 | #2超滤反洗水泵自动启 |  | digital
FW.CL_J0GCB23AP001CLOSE | 1664 | #3超滤反洗水泵自动停 |  | digital
FW.CL_J0GCB23AP001OPEN | 1665 | #3超滤反洗水泵自动启 |  | digital
FW.CL_J0GCB24AP001CLOSE | 1666 | #4超滤反洗水泵自动停 |  | digital
FW.CL_J0GCB24AP001OPEN | 1667 | #4超滤反洗水泵自动启 |  | digital
FW.CL_J0GCK11AP001CLOSE | 1668 | #1超滤给水泵自动停 |  | digital
FW.CL_J0GCK11AP001OPEN | 1669 | #1超滤给水泵自动启 |  | digital
FW.CL_J0GCK12AP001CLOSE | 1670 | #2超滤给水泵自动停 |  | digital
FW.CL_J0GCK12AP001OPEN | 1671 | #2超滤给水泵自动启 |  | digital
FW.CL_J0GCK13AP001CLOSE | 1672 | #3超滤给水泵自动停 |  | digital
FW.CL_J0GCK13AP001OPEN | 1673 | #3超滤给水泵自动启 |  | digital
FW.CL_J0GCK14AP001CLOSE | 1674 | #4超滤给水泵自动停 |  | digital
FW.CL_J0GCK14AP001OPEN | 1675 | #4超滤给水泵自动启 |  | digital
FW.CLBQG | 1676 | 超滤泵已全关 |  | digital
FW.CLFX_PD | 1677 | Ovation Control Builder |  | float32
FW.CLFXTIME1 | 1678 | #1超滤反洗排队时间 |  | float32
FW.CLFXTIME2 | 1679 | #2超滤反洗排队时间 |  | float32
FW.CLFXTIME3 | 1680 | #3超滤反洗排队时间 |  | float32
FW.CLFXTIME4 | 1681 | #4超滤反洗排队时间 |  | float32
FW.CLYX2 | 1682 | #2超滤反洗优先 |  | digital
FW.CLYX3 | 1683 | #3超滤反洗优先 |  | digital
FW.CLYX4 | 1684 | #4超滤反洗优先 |  | digital
FW.CLYX5 | 1685 | #1超滤增强反洗优先 |  | digital
FW.CLYX6 | 1686 | #2超滤增强反洗优先 |  | digital
FW.CLYX7 | 1687 | #3超滤增强反洗优先 |  | digital
FW.CLYX8 | 1688 | #4超滤增强反洗优先 |  | digital
FW.CLYXJT | 1689 | Ovation Control Builder |  | digital
FW.CLZQ_J0GCB21AP001_CLOSE | 1690 | 超滤增强反洗水泵顺控停 |  | digital
FW.CLZQ_J0GCB21AP001_OPEN | 1691 | 超滤增强反洗水泵顺控启 |  | digital
FW.CLZQFX_PD | 1692 | Ovation Control Builder |  | float32
FW.CLZQFXTIME1 | 1693 | #1超滤增强反洗步序排队时间 |  | float32
FW.CLZQFXTIME2 | 1694 | #2超滤增强反洗步序排队时间 |  | float32
FW.CLZQFXTIME3 | 1695 | #3超滤增强反洗步序排队时间 |  | float32
FW.CLZQFXTIME4 | 1696 | #4超滤增强反洗步序排队时间 |  | float32
FW.D | 1697 | Ovation Control Builder |  | digital
FW.DCXJ000 | 1698 | 母排电压 |  | float32
FW.DCXJ001 | 1699 | 负载电流 |  | float32
FW.DCXJ002 | 1700 | 电池电流 |  | float32
FW.DCXJ003 | 1701 | 电池温度 |  | float32
FW.DCXJ004 | 1702 | 环境温度 |  | float32
FW.DCXJ005 | 1703 | 电池容量值 |  | float32
FW.DCXJ006 | 1704 | A相交流电压 |  | float32
FW.DCXJ007 | 1705 | B相交流电压 |  | float32
FW.DCXJ008 | 1706 | C相交流电压 |  | float32
FW.DCXJ009 | 1707 | 1#整流模块输出电压 |  | float32
FW.DCXJ010 | 1708 | 2#整流模块输出电压 |  | float32
FW.DCXJ011 | 1709 | 3#整流模块输出电压 |  | float32
FW.DCXJ012 | 1710 | 4#整流模块输出电压 |  | float32
FW.DCXJ013 | 1711 | 5#整流模块输出电压 |  | float32
FW.DCXJ014 | 1712 | 6#整流模块输出电压 |  | float32
FW.DCXJ015 | 1713 | 7#整流模块输出电压 |  | float32
FW.DCXJ016 | 1714 | 8#整流模块输出电压 |  | float32
FW.DCXJ017 | 1715 | 9#整流模块输出电压 |  | float32
FW.DCXJ018 | 1716 | 10#整流模块输出电压 |  | float32
FW.DCXJ019 | 1717 | 11#整流模块输出电压 |  | float32
FW.DCXJ020 | 1718 | 12#整流模块输出电压 |  | float32
FW.DCXJ021 | 1719 | 1#整流模块输出电流 |  | float32
FW.DCXJ022 | 1720 | 2#整流模块输出电流 |  | float32
FW.DCXJ023 | 1721 | 3#整流模块输出电流 |  | float32
FW.DCXJ024 | 1722 | 4#整流模块输出电流 |  | float32
FW.DCXJ025 | 1723 | 5#整流模块输出电流 |  | float32
FW.DCXJ026 | 1724 | 6#整流模块输出电流 |  | float32
FW.DCXJ027 | 1725 | 7#整流模块输出电流 |  | float32
FW.DCXJ028 | 1726 | 8#整流模块输出电流 |  | float32
FW.DCXJ029 | 1727 | 9#整流模块输出电流 |  | float32
FW.DCXJ030 | 1728 | 10#整流模块输出电流 |  | float32
FW.DCXJ031 | 1729 | 11#整流模块输出电流 |  | float32
FW.DCXJ032 | 1730 | 12#整流模块输出电流 |  | float32
FW.DCXJ033 | 1731 | 电池充电状态 |  | float32
FW.DCXJ034 | 1732 | 交流过压告警点 |  | float32
FW.DCXJ035 | 1733 | 交流欠压告警点 |  | float32
FW.DCXJ036 | 1734 | 交流缺相告警点 |  | float32
FW.DCXJ037 | 1735 | 母排过压告警点 |  | float32
FW.DCXJ038 | 1736 | 母排欠压告警点 |  | float32
FW.DCXJ039 | 1737 | 电池温度高告警点 |  | float32
FW.DCXJ040 | 1738 | 电池温度低告警点 |  | float32
FW.DCXJ041 | 1739 | 环境温度高告警点 |  | float32
FW.DCXJ042 | 1740 | 环境温度低告警点 |  | float32
FW.DCXJ043 | 1741 | 浮充电压 |  | float32
FW.DCXJ044 | 1742 | 均充电压 |  | float32
FW.DCXJ045 | 1743 | 负载下电电压 |  | float32
FW.DCXJ046 | 1744 | 电池保护电压 |  | float32
FW.DCXJ047 | 1745 | 电池标称容量 |  | float32
FW.DCXJ048 | 1746 | 电池充电限流点 |  | float32
FW.DCXJ049 | 1747 | 定时均充周期 |  | float32
FW.DCXJ050 | 1748 | 电池温补系数 |  | float32
FW.DCXJ051 | 1749 | 电池测试终止电压 |  | float32
FW.DCXJ052 | 1750 | 电池测试终止时间 |  | float32
FW.DCXJ053 | 1751 | 电池测试终止容量 |  | float32
FW.DCXJ054 | 1752 | 电池组数 |  | float32
FW.DCXJ055 | 1753 | 模块最佳工作点 |  | float32
FW.DCXJ056 | 1754 | 模块循环开关周期 |  | float32
FW.DCXJ057 | 1755 | 负载波动比 |  | float32
FW.DCXJ058 | 1756 | 系统节能点 |  | float32
FW.DCXJ059 | 1757 | 最小工作模块数 |  | float32
FW.DCXJ060 | 1758 | 软件版本号 |  | float32
FW.DCXJ061 | 1759 | 时间，年 |  | float32
FW.DCXJ062 | 1760 | 时间，月日 |  | float32
FW.DCXJ063 | 1761 | 时间，时分 |  | float32
FW.DCXJ064 | 1762 | 时间，秒 |  | float32
FW.DCXJ065 | 1763 | 监控型号 |  | float32
FW.DCXJ066 | 1764 | 监控型号 |  | float32
FW.DCXJ067 | 1765 | 监控型号 |  | float32
FW.DCXJA000 | 1766 | 母排电压 |  | float32
FW.DCXJA001 | 1767 | 负载电流 |  | float32
FW.DCXJA002 | 1768 | 电池电流 |  | float32
FW.DCXJA003 | 1769 | 电池温度 |  | float32
FW.DCXJA004 | 1770 | 环境温度 |  | float32
FW.DCXJA005 | 1771 | 电池容量值 |  | float32
FW.DCXJA006 | 1772 | A相交流电压 |  | float32
FW.DCXJA007 | 1773 | B相交流电压 |  | float32
FW.DCXJA008 | 1774 | C相交流电压 |  | float32
FW.DCXJA009 | 1775 | 1#整流模块输出电压 |  | float32
FW.DCXJA010 | 1776 | 2#整流模块输出电压 |  | float32
FW.DCXJA011 | 1777 | 3#整流模块输出电压 |  | float32
FW.DCXJA012 | 1778 | 4#整流模块输出电压 |  | float32
FW.DCXJA013 | 1779 | 5#整流模块输出电压 |  | float32
FW.DCXJA014 | 1780 | 6#整流模块输出电压 |  | float32
FW.DCXJA015 | 1781 | 7#整流模块输出电压 |  | float32
FW.DCXJA016 | 1782 | 8#整流模块输出电压 |  | float32
FW.DCXJA017 | 1783 | 9#整流模块输出电压 |  | float32
FW.DCXJA018 | 1784 | 10#整流模块输出电压 |  | float32
FW.DCXJA019 | 1785 | 11#整流模块输出电压 |  | float32
FW.DCXJA020 | 1786 | 12#整流模块输出电压 |  | float32
FW.DCXJA021 | 1787 | 1#整流模块输出电流 |  | float32
FW.DCXJA022 | 1788 | 2#整流模块输出电流 |  | float32
FW.DCXJA023 | 1789 | 3#整流模块输出电流 |  | float32
FW.DCXJA024 | 1790 | 4#整流模块输出电流 |  | float32
FW.DCXJA025 | 1791 | 5#整流模块输出电流 |  | float32
FW.DCXJA026 | 1792 | 6#整流模块输出电流 |  | float32
FW.DCXJA027 | 1793 | 7#整流模块输出电流 |  | float32
FW.DCXJA028 | 1794 | 8#整流模块输出电流 |  | float32
FW.DCXJA029 | 1795 | 9#整流模块输出电流 |  | float32
FW.DCXJA030 | 1796 | 10#整流模块输出电流 |  | float32
FW.DCXJA031 | 1797 | 11#整流模块输出电流 |  | float32
FW.DCXJA032 | 1798 | 12#整流模块输出电流 |  | float32
FW.DCXJA033 | 1799 | 电池充电状态 |  | float32
FW.DCXJA034 | 1800 | 交流过压告警点 |  | float32
FW.DCXJA035 | 1801 | 交流欠压告警点 |  | float32
FW.DCXJA036 | 1802 | 交流缺相告警点 |  | float32
FW.DCXJA037 | 1803 | 母排过压告警点 |  | float32
FW.DCXJA038 | 1804 | 母排欠压告警点 |  | float32
FW.DCXJA039 | 1805 | 电池温度高告警点 |  | float32
FW.DCXJA040 | 1806 | 电池温度低告警点 |  | float32
FW.DCXJA041 | 1807 | 环境温度高告警点 |  | float32
FW.DCXJA042 | 1808 | 环境温度低告警点 |  | float32
FW.DCXJA043 | 1809 | 浮充电压 |  | float32
FW.DCXJA044 | 1810 | 均充电压 |  | float32
FW.DCXJA045 | 1811 | 负载下电电压 |  | float32
FW.DCXJA046 | 1812 | 电池保护电压 |  | float32
FW.DCXJA047 | 1813 | 电池标称容量 |  | float32
FW.DCXJA048 | 1814 | 电池充电限流点 |  | float32
FW.DCXJA049 | 1815 | 定时均充周期 |  | float32
FW.DCXJA050 | 1816 | 电池温补系数 |  | float32
FW.DCXJA051 | 1817 | 电池测试终止电压 |  | float32
FW.DCXJA052 | 1818 | 电池测试终止时间 |  | float32
FW.DCXJA053 | 1819 | 电池测试终止容量 |  | float32
FW.DCXJA054 | 1820 | 电池组数 |  | float32
FW.DCXJA055 | 1821 | 模块最佳工作点 |  | float32
FW.DCXJA056 | 1822 | 模块循环开关周期 |  | float32
FW.DCXJA057 | 1823 | 负载波动比 |  | float32
FW.DCXJA058 | 1824 | 系统节能点 |  | float32
FW.DCXJA059 | 1825 | 最小工作模块数 |  | float32
FW.DCXJA060 | 1826 | 软件版本号 |  | float32
FW.DCXJA061 | 1827 | 时间，年 |  | float32
FW.DCXJA062 | 1828 | 时间，月日 |  | float32
FW.DCXJA063 | 1829 | 时间，时分 |  | float32
FW.DCXJA064 | 1830 | 时间，秒 |  | float32
FW.DCXJA065 | 1831 | 监控型号 |  | float32
FW.DCXJA066 | 1832 | 监控型号 |  | float32
FW.DCXJA067 | 1833 | 监控型号 |  | float32
FW.DCXJB000 | 1834 | 第一组蓄电池电池电压 |  | float32
FW.DCXJB001 | 1835 | 第一组蓄电池电池电流 |  | float32
FW.DCXJB002 | 1836 | 第一组蓄电池电池电流 |  | float32
FW.DCXJB003 | 1837 | 第一组蓄电池电池温度 |  | float32
FW.DCXJC000 | 1838 | 第一组蓄电池电池电压 |  | float32
FW.DCXJC001 | 1839 | 第一组蓄电池电池电流 |  | float32
FW.DCXJC002 | 1840 | 第一组蓄电池电池电流 |  | float32
FW.DCXJC003 | 1841 | 第一组蓄电池电池温度 |  | float32
FW.DCXJDI000 | 1842 | 负载熔丝1断告警 |  | digital
FW.DCXJDI001 | 1843 | 负载熔丝2断告警 |  | digital
FW.DCXJDI002 | 1844 | 电池熔丝1断告警 |  | digital
FW.DCXJDI003 | 1845 | 电池熔丝2断告警 |  | digital
FW.DCXJDI004 | 1846 | 负载下电告警 |  | digital
FW.DCXJDI005 | 1847 | 电池保护告警 |  | digital
FW.DCXJDI006 | 1848 | 电池放电告警 |  | digital
FW.DCXJDI007 | 1849 | 电池测试故障告警 |  | digital
FW.DCXJDI008 | 1850 | 母排电压高告警 |  | digital
FW.DCXJDI009 | 1851 | 母排电压低告警 |  | digital
FW.DCXJDI010 | 1852 | 电池温度高告警 |  | digital
FW.DCXJDI011 | 1853 | 电池温度低告警 |  | digital
FW.DCXJDI012 | 1854 | 环境温度高告警 |  | digital
FW.DCXJDI013 | 1855 | 环境温度低告警 |  | digital
FW.DCXJDI014 | 1856 | 电池组1不平衡告警 |  | digital
FW.DCXJDI015 | 1857 | 电池组2不平衡告警 |  | digital
FW.DCXJDI016 | 1858 | 直流电压差别大告警 |  | digital
FW.DCXJDI017 | 1859 | 系统电流不平衡告警 |  | digital
FW.DCXJDI018 | 1860 | 模块限流状态 |  | digital
FW.DCXJDI019 | 1861 | 系统控制模式 |  | digital
FW.DCXJDI020 | 1862 | 节能告警状态 |  | digital
FW.DCXJDI021 | 1863 | 节能异常告警状态 |  | digital
FW.DCXJDI022 | 1864 | 节能允许 |  | digital
FW.DCXJDI023 | 1865 | 预留 |  | digital
FW.DCXJDI024 | 1866 | 防雷器故障告警 |  | digital
FW.DCXJDI025 | 1867 | 开关量输入2状态 |  | digital
FW.DCXJDI026 | 1868 | 开关量输入3状态 |  | digital
FW.DCXJDI027 | 1869 | 开关量输入4状态 |  | digital
FW.DCXJDI028 | 1870 | 开关量输入5状态 |  | digital
FW.DCXJDI029 | 1871 | 开关量输入6状态 |  | digital
FW.DCXJDI030 | 1872 | 开关量输入7状态 |  | digital
FW.DCXJDI031 | 1873 | 开关量输入8状态 |  | digital
FW.DCXJDIA000 | 1874 | 负载熔丝1断告警 |  | digital
FW.DCXJDIA001 | 1875 | 负载熔丝2断告警 |  | digital
FW.DCXJDIA002 | 1876 | 电池熔丝1断告警 |  | digital
FW.DCXJDIA003 | 1877 | 电池熔丝2断告警 |  | digital
FW.DCXJDIA004 | 1878 | 负载下电告警 |  | digital
FW.DCXJDIA005 | 1879 | 电池保护告警 |  | digital
FW.DCXJDIA006 | 1880 | 电池放电告警 |  | digital
FW.DCXJDIA007 | 1881 | 电池测试故障告警 |  | digital
FW.DCXJDIA008 | 1882 | 母排电压高告警 |  | digital
FW.DCXJDIA009 | 1883 | 母排电压低告警 |  | digital
FW.DCXJDIA010 | 1884 | 电池温度高告警 |  | digital
FW.DCXJDIA011 | 1885 | 电池温度低告警 |  | digital
FW.DCXJDIA012 | 1886 | 环境温度高告警 |  | digital
FW.DCXJDIA013 | 1887 | 环境温度低告警 |  | digital
FW.DCXJDIA014 | 1888 | 电池组1不平衡告警 |  | digital
FW.DCXJDIA015 | 1889 | 电池组2不平衡告警 |  | digital
FW.DCXJDIA016 | 1890 | 直流电压差别大告警 |  | digital
FW.DCXJDIA017 | 1891 | 系统电流不平衡告警 |  | digital
FW.DCXJDIA018 | 1892 | 模块限流状态 |  | digital
FW.DCXJDIA019 | 1893 | 系统控制模式 |  | digital
FW.DCXJDIA020 | 1894 | 节能告警状态 |  | digital
FW.DCXJDIA021 | 1895 | 节能异常告警状态 |  | digital
FW.DCXJDIA022 | 1896 | 节能允许 |  | digital
FW.DCXJDIA023 | 1897 | 预留 |  | digital
FW.DCXJDIA024 | 1898 | 防雷器故障告警 |  | digital
FW.DCXJDIA025 | 1899 | 开关量输入2状态 |  | digital
FW.DCXJDIA026 | 1900 | 开关量输入3状态 |  | digital
FW.DCXJDIA027 | 1901 | 开关量输入4状态 |  | digital
FW.DCXJDIA028 | 1902 | 开关量输入5状态 |  | digital
FW.DCXJDIA029 | 1903 | 开关量输入6状态 |  | digital
FW.DCXJDIA030 | 1904 | 开关量输入7状态 |  | digital
FW.DCXJDIA031 | 1905 | 开关量输入8状态 |  | digital
FW.DCXJDIB000 | 1906 | 第一组蓄电池电池组电压过压 |  | digital
FW.DCXJDIB001 | 1907 | 第一组蓄电池电池组电压欠压 |  | digital
FW.DCXJDIB002 | 1908 | 第一组蓄电池电池组充电过流 |  | digital
FW.DCXJDIB003 | 1909 | 第一组蓄电池电池环境温度过高 |  | digital
FW.DCXJDIB004 | 1910 | 第一组蓄电池电池环境温度过低 |  | digital
FW.DCXJDIB005 | 1911 | 第一组蓄电池电池差压超限 |  | digital
FW.DCXJDIB006 | 1912 | 第一组蓄电池电池剩余容量小于75 |  | digital
FW.DCXJDIB007 | 1913 | 第一组蓄电池电池剩余容量小于25 |  | digital
FW.DCXJDIC000 | 1914 | 第一组蓄电池电池组电压过低 |  | digital
FW.DCXJDIC001 | 1915 | 第一组蓄电池电池组电压欠压 |  | digital
FW.DCXJDIC002 | 1916 | 第一组蓄电池电池组充电过流 |  | digital
FW.DCXJDIC003 | 1917 | 第一组蓄电池电池环境温度过高 |  | digital
FW.DCXJDIC004 | 1918 | 第一组蓄电池电池环境温度过低 |  | digital
FW.DCXJDIC005 | 1919 | 第一组蓄电池电池压差超限 |  | digital
FW.DCXJDIC006 | 1920 | 第一组蓄电池电池剩余容量小于75 |  | digital
FW.DCXJDIC007 | 1921 | 第一组蓄电池电池剩余容量小于25 |  | digital
FW.DCXJW001 | 1922 | 浮充电压 |  | float32
FW.DCXJW002 | 1923 | 均充电压 |  | float32
FW.DCXJW003 | 1924 | 设置控制模式 |  | float32
FW.DCXJW004 | 1925 | 负载下电 |  | float32
FW.DCXJW005 | 1926 | 电池保护 |  | float32
FW.DCXJW006 | 1927 | 告警消音 |  | float32
FW.DCXJWA001 | 1928 | 浮充电压 |  | float32
FW.DCXJWA002 | 1929 | 均充电压 |  | float32
FW.DCXJWA003 | 1930 | 设置控制模式 |  | float32
FW.DCXJWA004 | 1931 | 负载下电 |  | float32
FW.DCXJWA005 | 1932 | 电池保护 |  | float32
FW.DCXJWA006 | 1933 | 告警消音 |  | float32
FW.DDJS | 1934 | 单加酸 |  | digital
FW.EDI_J0GCF51AA004_OC | 1935 | EDI-#1出水门自动停 |  | digital
FW.EDI_J0GCF51AA004_OP | 1936 | EDI-#1出水门自动启 |  | digital
FW.EDI_J0GCF51AA401_OC | 1937 | EDI-#1排污门自动停 |  | digital
FW.EDI_J0GCF51AA401_OP | 1938 | EDI-#1排污门自动启 |  | digital
FW.EDI_J0GCF51GH001_CP | 1939 | #1EDI整流装置自动停 |  | digital
FW.EDI_J0GCF51GH001_OP | 1940 | #1EDI整流装置自动启 |  | digital
FW.EDI_J0GCF52AA004_OC | 1941 | EDI-#2出水门自动停 |  | digital
FW.EDI_J0GCF52AA004_OP | 1942 | EDI-#2出水门自动启 |  | digital
FW.EDI_J0GCF52AA401_OC | 1943 | EDI-#2排污门自动停 |  | digital
FW.EDI_J0GCF52AA401_OP | 1944 | EDI-#2排污门自动启 |  | digital
FW.EDI_J0GCF52GH001_CP | 1945 | #2EDI整流装置自动停 |  | digital
FW.EDI_J0GCF52GH001_OP | 1946 | #2EDI整流装置自动启 |  | digital
FW.EDI_J0GCF53AA004_OC | 1947 | EDI-#3出水门自动停 |  | digital
FW.EDI_J0GCF53AA004_OP | 1948 | EDI-#3出水门自动启 |  | digital
FW.EDI_J0GCF53AA401_OC | 1949 | EDI-#3排污门自动停 |  | digital
FW.EDI_J0GCF53AA401_OP | 1950 | EDI-#3排污门自动启 |  | digital
FW.EDI_J0GCF53GH001_CP | 1951 | #3EDI整流装置自动停 |  | digital
FW.EDI_J0GCF53GH001_OP | 1952 | #3EDI整流装置自动启 |  | digital
FW.EDI_J0GCF54AA004_OC | 1953 | EDI-#4出水门自动停 |  | digital
FW.EDI_J0GCF54AA004_OP | 1954 | EDI-#4出水门自动启 |  | digital
FW.EDI_J0GCF54AA401_OC | 1955 | EDI-#4排污门自动停 |  | digital
FW.EDI_J0GCF54AA401_OP | 1956 | EDI-#4排污门自动启 |  | digital
FW.EDI_J0GCF54GH001_CP | 1957 | #4EDI整流装置自动停 |  | digital
FW.EDI_J0GCF54GH001_OP | 1958 | #4EDI整流装置自动启 |  | digital
FW.EDI_J0GCK51AP001_OC | 1959 | EDI-#1给水泵自动停 |  | digital
FW.EDI_J0GCK51AP001_OP | 1960 | EDI-#1给水泵自动启 |  | digital
FW.EDI_J0GCK52AP001_OC | 1961 | EDI-#2给水泵自动停 |  | digital
FW.EDI_J0GCK52AP001_OP | 1962 | EDI-#2给水泵自动启 |  | digital
FW.EDI_J0GCK53AP001_OC | 1963 | EDI-#3给水泵自动停 |  | digital
FW.EDI_J0GCK53AP001_OP | 1964 | EDI-#3给水泵自动启 |  | digital
FW.EDI_J0GCK54AP001_OC | 1965 | EDI-#4给水泵自动停 |  | digital
FW.EDI_J0GCK54AP001_OP | 1966 | EDI-#4给水泵自动启 |  | digital
FW.EJFST_J0GCB40AP001CP | 1967 | 二级反渗透冲洗水泵顺控停 |  | digital
FW.EJFST_J0GCB40AP001OP | 1968 | 二级反渗透冲洗水泵顺控启 |  | digital
FW.EJFSTFX_PD | 1969 | Ovation Control Builder |  | float32
FW.EJFSTFXJT | 1970 | Ovation Control Builder |  | digital
FW.EJFSTTIME1 | 1971 | #1二级反渗透排队时间 |  | float32
FW.EJFSTTIME2 | 1972 | #2二级反渗透排队时间 |  | float32
FW.EJFSTTIME3 | 1973 | #3二级反渗透排队时间 |  | float32
FW.EJFSTTIME4 | 1974 | #4二级反渗透排队时间 |  | float32
FW.EJFSTYX2 | 1975 | Ovation Control Builder |  | digital
FW.EJFSTYX3 | 1976 | Ovation Control Builder |  | digital
FW.EJFSTYX4 | 1977 | Ovation Control Builder |  | digital
FW.FSJT1 | 1978 | 废水设备停1 |  | digital
FW.FSJT2 | 1979 | 废水设备停2 |  | digital
FW.FSJT3 | 1980 | 废水设备停3 |  | digital
FW.FSJT4 | 1981 | 废水设备停4 |  | digital
FW.FSSBJT | 1982 | 废水设备急停 |  | digital
FW.FSTYX10 | 1983 | #2加非氧化性杀菌剂排队优先 |  | digital
FW.FSTYX11 | 1984 | #3加非氧化性杀菌剂排队优先 |  | digital
FW.FSTYX12 | 1985 | #4加非氧化性杀菌剂排队优先 |  | digital
FW.FSTYX2 | 1986 | #2一级反渗透排队优先 |  | digital
FW.FSTYX3 | 1987 | #3一级反渗透排队优先 |  | digital
FW.FSTYX4 | 1988 | #4一级反渗透排队优先 |  | digital
FW.FSTYX5 | 1989 | #1二级反渗透排队优先 |  | digital
FW.FSTYX6 | 1990 | #2二级反渗透排队优先 |  | digital
FW.FSTYX7 | 1991 | #3二级反渗透排队优先 |  | digital
FW.FSTYX8 | 1992 | #4二级反渗透排队优先 |  | digital
FW.FSTYX9 | 1993 | #1加非氧化性杀菌剂排队优先 |  | digital
FW.GLQ_Y0GRB10AA003_CLOSE | 1994 | 过滤器反洗进水门自动关 |  | digital
FW.GLQ_Y0GRB10AA003_OPEN | 1995 | 过滤器反洗进水门自动开 |  | digital
FW.GLQ_Y0GRB10AA004_CLOSE | 1996 | 过滤器进气电动门自动关 |  | digital
FW.GLQ_Y0GRB10AA004_OPEN | 1997 | 过滤器进气电动门自动开 |  | digital
FW.GLQ_Y0GRB10AA401_CLOSE | 1998 | 过滤器反洗排污门自动关 |  | digital
FW.GLQ_Y0GRB10AA401_OPEN | 1999 | 过滤器反洗排污门自动开 |  | digital
FW.GLQ_Y0GRK41AP001_CLOSE | 2000 | 过滤器运行-回用水池提升泵停 |  | digital
FW.GLQ_Y0GRK41AP001_OPEN | 2001 | 过滤器运行-回用水池提升泵启 |  | digital
FW.GYFSGN_CHOOSE | 2002 | 工业废水刮泥选择 |  | digital
FW.HYSCTSB1 | 2003 | 选择回用水池提升泵1 |  | digital
FW.HYSCTSB2 | 2004 | 选择回用水池提升泵2 |  | digital
FW.J0BHC01A_LP | 2005 | 厂区公用A段工作进线开关46A011 |  | int32
FW.J0BHC01A_LP1 | 2006 | A段进线开关DP输入 |  | int32
FW.J0BHC01A_LP2 | 2007 | A段进线开关DP输出 |  | int32
FW.J0BHC01ADDYZX | 2008 | A段进线开关低电压动作 |  | digital
FW.J0BHC01ADXZX | 2009 | A段进线开关PT断线 |  | digital
FW.J0BHC01AGZZX | 2010 | A段进线开关DP工作位 |  | digital
FW.J0BHC01AIA | 2011 |  |  | float32
FW.J0BHC01AIAL | 2012 | Ovation Control Builder |  | float32
FW.J0BHC01AIB | 2013 |  |  | float32
FW.J0BHC01AIC | 2014 |  |  | float32
FW.J0BHC01AJXZX | 2015 | A段进线开关DP检修位 |  | digital
FW.J0BHC01APFZX | 2016 | 厂区公用A段进线开关故障 |  | digital
FW.J0BHC01ARCZX | 2017 | 厂区公用A段进线开关远方 |  | digital
FW.J0BHC01ARDZX | 2018 | 厂区公用A段进线开关合闸 |  | digital
FW.J0BHC01ARPZX | 2019 | 厂区公用A段进线开关合闸位置 |  | digital
FW.J0BHC01ASYZX | 2020 | A段进线开关DP试验位 |  | digital
FW.J0BHC01ATDZX | 2021 | 厂区公用A段进线开关分闸 |  | digital
FW.J0BHC01ATPZX | 2022 | 厂区公用A段进线开关分闸位置 |  | digital
FW.J0BHC01BDDYZX | 2023 | A段母线PT低电压动作 |  | digital
FW.J0BHC01BDXZX | 2024 | 厂区公用A段PT断线 |  | digital
FW.J0BHC01BIA | 2025 |  |  | float32
FW.J0BHC01BIAL | 2026 | Ovation Control Builder |  | float32
FW.J0BHC01BIB | 2027 |  |  | float32
FW.J0BHC01BIC | 2028 |  |  | float32
FW.J0BHC01BUA | 2029 |  |  | float32
FW.J0BHC01BUB | 2030 |  |  | float32
FW.J0BHC01BUC | 2031 |  |  | float32
FW.J0BHD01A_LP | 2032 | 厂区公用B段工作进线开关46B011 |  | int32
FW.J0BHD01A_LP1 | 2033 | B段进线开关DP输入 |  | int32
FW.J0BHD01A_LP2 | 2034 | B段进线开关DP输出 |  | int32
FW.J0BHD01ADDYZX | 2035 | B段进线开关低电压动作 |  | digital
FW.J0BHD01ADXZX | 2036 | B段进线开关PT断线 |  | digital
FW.J0BHD01AGZZX | 2037 | B段进线开关DP工作位 |  | digital
FW.J0BHD01AIA | 2038 |  |  | float32
FW.J0BHD01AIAL | 2039 | Ovation Control Builder |  | float32
FW.J0BHD01AIB | 2040 |  |  | float32
FW.J0BHD01AIC | 2041 |  |  | float32
FW.J0BHD01AJXZX | 2042 | B段进线开关DP检修位 |  | digital
FW.J0BHD01APFZX | 2043 | 厂区公用B段进线开关故障 |  | digital
FW.J0BHD01ARCZX | 2044 | 厂区公用B段进线开关远方 |  | digital
FW.J0BHD01ARDZX | 2045 | 厂区公用B段进线开关合闸 |  | digital
FW.J0BHD01ARPZX | 2046 | 厂区公用B段进线开关合闸位置 |  | digital
FW.J0BHD01ASYZX | 2047 | B段进线开关DP试验位 |  | digital
FW.J0BHD01ATDZX | 2048 | 厂区公用B段进线开关分闸 |  | digital
FW.J0BHD01ATPZX | 2049 | 厂区公用B段进线开关分闸位置 |  | digital
FW.J0BHD01BDDYZX | 2050 | B段母线PT低电压动作 |  | digital
FW.J0BHD01BDXZX | 2051 | 厂区公用B段PT断线 |  | digital
FW.J0BHD01BIA | 2052 |  |  | float32
FW.J0BHD01BIAL | 2053 | Ovation Control Builder |  | float32
FW.J0BHD01BIB | 2054 |  |  | float32
FW.J0BHD01BIC | 2055 |  |  | float32
FW.J0BHD01BUA | 2056 |  |  | float32
FW.J0BHD01BUB | 2057 |  |  | float32
FW.J0BHD01BUC | 2058 |  |  | float32
FW.J0BHD11D_LP | 2059 | 厂区公用段母联开关46B114 |  | int32
FW.J0BHD11D_LP1 | 2060 | 母联开关DP输入 |  | int32
FW.J0BHD11D_LP2 | 2061 | 母联开关DP输出 |  | int32
FW.J0BHD11DGZZX | 2062 | 母联开关DP工作位 |  | digital
FW.J0BHD11DIA | 2063 |  |  | float32
FW.J0BHD11DIAL | 2064 | Ovation Control Builder |  | float32
FW.J0BHD11DIB | 2065 |  |  | float32
FW.J0BHD11DIC | 2066 |  |  | float32
FW.J0BHD11DJXZX | 2067 | 母联开关DP检修位 |  | digital
FW.J0BHD11DPFZX | 2068 | 厂区公用段母联开关故障 |  | digital
FW.J0BHD11DRCZX | 2069 | 厂区公用段母联开关远方 |  | digital
FW.J0BHD11DRDZX | 2070 | 厂区公用段母联开关合闸 |  | digital
FW.J0BHD11DRPZX | 2071 | 厂区公用段母联开关合闸位置 |  | digital
FW.J0BHD11DSYZX | 2072 | 母联开关DP试验位 |  | digital
FW.J0BHD11DTDZX | 2073 | 厂区公用段母联开关分闸 |  | digital
FW.J0BHD11DTPZX | 2074 | 厂区公用段母联开关分闸位置 |  | digital
FW.J0BHD11DUA | 2075 |  |  | float32
FW.J0BHE00CE201 | 2076 | 380V补给水A段母线AC线电压 | V | float32
FW.J0BHE00EH201 | 2077 | 380V补给水A段母线电压低 |  | digital
FW.J0BHE00EH202 | 2078 | 380V补给水A段PT保护装置故障 |  | digital
FW.J0BHE00EH203 | 2079 | 380V补给水A段PT回路断线 |  | digital
FW.J0BHE00GS001_LP | 2080 | 380V补给水分段断路器 |  | int32
FW.J0BHE00GS001I | 2081 | 380V补给水分段断路器电流 | A | float32
FW.J0BHE00GS001PF | 2082 | 380V补给水分段断路器综合故障 |  | digital
FW.J0BHE00GS001RC | 2083 | 380V补给水分段断路器远方控制 |  | digital
FW.J0BHE00GS001RD | 2084 | 380V补给水段分段断路器合闸 |  | digital
FW.J0BHE00GS001RP | 2085 | 380V补给水段分段断路器合闸位置 |  | digital
FW.J0BHE00GS001TD | 2086 | 380V补给水段分段断路器分闸 |  | digital
FW.J0BHE00GS001TP | 2087 | 380V补给水段分段断路器分闸位置 |  | digital
FW.J0BHF00CE201 | 2088 | 380V补给水B段母线AC线电压 | V | float32
FW.J0BHF00EH201 | 2089 | 380V补给水B段母线电压低 |  | digital
FW.J0BHF00EH202 | 2090 | 380V补给水B段PT保护装置故障 |  | digital
FW.J0BHF00EH203 | 2091 | 380V补给水B段PT回路断线 |  | digital
FW.J0BHT50GS002_LP | 2092 | 补给水A变380V侧断路器 |  | int32
FW.J0BHT50GS002I | 2093 | #1补给水变380V侧断路器电流 | A | float32
FW.J0BHT50GS002PF | 2094 | #1补给水变380V侧断路器综合故障 |  | digital
FW.J0BHT50GS002RC | 2095 | #1补给水变380V侧断路器远方控制 |  | digital
FW.J0BHT50GS002RD | 2096 | #1补给水变380V侧断路器合闸 |  | digital
FW.J0BHT50GS002RP | 2097 | #1补给水变380V侧断路器合闸位置 |  | digital
FW.J0BHT50GS002TD | 2098 | #1补给水变380V侧断路器分闸 |  | digital
FW.J0BHT50GS002TP | 2099 | #1补给水变380V侧断路器分闸位置 |  | digital
FW.J0BHT60GS002_LP | 2100 | 补给水B变380V侧断路器 |  | int32
FW.J0BHT60GS002I | 2101 | #2补给水变380V侧断路器电流 | A | float32
FW.J0BHT60GS002PF | 2102 | #2补给水变380V侧断路器综合故障 |  | digital
FW.J0BHT60GS002RC | 2103 | #2补给水变380V侧断路器远方控制 |  | digital
FW.J0BHT60GS002RD | 2104 | #2补给水变380V侧断路器合闸 |  | digital
FW.J0BHT60GS002RP | 2105 | #2补给水变380V侧断路器合闸位置 |  | digital
FW.J0BHT60GS002TD | 2106 | #2补给水变380V侧断路器分闸 |  | digital
FW.J0BHT60GS002TP | 2107 | #2补给水变380V侧断路器分闸位置 |  | digital
FW.J0CRP72BAPF | 2108 | 网络电源分配柜保安电源故障报警 |  | digital
FW.J0CRP72CYPF | 2109 | 网络电源分配柜厂用电电源故障 |  | digital
FW.J0CRP72DYPF | 2110 | 网络电源分配柜仪表电源故障报警 |  | digital
FW.J0CRP72PF | 2111 | 网络电源分配柜电源故障报警 |  | digital
FW.J0GAA31AA001_LP | 2112 | #1絮凝斜板沉淀池进水电动门 |  | int32
FW.J0GAA31AA001CD | 2113 | #1絮凝斜板沉淀池进水门关 |  | digital
FW.J0GAA31AA001CP | 2114 | #1絮凝斜板沉淀池进水门全关 |  | digital
FW.J0GAA31AA001F | 2115 | #1絮凝斜板沉淀池进水门故障 |  | digital
FW.J0GAA31AA001OD | 2116 | #1絮凝斜板沉淀池进水门打开 |  | digital
FW.J0GAA31AA001OP | 2117 | #1絮凝斜板沉淀池进水门全开 |  | digital
FW.J0GAA31AA001RC | 2118 | #1絮凝斜板沉淀池进水门远方 |  | digital
FW.J0GAA31CF101 | 2119 | #1絮凝斜板沉淀池进水流量 | t/h | float32
FW.J0GAA31CF101L | 2120 | #1絮凝斜板沉淀池进水流量累计 |  | float32
FW.J0GAA31CL101 | 2121 | #1絮凝斜板沉淀池泥位 | m | float32
FW.J0GAA31CQ101 | 2122 | #1絮凝斜板沉淀池出水浊度 | NTU | float32
FW.J0GAA32AA001_LP | 2123 | #2絮凝斜板沉淀池进水电动门 |  | int32
FW.J0GAA32AA001CD | 2124 | #2絮凝斜板沉淀池进水门关 |  | digital
FW.J0GAA32AA001CP | 2125 | #2絮凝斜板沉淀池进水门全关 |  | digital
FW.J0GAA32AA001F | 2126 | #2絮凝斜板沉淀池进水门故障 |  | digital
FW.J0GAA32AA001OD | 2127 | #2絮凝斜板沉淀池进水门打开 |  | digital
FW.J0GAA32AA001OP | 2128 | #2絮凝斜板沉淀池进水门全开 |  | digital
FW.J0GAA32AA001RC | 2129 | #2絮凝斜板沉淀池进水门远方 |  | digital
FW.J0GAA32CF101 | 2130 | #2絮凝斜板沉淀池进水流量 | t/h | float32
FW.J0GAA32CF101L | 2131 | #2絮凝斜板沉淀池进水流量累计 |  | float32
FW.J0GAA32CL101 | 2132 | #2絮凝斜板沉淀池泥位 | m | float32
FW.J0GAA32CQ101 | 2133 | #2絮凝斜板沉淀池出水浊度 | NTU | float32
FW.J0GAA43AA001_AC | 2134 | Ovation Control Builder |  | digital
FW.J0GAA43AA001_AO | 2135 | Ovation Control Builder |  | digital
FW.J0GAA43AA001_F | 2136 | Ovation Control Builder |  | digital
FW.J0GAA43AA001_MODE | 2137 | Ovation Control Builder |  | int32
FW.J0GAA43AA001_SPO | 2138 | Ovation Control Builder |  | float32
FW.J0GAA43AA001C | 2139 | #1空气擦洗重力池进水门指令 | % | float32
FW.J0GAA43AA001F | 2140 | #1空气擦洗重力池进水流量门故障 |  | digital
FW.J0GAA43AA001P | 2141 | #1空气擦洗重力池进水流量阀反馈 | % | float32
FW.J0GAA43AA001RC | 2142 | #1空气擦洗重力池进水流量门远方 |  | digital
FW.J0GAA43AA002_AC | 2143 | #1空气擦洗重力滤池出水门顺控停 |  | digital
FW.J0GAA43AA002_AO | 2144 | #1空气擦洗重力滤池出水门顺控启 |  | digital
FW.J0GAA43AA002_LP | 2145 | #1空气擦洗重力滤池出水气动门 |  | int32
FW.J0GAA43AA002CD | 2146 | #1空气擦洗重力池出水门关指令 |  | digital
FW.J0GAA43AA002CP | 2147 | #1空气擦洗重力池出水门全关 |  | digital
FW.J0GAA43AA002OD | 2148 | #1空气擦洗重力池出水门打开 |  | digital
FW.J0GAA43AA002OP | 2149 | #1空气擦洗重力池出水门全开 |  | digital
FW.J0GAA43AA002RC | 2150 | #1空气擦洗重力池出水门远方 |  | digital
FW.J0GAA43AA003_AC | 2151 | #1空气擦洗重力池连通门1顺控停 |  | digital
FW.J0GAA43AA003_AO | 2152 | #1空气擦洗重力池连通门1顺控启 |  | digital
FW.J0GAA43AA003_LP | 2153 | #1空气擦洗重力滤池连通气动门1 |  | int32
FW.J0GAA43AA003CD | 2154 | #1空气擦洗重力池连通门1关指令 |  | digital
FW.J0GAA43AA003CP | 2155 | #1空气擦洗重力池连通门1全关 |  | digital
FW.J0GAA43AA003OD | 2156 | #1空气擦洗重力池连通门1打开 |  | digital
FW.J0GAA43AA003OP | 2157 | #1空气擦洗重力池连通门1全开 |  | digital
FW.J0GAA43AA003RC | 2158 | #1空气擦洗重力池连通门1远方 |  | digital
FW.J0GAA43AA004_AC | 2159 | #1重力滤池连通门2顺控停 |  | digital
FW.J0GAA43AA004_AO | 2160 | #1重力滤池连通门2顺控启 |  | digital
FW.J0GAA43AA004_LP | 2161 | #1空气擦洗重力滤池连通气动门2 |  | int32
FW.J0GAA43AA004CD | 2162 | #1空气擦洗重力池连通门2关指令 |  | digital
FW.J0GAA43AA004CP | 2163 | #1空气擦洗重力池连通门2全关 |  | digital
FW.J0GAA43AA004OD | 2164 | #1空气擦洗重力池连通门2打开 |  | digital
FW.J0GAA43AA004OP | 2165 | #1空气擦洗重力池连通门2全开 |  | digital
FW.J0GAA43AA004RC | 2166 | #1空气擦洗重力池连通门2远方 |  | digital
FW.J0GAA43AA401_AC | 2167 | #1空气擦洗重力滤池正排门程控停 |  | digital
FW.J0GAA43AA401_AO | 2168 | #1空气擦洗重力滤池正排门程控启 |  | digital
FW.J0GAA43AA401_LP | 2169 | #1空气擦洗重力滤池正洗排水门 |  | int32
FW.J0GAA43AA401CD | 2170 | #1空气擦洗重力池正洗排水门关 |  | digital
FW.J0GAA43AA401CP | 2171 | #1空气擦洗重力池正洗排水门全关 |  | digital
FW.J0GAA43AA401OD | 2172 | #1空气擦洗重力池正洗排水门打开 |  | digital
FW.J0GAA43AA401OP | 2173 | #1空气擦洗重力池正洗排水门全开 |  | digital
FW.J0GAA43AA401RC | 2174 | #1空气擦洗重力池正洗排水门远方 |  | digital
FW.J0GAA43AA402_AC | 2175 | #1重力滤池反洗排水门顺控停 |  | digital
FW.J0GAA43AA402_AO | 2176 | #1重力滤池反洗排水门顺控启 |  | digital
FW.J0GAA43AA402_LP | 2177 | #1空气擦洗重力滤池反洗排水门 |  | int32
FW.J0GAA43AA402CD | 2178 | #1空气擦洗重力池反洗排水门关 |  | digital
FW.J0GAA43AA402CP | 2179 | #1空气擦洗重力池反洗排水门全关 |  | digital
FW.J0GAA43AA402OD | 2180 | #1空气擦洗重力池反洗排水门打开 |  | digital
FW.J0GAA43AA402OP | 2181 | #1空气擦洗重力池反洗排水门全开 |  | digital
FW.J0GAA43AA402RC | 2182 | #1空气擦洗重力池反洗排水门远方 |  | digital
FW.J0GAA43CP101 | 2183 | #1空气擦洗重力滤池出入口差压 | Mpa | float32
FW.J0GAA43CQ101 | 2184 | #1空气擦洗重力滤池出水浊度 | NTU | float32
FW.J0GAA44AA001_AC | 2185 | Ovation Control Builder |  | digital
FW.J0GAA44AA001_AO | 2186 | Ovation Control Builder |  | digital
FW.J0GAA44AA001_F | 2187 | Ovation Control Builder |  | digital
FW.J0GAA44AA001_MODE | 2188 | Ovation Control Builder |  | int32
FW.J0GAA44AA001_SPO | 2189 | Ovation Control Builder |  | float32
FW.J0GAA44AA001C | 2190 | #2空气擦洗重力池进水门指令 | % | float32
FW.J0GAA44AA001F | 2191 | #2空气擦洗重力池进水流量门故障 |  | digital
FW.J0GAA44AA001P | 2192 | #2空气擦洗重力池进水流量阀反馈 | % | float32
FW.J0GAA44AA001RC | 2193 | #2空气擦洗重力池进水流量门远方 |  | digital
FW.J0GAA44AA002_AC | 2194 | #2空气擦洗重力滤池出水门顺控停 |  | digital
FW.J0GAA44AA002_AO | 2195 | #2空气擦洗重力滤池出水门顺控启 |  | digital
FW.J0GAA44AA002_LP | 2196 | #2空气擦洗重力滤池出水气动门 |  | int32
FW.J0GAA44AA002CD | 2197 | #2空气擦洗重力池出水门关指令 |  | digital
FW.J0GAA44AA002CP | 2198 | #2空气擦洗重力池出水门全关 |  | digital
FW.J0GAA44AA002OD | 2199 | #2空气擦洗重力池出水门打开 |  | digital
FW.J0GAA44AA002OP | 2200 | #2空气擦洗重力池出水门全开 |  | digital
FW.J0GAA44AA002RC | 2201 | #2空气擦洗重力池出水门远方 |  | digital
FW.J0GAA44AA003_AC | 2202 | #2空气擦洗重力池连通门1顺控停 |  | digital
FW.J0GAA44AA003_AO | 2203 | #2空气擦洗重力池连通门1顺控启 |  | digital
FW.J0GAA44AA003_LP | 2204 | #2空气擦洗重力滤池连通气动门1 |  | int32
FW.J0GAA44AA003CD | 2205 | #2空气擦洗重力池连通门1关指令 |  | digital
FW.J0GAA44AA003CP | 2206 | #2空气擦洗重力池连通门1全关 |  | digital
FW.J0GAA44AA003OD | 2207 | #2空气擦洗重力池连通门1打开 |  | digital
FW.J0GAA44AA003OP | 2208 | #2空气擦洗重力池连通门1全开 |  | digital
FW.J0GAA44AA003RC | 2209 | #2空气擦洗重力池连通门1远方 |  | digital
FW.J0GAA44AA004_AC | 2210 | #2重力滤池连通门2顺控停 |  | digital
FW.J0GAA44AA004_AO | 2211 | #2重力滤池连通门2顺控启 |  | digital
FW.J0GAA44AA004_LP | 2212 | #2空气擦洗重力滤池连通气动门2 |  | int32
FW.J0GAA44AA004CD | 2213 | #2空气擦洗重力池连通门2关指令 |  | digital
FW.J0GAA44AA004CP | 2214 | #2空气擦洗重力池连通门2全关 |  | digital
FW.J0GAA44AA004OD | 2215 | #2空气擦洗重力池连通门2打开 |  | digital
FW.J0GAA44AA004OP | 2216 | #2空气擦洗重力池连通门2全开 |  | digital
FW.J0GAA44AA004RC | 2217 | #2空气擦洗重力池连通门2远方 |  | digital
FW.J0GAA44AA401_AC | 2218 | #2空气擦洗重力滤池正排门程控停 |  | digital
FW.J0GAA44AA401_AO | 2219 | #2空气擦洗重力滤池正排门程控启 |  | digital
FW.J0GAA44AA401_LP | 2220 | #2空气擦洗重力滤池正洗排水门 |  | int32
FW.J0GAA44AA401CD | 2221 | #2空气擦洗重力池正洗排水门关 |  | digital
FW.J0GAA44AA401CP | 2222 | #2空气擦洗重力池正洗排水门全关 |  | digital
FW.J0GAA44AA401OD | 2223 | #2空气擦洗重力池正洗排水门打开 |  | digital
FW.J0GAA44AA401OP | 2224 | #2空气擦洗重力池正洗排水门全开 |  | digital
FW.J0GAA44AA401RC | 2225 | #2空气擦洗重力池正洗排水门远方 |  | digital
FW.J0GAA44AA402_AC | 2226 | #2重力滤池反洗排水门顺控停 |  | digital
FW.J0GAA44AA402_AO | 2227 | #2重力滤池反洗排水门顺控启 |  | digital
FW.J0GAA44AA402_LP | 2228 | #2空气擦洗重力滤池反洗排水门 |  | int32
FW.J0GAA44AA402CD | 2229 | #2空气擦洗重力池反洗排水门关 |  | digital
FW.J0GAA44AA402CP | 2230 | #2空气擦洗重力池反洗排水门全关 |  | digital
FW.J0GAA44AA402OD | 2231 | #2空气擦洗重力池反洗排水门打开 |  | digital
FW.J0GAA44AA402OP | 2232 | #2空气擦洗重力池反洗排水门全开 |  | digital
FW.J0GAA44AA402RC | 2233 | #2空气擦洗重力池反洗排水门远方 |  | digital
FW.J0GAA44CP101 | 2234 | #2空气擦洗重力滤池出入口差压 | Mpa | float32
FW.J0GAA44CQ101 | 2235 | #2空气擦洗重力滤池出水浊度 | NTU | float32
FW.J0GAA45AA001_AC | 2236 | Ovation Control Builder |  | digital
FW.J0GAA45AA001_AO | 2237 | Ovation Control Builder |  | digital
FW.J0GAA45AA001_F | 2238 | Ovation Control Builder |  | digital
FW.J0GAA45AA001_MODE | 2239 | Ovation Control Builder |  | int32
FW.J0GAA45AA001_SPO | 2240 | Ovation Control Builder |  | float32
FW.J0GAA45AA001C | 2241 | #3空气擦洗重力池进水门指令 | % | float32
FW.J0GAA45AA001F | 2242 | #3空气擦洗重力池进水流量门故障 |  | digital
FW.J0GAA45AA001P | 2243 | #3空气擦洗重力池进水流量阀反馈 | % | float32
FW.J0GAA45AA001RC | 2244 | #3空气擦洗重力池进水流量门远方 |  | digital
FW.J0GAA45AA002_AC | 2245 | #3空气擦洗重力滤池出水门顺控停 |  | digital
FW.J0GAA45AA002_AO | 2246 | #3空气擦洗重力滤池出水门顺控启 |  | digital
FW.J0GAA45AA002_LP | 2247 | #3空气擦洗重力滤池出水气动门 |  | int32
FW.J0GAA45AA002CD | 2248 | #3空气擦洗重力池出水门关指令 |  | digital
FW.J0GAA45AA002CP | 2249 | #3空气擦洗重力池出水门全关 |  | digital
FW.J0GAA45AA002OD | 2250 | #3空气擦洗重力池出水门打开 |  | digital
FW.J0GAA45AA002OP | 2251 | #3空气擦洗重力池出水门全开 |  | digital
FW.J0GAA45AA002RC | 2252 | #3空气擦洗重力池出水门远方 |  | digital
FW.J0GAA45AA003_AC | 2253 | #3空气擦洗重力池连通门1顺控停 |  | digital
FW.J0GAA45AA003_AO | 2254 | #3空气擦洗重力池连通门1顺控启 |  | digital
FW.J0GAA45AA003_LP | 2255 | #3空气擦洗重力滤池连通气动门1 |  | int32
FW.J0GAA45AA003CD | 2256 | #3空气擦洗重力池连通门1关指令 |  | digital
FW.J0GAA45AA003CP | 2257 | #3空气擦洗重力池连通门1全关 |  | digital
FW.J0GAA45AA003OD | 2258 | #3空气擦洗重力池连通门1打开 |  | digital
FW.J0GAA45AA003OP | 2259 | #3空气擦洗重力池连通门1全开 |  | digital
FW.J0GAA45AA003RC | 2260 | #3空气擦洗重力池连通门1远方 |  | digital
FW.J0GAA45AA004_AC | 2261 | #3重力滤池连通门2顺控停 |  | digital
FW.J0GAA45AA004_AO | 2262 | #3重力滤池连通门2顺控启 |  | digital
FW.J0GAA45AA004_LP | 2263 | #3空气擦洗重力滤池连通气动门2 |  | int32
FW.J0GAA45AA004CD | 2264 | #3空气擦洗重力池连通门2关指令 |  | digital
FW.J0GAA45AA004CP | 2265 | #3空气擦洗重力池连通门2全关 |  | digital
FW.J0GAA45AA004OD | 2266 | #3空气擦洗重力池连通门2打开 |  | digital
FW.J0GAA45AA004OP | 2267 | #3空气擦洗重力池连通门2全开 |  | digital
FW.J0GAA45AA004RC | 2268 | #3空气擦洗重力池连通门2远方 |  | digital
FW.J0GAA45AA401_AC | 2269 | #3空气擦洗重力滤池正排门程控停 |  | digital
FW.J0GAA45AA401_AO | 2270 | #3空气擦洗重力滤池正排门程控启 |  | digital
FW.J0GAA45AA401_LP | 2271 | #3空气擦洗重力滤池正洗排水门 |  | int32
FW.J0GAA45AA401CD | 2272 | #3空气擦洗重力池正洗排水门关 |  | digital
FW.J0GAA45AA401CP | 2273 | #3空气擦洗重力池正洗排水门全关 |  | digital
FW.J0GAA45AA401OD | 2274 | #3空气擦洗重力池正洗排水门打开 |  | digital
FW.J0GAA45AA401OP | 2275 | #3空气擦洗重力池正洗排水门全开 |  | digital
FW.J0GAA45AA401RC | 2276 | #3空气擦洗重力池正洗排水门远方 |  | digital
FW.J0GAA45AA402_AC | 2277 | #3重力滤池反洗排水门顺控停 |  | digital
FW.J0GAA45AA402_AO | 2278 | #3重力滤池反洗排水门顺控启 |  | digital
FW.J0GAA45AA402_LP | 2279 | #3空气擦洗重力滤池反洗排水门 |  | int32
FW.J0GAA45AA402CD | 2280 | #3空气擦洗重力池反洗排水门关 |  | digital
FW.J0GAA45AA402CP | 2281 | #3空气擦洗重力池反洗排水门全关 |  | digital
FW.J0GAA45AA402OD | 2282 | #3空气擦洗重力池反洗排水门打开 |  | digital
FW.J0GAA45AA402OP | 2283 | #3空气擦洗重力池反洗排水门全开 |  | digital
FW.J0GAA45AA402RC | 2284 | #3空气擦洗重力池反洗排水门远方 |  | digital
FW.J0GAA45CP101 | 2285 | #3空气擦洗重力滤池出入口差压 | Mpa | float32
FW.J0GAA45CQ101 | 2286 | #3空气擦洗重力滤池出水浊度 | NTU | float32
FW.J0GAC01AN001_AC | 2287 | 净水站罗茨风机顺控停 |  | digital
FW.J0GAC01AN001_AO | 2288 | 净水站罗茨风机顺控启 |  | digital
FW.J0GAC01AN001_CHOOSE | 2289 | #1净水站罗茨风机选定 |  | digital
FW.J0GAC01AN001_LP | 2290 | #1净水站罗茨风机 |  | int32
FW.J0GAC01AN001PF | 2291 | #1罗茨风机综合故障 |  | digital
FW.J0GAC01AN001RC | 2292 | #1罗茨风机远方控制 |  | digital
FW.J0GAC01AN001RD | 2293 | #1罗茨风机启动指令 |  | digital
FW.J0GAC01AN001RP | 2294 | #1罗茨风机在运行 |  | digital
FW.J0GAC01AN001TD | 2295 | #1罗茨风机停止指令 |  | digital
FW.J0GAC02AN001_CHOOSE | 2296 | #2净水站罗茨风机选定 |  | digital
FW.J0GAC02AN001_LP | 2297 | #2净水站罗茨风机 |  | int32
FW.J0GAC02AN001PF | 2298 | #2罗茨风机综合故障 |  | digital
FW.J0GAC02AN001RC | 2299 | #2罗茨风机远方控制 |  | digital
FW.J0GAC02AN001RD | 2300 | #2罗茨风机启动指令 |  | digital
FW.J0GAC02AN001RP | 2301 | #2罗茨风机在运行 |  | digital
FW.J0GAC02AN001TD | 2302 | #2罗茨风机停止指令 |  | digital
FW.J0GAC63AA001_LP | 2303 | #1化学消防水水池进水电动门 |  | int32
FW.J0GAC63AA001CD | 2304 | #1化学消防水水池进水门关 |  | digital
FW.J0GAC63AA001CP | 2305 | #1化学消防水水池进水门全关 |  | digital
FW.J0GAC63AA001F | 2306 | #1化学消防水水池进水门故障 |  | digital
FW.J0GAC63AA001OD | 2307 | #1化学消防水水池进水门打开 |  | digital
FW.J0GAC63AA001OP | 2308 | #1化学消防水水池进水门全开 |  | digital
FW.J0GAC63AA001RC | 2309 | #1化学消防水水池进水门远方 |  | digital
FW.J0GAC65AA001_LP | 2310 | #2化学消防水水池进水电动门 |  | int32
FW.J0GAC65AA001CD | 2311 | #2化学消防水水池进水门关 |  | digital
FW.J0GAC65AA001CP | 2312 | #2化学消防水水池进水门全关 |  | digital
FW.J0GAC65AA001F | 2313 | #2化学消防水水池进水门故障 |  | digital
FW.J0GAC65AA001OD | 2314 | #2化学消防水水池进水门打开 |  | digital
FW.J0GAC65AA001OP | 2315 | #2化学消防水水池进水门全开 |  | digital
FW.J0GAC65AA001RC | 2316 | #2化学消防水水池进水门远方 |  | digital
FW.J0GAD01CL101 | 2317 | #1化学消防水水池液位 | m | float32
FW.J0GAD01CL102 | 2318 | #2化学消防水水池液位 | m | float32
FW.J0GAD02CL101 | 2319 | 生活水池液位 | m | float32
FW.J0GAN11AP001_LP | 2320 | 卸混凝剂磁力泵 |  | int32
FW.J0GAN11AP001PF | 2321 | 卸混凝剂磁力泵综合故障 |  | digital
FW.J0GAN11AP001RC | 2322 | 卸混凝剂磁力泵远方控制 |  | digital
FW.J0GAN11AP001RD | 2323 | 卸混凝剂磁力泵启动指令 |  | digital
FW.J0GAN11AP001RP | 2324 | 卸混凝剂磁力泵在运行 |  | digital
FW.J0GAN11AP001TD | 2325 | 卸混凝剂磁力泵停止指令 |  | digital
FW.J0GAN13AP001_LP | 2326 | 卸次氯酸钠磁力泵 |  | int32
FW.J0GAN13AP001PF | 2327 | 卸次氯酸钠磁力泵综合故障 |  | digital
FW.J0GAN13AP001RC | 2328 | 卸次氯酸钠磁力泵远方控制 |  | digital
FW.J0GAN13AP001RD | 2329 | 卸次氯酸钠磁力泵启动指令 |  | digital
FW.J0GAN13AP001RP | 2330 | 卸次氯酸钠磁力泵在运行 |  | digital
FW.J0GAN13AP001TD | 2331 | 卸次氯酸钠磁力泵停止指令 |  | digital
FW.J0GAN21AA002_LP | 2332 | #1混凝剂储罐出口气动门 |  | int32
FW.J0GAN21AA002CD | 2333 | #1混凝剂储罐出口气动门关指令 |  | digital
FW.J0GAN21AA002CP | 2334 | #1混凝剂储罐出口气动门全关 |  | digital
FW.J0GAN21AA002OD | 2335 | #1混凝剂储罐出口门打开指令 |  | digital
FW.J0GAN21AA002OP | 2336 | #1混凝剂储罐出口气动门全开 |  | digital
FW.J0GAN21AA002RC | 2337 | #1混凝剂储罐出口门远方 |  | digital
FW.J0GAN21CL501 | 2338 | #1混凝剂储罐液位 | m | float32
FW.J0GAN22AA002_LP | 2339 | #2混凝剂储罐出口气动门 |  | int32
FW.J0GAN22AA002CD | 2340 | #2混凝剂储罐出口气动门关指令 |  | digital
FW.J0GAN22AA002CP | 2341 | #2混凝剂储罐出口气动门全关 |  | digital
FW.J0GAN22AA002OD | 2342 | #2混凝剂储罐出口门打开指令 |  | digital
FW.J0GAN22AA002OP | 2343 | #2混凝剂储罐出口气动门全开 |  | digital
FW.J0GAN22AA002RC | 2344 | #2混凝剂储罐出口门远方 |  | digital
FW.J0GAN22CL501 | 2345 | #2混凝剂储罐液位 | m | float32
FW.J0GAN23AA001_LP | 2346 | 助凝剂制备装置出口气动门 |  | int32
FW.J0GAN23AA001CD | 2347 | 助凝剂制备装置出口气动门关指令 |  | digital
FW.J0GAN23AA001CP | 2348 | 助凝剂制备装置出口气动门全关 |  | digital
FW.J0GAN23AA001OD | 2349 | 助凝剂制备装置出口门打开指令 |  | digital
FW.J0GAN23AA001OP | 2350 | 助凝剂制备装置出口气动门全开 |  | digital
FW.J0GAN23AA001RC | 2351 | 助凝剂制备装置出口门远方 |  | digital
FW.J0GAN23AA002_LP | 2352 | Ovation Control Builder |  | int32
FW.J0GAN23AA002CD | 2353 | Ovation Control Builder |  | digital
FW.J0GAN23AA002OD | 2354 | 开助凝剂制备装置入口电磁阀 |  | digital
FW.J0GAN23AA002RC | 2355 | 助凝剂制备装置入口电磁阀远方 |  | digital
FW.J0GAN23AM001_F | 2356 | Ovation Control Builder |  | digital
FW.J0GAN23AM001_LP | 2357 | 助凝剂制备装置输送电机 |  | int32
FW.J0GAN23AM001_MODE | 2358 | Ovation Control Builder |  | int32
FW.J0GAN23AM001_SPO | 2359 | Ovation Control Builder |  | float32
FW.J0GAN23AM001C | 2360 | 助凝剂螺旋输送电机频率给定 | % | float32
FW.J0GAN23AM001P | 2361 | 助凝剂螺旋输送电机频率反馈 | % | float32
FW.J0GAN23AM001PF | 2362 | 助凝剂制备装置输送电机综合故障 |  | digital
FW.J0GAN23AM001RC | 2363 | 助凝剂制备装置输送电机远方控制 |  | digital
FW.J0GAN23AM001RD | 2364 | 助凝剂制备装置输送电机启动指令 |  | digital
FW.J0GAN23AM001RP | 2365 | 助凝剂制备装置输送电机在运行 |  | digital
FW.J0GAN23AM001TD | 2366 | 助凝剂制备装置输送电机停止指令 |  | digital
FW.J0GAN23AM002_LP | 2367 | #1助凝剂制备装置搅拌机 |  | int32
FW.J0GAN23AM002PF | 2368 | 助凝剂制备装置#1搅拌机故障 |  | digital
FW.J0GAN23AM002RC | 2369 | 助凝剂制备装置#1搅拌机远方 |  | digital
FW.J0GAN23AM002RD | 2370 | 助凝剂制备装置#1搅拌机启动 |  | digital
FW.J0GAN23AM002RP | 2371 | 助凝剂制备装置#1搅拌机在运行 |  | digital
FW.J0GAN23AM002TD | 2372 | 助凝剂制备装置#1搅拌机停止 |  | digital
FW.J0GAN23AM003_LP | 2373 | #2助凝剂制备装置搅拌机 |  | int32
FW.J0GAN23AM003PF | 2374 | 助凝剂制备装置#2搅拌机故障 |  | digital
FW.J0GAN23AM003RC | 2375 | 助凝剂制备装置#2搅拌机远方 |  | digital
FW.J0GAN23AM003RD | 2376 | 助凝剂制备装置#2搅拌机启动 |  | digital
FW.J0GAN23AM003RP | 2377 | 助凝剂制备装置#2搅拌机在运行 |  | digital
FW.J0GAN23AM003TD | 2378 | 助凝剂制备装置#2搅拌机停止 |  | digital
FW.J0GAN23CL001 | 2379 | 助凝剂干粉投加物位开关 |  | digital
FW.J0GAN23CL501 | 2380 | 助凝剂溶液搅拌箱液位 | m | float32
FW.J0GAN24AA002_LP | 2381 | 次氯酸钠储罐出口气动门 |  | int32
FW.J0GAN24AA002CD | 2382 | 次氯酸钠储罐出口气动门关闭指令 |  | digital
FW.J0GAN24AA002CP | 2383 | 次氯酸钠储罐出口气动门全关位置 |  | digital
FW.J0GAN24AA002OD | 2384 | 次氯酸钠储罐出口气动门打开指令 |  | digital
FW.J0GAN24AA002OP | 2385 | 次氯酸钠储罐出口气动门全开位置 |  | digital
FW.J0GAN24AA002RC | 2386 | 次氯酸钠储罐出口门远方 |  | digital
FW.J0GAN24AA012_LP | 2387 | 次氯酸钠计量箱出口气动门 |  | int32
FW.J0GAN24AA012CD | 2388 | 次氯酸钠计量箱出口气动门关指令 |  | digital
FW.J0GAN24AA012CP | 2389 | 次氯酸钠计量箱出口气动门全关 |  | digital
FW.J0GAN24AA012OD | 2390 | 次氯酸钠计量箱出口门打开指令 |  | digital
FW.J0GAN24AA012OP | 2391 | 次氯酸钠计量箱出口气动门全开 |  | digital
FW.J0GAN24AA012RC | 2392 | 次氯酸钠计量箱出口门远方 |  | digital
FW.J0GAN24CL501 | 2393 | 次氯酸钠储罐液位 | m | float32
FW.J0GAN24CL502 | 2394 | 次氯酸钠计量箱液位 | m | float32
FW.J0GAN31AA001_LP | 2395 | #1混凝剂溶液搅拌箱进口气动门 |  | int32
FW.J0GAN31AA001CD | 2396 | #1混凝剂溶液搅拌箱进口门关 |  | digital
FW.J0GAN31AA001CP | 2397 | #1混凝剂溶液搅拌箱进口门全关 |  | digital
FW.J0GAN31AA001OD | 2398 | #1混凝剂溶液搅拌箱进口门打开 |  | digital
FW.J0GAN31AA001OP | 2399 | #1混凝剂溶液搅拌箱进口门全开 |  | digital
FW.J0GAN31AA001RC | 2400 | #1混凝剂溶液搅拌箱进口门远方 |  | digital
FW.J0GAN31AA002_LP | 2401 | #1混凝剂溶液搅拌箱出口气动门 |  | int32
FW.J0GAN31AA002CD | 2402 | #1混凝剂溶液搅拌箱出口门关 |  | digital
FW.J0GAN31AA002CP | 2403 | #1混凝剂溶液搅拌箱出口门全关 |  | digital
FW.J0GAN31AA002OD | 2404 | #1混凝剂溶液搅拌箱出口门打开 |  | digital
FW.J0GAN31AA002OP | 2405 | #1混凝剂溶液搅拌箱出口门全开 |  | digital
FW.J0GAN31AA002RC | 2406 | #1混凝剂溶液搅拌箱出口门远方 |  | digital
FW.J0GAN31AM001_LP | 2407 | #1混凝剂搅拌电机 |  | int32
FW.J0GAN31AM001PF | 2408 | #1混凝剂搅拌电机综合故障 |  | digital
FW.J0GAN31AM001RC | 2409 | #1混凝剂搅拌电机远方控制 |  | digital
FW.J0GAN31AM001RD | 2410 | #1混凝剂搅拌电机启动指令 |  | digital
FW.J0GAN31AM001RP | 2411 | #1混凝剂搅拌电机在运行 |  | digital
FW.J0GAN31AM001TD | 2412 | #1混凝剂搅拌电机停止指令 |  | digital
FW.J0GAN31CL501 | 2413 | #1混凝剂溶液搅拌箱液位 | m | float32
FW.J0GAN32AA001_LP | 2414 | #2混凝剂溶液搅拌箱进口气动门 |  | int32
FW.J0GAN32AA001CD | 2415 | #2混凝剂溶液搅拌箱进口门关 |  | digital
FW.J0GAN32AA001CP | 2416 | #2混凝剂溶液搅拌箱进口门全关 |  | digital
FW.J0GAN32AA001OD | 2417 | #2混凝剂溶液搅拌箱进口门打开 |  | digital
FW.J0GAN32AA001OP | 2418 | #2混凝剂溶液搅拌箱进口门全开 |  | digital
FW.J0GAN32AA001RC | 2419 | #2混凝剂溶液搅拌箱进口门远方 |  | digital
FW.J0GAN32AA002_LP | 2420 | #2混凝剂溶液搅拌箱出口气动门 |  | int32
FW.J0GAN32AA002CD | 2421 | #2混凝剂溶液搅拌箱出口门关 |  | digital
FW.J0GAN32AA002CP | 2422 | #2混凝剂溶液搅拌箱出口门全关 |  | digital
FW.J0GAN32AA002OD | 2423 | #2混凝剂溶液搅拌箱出口门打开 |  | digital
FW.J0GAN32AA002OP | 2424 | #2混凝剂溶液搅拌箱出口门全开 |  | digital
FW.J0GAN32AA002RC | 2425 | #2混凝剂溶液搅拌箱出口门远方 |  | digital
FW.J0GAN32AM001_LP | 2426 | #2混凝剂搅拌电机 |  | int32
FW.J0GAN32AM001PF | 2427 | #2混凝剂搅拌电机综合故障 |  | digital
FW.J0GAN32AM001RC | 2428 | #2混凝剂搅拌电机远方控制 |  | digital
FW.J0GAN32AM001RD | 2429 | #2混凝剂搅拌电机启动指令 |  | digital
FW.J0GAN32AM001RP | 2430 | #2混凝剂搅拌电机在运行 |  | digital
FW.J0GAN32AM001TD | 2431 | #2混凝剂搅拌电机停止指令 |  | digital
FW.J0GAN32CL501 | 2432 | #2混凝剂溶液搅拌箱液位 | m | float32
FW.J0GAN35AP001_F | 2433 | Ovation Control Builder |  | digital
FW.J0GAN35AP001_LP | 2434 | #1次氯酸钠计量泵 |  | int32
FW.J0GAN35AP001_MODE | 2435 | Ovation Control Builder |  | int32
FW.J0GAN35AP001_SPO | 2436 | Ovation Control Builder |  | float32
FW.J0GAN35AP001C | 2437 | #1次氯酸钠泵变频器频率控制 | Hz | float32
FW.J0GAN35AP001F | 2438 | #1次氯酸钠计量泵故障 |  | digital
FW.J0GAN35AP001P | 2439 | #1次氯酸钠计量泵变频器频率反馈 | Hz | float32
FW.J0GAN35AP001RC | 2440 | #1次氯酸钠计量泵就地/远程 |  | digital
FW.J0GAN35AP001RD | 2441 | #1次氯酸钠计量泵启动指令 |  | digital
FW.J0GAN35AP001RP | 2442 | #1次氯酸钠计量泵在运行 |  | digital
FW.J0GAN35AP001TD | 2443 | #1次氯酸钠计量泵停止指令 |  | digital
FW.J0GAN36AP001_F | 2444 | Ovation Control Builder |  | digital
FW.J0GAN36AP001_LP | 2445 | #2次氯酸钠计量泵 |  | int32
FW.J0GAN36AP001_MODE | 2446 | Ovation Control Builder |  | int32
FW.J0GAN36AP001_SPO | 2447 | Ovation Control Builder |  | float32
FW.J0GAN36AP001C | 2448 | #2次氯酸钠泵变频器频率控制 | Hz | float32
FW.J0GAN36AP001F | 2449 | #2次氯酸钠计量泵故障 |  | digital
FW.J0GAN36AP001P | 2450 | #2次氯酸钠计量泵变频器频率反馈 | Hz | float32
FW.J0GAN36AP001RC | 2451 | #2次氯酸钠计量泵就地/远程 |  | digital
FW.J0GAN36AP001RD | 2452 | #2次氯酸钠计量泵启动指令 |  | digital
FW.J0GAN36AP001RP | 2453 | #2次氯酸钠计量泵在运行 |  | digital
FW.J0GAN36AP001TD | 2454 | #2次氯酸钠计量泵停止指令 |  | digital
FW.J0GAN37AP001_F | 2455 | Ovation Control Builder |  | digital
FW.J0GAN37AP001_LP | 2456 | #3次氯酸钠计量泵 |  | int32
FW.J0GAN37AP001_MODE | 2457 | Ovation Control Builder |  | int32
FW.J0GAN37AP001_SPO | 2458 | Ovation Control Builder |  | float32
FW.J0GAN37AP001C | 2459 | #3次氯酸钠泵变频器频率控制 | Hz | float32
FW.J0GAN37AP001F | 2460 | #3次氯酸钠计量泵故障 |  | digital
FW.J0GAN37AP001P | 2461 | #3次氯酸钠计量泵变频器频率反馈 | Hz | float32
FW.J0GAN37AP001RC | 2462 | #3次氯酸钠计量泵就地/远程 |  | digital
FW.J0GAN37AP001RD | 2463 | #3次氯酸钠计量泵启动指令 |  | digital
FW.J0GAN37AP001RP | 2464 | #3次氯酸钠计量泵在运行 |  | digital
FW.J0GAN37AP001TD | 2465 | #3次氯酸钠计量泵停止指令 |  | digital
FW.J0GAN38AP001_F | 2466 | Ovation Control Builder |  | digital
FW.J0GAN38AP001_LP | 2467 | #4次氯酸钠计量泵 |  | int32
FW.J0GAN38AP001_MODE | 2468 | Ovation Control Builder |  | int32
FW.J0GAN38AP001_SPO | 2469 | Ovation Control Builder |  | float32
FW.J0GAN38AP001C | 2470 | #4次氯酸钠泵变频器频率控制 | Hz | float32
FW.J0GAN38AP001F | 2471 | #4次氯酸钠计量泵故障 |  | digital
FW.J0GAN38AP001P | 2472 | #4次氯酸钠计量泵变频器频率反馈 | Hz | float32
FW.J0GAN38AP001RC | 2473 | #4次氯酸钠计量泵就地/远程 |  | digital
FW.J0GAN38AP001RD | 2474 | #4次氯酸钠计量泵启动指令 |  | digital
FW.J0GAN38AP001RP | 2475 | #4次氯酸钠计量泵在运行 |  | digital
FW.J0GAN38AP001TD | 2476 | #4次氯酸钠计量泵停止指令 |  | digital
FW.J0GAN41AP001_F | 2477 | Ovation Control Builder |  | digital
FW.J0GAN41AP001_LP | 2478 | #1混凝剂计量泵 |  | int32
FW.J0GAN41AP001_MODE | 2479 | Ovation Control Builder |  | int32
FW.J0GAN41AP001_SPO | 2480 | Ovation Control Builder |  | float32
FW.J0GAN41AP001C | 2481 | #1混凝剂计量泵变频器频率控制 | Hz | float32
FW.J0GAN41AP001F | 2482 | #1混凝剂计量泵故障 |  | digital
FW.J0GAN41AP001P | 2483 | #1混凝剂计量泵变频器频率反馈 | Hz | float32
FW.J0GAN41AP001RC | 2484 | #1混凝剂计量泵就地/远程 |  | digital
FW.J0GAN41AP001RD | 2485 | #1混凝剂计量泵启动指令 |  | digital
FW.J0GAN41AP001RP | 2486 | #1混凝剂计量泵在运行 |  | digital
FW.J0GAN41AP001TD | 2487 | #1混凝剂计量泵停止指令 |  | digital
FW.J0GAN42AP001_F | 2488 | Ovation Control Builder |  | digital
FW.J0GAN42AP001_LP | 2489 | #2混凝剂计量泵 |  | int32
FW.J0GAN42AP001_MODE | 2490 | Ovation Control Builder |  | int32
FW.J0GAN42AP001_SPO | 2491 | Ovation Control Builder |  | float32
FW.J0GAN42AP001C | 2492 | #2混凝剂计量泵变频器频率控制 | Hz | float32
FW.J0GAN42AP001F | 2493 | #2混凝剂计量泵故障 |  | digital
FW.J0GAN42AP001P | 2494 | #2混凝剂计量泵变频器频率反馈 | Hz | float32
FW.J0GAN42AP001RC | 2495 | #2混凝剂计量泵就地/远程 |  | digital
FW.J0GAN42AP001RD | 2496 | #2混凝剂计量泵启动指令 |  | digital
FW.J0GAN42AP001RP | 2497 | #2混凝剂计量泵在运行 |  | digital
FW.J0GAN42AP001TD | 2498 | #2混凝剂计量泵停止指令 |  | digital
FW.J0GAN43AP001_F | 2499 | Ovation Control Builder |  | digital
FW.J0GAN43AP001_LP | 2500 | #3混凝剂计量泵 |  | int32
FW.J0GAN43AP001_MODE | 2501 | Ovation Control Builder |  | int32
FW.J0GAN43AP001_SPO | 2502 | Ovation Control Builder |  | float32
FW.J0GAN43AP001C | 2503 | #3混凝剂计量泵变频器频率控制 | Hz | float32
FW.J0GAN43AP001F | 2504 | #3混凝剂计量泵故障 |  | digital
FW.J0GAN43AP001P | 2505 | #3混凝剂计量泵变频器频率反馈 | Hz | float32
FW.J0GAN43AP001RC | 2506 | #3混凝剂计量泵就地/远程 |  | digital
FW.J0GAN43AP001RD | 2507 | #3混凝剂计量泵启动指令 |  | digital
FW.J0GAN43AP001RP | 2508 | #3混凝剂计量泵在运行 |  | digital
FW.J0GAN43AP001TD | 2509 | #3混凝剂计量泵停止指令 |  | digital
FW.J0GAN44AP001_F | 2510 | Ovation Control Builder |  | digital
FW.J0GAN44AP001_LP | 2511 | #1助凝剂计量泵 |  | int32
FW.J0GAN44AP001_MODE | 2512 | Ovation Control Builder |  | int32
FW.J0GAN44AP001_SPO | 2513 | Ovation Control Builder |  | float32
FW.J0GAN44AP001C | 2514 | #1助凝剂计量泵变频器频率控制 | Hz | float32
FW.J0GAN44AP001F | 2515 | #1助凝剂计量泵故障 |  | digital
FW.J0GAN44AP001P | 2516 | #1助凝剂计量泵变频器频率反馈 | Hz | float32
FW.J0GAN44AP001RC | 2517 | #1助凝剂计量泵就地/远程 |  | digital
FW.J0GAN44AP001RD | 2518 | #1助凝剂计量泵启动指令 |  | digital
FW.J0GAN44AP001RP | 2519 | #1助凝剂计量泵在运行 |  | digital
FW.J0GAN44AP001TD | 2520 | #1助凝剂计量泵停止指令 |  | digital
FW.J0GAN45AP001_F | 2521 | Ovation Control Builder |  | digital
FW.J0GAN45AP001_LP | 2522 | #2助凝剂计量泵 |  | int32
FW.J0GAN45AP001_MODE | 2523 | Ovation Control Builder |  | int32
FW.J0GAN45AP001_SPO | 2524 | Ovation Control Builder |  | float32
FW.J0GAN45AP001C | 2525 | #2助凝剂计量泵变频器频率控制 | Hz | float32
FW.J0GAN45AP001F | 2526 | #2助凝剂计量泵故障 |  | digital
FW.J0GAN45AP001P | 2527 | #2助凝剂计量泵变频器频率反馈 | Hz | float32
FW.J0GAN45AP001RC | 2528 | #2助凝剂计量泵就地/远程 |  | digital
FW.J0GAN45AP001RD | 2529 | #2助凝剂计量泵启动指令 |  | digital
FW.J0GAN45AP001RP | 2530 | #2助凝剂计量泵在运行 |  | digital
FW.J0GAN45AP001TD | 2531 | #2助凝剂计量泵停止指令 |  | digital
FW.J0GAN46AP001_F | 2532 | Ovation Control Builder |  | digital
FW.J0GAN46AP001_LP | 2533 | #3助凝剂计量泵 |  | int32
FW.J0GAN46AP001_MODE | 2534 | Ovation Control Builder |  | int32
FW.J0GAN46AP001_SPO | 2535 | Ovation Control Builder |  | float32
FW.J0GAN46AP001C | 2536 | #3助凝剂计量泵变频器频率控制 | Hz | float32
FW.J0GAN46AP001F | 2537 | #3助凝剂计量泵故障 |  | digital
FW.J0GAN46AP001P | 2538 | #3助凝剂计量泵变频器频率反馈 | Hz | float32
FW.J0GAN46AP001RC | 2539 | #3助凝剂计量泵就地/远程 |  | digital
FW.J0GAN46AP001RD | 2540 | #3助凝剂计量泵启动指令 |  | digital
FW.J0GAN46AP001RP | 2541 | #3助凝剂计量泵在运行 |  | digital
FW.J0GAN46AP001TD | 2542 | #3助凝剂计量泵停止指令 |  | digital
FW.J0GAP02CP101 | 2543 | 罗茨风机出口压力 | Mpa | float32
FW.J0GAP11AA001_AC | 2544 | 罗茨风机出口母管疏水门顺控停 |  | digital
FW.J0GAP11AA001_AO | 2545 | 罗茨风机出口母管疏水门顺控启 |  | digital
FW.J0GAP11AA001_LP | 2546 | 罗茨风机出口母管疏水气动门 |  | int32
FW.J0GAP11AA001CD | 2547 | 罗茨风机出口母管疏水门关指令 |  | digital
FW.J0GAP11AA001CP | 2548 | 罗茨风机出口母管疏水气动门全关 |  | digital
FW.J0GAP11AA001OD | 2549 | 罗茨风机出口母管疏水门打开指令 |  | digital
FW.J0GAP11AA001OP | 2550 | 罗茨风机出口母管疏水气动门全开 |  | digital
FW.J0GAP11AA001RC | 2551 | 罗茨风机出口母管疏水门远方 |  | digital
FW.J0GAP23AA002_AC | 2552 | #1重力滤池反洗门顺控停 |  | digital
FW.J0GAP23AA002_AO | 2553 | #1重力滤池反洗门顺控启 |  | digital
FW.J0GAP23AA002_LP | 2554 | #1空气擦洗重力滤池反洗进气门 |  | int32
FW.J0GAP23AA002CD | 2555 | #1空气擦洗重力池反洗进气门关 |  | digital
FW.J0GAP23AA002CP | 2556 | #1空气擦洗重力池反洗进气门全关 |  | digital
FW.J0GAP23AA002OD | 2557 | #1空气擦洗重力池反洗进气门打开 |  | digital
FW.J0GAP23AA002OP | 2558 | #1空气擦洗重力池反洗进气门全开 |  | digital
FW.J0GAP23AA002RC | 2559 | #1空气擦洗重力池反洗进气门远方 |  | digital
FW.J0GAP24AA002_AC | 2560 | #2重力滤池反洗门顺控停 |  | digital
FW.J0GAP24AA002_AO | 2561 | #2重力滤池反洗门顺控启 |  | digital
FW.J0GAP24AA002_LP | 2562 | #2空气擦洗重力滤池反洗进气门 |  | int32
FW.J0GAP24AA002CD | 2563 | #2空气擦洗重力池反洗进气门关 |  | digital
FW.J0GAP24AA002CP | 2564 | #2空气擦洗重力池反洗进气门全关 |  | digital
FW.J0GAP24AA002OD | 2565 | #2空气擦洗重力池反洗进气门打开 |  | digital
FW.J0GAP24AA002OP | 2566 | #2空气擦洗重力池反洗进气门全开 |  | digital
FW.J0GAP24AA002RC | 2567 | #2空气擦洗重力池反洗进气门远方 |  | digital
FW.J0GAP25AA002_AC | 2568 | #3重力滤池反洗门顺控停 |  | digital
FW.J0GAP25AA002_AO | 2569 | #3重力滤池反洗门顺控启 |  | digital
FW.J0GAP25AA002_LP | 2570 | #3空气擦洗重力滤池反洗进气门 |  | int32
FW.J0GAP25AA002CD | 2571 | #3空气擦洗重力池反洗进气门关 |  | digital
FW.J0GAP25AA002CP | 2572 | #3空气擦洗重力池反洗进气门全关 |  | digital
FW.J0GAP25AA002OD | 2573 | #3空气擦洗重力池反洗进气门打开 |  | digital
FW.J0GAP25AA002OP | 2574 | #3空气擦洗重力池反洗进气门全开 |  | digital
FW.J0GAP25AA002RC | 2575 | #3空气擦洗重力池反洗进气门远方 |  | digital
FW.J0GAX11CP101 | 2576 | 净水站压缩空气储罐压力 | Mpa | float32
FW.J0GBS01AP001_CHOOSE | 2577 | #1排泥池提升泵备用投入 |  | digital
FW.J0GBS01AP001_LP | 2578 | #1排泥池提升泵 |  | int32
FW.J0GBS01AP001PF | 2579 | #1排泥池提升泵综合故障 |  | digital
FW.J0GBS01AP001RC | 2580 | #1排泥池提升泵远方控制 |  | digital
FW.J0GBS01AP001RD | 2581 | #1排泥池提升泵启动指令 |  | digital
FW.J0GBS01AP001RP | 2582 | #1排泥池提升泵在运行 |  | digital
FW.J0GBS01AP001TD | 2583 | #1排泥池提升泵停止指令 |  | digital
FW.J0GBS01CL101 | 2584 | 排泥池液位 | m | float32
FW.J0GBS02AP001_CHOOSE | 2585 | #2排泥池提升泵备用投入 |  | digital
FW.J0GBS02AP001_LP | 2586 | #2排泥池提升泵 |  | int32
FW.J0GBS02AP001PF | 2587 | #2排泥池提升泵综合故障 |  | digital
FW.J0GBS02AP001RC | 2588 | #2排泥池提升泵远方控制 |  | digital
FW.J0GBS02AP001RD | 2589 | #2排泥池提升泵启动指令 |  | digital
FW.J0GBS02AP001RP | 2590 | #2排泥池提升泵在运行 |  | digital
FW.J0GBS02AP001TD | 2591 | #2排泥池提升泵停止指令 |  | digital
FW.J0GBS02CP101 | 2592 | 排泥池提升泵出口压力 | Mpa | float32
FW.J0GCB11AA001_LP | 2593 | #1超滤装置进水气动门 |  | int32
FW.J0GCB11AA001CD | 2594 | #1超滤装置进水气动门关闭 |  | digital
FW.J0GCB11AA001CP | 2595 | #1超滤装置进水气动门关到位 |  | digital
FW.J0GCB11AA001OD | 2596 | #1超滤装置进水气动门开启 |  | digital
FW.J0GCB11AA001OP | 2597 | #1超滤装置进水气动门开到位 |  | digital
FW.J0GCB11AA002_LP | 2598 | #1超滤装置出水气动门 |  | int32
FW.J0GCB11AA002CD | 2599 | #1超滤装置出水气动门关闭 |  | digital
FW.J0GCB11AA002CP | 2600 | #1超滤装置出水气动门关到位 |  | digital
FW.J0GCB11AA002OD | 2601 | #1超滤装置出水气动门开启 |  | digital
FW.J0GCB11AA002OP | 2602 | #1超滤装置出水气动门开到位 |  | digital
FW.J0GCB11AA005_LP | 2603 | #1超滤装置反洗气动门 |  | int32
FW.J0GCB11AA005CD | 2604 | #1超滤装置反洗气动门关闭 |  | digital
FW.J0GCB11AA005CP | 2605 | #1超滤装置反洗气动门关到位 |  | digital
FW.J0GCB11AA005OD | 2606 | #1超滤装置反洗气动门开启 |  | digital
FW.J0GCB11AA005OP | 2607 | #1超滤装置反洗气动门开到位 |  | digital
FW.J0GCB11AA006_LP | 2608 | #1超滤装置进气气动门 |  | int32
FW.J0GCB11AA006CD | 2609 | #1超滤装置进气气动门关闭 |  | digital
FW.J0GCB11AA006CP | 2610 | #1超滤装置进气气动门关到位 |  | digital
FW.J0GCB11AA006OD | 2611 | #1超滤装置进气气动门开启 |  | digital
FW.J0GCB11AA006OP | 2612 | #1超滤装置进气气动门开到位 |  | digital
FW.J0GCB11AA401_LP | 2613 | #1超滤装置反洗下排水门 |  | int32
FW.J0GCB11AA401CD | 2614 | #1超滤反洗下排水门关闭 |  | digital
FW.J0GCB11AA401CP | 2615 | #1超滤反洗下排水门关到位 |  | digital
FW.J0GCB11AA401OD | 2616 | #1超滤反洗下排水门开启 |  | digital
FW.J0GCB11AA401OP | 2617 | #1超滤反洗下排水门开到位 |  | digital
FW.J0GCB11AA402_LP | 2618 | #1超滤装置反洗上排水门 |  | int32
FW.J0GCB11AA402CD | 2619 | #1超滤反洗上排水门关闭 |  | digital
FW.J0GCB11AA402CP | 2620 | #1超滤反洗上排水门关到位 |  | digital
FW.J0GCB11AA402OD | 2621 | #1超滤反洗上排水门开启 |  | digital
FW.J0GCB11AA402OP | 2622 | #1超滤反洗上排水门开到位 |  | digital
FW.J0GCB11AA403_LP | 2623 | #1超滤装置废洗排水气动门 |  | int32
FW.J0GCB11AA403CD | 2624 | #1超滤装置药洗排水门关闭 |  | digital
FW.J0GCB11AA403CP | 2625 | #1超滤装置药洗排水门关到位 |  | digital
FW.J0GCB11AA403OD | 2626 | #1超滤装置药洗排水门开启 |  | digital
FW.J0GCB11AA403OP | 2627 | #1超滤装置药洗排水门开到位 |  | digital
FW.J0GCB11CF101 | 2628 | #1超滤装置出水流量 |  | float32
FW.J0GCB11CF101L | 2629 | #1超滤装置出水流量累计 |  | float32
FW.J0GCB11CQ101 | 2630 | #1超滤装置出水浊度 | Hz | float32
FW.J0GCB11GF001_LPIN1 | 2631 | Ovation Control Builder |  | int32
FW.J0GCB11GF001_LPOUT1 | 2632 | Ovation Control Builder |  | int32
FW.J0GCB11GF001PF | 2633 | #1超滤门箱电源故障 |  | digital
FW.J0GCB12AA001_LP | 2634 | #2超滤装置进水气动门 |  | int32
FW.J0GCB12AA001CD | 2635 | #2超滤装置进水气动门关闭 |  | digital
FW.J0GCB12AA001CP | 2636 | #2超滤装置进水气动门关到位 |  | digital
FW.J0GCB12AA001OD | 2637 | #2超滤装置进水气动门开启 |  | digital
FW.J0GCB12AA001OP | 2638 | #2超滤装置进水气动门开到位 |  | digital
FW.J0GCB12AA002_LP | 2639 | #2超滤装置出水气动门 |  | int32
FW.J0GCB12AA002CD | 2640 | #2超滤装置出水气动门关闭 |  | digital
FW.J0GCB12AA002CP | 2641 | #2超滤装置出水气动门关到位 |  | digital
FW.J0GCB12AA002OD | 2642 | #2超滤装置出水气动门开启 |  | digital
FW.J0GCB12AA002OP | 2643 | #2超滤装置出水气动门开到位 |  | digital
FW.J0GCB12AA005_LP | 2644 | #2超滤装置反洗气动门 |  | int32
FW.J0GCB12AA005CD | 2645 | #2超滤装置反洗气动门关闭 |  | digital
FW.J0GCB12AA005CP | 2646 | #2超滤装置反洗气动门关到位 |  | digital
FW.J0GCB12AA005OD | 2647 | #2超滤装置反洗气动门开启 |  | digital
FW.J0GCB12AA005OP | 2648 | #2超滤装置反洗气动门开到位 |  | digital
FW.J0GCB12AA006_LP | 2649 | #2超滤装置进气气动门 |  | int32
FW.J0GCB12AA006CD | 2650 | #2超滤装置进气气动门关闭 |  | digital
FW.J0GCB12AA006CP | 2651 | #2超滤装置进气气动门关到位 |  | digital
FW.J0GCB12AA006OD | 2652 | #2超滤装置进气气动门开启 |  | digital
FW.J0GCB12AA006OP | 2653 | #2超滤装置进气气动门开到位 |  | digital
FW.J0GCB12AA401_LP | 2654 | #2超滤反洗下排水门 |  | int32
FW.J0GCB12AA401CD | 2655 | #2超滤反洗下排水门关闭 |  | digital
FW.J0GCB12AA401CP | 2656 | #2超滤反洗下排水门关到位 |  | digital
FW.J0GCB12AA401OD | 2657 | #2超滤反洗下排水门开启 |  | digital
FW.J0GCB12AA401OP | 2658 | #2超滤反洗下排水门开到位 |  | digital
FW.J0GCB12AA402_LP | 2659 | #2超滤装置反洗上排水门 |  | int32
FW.J0GCB12AA402CD | 2660 | #2超滤装置反洗上排水门关闭 |  | digital
FW.J0GCB12AA402CP | 2661 | #2超滤装置反洗上排水门关到位 |  | digital
FW.J0GCB12AA402OD | 2662 | #2超滤装置反洗上排水门开启 |  | digital
FW.J0GCB12AA402OP | 2663 | #2超滤装置反洗上排水门开到位 |  | digital
FW.J0GCB12AA403_LP | 2664 | #2超滤装置废洗排水气动门 |  | int32
FW.J0GCB12AA403CD | 2665 | #2超滤装置药洗排水门关闭 |  | digital
FW.J0GCB12AA403CP | 2666 | #2超滤装置药洗排水门关到位 |  | digital
FW.J0GCB12AA403OD | 2667 | #2超滤装置药洗排水门开启 |  | digital
FW.J0GCB12AA403OP | 2668 | #2超滤装置药洗排水门开到位 |  | digital
FW.J0GCB12CF101 | 2669 | #2超滤装置出水流量 |  | float32
FW.J0GCB12CF101L | 2670 | #2超滤装置出水流量累计 |  | float32
FW.J0GCB12CQ101 | 2671 | #2超滤装置出水浊度 | Hz | float32
FW.J0GCB12GF001_LPIN1 | 2672 | Ovation Control Builder |  | int32
FW.J0GCB12GF001_LPOUT1 | 2673 | Ovation Control Builder |  | int32
FW.J0GCB12GF001PF | 2674 | #2超滤门箱电源故障 |  | digital
FW.J0GCB13AA001_LP | 2675 | #3超滤装置进水气动门 |  | int32
FW.J0GCB13AA001CD | 2676 | #3超滤装置进水气动门关闭 |  | digital
FW.J0GCB13AA001CP | 2677 | #3超滤装置进水气动门关到位 |  | digital
FW.J0GCB13AA001OD | 2678 | #3超滤装置进水气动门开启 |  | digital
FW.J0GCB13AA001OP | 2679 | #3超滤装置进水气动门开到位 |  | digital
FW.J0GCB13AA002_LP | 2680 | #3超滤装置出水气动门 |  | int32
FW.J0GCB13AA002CD | 2681 | #3超滤装置出水气动门关闭 |  | digital
FW.J0GCB13AA002CP | 2682 | #3超滤装置出水气动门关到位 |  | digital
FW.J0GCB13AA002OD | 2683 | #3超滤装置出水气动门开启 |  | digital
FW.J0GCB13AA002OP | 2684 | #3超滤装置出水气动门开到位 |  | digital
FW.J0GCB13AA005_LP | 2685 | #3超滤装置反洗气动门 |  | int32
FW.J0GCB13AA005CD | 2686 | #3超滤装置反洗气动门关闭 |  | digital
FW.J0GCB13AA005CP | 2687 | #3超滤装置反洗气动门关到位 |  | digital
FW.J0GCB13AA005OD | 2688 | #3超滤装置反洗气动门开启 |  | digital
FW.J0GCB13AA005OP | 2689 | #3超滤装置反洗气动门开到位 |  | digital
FW.J0GCB13AA006_LP | 2690 | #3超滤装置进气气动门 |  | int32
FW.J0GCB13AA006CD | 2691 | #3超滤装置进气气动门关闭 |  | digital
FW.J0GCB13AA006CP | 2692 | #3超滤装置进气气动门关到位 |  | digital
FW.J0GCB13AA006OD | 2693 | #3超滤装置进气气动门开启 |  | digital
FW.J0GCB13AA006OP | 2694 | #3超滤装置进气气动门开到位 |  | digital
FW.J0GCB13AA401_LP | 2695 | #3超滤反洗下排水门 |  | int32
FW.J0GCB13AA401CD | 2696 | #3超滤反洗下排水门关闭 |  | digital
FW.J0GCB13AA401CP | 2697 | #3超滤反洗下排水门关到位 |  | digital
FW.J0GCB13AA401OD | 2698 | #3超滤反洗下排水门开启 |  | digital
FW.J0GCB13AA401OP | 2699 | #3超滤反洗下排水门开到位 |  | digital
FW.J0GCB13AA402_LP | 2700 | #3超滤装置反洗上排水门 |  | int32
FW.J0GCB13AA402CD | 2701 | #3超滤装置反洗上排水门关闭 |  | digital
FW.J0GCB13AA402CP | 2702 | #3超滤装置反洗上排水门关到位 |  | digital
FW.J0GCB13AA402OD | 2703 | #3超滤装置反洗上排水门开启 |  | digital
FW.J0GCB13AA402OP | 2704 | #3超滤装置反洗上排水门开到位 |  | digital
FW.J0GCB13AA403_LP | 2705 | #3超滤装置废洗排水气动门 |  | int32
FW.J0GCB13AA403CD | 2706 | #3超滤装置药洗排水门关闭 |  | digital
FW.J0GCB13AA403CP | 2707 | #3超滤装置药洗排水门关到位 |  | digital
FW.J0GCB13AA403OD | 2708 | #3超滤装置药洗排水门开启 |  | digital
FW.J0GCB13AA403OP | 2709 | #3超滤装置药洗排水门开到位 |  | digital
FW.J0GCB13CF101 | 2710 | #3超滤装置出水流量 |  | float32
FW.J0GCB13CF101L | 2711 | #3超滤装置出水流量累计 |  | float32
FW.J0GCB13CQ101 | 2712 | #3超滤装置出水浊度 | Hz | float32
FW.J0GCB13GF001_LPIN1 | 2713 | Ovation Control Builder |  | int32
FW.J0GCB13GF001_LPOUT1 | 2714 | Ovation Control Builder |  | int32
FW.J0GCB13GF001PF | 2715 | #3超滤门箱电源故障 |  | digital
FW.J0GCB14AA001_LP | 2716 | #4超滤装置进水气动门 |  | int32
FW.J0GCB14AA001CD | 2717 | #4超滤装置进水气动门关闭 |  | digital
FW.J0GCB14AA001CP | 2718 | #4超滤装置进水气动门关到位 |  | digital
FW.J0GCB14AA001OD | 2719 | #4超滤装置进水气动门开启 |  | digital
FW.J0GCB14AA001OP | 2720 | #4超滤装置进水气动门开到位 |  | digital
FW.J0GCB14AA002_LP | 2721 | #4超滤装置出水气动门 |  | int32
FW.J0GCB14AA002CD | 2722 | #4超滤装置出水气动门关闭 |  | digital
FW.J0GCB14AA002CP | 2723 | #4超滤装置出水气动门关到位 |  | digital
FW.J0GCB14AA002OD | 2724 | #4超滤装置出水气动门开启 |  | digital
FW.J0GCB14AA002OP | 2725 | #4超滤装置出水气动门开到位 |  | digital
FW.J0GCB14AA005_LP | 2726 | #4超滤装置反洗气动门 |  | int32
FW.J0GCB14AA005CD | 2727 | #4超滤装置反洗气动门关闭 |  | digital
FW.J0GCB14AA005CP | 2728 | #4超滤装置反洗气动门关到位 |  | digital
FW.J0GCB14AA005OD | 2729 | #4超滤装置反洗气动门开启 |  | digital
FW.J0GCB14AA005OP | 2730 | #4超滤装置反洗气动门开到位 |  | digital
FW.J0GCB14AA006_LP | 2731 | #4超滤装置进气气动门 |  | int32
FW.J0GCB14AA006CD | 2732 | #4超滤装置进气气动门关闭 |  | digital
FW.J0GCB14AA006CP | 2733 | #4超滤装置进气气动门关到位 |  | digital
FW.J0GCB14AA006OD | 2734 | #4超滤装置进气气动门开启 |  | digital
FW.J0GCB14AA006OP | 2735 | #4超滤装置进气气动门开到位 |  | digital
FW.J0GCB14AA401_LP | 2736 | #4超滤装置反洗下排水门 |  | int32
FW.J0GCB14AA401CD | 2737 | #4超滤装置反洗下排水门关闭 |  | digital
FW.J0GCB14AA401CP | 2738 | #4超滤装置反洗下排水门关到位 |  | digital
FW.J0GCB14AA401OD | 2739 | #4超滤装置反洗下排水门开启 |  | digital
FW.J0GCB14AA401OP | 2740 | #4超滤装置反洗下排水门开到位 |  | digital
FW.J0GCB14AA402_LP | 2741 | #4超滤装置反洗上排水门 |  | int32
FW.J0GCB14AA402CD | 2742 | #4超滤装置反洗上排水门关闭 |  | digital
FW.J0GCB14AA402CP | 2743 | #4超滤装置反洗上排水门关到位 |  | digital
FW.J0GCB14AA402OD | 2744 | #4超滤装置反洗上排水门开启 |  | digital
FW.J0GCB14AA402OP | 2745 | #4超滤装置反洗上排水门开到位 |  | digital
FW.J0GCB14AA403_LP | 2746 | #4超滤装置废洗排水气动门 |  | int32
FW.J0GCB14AA403CD | 2747 | #4超滤装置药洗排水门关闭 |  | digital
FW.J0GCB14AA403CP | 2748 | #4超滤装置药洗排水门关到位 |  | digital
FW.J0GCB14AA403OD | 2749 | #4超滤装置药洗排水门开启 |  | digital
FW.J0GCB14AA403OP | 2750 | #4超滤装置药洗排水门开到位 |  | digital
FW.J0GCB14CF101 | 2751 | #4超滤装置出水流量 |  | float32
FW.J0GCB14CF101L | 2752 | #4超滤装置出水流量累计 |  | float32
FW.J0GCB14CQ101 | 2753 | #4超滤装置出水浊度 | Hz | float32
FW.J0GCB14GF001_LPIN1 | 2754 | Ovation Control Builder |  | int32
FW.J0GCB14GF001_LPOUT1 | 2755 | Ovation Control Builder |  | int32
FW.J0GCB14GF001PF | 2756 | #4超滤门箱电源故障 |  | digital
FW.J0GCB21AP001_CHOOSE | 2757 | #1超滤反洗泵选择 |  | digital
FW.J0GCB21AP001_F | 2758 | Ovation Control Builder |  | digital
FW.J0GCB21AP001_LP | 2759 | #1超滤反洗泵 |  | int32
FW.J0GCB21AP001_LP1 | 2760 | Ovation Control Builder |  | int32
FW.J0GCB21AP001_LP2 | 2761 | Ovation Control Builder |  | int32
FW.J0GCB21AP001_MODE | 2762 | Ovation Control Builder |  | int32
FW.J0GCB21AP001_SPO | 2763 | Ovation Control Builder |  | float32
FW.J0GCB21AP001_SPPMT | 2764 | 超滤反洗水泵保护停 |  | digital
FW.J0GCB21AP001_STPMT | 2765 | 超滤反洗水泵启允许 |  | digital
FW.J0GCB21AP001C | 2766 | #1超滤反洗水泵频率给定 |  | float32
FW.J0GCB21AP001CL | 2767 | Ovation Control Builder |  | float32
FW.J0GCB21AP001I | 2768 | Ovation Control Builder |  | float32
FW.J0GCB21AP001IL | 2769 | #1超滤反洗水泵电流 |  | float32
FW.J0GCB21AP001P | 2770 | #1超滤反洗水泵频率反馈 |  | float32
FW.J0GCB21AP001PF | 2771 | #1超滤反洗泵故障 |  | digital
FW.J0GCB21AP001PL | 2772 | Ovation Control Builder |  | float32
FW.J0GCB21AP001RC | 2773 | #1超滤反洗泵远方 |  | digital
FW.J0GCB21AP001RD | 2774 | #1超滤反洗泵启动信号 |  | digital
FW.J0GCB21AP001RP | 2775 | #1超滤反洗泵运行 |  | digital
FW.J0GCB21AP001TD | 2776 | #1超滤反洗泵停止信号 |  | digital
FW.J0GCB22AP001_CHOOSE | 2777 | #2超滤反洗泵选择 |  | digital
FW.J0GCB22AP001_LP | 2778 | #2超滤反洗泵 |  | int32
FW.J0GCB22AP001_LPIN1 | 2779 | Ovation Control Builder |  | int32
FW.J0GCB22AP001_LPOUT1 | 2780 | Ovation Control Builder |  | int32
FW.J0GCB22AP001I | 2781 | Ovation Control Builder |  | float32
FW.J0GCB22AP001IL | 2782 | #2超滤反洗泵电流 |  | float32
FW.J0GCB22AP001RC | 2783 | #2超滤反洗泵远方 |  | digital
FW.J0GCB22AP001RD | 2784 | #2超滤反洗泵启动 |  | digital
FW.J0GCB22AP001RP | 2785 | #2超滤反洗泵运行 |  | digital
FW.J0GCB22AP001TD | 2786 | #2超滤反洗泵停止 |  | digital
FW.J0GCB30CF101 | 2787 | 超滤反洗保安过滤器进口流量 | Hz | float32
FW.J0GCB30CF101L | 2788 | 超滤反洗保安过滤器进口流量累计 |  | float32
FW.J0GCB30CP101 | 2789 | 超滤反洗水泵出口母管压力 | kPa | float32
FW.J0GCB30CP101L | 2790 | 超滤反洗水泵出口母管压力 |  | float32
FW.J0GCB30CP102 | 2791 | 超滤反洗保安过滤器进出口差压 | kPa | float32
FW.J0GCB30CP102L | 2792 | 超滤反洗保安过滤器进出口差压 |  | float32
FW.J0GCB40AP001_LP | 2793 | 反渗透冲洗水泵 |  | int32
FW.J0GCB40AP001_LPIN1 | 2794 | Ovation Control Builder |  | int32
FW.J0GCB40AP001_LPOUT1 | 2795 | Ovation Control Builder |  | int32
FW.J0GCB40AP001_SPPMT | 2796 | 反渗透冲洗水泵保护停 |  | digital
FW.J0GCB40AP001_STPMT | 2797 | 反渗透冲洗水泵启动允许 |  | digital
FW.J0GCB40AP001I | 2798 | Ovation Control Builder |  | float32
FW.J0GCB40AP001IL | 2799 | 反渗透冲洗水泵电流 |  | float32
FW.J0GCB40AP001PF | 2800 | 反渗透冲洗水泵故障 |  | digital
FW.J0GCB40AP001RC | 2801 | 反渗透冲洗水泵远方 |  | digital
FW.J0GCB40AP001RD | 2802 | 反渗透冲洗水泵启动 |  | digital
FW.J0GCB40AP001RP | 2803 | 反渗透冲洗水泵运行 |  | digital
FW.J0GCB40AP001TD | 2804 | 反渗透冲洗水泵停止 |  | digital
FW.J0GCC11CP101 | 2805 | 超滤反洗气罐出口母管压力 | Hz | float32
FW.J0GCC11CP101L | 2806 | 超滤反洗气罐出口母管压力 |  | float32
FW.J0GCC11CP102 | 2807 | 仪表及控制用气罐出口母管压力 | Hz | float32
FW.J0GCC11CP102L | 2808 | 仪表及控制用气罐出口母管压力 |  | float32
FW.J0GCF31AA005_LP | 2809 | #1一级反渗透进冲洗水门 |  | int32
FW.J0GCF31AA005CD | 2810 | #1一级反渗透进冲洗水门关闭 |  | digital
FW.J0GCF31AA005CP | 2811 | #1一级反渗透进冲洗水门关到位 |  | digital
FW.J0GCF31AA005OD | 2812 | #1一级反渗透进冲洗水门开启 |  | digital
FW.J0GCF31AA005OP | 2813 | #1一级反渗透进冲洗水门开到位 |  | digital
FW.J0GCF31AA055_LP | 2814 | #1一级反渗透产水排放门 |  | int32
FW.J0GCF31AA055CD | 2815 | #1一级反渗透产水排放门关闭 |  | digital
FW.J0GCF31AA055CP | 2816 | #1一级反渗透产水排放门关到位 |  | digital
FW.J0GCF31AA055OD | 2817 | #1一级反渗透产水排放门开启 |  | digital
FW.J0GCF31AA055OP | 2818 | #1一级反渗透产水排放门开到位 |  | digital
FW.J0GCF31AA402_LP | 2819 | #1一级反渗透浓水排放门 |  | int32
FW.J0GCF31AA402CD | 2820 | #1一级反渗透浓水排放门关闭 |  | digital
FW.J0GCF31AA402CP | 2821 | #1一级反渗透浓水排放门关到位 |  | digital
FW.J0GCF31AA402OD | 2822 | #1一级反渗透浓水排放门开启 |  | digital
FW.J0GCF31AA402OP | 2823 | #1一级反渗透浓水排放门开到位 |  | digital
FW.J0GCF31CF101 | 2824 | #1一级反渗透产水流量 | Hz | float32
FW.J0GCF31CF101L | 2825 | #1一级反渗透产水流量累计 |  | float32
FW.J0GCF31CF102 | 2826 | #1一级反渗透浓水流量 | Hz | float32
FW.J0GCF31CF102L | 2827 | #1一级反渗透浓水流量累计 |  | float32
FW.J0GCF31CP101 | 2828 | #1一级反渗透进水压力 | kPa | float32
FW.J0GCF31CP101L | 2829 | #1一级反渗透进水压力 |  | float32
FW.J0GCF31CP102 | 2830 | #1一级反渗透一段段间差压 | kPa | float32
FW.J0GCF31CP102L | 2831 | #1一级反渗透一段段间差压 |  | float32
FW.J0GCF31CP103 | 2832 | #1一级反渗透产水压力 | Hz | float32
FW.J0GCF31CP103L | 2833 | #1一级反渗透产水压力 |  | float32
FW.J0GCF31CP104 | 2834 | #1一级反渗透二段段间差压 | kPa | float32
FW.J0GCF31CP104L | 2835 | #1一级反渗透二段段间差压 |  | float32
FW.J0GCF31CQ101 | 2836 | #1一级反渗透装置产水电导率 | Hz | float32
FW.J0GCF31GF001_LPIN1 | 2837 | Ovation Control Builder |  | int32
FW.J0GCF31GF001_LPOUT1 | 2838 | Ovation Control Builder |  | int32
FW.J0GCF31GF001PF | 2839 | #1一级反渗透门箱电源故障 |  | digital
FW.J0GCF32AA005_LP | 2840 | #2一级反渗透进冲洗水门 |  | int32
FW.J0GCF32AA005CD | 2841 | #2一级反渗透进冲洗水门关闭 |  | digital
FW.J0GCF32AA005CP | 2842 | #2一级反渗透进冲洗水门关到位 |  | digital
FW.J0GCF32AA005OD | 2843 | #2一级反渗透进冲洗水门开启 |  | digital
FW.J0GCF32AA005OP | 2844 | #2一级反渗透进冲洗水门开到位 |  | digital
FW.J0GCF32AA055_LP | 2845 | #2一级反渗透产水排放门 |  | int32
FW.J0GCF32AA055CD | 2846 | #2一级反渗透产水排放门关闭 |  | digital
FW.J0GCF32AA055CP | 2847 | #2一级反渗透产水排放门关到位 |  | digital
FW.J0GCF32AA055OD | 2848 | #2一级反渗透产水排放门开启 |  | digital
FW.J0GCF32AA055OP | 2849 | #2一级反渗透产水排放门开到位 |  | digital
FW.J0GCF32AA402_LP | 2850 | #2一级反渗透浓水排放门 |  | int32
FW.J0GCF32AA402CD | 2851 | #2一级反渗透浓水排放门关闭 |  | digital
FW.J0GCF32AA402CP | 2852 | #2一级反渗透浓水排放门关到位 |  | digital
FW.J0GCF32AA402OD | 2853 | #2一级反渗透浓水排放门开启 |  | digital
FW.J0GCF32AA402OP | 2854 | #2一级反渗透浓水排放门开到位 |  | digital
FW.J0GCF32CF101 | 2855 | #2一级反渗透产水流量 | Hz | float32
FW.J0GCF32CF101L | 2856 | #2一级反渗透产水流量累计 |  | float32
FW.J0GCF32CF102 | 2857 | #2一级反渗透浓水流量 | Hz | float32
FW.J0GCF32CF102L | 2858 | #2一级反渗透浓水流量累计 |  | float32
FW.J0GCF32CP101 | 2859 | #2一级反渗透进水压力 | kPa | float32
FW.J0GCF32CP101L | 2860 | #2一级反渗透进水压力 |  | float32
FW.J0GCF32CP102 | 2861 | #2一级反渗透一段段间差压 | kPa | float32
FW.J0GCF32CP102L | 2862 | #2一级反渗透一段段间差压 |  | float32
FW.J0GCF32CP103 | 2863 | #2一级反渗透产水压力 | Hz | float32
FW.J0GCF32CP103L | 2864 | #2一级反渗透产水压力 |  | float32
FW.J0GCF32CP104 | 2865 | #2一级反渗透二段段间差压 | kPa | float32
FW.J0GCF32CP104L | 2866 | #2一级反渗透二段段间差压 |  | float32
FW.J0GCF32CQ101 | 2867 | #2一级反渗透装置产水电导率 | Hz | float32
FW.J0GCF32GF001_LPIN1 | 2868 | Ovation Control Builder |  | int32
FW.J0GCF32GF001_LPOUT1 | 2869 | Ovation Control Builder |  | int32
FW.J0GCF32GF001PF | 2870 | #2一级反渗透门箱电源故障 |  | digital
FW.J0GCF33AA005_LP | 2871 | #3一级反渗透进冲洗水门 |  | int32
FW.J0GCF33AA005CD | 2872 | #3一级反渗透进冲洗水门关闭 |  | digital
FW.J0GCF33AA005CP | 2873 | #3一级反渗透进冲洗水门关到位 |  | digital
FW.J0GCF33AA005OD | 2874 | #3一级反渗透进冲洗水门开启 |  | digital
FW.J0GCF33AA005OP | 2875 | #3一级反渗透进冲洗水门开到位 |  | digital
FW.J0GCF33AA055_LP | 2876 | #3一级反渗透产水排放门 |  | int32
FW.J0GCF33AA055CD | 2877 | #3一级反渗透产水排放门关闭 |  | digital
FW.J0GCF33AA055CP | 2878 | #3一级反渗透产水排放门关到位 |  | digital
FW.J0GCF33AA055OD | 2879 | #3一级反渗透产水排放门开启 |  | digital
FW.J0GCF33AA055OP | 2880 | #3一级反渗透产水排放门开到位 |  | digital
FW.J0GCF33AA402_LP | 2881 | #3一级反渗透浓水排放门 |  | int32
FW.J0GCF33AA402CD | 2882 | #3一级反渗透浓水排放门关闭 |  | digital
FW.J0GCF33AA402CP | 2883 | #3一级反渗透浓水排放门关到位 |  | digital
FW.J0GCF33AA402OD | 2884 | #3一级反渗透浓水排放门开启 |  | digital
FW.J0GCF33AA402OP | 2885 | #3一级反渗透浓水排放门开到位 |  | digital
FW.J0GCF33CF101 | 2886 | #3一级反渗透产水流量 | Hz | float32
FW.J0GCF33CF101L | 2887 | #3一级反渗透产水流量累计 |  | float32
FW.J0GCF33CF102 | 2888 | #3一级反渗透浓水流量 | Hz | float32
FW.J0GCF33CF102L | 2889 | #3一级反渗透浓水流量累计 |  | float32
FW.J0GCF33CP101 | 2890 | #3一级反渗透进水压力 | kPa | float32
FW.J0GCF33CP101L | 2891 | #3一级反渗透进水压力 |  | float32
FW.J0GCF33CP102 | 2892 | #3一级反渗透一段段间差压 | kPa | float32
FW.J0GCF33CP102L | 2893 | #3一级反渗透一段段间差压 |  | float32
FW.J0GCF33CP103 | 2894 | #3一级反渗透产水压力 | Hz | float32
FW.J0GCF33CP103L | 2895 | #3一级反渗透产水压力 |  | float32
FW.J0GCF33CP104 | 2896 | #3一级反渗透二段段间差压 | kPa | float32
FW.J0GCF33CP104L | 2897 | #3一级反渗透二段段间差压 |  | float32
FW.J0GCF33CQ101 | 2898 | #3一级反渗透装置产水电导率 | Hz | float32
FW.J0GCF33GF001_LPIN1 | 2899 | Ovation Control Builder |  | int32
FW.J0GCF33GF001_LPOUT1 | 2900 | Ovation Control Builder |  | int32
FW.J0GCF33GF001PF | 2901 | #3一级反渗透门箱电源故障 |  | digital
FW.J0GCF34AA005_LP | 2902 | #4一级反渗透进冲洗水门 |  | int32
FW.J0GCF34AA005CD | 2903 | #4一级反渗透进冲洗水门关闭 |  | digital
FW.J0GCF34AA005CP | 2904 | #4一级反渗透进冲洗水门关到位 |  | digital
FW.J0GCF34AA005OD | 2905 | #4一级反渗透进冲洗水门开启 |  | digital
FW.J0GCF34AA005OP | 2906 | #4一级反渗透进冲洗水门开到位 |  | digital
FW.J0GCF34AA055_LP | 2907 | #4一级反渗透产水排放门 |  | int32
FW.J0GCF34AA055CD | 2908 | #4一级反渗透产水排放门关闭 |  | digital
FW.J0GCF34AA055CP | 2909 | #4一级反渗透产水排放门关到位 |  | digital
FW.J0GCF34AA055OD | 2910 | #4一级反渗透产水排放门开启 |  | digital
FW.J0GCF34AA055OP | 2911 | #4一级反渗透产水排放门开到位 |  | digital
FW.J0GCF34AA402_LP | 2912 | #4一级反渗透浓水排放门 |  | int32
FW.J0GCF34AA402CD | 2913 | #4一级反渗透浓水排放门关闭 |  | digital
FW.J0GCF34AA402CP | 2914 | #4一级反渗透浓水排放门关到位 |  | digital
FW.J0GCF34AA402OD | 2915 | #4一级反渗透浓水排放门开启 |  | digital
FW.J0GCF34AA402OP | 2916 | #4一级反渗透浓水排放门开到位 |  | digital
FW.J0GCF34CF101 | 2917 | #4一级反渗透产水流量 | Hz | float32
FW.J0GCF34CF101L | 2918 | #4一级反渗透产水流量累计 |  | float32
FW.J0GCF34CF102 | 2919 | #4一级反渗透浓水流量 | Hz | float32
FW.J0GCF34CF102L | 2920 | #4一级反渗透浓水流量累计 |  | float32
FW.J0GCF34CP101 | 2921 | #4一级反渗透进水压力 | kPa | float32
FW.J0GCF34CP101L | 2922 | #4一级反渗透进水压力 |  | float32
FW.J0GCF34CP102 | 2923 | #4一级反渗透一段段间差压 | kPa | float32
FW.J0GCF34CP102L | 2924 | #4一级反渗透一段段间差压 |  | float32
FW.J0GCF34CP103 | 2925 | #4一级反渗透产水压力 | Hz | float32
FW.J0GCF34CP103L | 2926 | #4一级反渗透产水压力 |  | float32
FW.J0GCF34CP104 | 2927 | #4一级反渗透二段段间差压 | kPa | float32
FW.J0GCF34CP104L | 2928 | #4一级反渗透二段段间差压 |  | float32
FW.J0GCF34CQ101 | 2929 | #4一级反渗透装置产水电导率 | Hz | float32
FW.J0GCF34GF001_LPIN1 | 2930 | Ovation Control Builder |  | int32
FW.J0GCF34GF001_LPOUT1 | 2931 | Ovation Control Builder |  | int32
FW.J0GCF34GF001PF | 2932 | #4一级反渗透门箱电源故障 |  | digital
FW.J0GCF40CQ102 | 2933 | 一级反渗透产水箱进口母管PH值 | Hz | float32
FW.J0GCF41AA005_LP | 2934 | #1二级反渗透冲洗水门 |  | int32
FW.J0GCF41AA005CD | 2935 | #1二级反渗透冲洗水门关闭 |  | digital
FW.J0GCF41AA005CP | 2936 | #1二级反渗透冲洗水门关到位 |  | digital
FW.J0GCF41AA005OD | 2937 | #1二级反渗透冲洗水门开启 |  | digital
FW.J0GCF41AA005OP | 2938 | #1二级反渗透冲洗水门开到位 |  | digital
FW.J0GCF41AA401_LP | 2939 | #1二级反渗透产水排放门 |  | int32
FW.J0GCF41AA401CD | 2940 | #1二级反渗透产水排放门关闭 |  | digital
FW.J0GCF41AA401CP | 2941 | #1二级反渗透产水排放门关到位 |  | digital
FW.J0GCF41AA401OD | 2942 | #1二级反渗透产水排放门开启 |  | digital
FW.J0GCF41AA401OP | 2943 | #1二级反渗透产水排放门开到位 |  | digital
FW.J0GCF41AA402_LP | 2944 | #1二级反渗透浓水排放门 |  | int32
FW.J0GCF41AA402CD | 2945 | #1二级反渗透浓水排放门关闭 |  | digital
FW.J0GCF41AA402CP | 2946 | #1二级反渗透浓水排放门关到位 |  | digital
FW.J0GCF41AA402OD | 2947 | #1二级反渗透浓水排放门开启 |  | digital
FW.J0GCF41AA402OP | 2948 | #1二级反渗透浓水排放门开到位 |  | digital
FW.J0GCF41CF101 | 2949 | #1二级反渗透装置产水流量 | Hz | float32
FW.J0GCF41CF101L | 2950 | #1二级反渗透装置产水流量累计 |  | float32
FW.J0GCF41CF102 | 2951 | #1二级反渗透装置浓水流量 | Hz | float32
FW.J0GCF41CF102L | 2952 | #1二级反渗透装置浓水流量累计 |  | float32
FW.J0GCF41CP101 | 2953 | #1二级反渗透装置进水压力 | kPa | float32
FW.J0GCF41CP101L | 2954 | #1二级反渗透装置进水压力 |  | float32
FW.J0GCF41CP102 | 2955 | #1二级反渗透装置产水压力 | Hz | float32
FW.J0GCF41CP102L | 2956 | #1二级反渗透装置产水压力 |  | float32
FW.J0GCF41CP103 | 2957 | #1二级RO装置进水与段间差压 | kPa | float32
FW.J0GCF41CP103L | 2958 | #1二级RO装置进水与段间差压 |  | float32
FW.J0GCF41CP104 | 2959 | #1二级RO装置段间与浓水差压 | kPa | float32
FW.J0GCF41CP104L | 2960 | #1二级RO装置段间与浓水差压 |  | float32
FW.J0GCF41CQ101 | 2961 | #1二级反渗透装置产水电导率 | Hz | float32
FW.J0GCF41GF001_LPIN1 | 2962 | Ovation Control Builder |  | int32
FW.J0GCF41GF001_LPOUT1 | 2963 | Ovation Control Builder |  | int32
FW.J0GCF41GF001PF | 2964 | #1二级反渗透门箱电源故障 |  | digital
FW.J0GCF42AA005_LP | 2965 | #2二级反渗透冲洗水门 |  | int32
FW.J0GCF42AA005CD | 2966 | #2二级反渗透冲洗水门关闭 |  | digital
FW.J0GCF42AA005CP | 2967 | #2二级反渗透冲洗水门关到位 |  | digital
FW.J0GCF42AA005OD | 2968 | #2二级反渗透冲洗水门开启 |  | digital
FW.J0GCF42AA005OP | 2969 | #2二级反渗透冲洗水门开到位 |  | digital
FW.J0GCF42AA401_LP | 2970 | #2二级反渗透产水排放门 |  | int32
FW.J0GCF42AA401CD | 2971 | #2二级反渗透产水排放门关闭 |  | digital
FW.J0GCF42AA401CP | 2972 | #2二级反渗透产水排放门关到位 |  | digital
FW.J0GCF42AA401OD | 2973 | #2二级反渗透产水排放门开启 |  | digital
FW.J0GCF42AA401OP | 2974 | #2二级反渗透产水排放门开到位 |  | digital
FW.J0GCF42AA402_LP | 2975 | #2二级反渗透浓水排放门 |  | int32
FW.J0GCF42AA402CD | 2976 | #2二级反渗透浓水排放门关闭 |  | digital
FW.J0GCF42AA402CP | 2977 | #2二级反渗透浓水排放门关到位 |  | digital
FW.J0GCF42AA402OD | 2978 | #2二级反渗透浓水排放门开启 |  | digital
FW.J0GCF42AA402OP | 2979 | #2二级反渗透浓水排放门开到位 |  | digital
FW.J0GCF42CF101 | 2980 | #2二级反渗透装置产水流量 | Hz | float32
FW.J0GCF42CF101L | 2981 | #2二级反渗透装置产水流量累计 |  | float32
FW.J0GCF42CF102 | 2982 | #2二级反渗透装置浓水流量 | Hz | float32
FW.J0GCF42CF102L | 2983 | #2二级反渗透装置浓水流量累计 |  | float32
FW.J0GCF42CP101 | 2984 | #2二级反渗透装置进水压力 | kPa | float32
FW.J0GCF42CP101L | 2985 | #2二级反渗透装置进水压力 |  | float32
FW.J0GCF42CP102 | 2986 | #2二级反渗透装置产水压力 | Hz | float32
FW.J0GCF42CP102L | 2987 | #2二级反渗透装置产水压力 |  | float32
FW.J0GCF42CP103 | 2988 | #2二级RO装置进水与段间差压 | kPa | float32
FW.J0GCF42CP103L | 2989 | #2二级RO装置进水与段间差压 |  | float32
FW.J0GCF42CP104 | 2990 | #2二级RO装置段间与浓水差压 | kPa | float32
FW.J0GCF42CP104L | 2991 | #2二级RO装置段间与浓水差压 |  | float32
FW.J0GCF42CQ101 | 2992 | #2二级反渗透装置产水电导率 | Hz | float32
FW.J0GCF42GF001_LPIN1 | 2993 | Ovation Control Builder |  | int32
FW.J0GCF42GF001_LPOUT1 | 2994 | Ovation Control Builder |  | int32
FW.J0GCF42GF001PF | 2995 | #2二级反渗透门箱电源故障 |  | digital
FW.J0GCF43AA005_LP | 2996 | #3二级反渗透冲洗水门 |  | int32
FW.J0GCF43AA005CD | 2997 | #3二级反渗透冲洗水门关闭 |  | digital
FW.J0GCF43AA005CP | 2998 | #3二级反渗透冲洗水门关到位 |  | digital
FW.J0GCF43AA005OD | 2999 | #3二级反渗透冲洗水门开启 |  | digital
FW.J0GCF43AA005OP | 3000 | #3二级反渗透冲洗水门开到位 |  | digital
FW.J0GCF43AA401_LP | 3001 | #3二级反渗透产水排放门 |  | int32
FW.J0GCF43AA401CD | 3002 | #3二级反渗透产水排放门关闭 |  | digital
FW.J0GCF43AA401CP | 3003 | #3二级反渗透产水排放门关到位 |  | digital
FW.J0GCF43AA401OD | 3004 | #3二级反渗透产水排放门开启 |  | digital
FW.J0GCF43AA401OP | 3005 | #3二级反渗透产水排放门开到位 |  | digital
FW.J0GCF43AA402_LP | 3006 | #3二级反渗透浓水排放门 |  | int32
FW.J0GCF43AA402CD | 3007 | #3二级反渗透浓水排放门关闭 |  | digital
FW.J0GCF43AA402CP | 3008 | #3二级反渗透浓水排放门关到位 |  | digital
FW.J0GCF43AA402OD | 3009 | #3二级反渗透浓水排放门开启 |  | digital
FW.J0GCF43AA402OP | 3010 | #3二级反渗透浓水排放门开到位 |  | digital
FW.J0GCF43CF101 | 3011 | #3二级反渗透装置产水流量 | Hz | float32
FW.J0GCF43CF101L | 3012 | #3二级反渗透装置产水流量累计 |  | float32
FW.J0GCF43CF102 | 3013 | #3二级反渗透装置浓水流量 | Hz | float32
FW.J0GCF43CF102L | 3014 | #3二级反渗透装置浓水流量累计 |  | float32
FW.J0GCF43CP101 | 3015 | #3二级反渗透装置进水压力 | kPa | float32
FW.J0GCF43CP101L | 3016 | #3二级反渗透装置进水压力 |  | float32
FW.J0GCF43CP102 | 3017 | #3二级反渗透装置产水压力 | Hz | float32
FW.J0GCF43CP102L | 3018 | #3二级反渗透装置产水压力 |  | float32
FW.J0GCF43CP103 | 3019 | #3二级RO装置进水与段间差压 | kPa | float32
FW.J0GCF43CP103L | 3020 | #3二级RO装置进水与段间差压 |  | float32
FW.J0GCF43CP104 | 3021 | #3二级RO装置段间与浓水差压 | kPa | float32
FW.J0GCF43CP104L | 3022 | #3二级RO装置段间与浓水差压 |  | float32
FW.J0GCF43CQ101 | 3023 | #3二级反渗透装置产水电导率 | Hz | float32
FW.J0GCF43GF001_LPIN1 | 3024 | Ovation Control Builder |  | int32
FW.J0GCF43GF001_LPOUT1 | 3025 | Ovation Control Builder |  | int32
FW.J0GCF43GF001PF | 3026 | #3二级反渗透门箱电源故障 |  | digital
FW.J0GCF44AA005_LP | 3027 | #4二级反渗透冲洗水门 |  | int32
FW.J0GCF44AA005CD | 3028 | #4二级反渗透冲洗水门关闭 |  | digital
FW.J0GCF44AA005CP | 3029 | #4二级反渗透冲洗水门关到位 |  | digital
FW.J0GCF44AA005OD | 3030 | #4二级反渗透冲洗水门开启 |  | digital
FW.J0GCF44AA005OP | 3031 | #4二级反渗透冲洗水门开到位 |  | digital
FW.J0GCF44AA401_LP | 3032 | #4二级反渗透产水排放门 |  | int32
FW.J0GCF44AA401CD | 3033 | #4二级反渗透产水排放门关闭 |  | digital
FW.J0GCF44AA401CP | 3034 | #4二级反渗透产水排放门关到位 |  | digital
FW.J0GCF44AA401OD | 3035 | #4二级反渗透产水排放门开启 |  | digital
FW.J0GCF44AA401OP | 3036 | #4二级反渗透产水排放门开到位 |  | digital
FW.J0GCF44AA402_LP | 3037 | #4二级反渗透浓水排放门 |  | int32
FW.J0GCF44AA402CD | 3038 | #4二级反渗透浓水排放门关闭 |  | digital
FW.J0GCF44AA402CP | 3039 | #4二级反渗透浓水排放门关到位 |  | digital
FW.J0GCF44AA402OD | 3040 | #4二级反渗透浓水排放门开启 |  | digital
FW.J0GCF44AA402OP | 3041 | #4二级反渗透浓水排放门开到位 |  | digital
FW.J0GCF44CF101 | 3042 | #4二级反渗透装置产水流量 | Hz | float32
FW.J0GCF44CF101L | 3043 | #4二级反渗透装置产水流量累计 |  | float32
FW.J0GCF44CF102 | 3044 | #4二级反渗透装置浓水流量 | Hz | float32
FW.J0GCF44CF102L | 3045 | #4二级反渗透装置浓水流量累计 |  | float32
FW.J0GCF44CP101 | 3046 | #4二级反渗透装置进水压力 | kPa | float32
FW.J0GCF44CP101L | 3047 | #4二级反渗透装置进水压力 |  | float32
FW.J0GCF44CP102 | 3048 | #4二级反渗透装置产水压力 | Hz | float32
FW.J0GCF44CP102L | 3049 | #4二级反渗透装置产水压力 |  | float32
FW.J0GCF44CP103 | 3050 | #4二级RO装置进水与段间差压 | kPa | float32
FW.J0GCF44CP103L | 3051 | #4二级RO装置进水与段间差压 |  | float32
FW.J0GCF44CP104 | 3052 | #4二级RO装置段间与浓水差压 | kPa | float32
FW.J0GCF44CP104L | 3053 | #4二级RO装置段间与浓水差压 |  | float32
FW.J0GCF44CQ101 | 3054 | #4二级反渗透装置产水电导率 | Hz | float32
FW.J0GCF44GF001_LPIN1 | 3055 | Ovation Control Builder |  | int32
FW.J0GCF44GF001_LPOUT1 | 3056 | Ovation Control Builder |  | int32
FW.J0GCF44GF001PF | 3057 | #4二级反渗透门箱电源故障 |  | digital
FW.J0GCF51AA004_LP | 3058 | #1EDI装置产水气动门 |  | int32
FW.J0GCF51AA004CD | 3059 | #1EDI装置产水气动阀关闭 |  | digital
FW.J0GCF51AA004CP | 3060 | #1EDI装置产水气动阀关到位 |  | digital
FW.J0GCF51AA004OD | 3061 | #1EDI装置产水气动阀开启 |  | digital
FW.J0GCF51AA004OP | 3062 | #1EDI装置产水气动阀开到位 |  | digital
FW.J0GCF51AA401_LP | 3063 | #1EDI装置产水排放门 |  | int32
FW.J0GCF51AA401CD | 3064 | #1EDI装置产水排放阀关闭 |  | digital
FW.J0GCF51AA401CP | 3065 | #1EDI装置产水排放阀关到位 |  | digital
FW.J0GCF51AA401OD | 3066 | #1EDI装置产水排放阀开启 |  | digital
FW.J0GCF51AA401OP | 3067 | #1EDI装置产水排放阀开到位 |  | digital
FW.J0GCF51CF102 | 3068 | #1EDI装置产水流量 | Hz | float32
FW.J0GCF51CF102L | 3069 | #1EDI装置产水流量累计 |  | float32
FW.J0GCF51CF103 | 3070 | #1EDI装置浓水流量 | Hz | float32
FW.J0GCF51CF103L | 3071 | #1EDI装置浓水流量累计 |  | float32
FW.J0GCF51CF104 | 3072 | #1EDI装置极水流量 | Hz | float32
FW.J0GCF51CP101 | 3073 | #1EDI装置进水压力 | Hz | float32
FW.J0GCF51CP101L | 3074 | #1EDI装置进水压力 |  | float32
FW.J0GCF51CP102 | 3075 | #1EDI装置浓水进水压力 | Hz | float32
FW.J0GCF51CP102L | 3076 | #1EDI装置浓水进水压力 |  | float32
FW.J0GCF51CP103 | 3077 | #1EDI装置产水压力 | Hz | float32
FW.J0GCF51CP103L | 3078 | #1EDI装置产水压力 |  | float32
FW.J0GCF51CP104 | 3079 | #1EDI装置浓水压力 | Hz | float32
FW.J0GCF51CP104L | 3080 | #1EDI装置浓水压力 |  | float32
FW.J0GCF51CP105 | 3081 | #1EDI装置极水压力 | Hz | float32
FW.J0GCF51CP105L | 3082 | #1EDI装置极水压力 |  | float32
FW.J0GCF51CQ102 | 3083 | #1EDI装置产水电导率 | Hz | float32
FW.J0GCF51CQ103 | 3084 | #1EDI装置产水硅酸根浓度 | Hz | float32
FW.J0GCF51CQ103L | 3085 | #1EDI装置产水硅酸根浓度 | ppb | float32
FW.J0GCF51GF001_LPIN1 | 3086 | Ovation Control Builder |  | int32
FW.J0GCF51GF001_LPOUT1 | 3087 | Ovation Control Builder |  | int32
FW.J0GCF51GF001PF | 3088 | #1EDI阀岛电源故障 |  | digital
FW.J0GCF51GH001_LP | 3089 | #1EDI整流装置 |  | int32
FW.J0GCF51GH001EH001 | 3090 | #1EDI整流装置浓水流量低 |  | digital
FW.J0GCF51GH001EH002 | 3091 | #1EDI整流装置极水流量低 |  | digital
FW.J0GCF51GH001PF | 3092 | #1EDI整流装置故障 |  | digital
FW.J0GCF51GH001RC | 3093 | #1EDI整流装置远方控制 |  | digital
FW.J0GCF51GH001RD | 3094 | #1EDI整流装置启动指令 |  | digital
FW.J0GCF51GH001RP | 3095 | #1EDI整流装置运行状态 |  | digital
FW.J0GCF51GH001TD | 3096 | #1EDI整流装置停止指令 |  | digital
FW.J0GCF52AA004_LP | 3097 | #2EDI装置产水气动门 |  | int32
FW.J0GCF52AA004CD | 3098 | #2EDI装置产水气动阀关闭 |  | digital
FW.J0GCF52AA004CP | 3099 | #2EDI装置产水气动阀关到位 |  | digital
FW.J0GCF52AA004OD | 3100 | #2EDI装置产水气动阀开启 |  | digital
FW.J0GCF52AA004OP | 3101 | #2EDI装置产水气动阀开到位 |  | digital
FW.J0GCF52AA401_LP | 3102 | #2EDI装置产水排放门 |  | int32
FW.J0GCF52AA401CD | 3103 | #2EDI装置产水排放阀关闭 |  | digital
FW.J0GCF52AA401CP | 3104 | #2EDI装置产水排放阀关到位 |  | digital
FW.J0GCF52AA401OD | 3105 | #2EDI装置产水排放阀开启 |  | digital
FW.J0GCF52AA401OP | 3106 | #2EDI装置产水排放阀开到位 |  | digital
FW.J0GCF52CF102 | 3107 | #2EDI装置产水流量 | Hz | float32
FW.J0GCF52CF102L | 3108 | #2EDI装置产水流量累计 |  | float32
FW.J0GCF52CF103 | 3109 | #2EDI装置浓水流量 | Hz | float32
FW.J0GCF52CF103L | 3110 | #2EDI装置浓水流量累计 |  | float32
FW.J0GCF52CF104 | 3111 | #2EDI装置极水流量 | Hz | float32
FW.J0GCF52CP101 | 3112 | #2EDI装置进水压力 | Hz | float32
FW.J0GCF52CP101L | 3113 | #2EDI装置进水压力 |  | float32
FW.J0GCF52CP102 | 3114 | #2EDI装置浓水进水压力 | Hz | float32
FW.J0GCF52CP102L | 3115 | #2EDI装置浓水进水压力 |  | float32
FW.J0GCF52CP103 | 3116 | #2EDI装置产水压力 | Hz | float32
FW.J0GCF52CP103L | 3117 | #2EDI装置产水压力 |  | float32
FW.J0GCF52CP104 | 3118 | #2EDI装置浓水压力 | Hz | float32
FW.J0GCF52CP104L | 3119 | #2EDI装置浓水压力 |  | float32
FW.J0GCF52CP105 | 3120 | #2EDI装置极水压力 | Hz | float32
FW.J0GCF52CP105L | 3121 | #2EDI装置极水压力 |  | float32
FW.J0GCF52CQ102 | 3122 | #2EDI装置产水电导率 | Hz | float32
FW.J0GCF52CQ103 | 3123 | #2EDI产水硅酸根浓度 | Hz | float32
FW.J0GCF52CQ103L | 3124 | #2EDI装置产水硅酸根浓度 | ppb | float32
FW.J0GCF52GF001_LPIN1 | 3125 | Ovation Control Builder |  | int32
FW.J0GCF52GF001_LPOUT1 | 3126 | Ovation Control Builder |  | int32
FW.J0GCF52GF001PF | 3127 | #2EDI阀岛电源故障 |  | digital
FW.J0GCF52GH001_LP | 3128 | #2EDI整流装置 |  | int32
FW.J0GCF52GH001EH001 | 3129 | #2EDI整流装置浓水流量低 |  | digital
FW.J0GCF52GH001EH002 | 3130 | #2EDI整流装置极水流量低 |  | digital
FW.J0GCF52GH001PF | 3131 | #2EDI整流装置故障 |  | digital
FW.J0GCF52GH001RC | 3132 | #2EDI整流装置远方控制 |  | digital
FW.J0GCF52GH001RD | 3133 | #2EDI整流装置启动指令 |  | digital
FW.J0GCF52GH001RP | 3134 | #2EDI整流装置运行状态 |  | digital
FW.J0GCF52GH001TD | 3135 | #2EDI整流装置停止指令 |  | digital
FW.J0GCF53AA004_LP | 3136 | #3EDI装置产水气动门 |  | int32
FW.J0GCF53AA004CD | 3137 | #3EDI装置产水气动阀关闭 |  | digital
FW.J0GCF53AA004CP | 3138 | #3EDI装置产水气动阀关到位 |  | digital
FW.J0GCF53AA004OD | 3139 | #3EDI装置产水气动阀开启 |  | digital
FW.J0GCF53AA004OP | 3140 | #3EDI装置产水气动阀开到位 |  | digital
FW.J0GCF53AA401_LP | 3141 | #3EDI装置产水排放门 |  | int32
FW.J0GCF53AA401CD | 3142 | #3EDI装置产水排放阀关闭 |  | digital
FW.J0GCF53AA401CP | 3143 | #3EDI装置产水排放阀关到位 |  | digital
FW.J0GCF53AA401OD | 3144 | #3EDI装置产水排放阀开启 |  | digital
FW.J0GCF53AA401OP | 3145 | #3EDI装置产水排放阀开到位 |  | digital
FW.J0GCF53CF102 | 3146 | #3EDI装置产水流量 | Hz | float32
FW.J0GCF53CF102L | 3147 | #3EDI装置产水流量累计 |  | float32
FW.J0GCF53CF103 | 3148 | #3EDI装置浓水流量 | Hz | float32
FW.J0GCF53CF103L | 3149 | #3EDI装置浓水流量累计 |  | float32
FW.J0GCF53CF104 | 3150 | #3EDI装置极水流量 | Hz | float32
FW.J0GCF53CP101 | 3151 | #3EDI装置进水压力 | Hz | float32
FW.J0GCF53CP101L | 3152 | #3EDI装置进水压力 |  | float32
FW.J0GCF53CP102 | 3153 | #3EDI装置浓水进水压力 | Hz | float32
FW.J0GCF53CP102L | 3154 | #3EDI装置浓水进水压力 |  | float32
FW.J0GCF53CP103 | 3155 | #3EDI装置产水压力 | Hz | float32
FW.J0GCF53CP103L | 3156 | #3EDI装置产水压力 |  | float32
FW.J0GCF53CP104 | 3157 | #3EDI装置浓水压力 | Hz | float32
FW.J0GCF53CP104L | 3158 | #3EDI装置浓水压力 |  | float32
FW.J0GCF53CP105 | 3159 | #3EDI装置极水压力 | Hz | float32
FW.J0GCF53CP105L | 3160 | #3EDI装置极水压力 |  | float32
FW.J0GCF53CQ102 | 3161 | #3EDI装置产水电导率 | Hz | float32
FW.J0GCF53CQ103 | 3162 | #3EDI装置产水硅酸根浓度 | Hz | float32
FW.J0GCF53CQ103L | 3163 | #3EDI装置产水硅酸根浓度 | ppb | float32
FW.J0GCF53GF001_LPIN1 | 3164 | Ovation Control Builder |  | int32
FW.J0GCF53GF001_LPOUT1 | 3165 | Ovation Control Builder |  | int32
FW.J0GCF53GF001PF | 3166 | #3EDI阀岛电源故障 |  | digital
FW.J0GCF53GH001_LP | 3167 | #3EDI整流装置 |  | int32
FW.J0GCF53GH001EH001 | 3168 | #3EDI整流装置浓水流量低 |  | digital
FW.J0GCF53GH001EH002 | 3169 | #3EDI整流装置极水流量低 |  | digital
FW.J0GCF53GH001PF | 3170 | #3EDI整流装置故障 |  | digital
FW.J0GCF53GH001RC | 3171 | #3EDI整流装置远方控制 |  | digital
FW.J0GCF53GH001RD | 3172 | #3EDI整流装置启动指令 |  | digital
FW.J0GCF53GH001RP | 3173 | #3EDI整流装置运行状态 |  | digital
FW.J0GCF53GH001TD | 3174 | #3EDI整流装置停止指令 |  | digital
FW.J0GCF54AA004_LP | 3175 | #4EDI装置产水气动门 |  | int32
FW.J0GCF54AA004CD | 3176 | #4DI装置产水气动阀关闭 |  | digital
FW.J0GCF54AA004CP | 3177 | #4EDI装置产水气动阀关到位 |  | digital
FW.J0GCF54AA004OD | 3178 | #4EDI装置产水气动阀开启 |  | digital
FW.J0GCF54AA004OP | 3179 | #4EDI装置产水气动阀开到位 |  | digital
FW.J0GCF54AA401_LP | 3180 | #4EDI装置产水排放门 |  | int32
FW.J0GCF54AA401CD | 3181 | #4EDI装置产水排放阀关闭 |  | digital
FW.J0GCF54AA401CP | 3182 | #4EDI装置产水排放阀关到位 |  | digital
FW.J0GCF54AA401OD | 3183 | #4EDI装置产水排放阀开启 |  | digital
FW.J0GCF54AA401OP | 3184 | #4EDI装置产水排放阀开到位 |  | digital
FW.J0GCF54CF102 | 3185 | #4EDI装置产水流量 | Hz | float32
FW.J0GCF54CF102L | 3186 | #4EDI装置产水流量累计 |  | float32
FW.J0GCF54CF103 | 3187 | #4EDI装置浓水流量 | Hz | float32
FW.J0GCF54CF103L | 3188 | #4EDI装置浓水流量累计 |  | float32
FW.J0GCF54CF104 | 3189 | #4EDI装置极水流量 | Hz | float32
FW.J0GCF54CP101 | 3190 | #4EDI装置进水压力 | Hz | float32
FW.J0GCF54CP101L | 3191 | #4EDI装置进水压力 |  | float32
FW.J0GCF54CP102 | 3192 | #4EDI装置浓水进水压力 | Hz | float32
FW.J0GCF54CP102L | 3193 | #4EDI装置浓水进水压力 |  | float32
FW.J0GCF54CP103 | 3194 | #4EDI装置产水压力 | Hz | float32
FW.J0GCF54CP103L | 3195 | #4EDI装置产水压力 |  | float32
FW.J0GCF54CP104 | 3196 | #4EDI装置浓水压力 | Hz | float32
FW.J0GCF54CP104L | 3197 | #4EDI装置浓水压力 |  | float32
FW.J0GCF54CP105 | 3198 | #4EDI装置极水压力 | Hz | float32
FW.J0GCF54CP105L | 3199 | #4EDI装置极水压力 |  | float32
FW.J0GCF54CQ102 | 3200 | #4EDI装置产水电导率 | Hz | float32
FW.J0GCF54CQ103 | 3201 | #4EDI装置产水硅酸根浓度 | Hz | float32
FW.J0GCF54CQ103L | 3202 | #4EDI装置产水硅酸根浓度 | ppb | float32
FW.J0GCF54GF001_LPIN1 | 3203 | Ovation Control Builder |  | int32
FW.J0GCF54GF001_LPOUT1 | 3204 | Ovation Control Builder |  | int32
FW.J0GCF54GF001PF | 3205 | #4EDI阀岛电源故障 |  | digital
FW.J0GCF54GH001_LP | 3206 | #4EDI整流装置 |  | int32
FW.J0GCF54GH001EH001 | 3207 | #4EDI整流装置浓水流量低 |  | digital
FW.J0GCF54GH001EH002 | 3208 | #4EDI整流装置浓水流量低 |  | digital
FW.J0GCF54GH001PF | 3209 | #4EDI整流装置故障 |  | digital
FW.J0GCF54GH001RC | 3210 | #4EDI整流装置远方控制 |  | digital
FW.J0GCF54GH001RD | 3211 | #4EDI整流装置启动指令 |  | digital
FW.J0GCF54GH001RP | 3212 | #4EDI整流装置运行状态 |  | digital
FW.J0GCF54GH001TD | 3213 | #4EDI整流装置停止指令 |  | digital
FW.J0GCK10CQ101 | 3214 | 超滤装置母管浊度 | Hz | float32
FW.J0GCK11AA005_LP | 3215 | #1超滤给水泵再循环门 |  | int32
FW.J0GCK11AA005CD | 3216 | #1超滤升压泵再循环阀关闭 |  | digital
FW.J0GCK11AA005CP | 3217 | #1超滤升压泵再循环阀关到位 |  | digital
FW.J0GCK11AA005OD | 3218 | #1超滤升压泵再循环阀开启 |  | digital
FW.J0GCK11AA005OP | 3219 | #1超滤升压泵再循环阀开到位 |  | digital
FW.J0GCK11AP001_F | 3220 | Ovation Control Builder |  | digital
FW.J0GCK11AP001_LP | 3221 | #1超滤给水泵 |  | int32
FW.J0GCK11AP001_LP1 | 3222 | Ovation Control Builder |  | int32
FW.J0GCK11AP001_LP2 | 3223 | Ovation Control Builder |  | int32
FW.J0GCK11AP001_MODE | 3224 | Ovation Control Builder |  | int32
FW.J0GCK11AP001_SPO | 3225 | Ovation Control Builder |  | float32
FW.J0GCK11AP001_SPPMT | 3226 | #1超滤给水泵保护停 |  | digital
FW.J0GCK11AP001_STPMT | 3227 | #1超滤给水泵启允许 |  | digital
FW.J0GCK11AP001C | 3228 | #1超滤给水泵给定 |  | float32
FW.J0GCK11AP001CL | 3229 | Ovation Control Builder |  | float32
FW.J0GCK11AP001I | 3230 | #1??????? |  | float32
FW.J0GCK11AP001IL | 3231 | #1超滤给水泵电流 |  | float32
FW.J0GCK11AP001P | 3232 | #1超滤给水泵反馈 |  | float32
FW.J0GCK11AP001PF | 3233 | #1超滤给水泵故障 |  | digital
FW.J0GCK11AP001PL | 3234 | Ovation Control Builder |  | float32
FW.J0GCK11AP001RC | 3235 | #1超滤给水泵远方 |  | digital
FW.J0GCK11AP001RD | 3236 | #1超滤给水泵启动 |  | digital
FW.J0GCK11AP001RP | 3237 | #1超滤给水泵运行 |  | digital
FW.J0GCK11AP001TD | 3238 | #1超滤给水泵停止 |  | digital
FW.J0GCK11CF101 | 3239 | #1超滤装置进水流量 | Hz | float32
FW.J0GCK11CF101L | 3240 | #1超滤装置进水流量累计 |  | float32
FW.J0GCK11CP001H | 3241 | #1自清洗过滤器进出口差压高 |  | digital
FW.J0GCK11GF001_LPIN1 | 3242 | Ovation Control Builder |  | int32
FW.J0GCK11GF001_LPOUT1 | 3243 | Ovation Control Builder |  | int32
FW.J0GCK12AA005_LP | 3244 | #2超滤给水泵再循环门 |  | int32
FW.J0GCK12AA005CD | 3245 | #2超滤给水泵再循环门关闭 |  | digital
FW.J0GCK12AA005CP | 3246 | #2超滤给水泵再循环门关到位 |  | digital
FW.J0GCK12AA005OD | 3247 | #2超滤给水泵再循环门开启 |  | digital
FW.J0GCK12AA005OP | 3248 | #2超滤给水泵再循环门开到位 |  | digital
FW.J0GCK12AP001_F | 3249 | Ovation Control Builder |  | digital
FW.J0GCK12AP001_LP | 3250 | #2超滤给水泵 |  | int32
FW.J0GCK12AP001_LP1 | 3251 | Ovation Control Builder |  | int32
FW.J0GCK12AP001_LP2 | 3252 | Ovation Control Builder |  | int32
FW.J0GCK12AP001_MODE | 3253 | Ovation Control Builder |  | int32
FW.J0GCK12AP001_SPO | 3254 | Ovation Control Builder |  | float32
FW.J0GCK12AP001_SPPMT | 3255 | #2超滤给水泵保护停 |  | digital
FW.J0GCK12AP001_STPMT | 3256 | #2超滤给水泵启允许 |  | digital
FW.J0GCK12AP001C | 3257 | #2超滤给水泵频率给定 |  | float32
FW.J0GCK12AP001CL | 3258 | Ovation Control Builder |  | float32
FW.J0GCK12AP001I | 3259 | #2??????? |  | float32
FW.J0GCK12AP001IL | 3260 | #2超滤给水泵电流 |  | float32
FW.J0GCK12AP001P | 3261 | #2超滤给水泵反馈 |  | float32
FW.J0GCK12AP001PF | 3262 | #2超滤给水泵故障 |  | digital
FW.J0GCK12AP001PL | 3263 | Ovation Control Builder |  | float32
FW.J0GCK12AP001RC | 3264 | #2超滤给水泵远方 |  | digital
FW.J0GCK12AP001RD | 3265 | #2超滤给水泵启动 |  | digital
FW.J0GCK12AP001RP | 3266 | #2超滤给水泵运行 |  | digital
FW.J0GCK12AP001TD | 3267 | #2超滤给水泵停止 |  | digital
FW.J0GCK12CF101 | 3268 | #2超滤装置进水流量 | Hz | float32
FW.J0GCK12CF101L | 3269 | #2超滤装置进水流量累计 |  | float32
FW.J0GCK12CP001H | 3270 | #2自清洗过滤器进出口差压高 |  | digital
FW.J0GCK13AA005_LP | 3271 | #3超滤给水泵再循环门 |  | int32
FW.J0GCK13AA005CD | 3272 | #3超滤给水泵再循环门关闭 |  | digital
FW.J0GCK13AA005CP | 3273 | #3超滤给水泵再循环门关到位 |  | digital
FW.J0GCK13AA005OD | 3274 | #3超滤给水泵再循环门开启 |  | digital
FW.J0GCK13AA005OP | 3275 | #3超滤给水泵再循环门开到位 |  | digital
FW.J0GCK13AP001_F | 3276 | Ovation Control Builder |  | digital
FW.J0GCK13AP001_LP | 3277 | #3超滤给水泵 |  | int32
FW.J0GCK13AP001_LP1 | 3278 | Ovation Control Builder |  | int32
FW.J0GCK13AP001_LP2 | 3279 | Ovation Control Builder |  | int32
FW.J0GCK13AP001_MODE | 3280 | Ovation Control Builder |  | int32
FW.J0GCK13AP001_SPO | 3281 | Ovation Control Builder |  | float32
FW.J0GCK13AP001_SPPMT | 3282 | #3超滤给水泵保护停 |  | digital
FW.J0GCK13AP001_STPMT | 3283 | #3超滤给水泵启允许 |  | digital
FW.J0GCK13AP001C | 3284 | #3超滤给水泵给定 |  | float32
FW.J0GCK13AP001CL | 3285 | Ovation Control Builder |  | float32
FW.J0GCK13AP001I | 3286 | #3??????? |  | float32
FW.J0GCK13AP001IL | 3287 | #3超滤给水泵电流 |  | float32
FW.J0GCK13AP001P | 3288 | #3超滤给水泵反馈 |  | float32
FW.J0GCK13AP001PF | 3289 | #3超滤给水泵故障 |  | digital
FW.J0GCK13AP001PL | 3290 | Ovation Control Builder |  | float32
FW.J0GCK13AP001RC | 3291 | #3超滤给水泵远方 |  | digital
FW.J0GCK13AP001RD | 3292 | #3超滤给水泵启动 |  | digital
FW.J0GCK13AP001RP | 3293 | #3超滤给水泵运行 |  | digital
FW.J0GCK13AP001TD | 3294 | #3超滤给水泵停止 |  | digital
FW.J0GCK13CF101 | 3295 | #3超滤装置进水流量 | Hz | float32
FW.J0GCK13CF101L | 3296 | #3超滤装置进水流量累计 |  | float32
FW.J0GCK13CP001H | 3297 | #3自清洗过滤器进出口差压高 |  | digital
FW.J0GCK14AA005_LP | 3298 | #4超滤给水泵再循环门 |  | int32
FW.J0GCK14AA005CD | 3299 | #4超滤给水泵再循环门关闭 |  | digital
FW.J0GCK14AA005CP | 3300 | #4超滤给水泵再循环门关到位 |  | digital
FW.J0GCK14AA005OD | 3301 | #4超滤给水泵再循环门开启 |  | digital
FW.J0GCK14AA005OP | 3302 | #4超滤给水泵再循环门开到位 |  | digital
FW.J0GCK14AP001_F | 3303 | Ovation Control Builder |  | digital
FW.J0GCK14AP001_LP | 3304 | #4超滤给水泵 |  | int32
FW.J0GCK14AP001_LP1 | 3305 | Ovation Control Builder |  | int32
FW.J0GCK14AP001_LP2 | 3306 | Ovation Control Builder |  | int32
FW.J0GCK14AP001_MODE | 3307 | Ovation Control Builder |  | int32
FW.J0GCK14AP001_SPO | 3308 | Ovation Control Builder |  | float32
FW.J0GCK14AP001_SPPMT | 3309 | #4超滤给水泵保护停 |  | digital
FW.J0GCK14AP001_STPMT | 3310 | #4超滤给水泵启允许 |  | digital
FW.J0GCK14AP001C | 3311 | #4超滤给水泵给定 |  | float32
FW.J0GCK14AP001CL | 3312 | Ovation Control Builder |  | float32
FW.J0GCK14AP001I | 3313 | #4??????? |  | float32
FW.J0GCK14AP001IL | 3314 | #4超滤给水泵电流 |  | float32
FW.J0GCK14AP001P | 3315 | #4超滤给水泵反馈 |  | float32
FW.J0GCK14AP001PF | 3316 | #4超滤给水泵故障 |  | digital
FW.J0GCK14AP001PL | 3317 | Ovation Control Builder |  | float32
FW.J0GCK14AP001RC | 3318 | #4超滤给水泵远方 |  | digital
FW.J0GCK14AP001RD | 3319 | #4超滤给水泵启动 |  | digital
FW.J0GCK14AP001RP | 3320 | #4超滤给水泵运行 |  | digital
FW.J0GCK14AP001TD | 3321 | #4超滤给水泵停止 |  | digital
FW.J0GCK14CF101 | 3322 | #4超滤装置进水流量 | Hz | float32
FW.J0GCK14CF101L | 3323 | #4超滤装置进水流量累计 |  | float32
FW.J0GCK14CP001H | 3324 | #4自清洗过滤器进出口差压高 |  | digital
FW.J0GCK20CL101 | 3325 | #1超滤水箱液位 | Hz | float32
FW.J0GCK20CL102 | 3326 | #2超滤水箱液位 | Hz | float32
FW.J0GCK21AP001_LP | 3327 | #1一级反渗透给水泵 |  | int32
FW.J0GCK21AP001_LPIN1 | 3328 | Ovation Control Builder |  | int32
FW.J0GCK21AP001_LPIN11 | 3329 | Ovation Control Builder |  | int32
FW.J0GCK21AP001I | 3330 | Ovation Control Builder |  | float32
FW.J0GCK21AP001IL | 3331 | #1一级反渗透给水泵电流 |  | float32
FW.J0GCK21AP001RC | 3332 | #1一级反渗透给水泵远方 |  | digital
FW.J0GCK21AP001RD | 3333 | #1一级反渗透给水泵启动 |  | digital
FW.J0GCK21AP001RP | 3334 | #1一级反渗透给水泵运行 |  | digital
FW.J0GCK21AP001TD | 3335 | #1一级反渗透给水泵停止 |  | digital
FW.J0GCK22AP001_LP | 3336 | #2一级反渗透给水泵 |  | int32
FW.J0GCK22AP001_LPIN1 | 3337 | Ovation Control Builder |  | int32
FW.J0GCK22AP001_LPOUT1 | 3338 | Ovation Control Builder |  | int32
FW.J0GCK22AP001I | 3339 | Ovation Control Builder |  | float32
FW.J0GCK22AP001IL | 3340 | #2一级反渗透给水泵电流 |  | float32
FW.J0GCK22AP001RC | 3341 | #2一级反渗透给水泵远方 |  | digital
FW.J0GCK22AP001RD | 3342 | #2一级反渗透给水泵启动 |  | digital
FW.J0GCK22AP001RP | 3343 | #2一级反渗透给水泵运行 |  | digital
FW.J0GCK22AP001TD | 3344 | #2一级反渗透给水泵停止 |  | digital
FW.J0GCK23AP001_LP | 3345 | #3一级反渗透给水泵 |  | int32
FW.J0GCK23AP001_LPIN1 | 3346 | Ovation Control Builder |  | int32
FW.J0GCK23AP001_LPOUT1 | 3347 | Ovation Control Builder |  | int32
FW.J0GCK23AP001I | 3348 | Ovation Control Builder |  | float32
FW.J0GCK23AP001IL | 3349 | #3一级反渗透给水泵电流 |  | float32
FW.J0GCK23AP001RC | 3350 | #3一级反渗透给水泵远方 |  | digital
FW.J0GCK23AP001RD | 3351 | #3一级反渗透给水泵启动 |  | digital
FW.J0GCK23AP001RP | 3352 | #3一级反渗透给水泵运行 |  | digital
FW.J0GCK23AP001TD | 3353 | #3一级反渗透给水泵停止 |  | digital
FW.J0GCK24AP001_LP | 3354 | #4一级反渗透给水泵 |  | int32
FW.J0GCK24AP001_LPIN1 | 3355 | Ovation Control Builder |  | int32
FW.J0GCK24AP001_LPOUT1 | 3356 | Ovation Control Builder |  | int32
FW.J0GCK24AP001I | 3357 | Ovation Control Builder |  | float32
FW.J0GCK24AP001IL | 3358 | #4一级反渗透给水泵电流 |  | float32
FW.J0GCK24AP001RC | 3359 | #4一级反渗透给水泵远方 |  | digital
FW.J0GCK24AP001RD | 3360 | #4一级反渗透给水泵启动 |  | digital
FW.J0GCK24AP001RP | 3361 | #4一级反渗透给水泵运行 |  | digital
FW.J0GCK24AP001TD | 3362 | #4一级反渗透给水泵停止 |  | digital
FW.J0GCK30CF101 | 3363 | 一级RO保安过滤器进口母管流量 | Hz | float32
FW.J0GCK30CF101L | 3364 | 一级RO保安过滤器进口母管流量累 |  | float32
FW.J0GCK30CP101 | 3365 | 一级反渗透给水泵出口母管压力 |  | float32
FW.J0GCK30CP101L | 3366 | 一级反渗透给水泵出口母管压力 |  | float32
FW.J0GCK30CQ101 | 3367 | 反渗透保安过滤器进水母管PH表 | Hz | float32
FW.J0GCK30CQ102 | 3368 | RO保安过滤器进水母管导电度 | Hz | float32
FW.J0GCK30CQ103 | 3369 | 反渗透保安过滤器进水母管ORP表 | Hz | float32
FW.J0GCK30CQ104 | 3370 | 反渗透保安过滤器进水母管余氯值 | mg/L | float32
FW.J0GCK30CQ105 | 3371 | 反渗透保安过滤器进水母管SDI表 |  | float32
FW.J0GCK30CT101 | 3372 | 一级RO保安过滤器进口母管水温 | Hz | float32
FW.J0GCK31AA002_LP | 3373 | #1一级反渗透保安过滤器进水门 |  | int32
FW.J0GCK31AA002CD | 3374 | #1一级反渗保安过滤进水门关闭 |  | digital
FW.J0GCK31AA002CP | 3375 | #1一级反渗保安过滤进水门关到 |  | digital
FW.J0GCK31AA002OD | 3376 | #1一级反渗保安过滤进水门开启 |  | digital
FW.J0GCK31AA002OP | 3377 | #1一级反渗保安过滤进水门开到 |  | digital
FW.J0GCK31AP001_F | 3378 | Ovation Control Builder |  | digital
FW.J0GCK31AP001_LP | 3379 | #1一级反渗透高压泵 |  | int32
FW.J0GCK31AP001_LP1 | 3380 | Ovation Control Builder |  | int32
FW.J0GCK31AP001_LP2 | 3381 | Ovation Control Builder |  | int32
FW.J0GCK31AP001_MODE | 3382 | Ovation Control Builder |  | int32
FW.J0GCK31AP001_SPO | 3383 | Ovation Control Builder |  | float32
FW.J0GCK31AP001C | 3384 | #1一级反渗透高压泵频率给定 |  | float32
FW.J0GCK31AP001CL | 3385 | Ovation Control Builder |  | float32
FW.J0GCK31AP001I | 3386 | Ovation Control Builder |  | float32
FW.J0GCK31AP001IL | 3387 | #1一级反渗透高压泵电流 |  | float32
FW.J0GCK31AP001P | 3388 | #1一级反渗透高压泵频率反馈 |  | float32
FW.J0GCK31AP001PF | 3389 | #1一级反渗透高压泵故障 |  | digital
FW.J0GCK31AP001PL | 3390 | Ovation Control Builder |  | float32
FW.J0GCK31AP001RC | 3391 | #1一级反渗透高压泵远方 |  | digital
FW.J0GCK31AP001RD | 3392 | #1一级反渗透高压泵启动 |  | digital
FW.J0GCK31AP001RP | 3393 | #1一级反渗透高压泵运行 |  | digital
FW.J0GCK31AP001TD | 3394 | #1一级反渗透高压泵停止 |  | digital
FW.J0GCK31CP001L | 3395 | #1一级反渗透高压泵进口压力低 |  | digital
FW.J0GCK31CP002H | 3396 | #1一级反渗透高压泵出口压力高 |  | digital
FW.J0GCK31CP101 | 3397 | #1一级RO保安过滤器进出口差压 | kPa | float32
FW.J0GCK31CP101L | 3398 | #1一级RO保安过滤器进出口差压 |  | float32
FW.J0GCK31GF001_LPIN1 | 3399 | Ovation Control Builder |  | int32
FW.J0GCK31GF001_LPOUT1 | 3400 | Ovation Control Builder |  | int32
FW.J0GCK31GF001PF | 3401 | 一级RO保安过器电磁阀箱电源故障 |  | digital
FW.J0GCK32AA002_LP | 3402 | #2一级反渗透保安过滤器进水门 |  | int32
FW.J0GCK32AA002CD | 3403 | #2一级反渗保安过滤进水门关闭 |  | digital
FW.J0GCK32AA002CP | 3404 | #2一级反渗保安过滤进水门关到 |  | digital
FW.J0GCK32AA002OD | 3405 | #2一级反渗保安过滤进水门开启 |  | digital
FW.J0GCK32AA002OP | 3406 | #2一级反渗保安过滤进水门开到 |  | digital
FW.J0GCK32AP001_F | 3407 | Ovation Control Builder |  | digital
FW.J0GCK32AP001_LP | 3408 | #2一级反渗透高压泵 |  | int32
FW.J0GCK32AP001_LP1 | 3409 | Ovation Control Builder |  | int32
FW.J0GCK32AP001_LP2 | 3410 | Ovation Control Builder |  | int32
FW.J0GCK32AP001_MODE | 3411 | Ovation Control Builder |  | int32
FW.J0GCK32AP001_SPO | 3412 | Ovation Control Builder |  | float32
FW.J0GCK32AP001C | 3413 | #2一级反渗透高压泵频率给定 |  | float32
FW.J0GCK32AP001CL | 3414 | Ovation Control Builder |  | float32
FW.J0GCK32AP001I | 3415 | Ovation Control Builder |  | float32
FW.J0GCK32AP001IL | 3416 | #2一级反渗透高压泵电流 |  | float32
FW.J0GCK32AP001P | 3417 | #2一级反渗透高压泵频率反馈 |  | float32
FW.J0GCK32AP001PF | 3418 | #2一级反渗透高压泵故障 |  | digital
FW.J0GCK32AP001PL | 3419 | Ovation Control Builder |  | float32
FW.J0GCK32AP001RC | 3420 | #2一级反渗透高压泵远方 |  | digital
FW.J0GCK32AP001RD | 3421 | #2一级反渗透高压泵启动 |  | digital
FW.J0GCK32AP001RP | 3422 | #2一级反渗透高压泵运行 |  | digital
FW.J0GCK32AP001TD | 3423 | #2一级反渗透高压泵停止 |  | digital
FW.J0GCK32CP001L | 3424 | #2一级反渗透高压泵进口压力低 |  | digital
FW.J0GCK32CP002H | 3425 | #2一级反渗透高压泵出口压力高 |  | digital
FW.J0GCK32CP101 | 3426 | #2一级RO保安过滤器进出口差压 | kPa | float32
FW.J0GCK32CP101L | 3427 | #2一级RO保安过滤器进出口差压 |  | float32
FW.J0GCK33AA002_LP | 3428 | #3一级反渗透保安过滤器进水门 |  | int32
FW.J0GCK33AA002CD | 3429 | #3一级反渗保安过滤进水门关闭 |  | digital
FW.J0GCK33AA002CP | 3430 | #3一级反渗保安过滤进水门关到 |  | digital
FW.J0GCK33AA002OD | 3431 | #3一级反渗保安过滤进水门开启 |  | digital
FW.J0GCK33AA002OP | 3432 | #3一级反渗保安过滤进水门开到 |  | digital
FW.J0GCK33AP001_F | 3433 | Ovation Control Builder |  | digital
FW.J0GCK33AP001_LP | 3434 | #3一级反渗透高压泵 |  | int32
FW.J0GCK33AP001_LP1 | 3435 | Ovation Control Builder |  | int32
FW.J0GCK33AP001_LP2 | 3436 | Ovation Control Builder |  | int32
FW.J0GCK33AP001_MODE | 3437 | Ovation Control Builder |  | int32
FW.J0GCK33AP001_SPO | 3438 | Ovation Control Builder |  | float32
FW.J0GCK33AP001C | 3439 | #3一级反渗透高压泵频率给定 |  | float32
FW.J0GCK33AP001CL | 3440 | Ovation Control Builder |  | float32
FW.J0GCK33AP001I | 3441 | Ovation Control Builder |  | float32
FW.J0GCK33AP001IL | 3442 | #3一级反渗透高压泵电流 |  | float32
FW.J0GCK33AP001P | 3443 | #3一级反渗透高压泵频率反馈 |  | float32
FW.J0GCK33AP001PF | 3444 | #3一级反渗透高压泵故障 |  | digital
FW.J0GCK33AP001PL | 3445 | Ovation Control Builder |  | float32
FW.J0GCK33AP001RC | 3446 | #3一级反渗透高压泵远方 |  | digital
FW.J0GCK33AP001RD | 3447 | #3一级反渗透高压泵启动 |  | digital
FW.J0GCK33AP001RP | 3448 | #3一级反渗透高压泵运行 |  | digital
FW.J0GCK33AP001TD | 3449 | #3一级反渗透高压泵停止 |  | digital
FW.J0GCK33CP001L | 3450 | #3一级反渗透高压泵进口压力低 |  | digital
FW.J0GCK33CP002H | 3451 | #3一级反渗透高压泵出口压力高 |  | digital
FW.J0GCK33CP101 | 3452 | #3一级RO保安过滤器进出口差压 | kPa | float32
FW.J0GCK33CP101L | 3453 | #3一级RO保安过滤器进出口差压 |  | float32
FW.J0GCK34AA002_LP | 3454 | #4一级反渗透保安过滤器进水门 |  | int32
FW.J0GCK34AA002CD | 3455 | #4一级反渗保安过滤进水门关闭 |  | digital
FW.J0GCK34AA002CP | 3456 | #4一级反渗保安过滤进水门关到 |  | digital
FW.J0GCK34AA002OD | 3457 | #4一级反渗保安过滤进水门开启 |  | digital
FW.J0GCK34AA002OP | 3458 | #4一级反渗保安过滤进水门开到 |  | digital
FW.J0GCK34AP001_F | 3459 | Ovation Control Builder |  | digital
FW.J0GCK34AP001_LP | 3460 | #4一级反渗透高压泵 |  | int32
FW.J0GCK34AP001_LP1 | 3461 | Ovation Control Builder |  | int32
FW.J0GCK34AP001_LP2 | 3462 | Ovation Control Builder |  | int32
FW.J0GCK34AP001_MODE | 3463 | Ovation Control Builder |  | int32
FW.J0GCK34AP001_SPO | 3464 | Ovation Control Builder |  | float32
FW.J0GCK34AP001C | 3465 | #4一级反渗透高压泵频率给定 |  | float32
FW.J0GCK34AP001CL | 3466 | Ovation Control Builder |  | float32
FW.J0GCK34AP001I | 3467 | Ovation Control Builder |  | float32
FW.J0GCK34AP001IL | 3468 | #4一级反渗透高压泵电流 |  | float32
FW.J0GCK34AP001P | 3469 | #4一级反渗透高压泵频率反馈 |  | float32
FW.J0GCK34AP001PF | 3470 | #4一级反渗透高压泵故障 |  | digital
FW.J0GCK34AP001PL | 3471 | Ovation Control Builder |  | float32
FW.J0GCK34AP001RC | 3472 | #4一级反渗透高压泵远方 |  | digital
FW.J0GCK34AP001RD | 3473 | #4一级反渗透高压泵启动 |  | digital
FW.J0GCK34AP001RP | 3474 | #4一级反渗透高压泵运行 |  | digital
FW.J0GCK34AP001TD | 3475 | #4一级反渗透高压泵停止 |  | digital
FW.J0GCK34CP001L | 3476 | #4一级反渗透高压泵进口压力低 |  | digital
FW.J0GCK34CP002H | 3477 | #4一级反渗透高压泵出口压力高 |  | digital
FW.J0GCK34CP101 | 3478 | #4一级RO保安过滤器进出口差压 | kPa | float32
FW.J0GCK34CP101L | 3479 | #4一级RO保安过滤器进出口差压 |  | float32
FW.J0GCK40CL101 | 3480 | #1一级反渗透产水箱液位 | Hz | float32
FW.J0GCK40CL102 | 3481 | #2一级反渗透产水箱液位 | Hz | float32
FW.J0GCK40CQ101 | 3482 | 一级反渗透产水箱出水母管电导率 | Hz | float32
FW.J0GCK40CQ102 | 3483 | 一级反渗透装置母管PH | Hz | float32
FW.J0GCK41AA003_LP | 3484 | #1二级反渗透高压泵出口门 |  | int32
FW.J0GCK41AA003CD | 3485 | #1二级反渗透高压泵出口门关闭 |  | digital
FW.J0GCK41AA003CP | 3486 | #1二级反渗透高压泵出口门关到 |  | digital
FW.J0GCK41AA003OD | 3487 | #1二级反渗透高压泵出口门开启 |  | digital
FW.J0GCK41AA003OP | 3488 | #1二级反渗透高压泵出口门开到 |  | digital
FW.J0GCK41AP001_F | 3489 | Ovation Control Builder |  | digital
FW.J0GCK41AP001_LP | 3490 | #1二级反渗透高压泵 |  | int32
FW.J0GCK41AP001_LP1 | 3491 | Ovation Control Builder |  | int32
FW.J0GCK41AP001_LP2 | 3492 | Ovation Control Builder |  | int32
FW.J0GCK41AP001_MODE | 3493 | Ovation Control Builder |  | int32
FW.J0GCK41AP001_SPO | 3494 | Ovation Control Builder |  | float32
FW.J0GCK41AP001C | 3495 | #1二级反渗透高压泵给定 |  | float32
FW.J0GCK41AP001CL | 3496 | Ovation Control Builder |  | float32
FW.J0GCK41AP001I | 3497 | Ovation Control Builder |  | float32
FW.J0GCK41AP001IL | 3498 | 1号二级反渗透高压泵电流 |  | float32
FW.J0GCK41AP001P | 3499 | #1二级反渗透高压泵反馈 |  | float32
FW.J0GCK41AP001PF | 3500 | #1二级反渗透高压泵故障 |  | digital
FW.J0GCK41AP001PL | 3501 | Ovation Control Builder |  | float32
FW.J0GCK41AP001RC | 3502 | #1二级反渗透高压泵远方 |  | digital
FW.J0GCK41AP001RD | 3503 | #1二级反渗透高压泵启动 |  | digital
FW.J0GCK41AP001RP | 3504 | #1二级反渗透高压泵运行 |  | digital
FW.J0GCK41AP001TD | 3505 | #1二级反渗透高压泵停止 |  | digital
FW.J0GCK41CP002H | 3506 | #1二级反渗透高压泵出口压力高 |  | digital
FW.J0GCK41CP101 | 3507 | #1二级RO保安过滤器进出口差压 | Hz | float32
FW.J0GCK41CP101L | 3508 | #1二级RO保安过滤器进出口差压 |  | float32
FW.J0GCK42AA003_LP | 3509 | #2二级反渗透高压泵出口门 |  | int32
FW.J0GCK42AA003CD | 3510 | #2二级反渗透高压泵出口阀关闭 |  | digital
FW.J0GCK42AA003CP | 3511 | #2二级反渗透高压泵出口阀关到 |  | digital
FW.J0GCK42AA003OD | 3512 | #2二级反渗透高压泵出口阀开启 |  | digital
FW.J0GCK42AA003OP | 3513 | #2二级反渗高压泵出口阀开到位 |  | digital
FW.J0GCK42AP001_F | 3514 | Ovation Control Builder |  | digital
FW.J0GCK42AP001_LP | 3515 | #2二级反渗透高压泵 |  | int32
FW.J0GCK42AP001_LP1 | 3516 | Ovation Control Builder |  | int32
FW.J0GCK42AP001_LP2 | 3517 | Ovation Control Builder |  | int32
FW.J0GCK42AP001_MODE | 3518 | Ovation Control Builder |  | int32
FW.J0GCK42AP001_SPO | 3519 | Ovation Control Builder |  | float32
FW.J0GCK42AP001C | 3520 | #2二级反渗透高压泵给定 |  | float32
FW.J0GCK42AP001CL | 3521 | Ovation Control Builder |  | float32
FW.J0GCK42AP001I | 3522 | Ovation Control Builder |  | float32
FW.J0GCK42AP001IL | 3523 | #2二级反渗透高压泵电流 |  | float32
FW.J0GCK42AP001P | 3524 | #2二级反渗透高压泵反馈 |  | float32
FW.J0GCK42AP001PF | 3525 | #2二级反渗透高压泵故障 |  | digital
FW.J0GCK42AP001PL | 3526 | Ovation Control Builder |  | float32
FW.J0GCK42AP001RC | 3527 | #2二级反渗透高压泵远方 |  | digital
FW.J0GCK42AP001RD | 3528 | #2二级反渗透高压泵启动 |  | digital
FW.J0GCK42AP001RP | 3529 | #2二级反渗透高压泵运行 |  | digital
FW.J0GCK42AP001TD | 3530 | #2二级反渗透高压泵停止 |  | digital
FW.J0GCK42CP002H | 3531 | #2二级反渗透高压泵出口压力高 |  | digital
FW.J0GCK42CP101 | 3532 | #2二级RO保安过滤器进出口差压 | Hz | float32
FW.J0GCK42CP101L | 3533 | #2二级RO保安过滤器进出口差压 |  | float32
FW.J0GCK43AA003_LP | 3534 | #3二级反渗透高压泵出口门 |  | int32
FW.J0GCK43AA003CD | 3535 | #3二级反渗透高压泵出口阀关闭 |  | digital
FW.J0GCK43AA003CP | 3536 | #3二级反渗透高压泵出口阀关到 |  | digital
FW.J0GCK43AA003OD | 3537 | #3二级反渗透高压泵出口阀开启 |  | digital
FW.J0GCK43AA003OP | 3538 | #3二级反渗透高压泵出口阀开到 |  | digital
FW.J0GCK43AP001_F | 3539 | Ovation Control Builder |  | digital
FW.J0GCK43AP001_LP | 3540 | #3二级反渗透高压泵 |  | int32
FW.J0GCK43AP001_LP1 | 3541 | Ovation Control Builder |  | int32
FW.J0GCK43AP001_LP2 | 3542 | Ovation Control Builder |  | int32
FW.J0GCK43AP001_MODE | 3543 | Ovation Control Builder |  | int32
FW.J0GCK43AP001_SPO | 3544 | Ovation Control Builder |  | float32
FW.J0GCK43AP001C | 3545 | #3二级反渗透高压泵给定 |  | float32
FW.J0GCK43AP001CL | 3546 | Ovation Control Builder |  | float32
FW.J0GCK43AP001I | 3547 | Ovation Control Builder |  | float32
FW.J0GCK43AP001IL | 3548 | #3二级反渗透高压泵电流 |  | float32
FW.J0GCK43AP001P | 3549 | #3二级反渗透高压泵反馈 |  | float32
FW.J0GCK43AP001PF | 3550 | #3二级反渗透高压泵故障 |  | digital
FW.J0GCK43AP001PL | 3551 | Ovation Control Builder |  | float32
FW.J0GCK43AP001RC | 3552 | #3二级反渗透高压泵远方 |  | digital
FW.J0GCK43AP001RD | 3553 | #3二级反渗透高压泵启动 |  | digital
FW.J0GCK43AP001RP | 3554 | #3二级反渗透高压泵运行 |  | digital
FW.J0GCK43AP001TD | 3555 | #3二级反渗透高压泵停止 |  | digital
FW.J0GCK43CP002H | 3556 | #3二级反渗透高压泵出口压力高 |  | digital
FW.J0GCK43CP101 | 3557 | #3二级RO保安过滤器进出口差压 | Hz | float32
FW.J0GCK43CP101L | 3558 | #3二级RO保安过滤器进出口差压 |  | float32
FW.J0GCK44AA003_LP | 3559 | #4二级反渗透高压泵出口门 |  | int32
FW.J0GCK44AA003CD | 3560 | #4二级反渗透高压泵出口阀关闭 |  | digital
FW.J0GCK44AA003CP | 3561 | #4二级反渗透高压泵出口阀关到 |  | digital
FW.J0GCK44AA003OD | 3562 | #4二级反渗透高压泵出口阀开启 |  | digital
FW.J0GCK44AA003OP | 3563 | #4二级反渗透高压泵出口阀开到 |  | digital
FW.J0GCK44AP001_F | 3564 | Ovation Control Builder |  | digital
FW.J0GCK44AP001_LP | 3565 | #4二级反渗透高压泵 |  | int32
FW.J0GCK44AP001_LP1 | 3566 | Ovation Control Builder |  | int32
FW.J0GCK44AP001_LP2 | 3567 | Ovation Control Builder |  | int32
FW.J0GCK44AP001_MODE | 3568 | Ovation Control Builder |  | int32
FW.J0GCK44AP001_SPO | 3569 | Ovation Control Builder |  | float32
FW.J0GCK44AP001C | 3570 | #4二级反渗透高压泵给定 |  | float32
FW.J0GCK44AP001CL | 3571 | Ovation Control Builder |  | float32
FW.J0GCK44AP001I | 3572 | Ovation Control Builder |  | float32
FW.J0GCK44AP001IL | 3573 | #4二级反渗透高压泵电流 |  | float32
FW.J0GCK44AP001P | 3574 | #4二级反渗透高压泵反馈 |  | float32
FW.J0GCK44AP001PF | 3575 | #4二级反渗透高压泵故障 |  | digital
FW.J0GCK44AP001PL | 3576 | Ovation Control Builder |  | float32
FW.J0GCK44AP001RC | 3577 | #4二级反渗透高压泵远方 |  | digital
FW.J0GCK44AP001RD | 3578 | #4二级反渗透高压泵启动 |  | digital
FW.J0GCK44AP001RP | 3579 | #4二级反渗透高压泵运行 |  | digital
FW.J0GCK44AP001TD | 3580 | #4二级反渗透高压泵停止 |  | digital
FW.J0GCK44CP002H | 3581 | #4二级反渗透高压泵出口压力高 |  | digital
FW.J0GCK44CP101 | 3582 | #4二级RO保安过滤器进出口差压 | Hz | float32
FW.J0GCK44CP101L | 3583 | #4二级RO保安过滤器进出口差压 |  | float32
FW.J0GCK50CL101 | 3584 | #1二级反渗透产水箱液位 | Hz | float32
FW.J0GCK50CL102 | 3585 | #2二级反渗透产水箱液位 |  | float32
FW.J0GCK51AP001_F | 3586 | Ovation Control Builder |  | digital
FW.J0GCK51AP001_LP | 3587 | #1EDI给水泵 |  | int32
FW.J0GCK51AP001_LP1 | 3588 | Ovation Control Builder |  | int32
FW.J0GCK51AP001_LP2 | 3589 | Ovation Control Builder |  | int32
FW.J0GCK51AP001_MODE | 3590 | Ovation Control Builder |  | int32
FW.J0GCK51AP001_SPO | 3591 | Ovation Control Builder |  | float32
FW.J0GCK51AP001C | 3592 | #1EDI给水泵给定 |  | float32
FW.J0GCK51AP001CL | 3593 | Ovation Control Builder |  | float32
FW.J0GCK51AP001I | 3594 |  |  | float32
FW.J0GCK51AP001IL | 3595 | #1EDI升压泵电流 |  | float32
FW.J0GCK51AP001P | 3596 | #1EDI给水泵反馈 |  | float32
FW.J0GCK51AP001PF | 3597 | #1EDI给水泵故障 |  | digital
FW.J0GCK51AP001PL | 3598 | Ovation Control Builder |  | float32
FW.J0GCK51AP001RC | 3599 | #1EDI给水泵远方 |  | digital
FW.J0GCK51AP001RD | 3600 | #1EDI给水泵启动 |  | digital
FW.J0GCK51AP001RP | 3601 | #1EDI给水泵运行 |  | digital
FW.J0GCK51AP001TD | 3602 | #1EDI给水泵停止 |  | digital
FW.J0GCK51CF101 | 3603 | #1EDI装置进水流量 | Hz | float32
FW.J0GCK51CF101L | 3604 | #1EDI装置进水流量累计 |  | float32
FW.J0GCK51CP101 | 3605 | #1EDI保安过滤器进出口差压 | Hz | float32
FW.J0GCK51CP101L | 3606 | #1EDI保安过滤器进出口差压 |  | float32
FW.J0GCK51CQ101 | 3607 | EDI给水泵进水母管PH | Hz | float32
FW.J0GCK51CQ102 | 3608 | EDI给水泵进水母管电导率 | Hz | float32
FW.J0GCK52AP001_F | 3609 | Ovation Control Builder |  | digital
FW.J0GCK52AP001_LP | 3610 | #2EDI给水泵 |  | int32
FW.J0GCK52AP001_LP1 | 3611 | Ovation Control Builder |  | int32
FW.J0GCK52AP001_LP2 | 3612 | Ovation Control Builder |  | int32
FW.J0GCK52AP001_MODE | 3613 | Ovation Control Builder |  | int32
FW.J0GCK52AP001_SPO | 3614 | Ovation Control Builder |  | float32
FW.J0GCK52AP001C | 3615 | #2EDI给水泵给定 |  | float32
FW.J0GCK52AP001CL | 3616 | Ovation Control Builder |  | float32
FW.J0GCK52AP001I | 3617 | Ovation Control Builder |  | float32
FW.J0GCK52AP001IL | 3618 | #2EDI升压泵电流 |  | float32
FW.J0GCK52AP001P | 3619 | #2EDI给水泵反馈 |  | float32
FW.J0GCK52AP001PF | 3620 | #2EDI给水泵故障 |  | digital
FW.J0GCK52AP001PL | 3621 | Ovation Control Builder |  | float32
FW.J0GCK52AP001RC | 3622 | #2EDI给水泵远方 |  | digital
FW.J0GCK52AP001RD | 3623 | #2EDI给水泵启动 |  | digital
FW.J0GCK52AP001RP | 3624 | #2EDI给水泵运行 |  | digital
FW.J0GCK52AP001TD | 3625 | #2EDI给水泵停止 |  | digital
FW.J0GCK52CF101 | 3626 | #2EDI装置进水流量 | Hz | float32
FW.J0GCK52CF101L | 3627 | #2EDI装置进水流量累计 |  | float32
FW.J0GCK52CP101 | 3628 | #2EDI保安过滤器进出口差压 | Hz | float32
FW.J0GCK52CP101L | 3629 | #2EDI保安过滤器进出口差压 |  | float32
FW.J0GCK53AP001_F | 3630 | Ovation Control Builder |  | digital
FW.J0GCK53AP001_LP | 3631 | #3EDI给水泵 |  | int32
FW.J0GCK53AP001_LP1 | 3632 | Ovation Control Builder |  | int32
FW.J0GCK53AP001_LP2 | 3633 | Ovation Control Builder |  | int32
FW.J0GCK53AP001_MODE | 3634 | Ovation Control Builder |  | int32
FW.J0GCK53AP001_SPO | 3635 | Ovation Control Builder |  | float32
FW.J0GCK53AP001C | 3636 | #3EDI给水泵给定 |  | float32
FW.J0GCK53AP001CL | 3637 | Ovation Control Builder |  | float32
FW.J0GCK53AP001I | 3638 | Ovation Control Builder |  | float32
FW.J0GCK53AP001IL | 3639 | #3EDI升压泵电流 |  | float32
FW.J0GCK53AP001P | 3640 | #3EDI给水泵反馈 |  | float32
FW.J0GCK53AP001PF | 3641 | #3EDI给水泵故障 |  | digital
FW.J0GCK53AP001PL | 3642 | Ovation Control Builder |  | float32
FW.J0GCK53AP001RC | 3643 | #3EDI给水泵远方 |  | digital
FW.J0GCK53AP001RD | 3644 | #3EDI给水泵启动 |  | digital
FW.J0GCK53AP001RP | 3645 | #3EDI给水泵运行 |  | digital
FW.J0GCK53AP001TD | 3646 | #3EDI给水泵停止 |  | digital
FW.J0GCK53CF101 | 3647 | #3EDI装置进水流量 | Hz | float32
FW.J0GCK53CF101L | 3648 | #3EDI装置进水流量累计 |  | float32
FW.J0GCK53CP101 | 3649 | #3EDI保安过滤器进出口差压 | Hz | float32
FW.J0GCK53CP101L | 3650 | #3EDI保安过滤器进出口差压 |  | float32
FW.J0GCK54AP001_F | 3651 | Ovation Control Builder |  | digital
FW.J0GCK54AP001_LP | 3652 | #4EDI给水泵 |  | int32
FW.J0GCK54AP001_LP1 | 3653 | Ovation Control Builder |  | int32
FW.J0GCK54AP001_LP2 | 3654 | Ovation Control Builder |  | int32
FW.J0GCK54AP001_MODE | 3655 | Ovation Control Builder |  | int32
FW.J0GCK54AP001_SPO | 3656 | Ovation Control Builder |  | float32
FW.J0GCK54AP001C | 3657 | #4EDI给水泵频率给定 |  | float32
FW.J0GCK54AP001CL | 3658 | Ovation Control Builder |  | float32
FW.J0GCK54AP001I | 3659 | Ovation Control Builder |  | float32
FW.J0GCK54AP001IL | 3660 | #4EDI升压泵电流 |  | float32
FW.J0GCK54AP001P | 3661 | #4EDI给水泵反馈 |  | float32
FW.J0GCK54AP001PF | 3662 | #4EDI给水泵故障 |  | digital
FW.J0GCK54AP001PL | 3663 | Ovation Control Builder |  | float32
FW.J0GCK54AP001RC | 3664 | #4EDI给水泵远方 |  | digital
FW.J0GCK54AP001RD | 3665 | #4EDI给水泵启动 |  | digital
FW.J0GCK54AP001RP | 3666 | #4EDI给水泵运行 |  | digital
FW.J0GCK54AP001TD | 3667 | #4EDI给水泵停止 |  | digital
FW.J0GCK54CF101 | 3668 | #4EDI装置进水流量 | Hz | float32
FW.J0GCK54CF101L | 3669 | #4EDI装置进水流量累计 |  | float32
FW.J0GCK54CP101 | 3670 | #4EDI保安过滤器进出口差压 | Hz | float32
FW.J0GCK54CP101L | 3671 | #4EDI保安过滤器进出口差压 |  | float32
FW.J0GCK60CF101 | 3672 | 除盐水供水母管流量A | Hz | float32
FW.J0GCK60CF101B | 3673 | 除盐水供水母管流量B | Hz | float32
FW.J0GCK60CF101L | 3674 | 除盐水供水母管流量累计 |  | float32
FW.J0GCK60CP101 | 3675 | 除盐水供水母管压力 | Hz | float32
FW.J0GCK60CP101L | 3676 | 除盐水供水母管压力 |  | float32
FW.J0GCK60CQ101 | 3677 | 除盐水供水母管电导率 | Hz | float32
FW.J0GCK60CQ102 | 3678 | 除盐水供水母管硅酸根浓度 | Hz | float32
FW.J0GCK61AP001_LP | 3679 | #1除盐水泵 |  | int32
FW.J0GCK61AP001_LPIN1 | 3680 | Ovation Control Builder |  | int32
FW.J0GCK61AP001_LPOUT1 | 3681 | Ovation Control Builder |  | int32
FW.J0GCK61AP001I | 3682 | Ovation Control Builder |  | float32
FW.J0GCK61AP001IL | 3683 | #1除盐水泵电流 |  | float32
FW.J0GCK61AP001RC | 3684 | #1除盐水泵远方 |  | digital
FW.J0GCK61AP001RD | 3685 | #1除盐水泵启动 |  | digital
FW.J0GCK61AP001RP | 3686 | #1除盐水泵运行 |  | digital
FW.J0GCK61AP001TD | 3687 | #1除盐水泵停止 |  | digital
FW.J0GCK62AP001_LP | 3688 | #2除盐水泵 |  | int32
FW.J0GCK62AP001_LPIN1 | 3689 | Ovation Control Builder |  | int32
FW.J0GCK62AP001_LPOUT1 | 3690 | Ovation Control Builder |  | int32
FW.J0GCK62AP001I | 3691 | Ovation Control Builder |  | float32
FW.J0GCK62AP001IL | 3692 | #2除盐水泵电流 |  | float32
FW.J0GCK62AP001RC | 3693 | #2除盐水泵远方 |  | digital
FW.J0GCK62AP001RD | 3694 | #2除盐水泵启动 |  | digital
FW.J0GCK62AP001RP | 3695 | #2除盐水泵运行 |  | digital
FW.J0GCK62AP001TD | 3696 | #2除盐水泵停止 |  | digital
FW.J0GCK62CT301 | 3697 | #2除盐水泵电机线圈温度1 | ℃ | float32
FW.J0GCK62CT302 | 3698 | #2除盐水泵电机线圈温度2 | DEG | float32
FW.J0GCK62CT303 | 3699 | #2除盐水泵电机线圈温度3 | DEG | float32
FW.J0GCK62CT304 | 3700 | #2除盐水泵电机线圈温度4 | DEG | float32
FW.J0GCK62CT305 | 3701 | #2除盐水泵电机线圈温度5 | DEG | float32
FW.J0GCK62CT306 | 3702 | #2除盐水泵电机线圈温度6 | DEG | float32
FW.J0GCK62CT307 | 3703 | #2除盐水泵电机前轴承温度 | DEG | float32
FW.J0GCK62CT308 | 3704 | #2除盐水泵电机后轴承温度 | DEG | float32
FW.J0GCK63AP001_F | 3705 | Ovation Control Builder |  | digital
FW.J0GCK63AP001_LP | 3706 | #3除盐水泵 |  | int32
FW.J0GCK63AP001_LP1 | 3707 | Ovation Control Builder |  | int32
FW.J0GCK63AP001_LP2 | 3708 | Ovation Control Builder |  | int32
FW.J0GCK63AP001_MODE | 3709 | Ovation Control Builder |  | int32
FW.J0GCK63AP001_SPO | 3710 | Ovation Control Builder |  | float32
FW.J0GCK63AP001C | 3711 | #3除盐水泵频率给定 |  | float32
FW.J0GCK63AP001CL | 3712 | Ovation Control Builder |  | float32
FW.J0GCK63AP001I | 3713 | Ovation Control Builder |  | float32
FW.J0GCK63AP001IL | 3714 | #3除盐水泵电流 |  | float32
FW.J0GCK63AP001P | 3715 | #3除盐水泵频率反馈 |  | float32
FW.J0GCK63AP001PF | 3716 | #3除盐水泵故障 |  | digital
FW.J0GCK63AP001PL | 3717 | Ovation Control Builder |  | float32
FW.J0GCK63AP001RC | 3718 | #3除盐水泵远方 |  | digital
FW.J0GCK63AP001RD | 3719 | #3除盐水泵启动 |  | digital
FW.J0GCK63AP001RP | 3720 | #3除盐水泵运行 |  | digital
FW.J0GCK63AP001TD | 3721 | #3除盐水泵停止 |  | digital
FW.J0GCK63CT301 | 3722 | #3除盐水泵电机线圈温度1 | DEG | float32
FW.J0GCK63CT302 | 3723 | #3除盐水泵电机线圈温度2 | DEG | float32
FW.J0GCK63CT303 | 3724 | #3除盐水泵电机线圈温度3 | DEG | float32
FW.J0GCK63CT304 | 3725 | #3除盐水泵电机线圈温度4 | DEG | float32
FW.J0GCK63CT305 | 3726 | #3除盐水泵电机线圈温度5 | DEG | float32
FW.J0GCK63CT306 | 3727 | #3除盐水泵电机线圈温度6 | DEG | float32
FW.J0GCK63CT307 | 3728 | #3除盐水泵电机前轴承温度 | DEG | float32
FW.J0GCK63CT308 | 3729 | #3除盐水泵电机后轴承温度 | DEG | float32
FW.J0GCK64AP001_F | 3730 | Ovation Control Builder |  | digital
FW.J0GCK64AP001_LP | 3731 | #4除盐水泵 |  | int32
FW.J0GCK64AP001_LP1 | 3732 | Ovation Control Builder |  | int32
FW.J0GCK64AP001_LP2 | 3733 | Ovation Control Builder |  | int32
FW.J0GCK64AP001_MODE | 3734 | Ovation Control Builder |  | int32
FW.J0GCK64AP001_SPO | 3735 | Ovation Control Builder |  | float32
FW.J0GCK64AP001C | 3736 | #4除盐水泵频率给定 |  | float32
FW.J0GCK64AP001CL | 3737 | Ovation Control Builder |  | float32
FW.J0GCK64AP001I | 3738 | Ovation Control Builder |  | float32
FW.J0GCK64AP001IL | 3739 | #4除盐水泵电流 |  | float32
FW.J0GCK64AP001P | 3740 | #4除盐水泵频率反馈 |  | float32
FW.J0GCK64AP001PF | 3741 | #4除盐水泵故障 |  | digital
FW.J0GCK64AP001PL | 3742 | Ovation Control Builder |  | float32
FW.J0GCK64AP001RC | 3743 | #4除盐水泵远方 |  | digital
FW.J0GCK64AP001RD | 3744 | #4除盐水泵启动 |  | digital
FW.J0GCK64AP001RP | 3745 | #4除盐水泵运行 |  | digital
FW.J0GCK64AP001TD | 3746 | #4除盐水泵停止 |  | digital
FW.J0GCK64CT301 | 3747 | #4除盐水泵电机线圈温度1 | DEG | float32
FW.J0GCK64CT302 | 3748 | #4除盐水泵电机线圈温度2 | DEG | float32
FW.J0GCK64CT303 | 3749 | #4除盐水泵电机线圈温度3 | DEG | float32
FW.J0GCK64CT304 | 3750 | #4除盐水泵电机线圈温度4 | DEG | float32
FW.J0GCK64CT305 | 3751 | #4除盐水泵电机线圈温度5 | DEG | float32
FW.J0GCK64CT306 | 3752 | #4除盐水泵电机线圈温度6 | DEG | float32
FW.J0GCK64CT307 | 3753 | #4除盐水泵电机前轴承温度 | DEG | float32
FW.J0GCK64CT308 | 3754 | #4除盐水泵电机后轴承温度 | DEG | float32
FW.J0GCL61AP001_LP | 3755 | #1回收水泵 |  | int32
FW.J0GCL61AP001_LPIN1 | 3756 | Ovation Control Builder |  | int32
FW.J0GCL61AP001_LPOUT1 | 3757 | Ovation Control Builder |  | int32
FW.J0GCL61AP001I | 3758 | Ovation Control Builder |  | float32
FW.J0GCL61AP001IL | 3759 | #1回收水泵电流 |  | float32
FW.J0GCL61AP001RC | 3760 | #1回收水泵远方 |  | digital
FW.J0GCL61AP001RD | 3761 | #1回收水泵启动 |  | digital
FW.J0GCL61AP001RP | 3762 | #1回收水泵运行 |  | digital
FW.J0GCL61AP001TD | 3763 | #1回收水泵停止 |  | digital
FW.J0GCL61CL101 | 3764 | #1回收水池液位 | Hz | float32
FW.J0GCL61CL101_LSTR | 3765 | #1回收水泵联锁投入 |  | digital
FW.J0GCL61CP101 | 3766 | 回收水泵出口母管压力 | Hz | float32
FW.J0GCL62AP001_LP | 3767 | #2回收水泵 |  | int32
FW.J0GCL62AP001_LPIN1 | 3768 | Ovation Control Builder |  | int32
FW.J0GCL62AP001_LPOUT1 | 3769 | Ovation Control Builder |  | int32
FW.J0GCL62AP001I | 3770 | Ovation Control Builder |  | float32
FW.J0GCL62AP001IL | 3771 | #2回收水泵电流 |  | float32
FW.J0GCL62AP001RC | 3772 | #2回收水泵远方 |  | digital
FW.J0GCL62AP001RD | 3773 | #2回收水泵启动 |  | digital
FW.J0GCL62AP001RP | 3774 | #2回收水泵运行 |  | digital
FW.J0GCL62AP001TD | 3775 | #2回收水泵停止 |  | digital
FW.J0GCL62CL101 | 3776 | #2回收水池液位 | Hz | float32
FW.J0GCL62CL101_LSTR | 3777 | #2回收水泵联锁投入 |  | digital
FW.J0GCL70CL101 | 3778 | 一级RO浓水缓冲池液位 | m | float32
FW.J0GCL71AP001_LP | 3779 | #1一级RO浓水排水泵 |  | int32
FW.J0GCL71AP001_LSTR | 3780 | #1一级RO浓水排水泵联锁投入 |  | digital
FW.J0GCL71AP001I | 3781 | #1一级反渗透浓水排水泵电流 | A | float32
FW.J0GCL71AP001PF | 3782 | #1一级RO浓水排水泵故障 |  | digital
FW.J0GCL71AP001RC | 3783 | #1一级RO浓水排水泵在远控 |  | digital
FW.J0GCL71AP001RD | 3784 | #1一级RO浓水排水泵合闸指令 |  | digital
FW.J0GCL71AP001RI | 3785 | #1一级反渗透浓水排水泵电流 | A | float32
FW.J0GCL71AP001RP | 3786 | #1一级RO浓水排水泵在运行 |  | digital
FW.J0GCL71AP001TD | 3787 | #1一级RO浓水排水泵跳闸指令 |  | digital
FW.J0GCL71AP001TP | 3788 | #1一级RO浓水排水泵已停止 |  | digital
FW.J0GCL72AP001_LP | 3789 | #2一级RO浓水排水泵 |  | int32
FW.J0GCL72AP001_LSTR | 3790 | #2一级RO浓水排水泵联锁投入 |  | digital
FW.J0GCL72AP001I | 3791 | #2一级反渗透浓水排水泵电流 | A | float32
FW.J0GCL72AP001PF | 3792 | #2一级RO浓水排水泵综合故障 |  | digital
FW.J0GCL72AP001RC | 3793 | #2一级RO浓水排水泵在远控 |  | digital
FW.J0GCL72AP001RD | 3794 | #2一级RO浓水排水泵合闸指令 |  | digital
FW.J0GCL72AP001RI | 3795 | #2一级RO浓水排水泵电流 | A | float32
FW.J0GCL72AP001RP | 3796 | #2一级RO浓水排水泵在运行 |  | digital
FW.J0GCL72AP001TD | 3797 | #2一级RO浓水排水泵跳闸指令 |  | digital
FW.J0GCL72AP001TP | 3798 | #2一级RO浓水排水泵已停止 |  | digital
FW.J0GCL73AP001_LP | 3799 | #3一级RO浓水排水泵 |  | int32
FW.J0GCL73AP001_LSTR | 3800 | #3一级RO浓水排水泵联锁投入 |  | digital
FW.J0GCL73AP001I | 3801 | #3一级反渗透浓水排水泵电流 | A | float32
FW.J0GCL73AP001PF | 3802 | #3一级RO浓水排水泵综合故障 |  | digital
FW.J0GCL73AP001RC | 3803 | #3一级RO浓水排水泵在远控 |  | digital
FW.J0GCL73AP001RD | 3804 | #3一级RO浓水排水泵合闸指令 |  | digital
FW.J0GCL73AP001RI | 3805 | #3一级RO浓水排水泵电流 | A | float32
FW.J0GCL73AP001RP | 3806 | #3一级RO浓水排水泵在运行 |  | digital
FW.J0GCL73AP001TD | 3807 | #3一级RO浓水排水泵分闸指令 |  | digital
FW.J0GCL73AP001TP | 3808 | #3一级RO浓水排水泵已停止 |  | digital
FW.J0GCQ11AP001_CHOOSE | 3809 | #1杀菌剂计量泵选择 |  | digital
FW.J0GCQ11AP001_F | 3810 | Ovation Control Builder |  | digital
FW.J0GCQ11AP001_LP | 3811 | #1杀菌剂计量泵 |  | int32
FW.J0GCQ11AP001_LP1 | 3812 | Ovation Control Builder |  | int32
FW.J0GCQ11AP001_LP2 | 3813 | Ovation Control Builder |  | int32
FW.J0GCQ11AP001_MODE | 3814 | Ovation Control Builder |  | int32
FW.J0GCQ11AP001_SPO | 3815 | Ovation Control Builder |  | float32
FW.J0GCQ11AP001C | 3816 | #1杀菌剂计量泵频率给定 |  | float32
FW.J0GCQ11AP001CL | 3817 | Ovation Control Builder |  | float32
FW.J0GCQ11AP001I | 3818 | Ovation Control Builder |  | float32
FW.J0GCQ11AP001IL | 3819 | #1杀菌剂计量泵电流 |  | float32
FW.J0GCQ11AP001P | 3820 | #1杀菌剂计量泵频率反馈 |  | float32
FW.J0GCQ11AP001PF | 3821 | #1杀菌剂计量泵故障 |  | digital
FW.J0GCQ11AP001PL | 3822 | Ovation Control Builder |  | float32
FW.J0GCQ11AP001RC | 3823 | #1杀菌剂计量泵远方 |  | digital
FW.J0GCQ11AP001RD | 3824 | #1杀菌剂计量泵启动 |  | digital
FW.J0GCQ11AP001RP | 3825 | #1杀菌剂计量泵运行 |  | digital
FW.J0GCQ11AP001TD | 3826 | #1杀菌剂计量泵停止 |  | digital
FW.J0GCQ11AP002_CHOOSE | 3827 | #2杀菌剂计量泵选择 |  | digital
FW.J0GCQ11AP002_F | 3828 | Ovation Control Builder |  | digital
FW.J0GCQ11AP002_LP | 3829 | #2杀菌剂计量泵 |  | int32
FW.J0GCQ11AP002_LP1 | 3830 | Ovation Control Builder |  | int32
FW.J0GCQ11AP002_LP2 | 3831 | Ovation Control Builder |  | int32
FW.J0GCQ11AP002_MODE | 3832 | Ovation Control Builder |  | int32
FW.J0GCQ11AP002_SPO | 3833 | Ovation Control Builder |  | float32
FW.J0GCQ11AP002C | 3834 | #2杀菌剂计量泵频率给定 |  | float32
FW.J0GCQ11AP002CL | 3835 | Ovation Control Builder |  | float32
FW.J0GCQ11AP002I | 3836 | Ovation Control Builder |  | float32
FW.J0GCQ11AP002IL | 3837 | #2杀菌剂计量泵电流 |  | float32
FW.J0GCQ11AP002P | 3838 | #2杀菌剂计量泵频率反馈 |  | float32
FW.J0GCQ11AP002PF | 3839 | #2杀菌剂计量泵故障 |  | digital
FW.J0GCQ11AP002PL | 3840 | Ovation Control Builder |  | float32
FW.J0GCQ11AP002RC | 3841 | #2杀菌剂计量泵远方 |  | digital
FW.J0GCQ11AP002RD | 3842 | #2杀菌剂计量泵启动 |  | digital
FW.J0GCQ11AP002RP | 3843 | #2杀菌剂计量泵运行 |  | digital
FW.J0GCQ11AP002TD | 3844 | #2杀菌剂计量泵停止 |  | digital
FW.J0GCQ11CL501 | 3845 | 次氯酸钠溶液箱液位 | Hz | float32
FW.J0GCQ21AP001_CHOOSE | 3846 | #1加酸计量泵选择 |  | digital
FW.J0GCQ21AP001_F | 3847 | Ovation Control Builder |  | digital
FW.J0GCQ21AP001_LP | 3848 | #1加酸计量泵 |  | int32
FW.J0GCQ21AP001_LP1 | 3849 | Ovation Control Builder |  | int32
FW.J0GCQ21AP001_LP2 | 3850 | Ovation Control Builder |  | int32
FW.J0GCQ21AP001_MODE | 3851 | Ovation Control Builder |  | int32
FW.J0GCQ21AP001_SPO | 3852 | Ovation Control Builder |  | float32
FW.J0GCQ21AP001C | 3853 | #1加酸计量泵频率给定 |  | float32
FW.J0GCQ21AP001CL | 3854 | Ovation Control Builder |  | float32
FW.J0GCQ21AP001I | 3855 | Ovation Control Builder |  | float32
FW.J0GCQ21AP001IL | 3856 | #1加酸计量泵电流 |  | float32
FW.J0GCQ21AP001P | 3857 | #1加酸计量泵频率反馈 |  | float32
FW.J0GCQ21AP001PF | 3858 | #1加酸计量泵故障 |  | digital
FW.J0GCQ21AP001PL | 3859 | Ovation Control Builder |  | float32
FW.J0GCQ21AP001RC | 3860 | #1加酸计量泵远方 |  | digital
FW.J0GCQ21AP001RD | 3861 | #1加酸计量泵启动 |  | digital
FW.J0GCQ21AP001RP | 3862 | #1加酸计量泵运行 |  | digital
FW.J0GCQ21AP001TD | 3863 | #1加酸计量泵停止 |  | digital
FW.J0GCQ21CL501 | 3864 | 次酸溶液箱液位 | Hz | float32
FW.J0GCQ22AP002_CHOOSE | 3865 | #2加酸计量泵选择 |  | digital
FW.J0GCQ22AP002_F | 3866 | Ovation Control Builder |  | digital
FW.J0GCQ22AP002_LP | 3867 | #2加酸计量泵 |  | int32
FW.J0GCQ22AP002_LP1 | 3868 | Ovation Control Builder |  | int32
FW.J0GCQ22AP002_LP2 | 3869 | Ovation Control Builder |  | int32
FW.J0GCQ22AP002_MODE | 3870 | Ovation Control Builder |  | int32
FW.J0GCQ22AP002_SPO | 3871 | Ovation Control Builder |  | float32
FW.J0GCQ22AP002C | 3872 | #2加酸计量泵频率给定 |  | float32
FW.J0GCQ22AP002CL | 3873 | Ovation Control Builder |  | float32
FW.J0GCQ22AP002I | 3874 | Ovation Control Builder |  | float32
FW.J0GCQ22AP002IL | 3875 | #2加酸计量泵电流 |  | float32
FW.J0GCQ22AP002P | 3876 | #2加酸计量泵频率反馈 |  | float32
FW.J0GCQ22AP002PF | 3877 | #2加酸计量泵故障 |  | digital
FW.J0GCQ22AP002PL | 3878 | Ovation Control Builder |  | float32
FW.J0GCQ22AP002RC | 3879 | #2加酸计量泵远方 |  | digital
FW.J0GCQ22AP002RD | 3880 | #2加酸计量泵启动 |  | digital
FW.J0GCQ22AP002RP | 3881 | #2加酸计量泵运行 |  | digital
FW.J0GCQ22AP002TD | 3882 | #2加酸计量泵停止 |  | digital
FW.J0GCQ31AP001_CHOOSE | 3883 | #1阻垢剂计量泵选择 |  | digital
FW.J0GCQ31AP001_F | 3884 | Ovation Control Builder |  | digital
FW.J0GCQ31AP001_LP | 3885 | #1阻垢剂计量泵 |  | int32
FW.J0GCQ31AP001_LP1 | 3886 | Ovation Control Builder |  | int32
FW.J0GCQ31AP001_LP2 | 3887 | Ovation Control Builder |  | int32
FW.J0GCQ31AP001_MODE | 3888 | Ovation Control Builder |  | int32
FW.J0GCQ31AP001_SPO | 3889 | Ovation Control Builder |  | float32
FW.J0GCQ31AP001C | 3890 | #1阻垢剂计量泵给定 |  | float32
FW.J0GCQ31AP001CL | 3891 | Ovation Control Builder |  | float32
FW.J0GCQ31AP001I | 3892 | Ovation Control Builder |  | float32
FW.J0GCQ31AP001IL | 3893 | #1阻垢剂计量泵电流 |  | float32
FW.J0GCQ31AP001P | 3894 | #1阻垢剂计量泵反馈 |  | float32
FW.J0GCQ31AP001PF | 3895 | #1阻垢剂计量泵故障 |  | digital
FW.J0GCQ31AP001PL | 3896 | Ovation Control Builder |  | float32
FW.J0GCQ31AP001RC | 3897 | #1阻垢剂计量泵远方 |  | digital
FW.J0GCQ31AP001RD | 3898 | #1阻垢剂计量泵启动 |  | digital
FW.J0GCQ31AP001RP | 3899 | #1阻垢剂计量泵运行 |  | digital
FW.J0GCQ31AP001TD | 3900 | #1阻垢剂计量泵停止 |  | digital
FW.J0GCQ31AP002_CHOOSE | 3901 | #2阻垢剂计量泵选择 |  | digital
FW.J0GCQ31AP002_F | 3902 | Ovation Control Builder |  | digital
FW.J0GCQ31AP002_LP | 3903 | #2阻垢剂计量泵 |  | int32
FW.J0GCQ31AP002_LP1 | 3904 | Ovation Control Builder |  | int32
FW.J0GCQ31AP002_LP2 | 3905 | Ovation Control Builder |  | int32
FW.J0GCQ31AP002_MODE | 3906 | Ovation Control Builder |  | int32
FW.J0GCQ31AP002_SPO | 3907 | Ovation Control Builder |  | float32
FW.J0GCQ31AP002C | 3908 | #2阻垢剂计量泵给定 |  | float32
FW.J0GCQ31AP002CL | 3909 | Ovation Control Builder |  | float32
FW.J0GCQ31AP002I | 3910 | Ovation Control Builder |  | float32
FW.J0GCQ31AP002IL | 3911 | #2阻垢剂计量泵电流 |  | float32
FW.J0GCQ31AP002P | 3912 | #2阻垢剂计量泵反馈 |  | float32
FW.J0GCQ31AP002PF | 3913 | #2阻垢剂计量泵故障 |  | digital
FW.J0GCQ31AP002PL | 3914 | Ovation Control Builder |  | float32
FW.J0GCQ31AP002RC | 3915 | #2阻垢剂计量泵远方 |  | digital
FW.J0GCQ31AP002RD | 3916 | #2阻垢剂计量泵启动 |  | digital
FW.J0GCQ31AP002RP | 3917 | #2阻垢剂计量泵运行 |  | digital
FW.J0GCQ31AP002TD | 3918 | #2阻垢剂计量泵停止 |  | digital
FW.J0GCQ31CL501 | 3919 | #1阻垢剂溶液箱液位 | Hz | float32
FW.J0GCQ31CL502 | 3920 | #2阻垢剂溶液箱液位 | Hz | float32
FW.J0GCQ41AP001_CHOOSE | 3921 | #1还原剂计量泵选择 |  | digital
FW.J0GCQ41AP001_F | 3922 | Ovation Control Builder |  | digital
FW.J0GCQ41AP001_LP | 3923 | #1还原剂计量泵 |  | int32
FW.J0GCQ41AP001_LP1 | 3924 | Ovation Control Builder |  | int32
FW.J0GCQ41AP001_LP2 | 3925 | Ovation Control Builder |  | int32
FW.J0GCQ41AP001_MODE | 3926 | Ovation Control Builder |  | int32
FW.J0GCQ41AP001_SPO | 3927 | Ovation Control Builder |  | float32
FW.J0GCQ41AP001C | 3928 | #1还原剂计量泵给定 |  | float32
FW.J0GCQ41AP001CL | 3929 | Ovation Control Builder |  | float32
FW.J0GCQ41AP001I | 3930 | Ovation Control Builder |  | float32
FW.J0GCQ41AP001IL | 3931 | #1还原剂计量泵电流 |  | float32
FW.J0GCQ41AP001P | 3932 | #1还原剂计量泵反馈 |  | float32
FW.J0GCQ41AP001PF | 3933 | #1还原剂计量泵故障 |  | digital
FW.J0GCQ41AP001PL | 3934 | Ovation Control Builder |  | float32
FW.J0GCQ41AP001RC | 3935 | #1还原剂计量泵远方 |  | digital
FW.J0GCQ41AP001RD | 3936 | #1还原剂计量泵启动 |  | digital
FW.J0GCQ41AP001RP | 3937 | #1还原剂计量泵运行 |  | digital
FW.J0GCQ41AP001TD | 3938 | #1还原剂计量泵停止 |  | digital
FW.J0GCQ41AP002_CHOOSE | 3939 | #2还原剂计量泵选择 |  | digital
FW.J0GCQ41AP002_F | 3940 | Ovation Control Builder |  | digital
FW.J0GCQ41AP002_LP | 3941 | #2还原剂计量泵 |  | int32
FW.J0GCQ41AP002_LP1 | 3942 | Ovation Control Builder |  | int32
FW.J0GCQ41AP002_LP2 | 3943 | Ovation Control Builder |  | int32
FW.J0GCQ41AP002_MODE | 3944 | Ovation Control Builder |  | int32
FW.J0GCQ41AP002_SPO | 3945 | Ovation Control Builder |  | float32
FW.J0GCQ41AP002C | 3946 | #2还原剂计量泵给定 |  | float32
FW.J0GCQ41AP002CL | 3947 | Ovation Control Builder |  | float32
FW.J0GCQ41AP002I | 3948 | Ovation Control Builder |  | float32
FW.J0GCQ41AP002IL | 3949 | #2还原剂计量泵电流 |  | float32
FW.J0GCQ41AP002P | 3950 | #2还原剂计量泵反馈 |  | float32
FW.J0GCQ41AP002PF | 3951 | #2还原剂计量泵故障 |  | digital
FW.J0GCQ41AP002PL | 3952 | Ovation Control Builder |  | float32
FW.J0GCQ41AP002RC | 3953 | #2还原剂计量泵远方 |  | digital
FW.J0GCQ41AP002RD | 3954 | #2还原剂计量泵启动 |  | digital
FW.J0GCQ41AP002RP | 3955 | #2还原剂计量泵运行 |  | digital
FW.J0GCQ41AP002TD | 3956 | #2还原剂计量泵停止 |  | digital
FW.J0GCQ41CL501 | 3957 | #1还原剂溶液箱液位 | Hz | float32
FW.J0GCQ41CL502 | 3958 | #2还原剂溶液箱液位 | Hz | float32
FW.J0GCQ51AP001_CHOOSE | 3959 | #1碱计量泵选择 |  | digital
FW.J0GCQ51AP001_F | 3960 | Ovation Control Builder |  | digital
FW.J0GCQ51AP001_LP | 3961 | #1碱计量泵 |  | int32
FW.J0GCQ51AP001_LP1 | 3962 | Ovation Control Builder |  | int32
FW.J0GCQ51AP001_LP2 | 3963 | Ovation Control Builder |  | int32
FW.J0GCQ51AP001_MODE | 3964 | Ovation Control Builder |  | int32
FW.J0GCQ51AP001_SPO | 3965 | Ovation Control Builder |  | float32
FW.J0GCQ51AP001C | 3966 | #1超滤反洗碱计量泵给定 |  | float32
FW.J0GCQ51AP001CL | 3967 | Ovation Control Builder |  | float32
FW.J0GCQ51AP001I | 3968 | Ovation Control Builder |  | float32
FW.J0GCQ51AP001IL | 3969 | #1超滤反洗碱计量泵电流 |  | float32
FW.J0GCQ51AP001P | 3970 | #1超滤反洗碱计量泵反馈 |  | float32
FW.J0GCQ51AP001PF | 3971 | #1碱计量泵故障 |  | digital
FW.J0GCQ51AP001PL | 3972 | Ovation Control Builder |  | float32
FW.J0GCQ51AP001RC | 3973 | #1碱计量泵远方 |  | digital
FW.J0GCQ51AP001RD | 3974 | #1碱计量泵启动 |  | digital
FW.J0GCQ51AP001RP | 3975 | #1超滤反洗加碱计量泵运行 |  | digital
FW.J0GCQ51AP001TD | 3976 | #1碱计量泵停止 |  | digital
FW.J0GCQ51AP002_CHOOSE | 3977 | #2碱计量泵选择 |  | digital
FW.J0GCQ51AP002_F | 3978 | Ovation Control Builder |  | digital
FW.J0GCQ51AP002_LP | 3979 | #2碱计量泵 |  | int32
FW.J0GCQ51AP002_LP1 | 3980 | Ovation Control Builder |  | int32
FW.J0GCQ51AP002_LP2 | 3981 | Ovation Control Builder |  | int32
FW.J0GCQ51AP002_MODE | 3982 | Ovation Control Builder |  | int32
FW.J0GCQ51AP002_SPO | 3983 | Ovation Control Builder |  | float32
FW.J0GCQ51AP002C | 3984 | #2超滤反洗碱计量泵给定 |  | float32
FW.J0GCQ51AP002CL | 3985 | Ovation Control Builder |  | float32
FW.J0GCQ51AP002I | 3986 | Ovation Control Builder |  | float32
FW.J0GCQ51AP002IL | 3987 | #2超滤反洗碱计量泵电流 |  | float32
FW.J0GCQ51AP002P | 3988 | #2超滤反洗碱计量泵反馈 |  | float32
FW.J0GCQ51AP002PF | 3989 | 2号碱计量泵故障 |  | digital
FW.J0GCQ51AP002PL | 3990 | Ovation Control Builder |  | float32
FW.J0GCQ51AP002RC | 3991 | #2碱计量泵远方 |  | digital
FW.J0GCQ51AP002RD | 3992 | #2碱计量泵启动 |  | digital
FW.J0GCQ51AP002RP | 3993 | #2超滤反洗加碱计量泵运行 |  | digital
FW.J0GCQ51AP002TD | 3994 | #2碱计量泵停止 |  | digital
FW.J0GCQ51AP003_CHOOSE | 3995 | #3碱计量泵选择 |  | digital
FW.J0GCQ51AP003_F | 3996 | Ovation Control Builder |  | digital
FW.J0GCQ51AP003_LP | 3997 | #3碱计量泵 |  | int32
FW.J0GCQ51AP003_LP1 | 3998 | Ovation Control Builder |  | int32
FW.J0GCQ51AP003_LP2 | 3999 | Ovation Control Builder |  | int32
FW.J0GCQ51AP003_MODE | 4000 | Ovation Control Builder |  | int32
FW.J0GCQ51AP003_SPO | 4001 | Ovation Control Builder |  | float32
FW.J0GCQ51AP003C | 4002 | #1反渗透碱计量泵给定 |  | float32
FW.J0GCQ51AP003CL | 4003 | Ovation Control Builder |  | float32
FW.J0GCQ51AP003I | 4004 | Ovation Control Builder |  | float32
FW.J0GCQ51AP003IL | 4005 | #1反渗透碱计量泵电流 |  | float32
FW.J0GCQ51AP003P | 4006 | #1反渗透碱计量泵反馈 |  | float32
FW.J0GCQ51AP003PF | 4007 | #3碱计量泵故障 |  | digital
FW.J0GCQ51AP003PL | 4008 | Ovation Control Builder |  | float32
FW.J0GCQ51AP003RC | 4009 | #3碱计量泵远方 |  | digital
FW.J0GCQ51AP003RD | 4010 | #3碱计量泵启动 |  | digital
FW.J0GCQ51AP003RP | 4011 | #1二级反渗透加碱计量泵运行 |  | digital
FW.J0GCQ51AP003TD | 4012 | #3碱计量泵停止 |  | digital
FW.J0GCQ51AP004_CHOOSE | 4013 | #4碱计量泵选择 |  | digital
FW.J0GCQ51AP004_F | 4014 | Ovation Control Builder |  | digital
FW.J0GCQ51AP004_LP | 4015 | #4碱计量泵 |  | int32
FW.J0GCQ51AP004_LP1 | 4016 | Ovation Control Builder |  | int32
FW.J0GCQ51AP004_LP2 | 4017 | Ovation Control Builder |  | int32
FW.J0GCQ51AP004_MODE | 4018 | Ovation Control Builder |  | int32
FW.J0GCQ51AP004_SPO | 4019 | Ovation Control Builder |  | float32
FW.J0GCQ51AP004C | 4020 | #2反渗透碱计量泵给定 |  | float32
FW.J0GCQ51AP004CL | 4021 | Ovation Control Builder |  | float32
FW.J0GCQ51AP004I | 4022 | Ovation Control Builder |  | float32
FW.J0GCQ51AP004IL | 4023 | #2反渗透碱计量泵电流 |  | float32
FW.J0GCQ51AP004P | 4024 | #2反渗透碱计量泵反馈 |  | float32
FW.J0GCQ51AP004PF | 4025 | #4碱计量泵故障 |  | digital
FW.J0GCQ51AP004PL | 4026 | Ovation Control Builder |  | float32
FW.J0GCQ51AP004RC | 4027 | #4碱计量泵远方 |  | digital
FW.J0GCQ51AP004RD | 4028 | #4碱计量泵启动 |  | digital
FW.J0GCQ51AP004RP | 4029 | #2二级反渗透加碱计量泵运行 |  | digital
FW.J0GCQ51AP004TD | 4030 | #4碱计量泵停止 |  | digital
FW.J0GCQ51CL501 | 4031 | #1超滤反洗碱溶液箱液位 | Hz | float32
FW.J0GCQ51CL502 | 4032 | #2超滤反洗碱溶液箱液位 | Hz | float32
FW.J0GCQ61AP001_F | 4033 | Ovation Control Builder |  | digital
FW.J0GCQ61AP001_LP | 4034 | 加非氧化性杀菌剂计量泵 |  | int32
FW.J0GCQ61AP001_LP1 | 4035 | Ovation Control Builder |  | int32
FW.J0GCQ61AP001_LP2 | 4036 | Ovation Control Builder |  | int32
FW.J0GCQ61AP001_MODE | 4037 | Ovation Control Builder |  | int32
FW.J0GCQ61AP001_SPO | 4038 | Ovation Control Builder |  | float32
FW.J0GCQ61AP001C | 4039 | 加非氧化性杀菌剂计量泵给定 |  | float32
FW.J0GCQ61AP001CL | 4040 | Ovation Control Builder |  | float32
FW.J0GCQ61AP001I | 4041 | Ovation Control Builder |  | float32
FW.J0GCQ61AP001IL | 4042 | 加非氧化性杀菌剂计量泵电流 |  | float32
FW.J0GCQ61AP001P | 4043 | 加非氧化性杀菌剂计量泵反馈 |  | float32
FW.J0GCQ61AP001PF | 4044 | 加非氧化性杀菌剂计量泵故障 |  | digital
FW.J0GCQ61AP001PL | 4045 | Ovation Control Builder |  | float32
FW.J0GCQ61AP001RC | 4046 | 加非氧化性杀菌剂计量泵远方 |  | digital
FW.J0GCQ61AP001RD | 4047 | 加非氧化性杀菌剂计量泵启动 |  | digital
FW.J0GCQ61AP001RP | 4048 | 加非氧化性杀菌剂计量泵运行 |  | digital
FW.J0GCQ61AP001TD | 4049 | 加非氧化性杀菌剂计量泵停止 |  | digital
FW.J0GCQ61CL501 | 4050 | 加非氧化性杀菌剂溶液箱液位 | Hz | float32
FW.J0GKA00AA001_LP | 4051 | 生活水池进水电动蝶门 |  | int32
FW.J0GKA00AA001CD | 4052 | 生活水池进水电动门关闭指令 |  | digital
FW.J0GKA00AA001CP | 4053 | 生活水池进水电动门全关位置 |  | digital
FW.J0GKA00AA001F | 4054 | 生活水池进水电动门综合故障 |  | digital
FW.J0GKA00AA001OD | 4055 | 生活水池进水电动门打开指令 |  | digital
FW.J0GKA00AA001OP | 4056 | 生活水池进水电动门全开位置 |  | digital
FW.J0GKA00AA001RC | 4057 | 生活水池进水电动门在远控 |  | digital
FW.J0GKB10CF101 | 4058 | 室外生活给水管网流量 | t/h | float32
FW.J0GKB10CP101 | 4059 | 室外生活给水管网压力 | Mpa | float32
FW.J0GKB10GH001LH | 4060 | 生活水池液位高 |  | digital
FW.J0GKB10GH001LL | 4061 | 生活水池液位低 |  | digital
FW.J0GKB10GH001PF | 4062 | 生活给水设备变频控制箱综合故障 |  | digital
FW.J0GKB10GH001PT | 4063 | 生活给水泵出口母管压力 | Mpa | float32
FW.J0GKB11AP001PF | 4064 | #1生活水主泵综合故障 |  | digital
FW.J0GKB11AP001RP | 4065 | #1生活水主泵在运行 |  | digital
FW.J0GKB12AP001PF | 4066 | #2生活水主泵综合故障 |  | digital
FW.J0GKB12AP001RP | 4067 | #2生活水主泵在运行 |  | digital
FW.J0GKB13AP001PF | 4068 | #3生活水主泵综合故障 |  | digital
FW.J0GKB13AP001RP | 4069 | #3生活水主泵在运行 |  | digital
FW.J0GKB14AP001PF | 4070 | 生活水补水泵综合故障 |  | digital
FW.J0GKB14AP001RP | 4071 | 生活水补水泵在运行 |  | digital
FW.J0GKB35AA001_LP | 4072 | #1混凝剂溶液搅拌箱进水门 |  | int32
FW.J0GKB35AA001OD | 4073 | 开#1混凝剂溶液搅拌箱进水门 |  | digital
FW.J0GKB35AA001RC | 4074 | #1混凝剂溶液搅拌箱进水门远方 |  | digital
FW.J0GKB36AA001_LP | 4075 | #2混凝剂溶液搅拌箱进水门 |  | int32
FW.J0GKB36AA001OD | 4076 | 开#2混凝剂溶液搅拌箱进水门 |  | digital
FW.J0GKB36AA001RC | 4077 | #2混凝剂溶液搅拌箱进水门远方 |  | digital
FW.J0GMF12CL101 | 4078 | 消防水泵房集水液位 | m | float32
FW.J0GNB10AM001_LP | 4079 | 工业废水pH值调整池电动搅拌器 |  | int32
FW.J0GNB10AM001PF | 4080 | pH值调整池电动搅拌器综合故障 |  | digital
FW.J0GNB10AM001RC | 4081 | pH值调整池电动搅拌器远方控制 |  | digital
FW.J0GNB10AM001RD | 4082 | pH值调整池电动搅拌器启动指令 |  | digital
FW.J0GNB10AM001RP | 4083 | pH值调整池电动搅拌器在运行 |  | digital
FW.J0GNB10AM001TD | 4084 | pH值调整池电动搅拌器停止指令 |  | digital
FW.J0GNB10CQ101 | 4085 | pH值调整池PH值 | pH | float32
FW.J0GNB20AM001_LP | 4086 | 工业废水反应池电动搅拌器 |  | int32
FW.J0GNB20AM001PF | 4087 | 反应池电动搅拌器综合故障 |  | digital
FW.J0GNB20AM001RC | 4088 | 反应池电动搅拌器远方控制 |  | digital
FW.J0GNB20AM001RD | 4089 | 反应池电动搅拌器启动指令 |  | digital
FW.J0GNB20AM001RP | 4090 | 反应池电动搅拌器在运行 |  | digital
FW.J0GNB20AM001TD | 4091 | 反应池电动搅拌器停止指令 |  | digital
FW.J0GNB30AM001_LP | 4092 | 工业废水絮凝池电动搅拌器 |  | int32
FW.J0GNB30AM001PF | 4093 | 絮凝池电动搅拌器综合故障 |  | digital
FW.J0GNB30AM001RC | 4094 | 絮凝池电动搅拌器远方控制 |  | digital
FW.J0GNB30AM001RD | 4095 | 絮凝池电动搅拌器启动指令 |  | digital
FW.J0GNB30AM001RP | 4096 | 絮凝池电动搅拌器在运行 |  | digital
FW.J0GNB30AM001TD | 4097 | 絮凝池电动搅拌器停止指令 |  | digital
FW.J0GNB40AM001_LP | 4098 | 工业废水斜板澄清器刮泥机 |  | int32
FW.J0GNB40AM001PF | 4099 | 斜板澄清器中心传动刮泥机故障 |  | digital
FW.J0GNB40AM001RC | 4100 | 斜板澄清器中心传动刮泥机远方 |  | digital
FW.J0GNB40AM001RD | 4101 | 斜板澄清器中心传动刮泥机启动 |  | digital
FW.J0GNB40AM001RP | 4102 | 斜板澄清器中心传动刮泥机在运行 |  | digital
FW.J0GNB40AM001RP_1 | 4103 | 刮泥机运行时间加1 |  | float32
FW.J0GNB40AM001RP_TIME | 4104 | 刮泥机运行时间累计 |  | float32
FW.J0GNB40AM001TD | 4105 | 斜板澄清器中心传动刮泥机停止 |  | digital
FW.J0GNB40CL101 | 4106 | 斜板澄清器液位 | m | float32
FW.J0GNB50CQ101 | 4107 | 无阀过滤器出口浊度 | NTU | float32
FW.J0GNC10CL101 | 4108 | 非经常性废水贮存池液位 | m | float32
FW.J0GNC10CP101 | 4109 | 罗茨风机出口母管压力 | Mpa | float32
FW.J0GNC10CQ101 | 4110 | 非经常性废水贮存池PH值 | pH | float32
FW.J0GNC11AN001_CHOOSE | 4111 | #1罗茨风机选择 |  | digital
FW.J0GNC11AN001_LP | 4112 | #1工业废水罗茨风机 |  | int32
FW.J0GNC11AN001PF | 4113 | #1罗茨风机综合故障 |  | digital
FW.J0GNC11AN001RC | 4114 | #1罗茨风机在远控 |  | digital
FW.J0GNC11AN001RD | 4115 | #1罗茨风机启动指令 |  | digital
FW.J0GNC11AN001RP | 4116 | #1罗茨风机在运行 |  | digital
FW.J0GNC11AN001TD | 4117 | #1罗茨风机已停止 |  | digital
FW.J0GNC12AN001_CHOOSE | 4118 | #2罗茨风机选择 |  | digital
FW.J0GNC12AN001_LP | 4119 | #2工业废水罗茨风机 |  | int32
FW.J0GNC12AN001PF | 4120 | #2罗茨风机综合故障 |  | digital
FW.J0GNC12AN001RC | 4121 | #2罗茨风机在远控 |  | digital
FW.J0GNC12AN001RD | 4122 | #2罗茨风机启动指令 |  | digital
FW.J0GNC12AN001RP | 4123 | #2罗茨风机在运行 |  | digital
FW.J0GNC12AN001TD | 4124 | #2罗茨风机已停止 |  | digital
FW.J0GNE31CL101 | 4125 | #1酸溶液箱液位 | m | float32
FW.J0GNE32CL101 | 4126 | #2酸溶液箱液位 | m | float32
FW.J0GNE33AP001_CHOOSE | 4127 | #1酸计量泵联锁投入 |  | digital
FW.J0GNE33AP001_F | 4128 | Ovation Control Builder |  | digital
FW.J0GNE33AP001_LP | 4129 | #1工业废水酸计量泵 |  | int32
FW.J0GNE33AP001_MODE | 4130 | Ovation Control Builder |  | int32
FW.J0GNE33AP001_SPO | 4131 | Ovation Control Builder |  | float32
FW.J0GNE33AP001C | 4132 | #1加酸计量泵频率给定 | Hz | float32
FW.J0GNE33AP001P | 4133 | #1加酸计量泵频率反馈 | Hz | float32
FW.J0GNE33AP001PF | 4134 | #1酸计量泵综合故障 |  | digital
FW.J0GNE33AP001RD | 4135 | #1酸计量泵启动 |  | digital
FW.J0GNE33AP001RP | 4136 | #1酸计量泵在运行 |  | digital
FW.J0GNE33AP001TD | 4137 | #1酸计量泵停止 |  | digital
FW.J0GNE34AP001_CHOOSE | 4138 | #2酸计量泵联锁投入 |  | digital
FW.J0GNE34AP001_F | 4139 | Ovation Control Builder |  | digital
FW.J0GNE34AP001_LP | 4140 | #2工业废水酸计量泵 |  | int32
FW.J0GNE34AP001_MODE | 4141 | Ovation Control Builder |  | int32
FW.J0GNE34AP001_SPO | 4142 | Ovation Control Builder |  | float32
FW.J0GNE34AP001C | 4143 | #2加酸计量泵频率给定 | Hz | float32
FW.J0GNE34AP001P | 4144 | #2加酸计量泵频率反馈 | Hz | float32
FW.J0GNE34AP001PF | 4145 | #2酸计量泵综合故障 |  | digital
FW.J0GNE34AP001RD | 4146 | #2酸计量泵启动 |  | digital
FW.J0GNE34AP001RP | 4147 | #2酸计量泵在运行 |  | digital
FW.J0GNE34AP001TD | 4148 | #2酸计量泵停止 |  | digital
FW.J0GNE35AP001_CHOOSE | 4149 | #3酸计量泵联锁投入 |  | digital
FW.J0GNE35AP001_F | 4150 | Ovation Control Builder |  | digital
FW.J0GNE35AP001_LP | 4151 | #3工业废水酸计量泵 |  | int32
FW.J0GNE35AP001_MODE | 4152 | Ovation Control Builder |  | int32
FW.J0GNE35AP001_SPO | 4153 | Ovation Control Builder |  | float32
FW.J0GNE35AP001C | 4154 | #3加酸计量泵频率给定 | Hz | float32
FW.J0GNE35AP001P | 4155 | #3加酸计量泵频率反馈 | Hz | float32
FW.J0GNE35AP001PF | 4156 | #3酸计量泵综合故障 |  | digital
FW.J0GNE35AP001RD | 4157 | #3酸计量泵启动 |  | digital
FW.J0GNE35AP001RP | 4158 | #3酸计量泵在运行 |  | digital
FW.J0GNE35AP001TD | 4159 | #3酸计量泵启动 |  | digital
FW.J0GNL20CP101 | 4160 | 废水贮存池输送泵出口母管压力 | Mpa | float32
FW.J0GNL21AP001_CHOOSE | 4161 | #1废水输送泵联锁投入 |  | digital
FW.J0GNL21AP001_LP | 4162 | #1工业废水输送泵 |  | int32
FW.J0GNL21AP001PF | 4163 | #1废水输送泵综合故障 |  | digital
FW.J0GNL21AP001RC | 4164 | #1废水输送泵远方控制 |  | digital
FW.J0GNL21AP001RD | 4165 | #1废水输送泵启动指令 |  | digital
FW.J0GNL21AP001RP | 4166 | #1废水输送泵在运行 |  | digital
FW.J0GNL21AP001TD | 4167 | #1废水输送泵停止指令 |  | digital
FW.J0GNL21CL101 | 4168 | 经常性废水贮存池液位 | m | float32
FW.J0GNL21CQ101 | 4169 | 经常性废水贮存池PH值 | pH | float32
FW.J0GNL22AP001_CHOOSE | 4170 | #2废水输送泵联锁投入 |  | digital
FW.J0GNL22AP001_LP | 4171 | #2工业废水输送泵 |  | int32
FW.J0GNL22AP001PF | 4172 | #2废水输送泵综合故障 |  | digital
FW.J0GNL22AP001RC | 4173 | #2废水输送泵远方控制 |  | digital
FW.J0GNL22AP001RD | 4174 | #2废水输送泵启动指令 |  | digital
FW.J0GNL22AP001RP | 4175 | #2废水输送泵在运行 |  | digital
FW.J0GNL22AP001TD | 4176 | #2废水输送泵停止指令 |  | digital
FW.J0GNL31CF101 | 4177 | PH值调整池进口母管流量 | t/h | float32
FW.J0GNL40CF101 | 4178 | 厂区回用水管进口母管流量 | m | float32
FW.J0GNL40CL101 | 4179 | 清净水池液位 | m | float32
FW.J0GNL40CP101 | 4180 | 厂区回用水管出口母管压力 | Mpa | float32
FW.J0GNL40CQ101 | 4181 | 厂区回用水管出口母管COD | Hz | float32
FW.J0GNL40CT301 | 4182 | 厂区回用水管出口母管温度 | ℃ | float32
FW.J0GNL41AP001_LP | 4183 | #1工业废水清净水池回用水泵 |  | int32
FW.J0GNL41AP001PF | 4184 | #1清净水池回用水泵综合故障 |  | digital
FW.J0GNL41AP001RC | 4185 | #1清净水池回用水泵远方控制 |  | digital
FW.J0GNL41AP001RD | 4186 | #1清净水池回用水泵启动指令 |  | digital
FW.J0GNL41AP001RP | 4187 | #1清净水池回用水泵在运行 |  | digital
FW.J0GNL41AP001TD | 4188 | #1清净水池回用水泵停止指令 |  | digital
FW.J0GNL42AP001_LP | 4189 | #2工业废水清净水池回用水泵 |  | int32
FW.J0GNL42AP001PF | 4190 | #2清净水池回用水泵综合故障 |  | digital
FW.J0GNL42AP001RC | 4191 | #2清净水池回用水泵远方控制 |  | digital
FW.J0GNL42AP001RD | 4192 | #2清净水池回用水泵启动指令 |  | digital
FW.J0GNL42AP001RP | 4193 | #2清净水池回用水泵在运行 |  | digital
FW.J0GNL42AP001TD | 4194 | #2清净水池回用水泵停止指令 |  | digital
FW.J0GNN11CL101 | 4195 | #1碱溶液箱液位 | m | float32
FW.J0GNN12CL101 | 4196 | #2碱溶液箱液位 | m | float32
FW.J0GNN30CL101 | 4197 | 酸贮存罐液位 | m | float32
FW.J0GNN50CL101 | 4198 | 碱贮存罐液位 | m | float32
FW.J0GNQ13AP001_CHOOSE | 4199 | #1碱计量泵联锁投入 |  | digital
FW.J0GNQ13AP001_F | 4200 | Ovation Control Builder |  | digital
FW.J0GNQ13AP001_LP | 4201 | #1工业废水碱计量泵 |  | int32
FW.J0GNQ13AP001_MODE | 4202 | Ovation Control Builder |  | int32
FW.J0GNQ13AP001_SPO | 4203 | Ovation Control Builder |  | float32
FW.J0GNQ13AP001C | 4204 | #1加碱计量泵频率给定 | Hz | float32
FW.J0GNQ13AP001P | 4205 | #1加碱计量泵频率反馈 | Hz | float32
FW.J0GNQ13AP001PF | 4206 | #1碱计量泵综合故障 |  | digital
FW.J0GNQ13AP001RD | 4207 | #1碱计量泵启动 |  | digital
FW.J0GNQ13AP001RP | 4208 | #1碱计量泵在运行 |  | digital
FW.J0GNQ13AP001TD | 4209 | #1碱计量泵停止 |  | digital
FW.J0GNQ14AP001_CHOOSE | 4210 | #2碱计量泵联锁投入 |  | digital
FW.J0GNQ14AP001_F | 4211 | Ovation Control Builder |  | digital
FW.J0GNQ14AP001_LP | 4212 | #2工业废水碱计量泵 |  | int32
FW.J0GNQ14AP001_MODE | 4213 | Ovation Control Builder |  | int32
FW.J0GNQ14AP001_SPO | 4214 | Ovation Control Builder |  | float32
FW.J0GNQ14AP001C | 4215 | #2加碱计量泵频率给定 | Hz | float32
FW.J0GNQ14AP001P | 4216 | #2加碱计量泵频率反馈 | Hz | float32
FW.J0GNQ14AP001PF | 4217 | #2碱计量泵综合故障 |  | digital
FW.J0GNQ14AP001RD | 4218 | #2碱计量泵启动 |  | digital
FW.J0GNQ14AP001RP | 4219 | #2碱计量泵在运行 |  | digital
FW.J0GNQ14AP001TD | 4220 | #2碱计量泵停止 |  | digital
FW.J0GNQ15AP001_CHOOSE | 4221 | #3碱计量泵联锁投入 |  | digital
FW.J0GNQ15AP001_F | 4222 | Ovation Control Builder |  | digital
FW.J0GNQ15AP001_LP | 4223 | #3工业废水碱计量泵 |  | int32
FW.J0GNQ15AP001_MODE | 4224 | Ovation Control Builder |  | int32
FW.J0GNQ15AP001_SPO | 4225 | Ovation Control Builder |  | float32
FW.J0GNQ15AP001C | 4226 | #3加碱计量泵频率给定 | Hz | float32
FW.J0GNQ15AP001P | 4227 | #3加碱计量泵频率反馈 | Hz | float32
FW.J0GNQ15AP001PF | 4228 | #3碱计量泵综合故障 |  | digital
FW.J0GNQ15AP001RD | 4229 | #3碱计量泵启动 |  | digital
FW.J0GNQ15AP001RP | 4230 | #3碱计量泵在运行 |  | digital
FW.J0GNQ15AP001TD | 4231 | #3碱计量泵停止 |  | digital
FW.J0GNQ21AM001_LP | 4232 | #1工业废水混凝剂电动搅拌器 |  | int32
FW.J0GNQ21AM001PF | 4233 | #1混凝剂溶液搅拌箱搅拌器故障 |  | digital
FW.J0GNQ21AM001RC | 4234 | #1混凝剂溶液搅拌箱搅拌器远方 |  | digital
FW.J0GNQ21AM001RD | 4235 | #1混凝剂溶液搅拌箱搅拌器启动 |  | digital
FW.J0GNQ21AM001RP | 4236 | #1混凝剂溶液搅拌箱搅拌器运行 |  | digital
FW.J0GNQ21AM001TD | 4237 | #1混凝剂溶液搅拌箱搅拌器停止 |  | digital
FW.J0GNQ21CL101 | 4238 | #1混凝剂溶液搅拌箱液位 | m | float32
FW.J0GNQ22AM001_LP | 4239 | #2工业废水混凝剂电动搅拌器 |  | int32
FW.J0GNQ22AM001PF | 4240 | #2混凝剂溶液搅拌箱搅拌器故障 |  | digital
FW.J0GNQ22AM001RC | 4241 | #2混凝剂溶液搅拌箱搅拌器远方 |  | digital
FW.J0GNQ22AM001RD | 4242 | #2混凝剂溶液搅拌箱搅拌器启动 |  | digital
FW.J0GNQ22AM001RP | 4243 | #2混凝剂溶液搅拌箱搅拌器运行 |  | digital
FW.J0GNQ22AM001TD | 4244 | #2混凝剂溶液搅拌箱搅拌器停止 |  | digital
FW.J0GNQ22CL101 | 4245 | #2混凝剂溶液搅拌箱液位 | m | float32
FW.J0GNQ23AP001_CHOOSE | 4246 | #1混凝剂溶计量泵选择 |  | digital
FW.J0GNQ23AP001_LP | 4247 | #1工业废水废水混凝剂计量泵 |  | int32
FW.J0GNQ23AP001PF | 4248 | #1混凝剂溶计量泵综合故障 |  | digital
FW.J0GNQ23AP001RC | 4249 | #1混凝剂溶计量泵远方控制 |  | digital
FW.J0GNQ23AP001RD | 4250 | #1混凝剂溶计量泵启动指令 |  | digital
FW.J0GNQ23AP001RP | 4251 | #1混凝剂溶计量泵在运行 |  | digital
FW.J0GNQ23AP001TD | 4252 | #1混凝剂溶计量泵停止指令 |  | digital
FW.J0GNQ24AP001_CHOOSE | 4253 | #2混凝剂溶计量泵选择 |  | digital
FW.J0GNQ24AP001_LP | 4254 | #2工业废水废水混凝剂计量泵 |  | int32
FW.J0GNQ24AP001PF | 4255 | #2混凝剂溶计量泵综合故障 |  | digital
FW.J0GNQ24AP001RC | 4256 | #2混凝剂溶计量泵远方控制 |  | digital
FW.J0GNQ24AP001RD | 4257 | #2混凝剂溶计量泵启动指令 |  | digital
FW.J0GNQ24AP001RP | 4258 | #2混凝剂溶计量泵在运行 |  | digital
FW.J0GNQ24AP001TD | 4259 | #2混凝剂溶计量泵停止指令 |  | digital
FW.J0GNQ30AM001_LP | 4260 | #1工业废水助凝剂/脱水剂搅拌器 |  | int32
FW.J0GNQ30AM001PF | 4261 | #1助凝剂/脱水剂搅拌器综合故障 |  | digital
FW.J0GNQ30AM001RC | 4262 | #1助凝剂/脱水剂搅拌器远方控制 |  | digital
FW.J0GNQ30AM001RD | 4263 | #1助凝剂/脱水剂搅拌器启动指令 |  | digital
FW.J0GNQ30AM001RP | 4264 | #1助凝剂/脱水剂搅拌器在运行 |  | digital
FW.J0GNQ30AM001TD | 4265 | #1助凝剂/脱水剂搅拌器停止指令 |  | digital
FW.J0GNQ30AM002_LP | 4266 | #2工业废水助凝剂/脱水剂搅拌器 |  | int32
FW.J0GNQ30AM002PF | 4267 | #2助凝剂/脱水剂搅拌器综合故障 |  | digital
FW.J0GNQ30AM002RC | 4268 | #2助凝剂/脱水剂搅拌器远方控制 |  | digital
FW.J0GNQ30AM002RD | 4269 | #2助凝剂/脱水剂搅拌器启动指令 |  | digital
FW.J0GNQ30AM002RP | 4270 | #2助凝剂/脱水剂搅拌器在运行 |  | digital
FW.J0GNQ30AM002TD | 4271 | #2助凝剂/脱水剂搅拌器停止指令 |  | digital
FW.J0GNQ30AM003_LP | 4272 | PAM振荡电机 |  | int32
FW.J0GNQ30AM003PF | 4273 | PAM振荡电机综合故障 |  | digital
FW.J0GNQ30AM003RC | 4274 | PAM振荡电机远方控制 |  | digital
FW.J0GNQ30AM003RD | 4275 | PAM振荡电机启动指令 |  | digital
FW.J0GNQ30AM003RP | 4276 | PAM振荡电机在运行 |  | digital
FW.J0GNQ30AM003TD | 4277 | PAM振荡电机停止指令 |  | digital
FW.J0GNQ30AM004_LP | 4278 | PAM电加热 |  | int32
FW.J0GNQ30AM004RC | 4279 | PAM电加热远方控制 |  | digital
FW.J0GNQ30AM004RD | 4280 | PAM电加热启动指令 |  | digital
FW.J0GNQ30AM004RP | 4281 | PAM电加热在运行 |  | digital
FW.J0GNQ30AM004TD | 4282 | PAM电加热停止指令 |  | digital
FW.J0GNQ30AP001_F | 4283 | Ovation Control Builder |  | digital
FW.J0GNQ30AP001_LP | 4284 | 助凝剂/脱水剂干投机 |  | int32
FW.J0GNQ30AP001_MODE | 4285 | Ovation Control Builder |  | int32
FW.J0GNQ30AP001_SPO | 4286 | Ovation Control Builder |  | float32
FW.J0GNQ30AP001C | 4287 | 助凝剂/脱水剂干投机频率给定 | Hz | float32
FW.J0GNQ30AP001P | 4288 | 助凝剂/脱水剂干投机频率反馈 | Hz | float32
FW.J0GNQ30AP001PF | 4289 | 助凝剂/脱水剂干投机综合故障 |  | digital
FW.J0GNQ30AP001RC | 4290 | 助凝剂/脱水剂干投机远方控制 |  | digital
FW.J0GNQ30AP001RD | 4291 | 助凝剂/脱水剂干投机启动指令 |  | digital
FW.J0GNQ30AP001RP | 4292 | 助凝剂/脱水剂干投机在运行 |  | digital
FW.J0GNQ30AP001TD | 4293 | 助凝剂/脱水剂干投机停止指令 |  | digital
FW.J0GNQ30CL101 | 4294 | 助凝剂/脱水剂干投机液位 | m | float32
FW.J0GNQ31AP001_CHOOSE | 4295 | #1助凝剂计量泵选择 |  | digital
FW.J0GNQ31AP001_LP | 4296 | #1废水助凝剂计量泵 |  | int32
FW.J0GNQ31AP001PF | 4297 | #1助凝剂计量泵综合故障 |  | digital
FW.J0GNQ31AP001RC | 4298 | #1助凝剂计量泵远方控制 |  | digital
FW.J0GNQ31AP001RD | 4299 | #1助凝剂计量泵启动指令 |  | digital
FW.J0GNQ31AP001RP | 4300 | #1助凝剂计量泵在运行 |  | digital
FW.J0GNQ31AP001TD | 4301 | #1助凝剂计量泵停止指令 |  | digital
FW.J0GNQ32AP001_CHOOSE | 4302 | #2助凝剂计量泵选择 |  | digital
FW.J0GNQ32AP001_LP | 4303 | #2废水助凝剂计量泵 |  | int32
FW.J0GNQ32AP001PF | 4304 | #2助凝剂计量泵综合故障 |  | digital
FW.J0GNQ32AP001RC | 4305 | #2助凝剂计量泵远方控制 |  | digital
FW.J0GNQ32AP001RD | 4306 | #2助凝剂计量泵启动指令 |  | digital
FW.J0GNQ32AP001RP | 4307 | #2助凝剂计量泵在运行 |  | digital
FW.J0GNQ32AP001TD | 4308 | #2助凝剂计量泵停止指令 |  | digital
FW.J0GNQ33AP001_CHOOSE | 4309 | #1废水脱水剂计量泵选择 |  | digital
FW.J0GNQ33AP001_LP | 4310 | #1废水脱水剂计量泵 |  | int32
FW.J0GNQ33AP001PF | 4311 | #1脱水剂计量泵综合故障 |  | digital
FW.J0GNQ33AP001RC | 4312 | #1脱水剂计量泵远方控制 |  | digital
FW.J0GNQ33AP001RD | 4313 | #1脱水剂计量泵启动指令 |  | digital
FW.J0GNQ33AP001RP | 4314 | #1脱水剂计量泵在运行 |  | digital
FW.J0GNQ33AP001TD | 4315 | #1脱水剂计量泵停止指令 |  | digital
FW.J0GNQ34AP001_CHOOSE | 4316 | #2废水脱水剂计量泵选择 |  | digital
FW.J0GNQ34AP001_LP | 4317 | #2废水脱水剂计量泵 |  | int32
FW.J0GNQ34AP001PF | 4318 | #2脱水剂计量泵综合故障 |  | digital
FW.J0GNQ34AP001RC | 4319 | #2脱水剂计量泵远方控制 |  | digital
FW.J0GNQ34AP001RD | 4320 | #2脱水剂计量泵启动指令 |  | digital
FW.J0GNQ34AP001RP | 4321 | #2脱水剂计量泵在运行 |  | digital
FW.J0GNQ34AP001TD | 4322 | #2脱水剂计量泵停止指令 |  | digital
FW.J0GNQ41AM001_LP | 4323 | #1次氯酸钠电动搅拌器 |  | int32
FW.J0GNQ41AM001PF | 4324 | #1次氯酸钠溶液箱搅拌器故障 |  | digital
FW.J0GNQ41AM001RC | 4325 | #1次氯酸钠溶液箱搅拌器远方 |  | digital
FW.J0GNQ41AM001RD | 4326 | #1次氯酸钠溶液箱搅拌器启动 |  | digital
FW.J0GNQ41AM001RP | 4327 | #1次氯酸钠溶液箱搅拌器运行 |  | digital
FW.J0GNQ41AM001TD | 4328 | #1次氯酸钠溶液箱搅拌器停止 |  | digital
FW.J0GNQ41CL101 | 4329 | #1次氯酸钠溶液箱液位 | m | float32
FW.J0GNQ42AM001_LP | 4330 | #2次氯酸钠电动搅拌器 |  | int32
FW.J0GNQ42AM001PF | 4331 | #2次氯酸钠溶液箱搅拌器故障 |  | digital
FW.J0GNQ42AM001RC | 4332 | #2次氯酸钠溶液箱搅拌器远方 |  | digital
FW.J0GNQ42AM001RD | 4333 | #2次氯酸钠溶液箱搅拌器启动 |  | digital
FW.J0GNQ42AM001RP | 4334 | #2次氯酸钠溶液箱搅拌器运行 |  | digital
FW.J0GNQ42AM001TD | 4335 | #2次氯酸钠溶液箱搅拌器停止 |  | digital
FW.J0GNQ42CL101 | 4336 | #2次氯酸钠溶液箱液位 | m | float32
FW.J0GNQ43AP001_LP | 4337 | #1废水次氯酸钠计量泵 |  | int32
FW.J0GNQ43AP001PF | 4338 | #1次氯酸钠计量泵综合故障 |  | digital
FW.J0GNQ43AP001RC | 4339 | #1次氯酸钠计量泵远方控制 |  | digital
FW.J0GNQ43AP001RD | 4340 | #1次氯酸钠计量泵启动指令 |  | digital
FW.J0GNQ43AP001RP | 4341 | #1次氯酸钠计量泵在运行 |  | digital
FW.J0GNQ43AP001TD | 4342 | #1次氯酸钠计量泵停止指令 |  | digital
FW.J0GNQ44AP001_LP | 4343 | #2废水次氯酸钠计量泵 |  | int32
FW.J0GNQ44AP001PF | 4344 | #2次氯酸钠计量泵综合故障 |  | digital
FW.J0GNQ44AP001RC | 4345 | #2次氯酸钠计量泵远方控制 |  | digital
FW.J0GNQ44AP001RD | 4346 | #2次氯酸钠计量泵启动指令 |  | digital
FW.J0GNQ44AP001RP | 4347 | #2次氯酸钠计量泵在运行 |  | digital
FW.J0GNQ44AP001TD | 4348 | #2次氯酸钠计量泵停止指令 |  | digital
FW.J0GNR10AM001_LP | 4349 | 最终中和池电动搅拌器 |  | int32
FW.J0GNR10AM001PF | 4350 | 最终中和池电动搅拌器综合故障 |  | digital
FW.J0GNR10AM001RC | 4351 | 最终中和池电动搅拌器远方控制 |  | digital
FW.J0GNR10AM001RD | 4352 | 最终中和池电动搅拌器启动指令 |  | digital
FW.J0GNR10AM001RP | 4353 | 最终中和池电动搅拌器在运行 |  | digital
FW.J0GNR10AM001TD | 4354 | 最终中和池电动搅拌器停止指令 |  | digital
FW.J0GNR10CL101 | 4355 | 最终中和池液位 | m | float32
FW.J0GNR10CQ101 | 4356 | 最终中和池PH值 | pH | float32
FW.J0GNS10AM001_LP | 4357 | 废水污泥浓缩池刮泥机 |  | int32
FW.J0GNS10AM001PF | 4358 | 污泥浓缩池刮泥机综合故障 |  | digital
FW.J0GNS10AM001RC | 4359 | 污泥浓缩池刮泥机远方控制 |  | digital
FW.J0GNS10AM001RD | 4360 | 污泥浓缩池刮泥机启动指令 |  | digital
FW.J0GNS10AM001RP | 4361 | 污泥浓缩池刮泥机在运行 |  | digital
FW.J0GNS10AM001TD | 4362 | 污泥浓缩池刮泥机停止指令 |  | digital
FW.J0GNS10CL101 | 4363 | 污泥浓缩池泥位 | m | float32
FW.J0GNS10CP101 | 4364 | 污泥输送泵出口母管压力 | Mpa | float32
FW.J0GNS11AP001_CHOOSE | 4365 | #1废水污泥输送泵选择 |  | digital
FW.J0GNS11AP001_LP | 4366 | #1废水污泥输送泵 |  | int32
FW.J0GNS11AP001PF | 4367 | #1污泥输送泵综合故障 |  | digital
FW.J0GNS11AP001RC | 4368 | #1污泥输送泵远方控制 |  | digital
FW.J0GNS11AP001RD | 4369 | #1污泥输送泵启动指令 |  | digital
FW.J0GNS11AP001RP | 4370 | #1污泥输送泵在运行 |  | digital
FW.J0GNS11AP001TD | 4371 | #1污泥输送泵停止指令 |  | digital
FW.J0GNS12AP001_CHOOSE | 4372 | #2废水污泥输送泵选择 |  | digital
FW.J0GNS12AP001_LP | 4373 | #2废水污泥输送泵 |  | int32
FW.J0GNS12AP001PF | 4374 | #2污泥输送泵综合故障 |  | digital
FW.J0GNS12AP001RC | 4375 | #2污泥输送泵远方控制 |  | digital
FW.J0GNS12AP001RD | 4376 | #2污泥输送泵启动指令 |  | digital
FW.J0GNS12AP001RP | 4377 | #2污泥输送泵在运行 |  | digital
FW.J0GNS12AP001TD | 4378 | #2污泥输送泵停止指令 |  | digital
FW.J0GNS21AT001_LP | 4379 | 工业废水离心脱水机 |  | int32
FW.J0GNS21AT001CX | 4380 | 离心脱水机电磁阀反馈 |  | digital
FW.J0GNS21AT001LS1 | 4381 | 离心脱水机进料联锁 |  | digital
FW.J0GNS21AT001LS2 | 4382 | 离心脱水机排泥装置联锁 |  | digital
FW.J0GNS21AT001PF | 4383 | 离心脱水机综合故障 |  | digital
FW.J0GNS21AT001RD | 4384 | 离心脱水机启动指令 |  | digital
FW.J0GNS21AT001RP | 4385 | 离心脱水机在运行 |  | digital
FW.J0GNS21AT001TD | 4386 | 离心脱水机停止指令 |  | digital
FW.J0GNS21BB001_LP | 4387 | 工业废水电动污泥斗 |  | int32
FW.J0GNS21BB001PF | 4388 | 电动污泥斗综合故障 |  | digital
FW.J0GNS21BB001RC | 4389 | 电动污泥斗远方控制 |  | digital
FW.J0GNS21BB001RD | 4390 | 电动污泥斗启动指令 |  | digital
FW.J0GNS21BB001RP | 4391 | 电动污泥斗在运行 |  | digital
FW.J0GNS21BB001TD | 4392 | 电动污泥斗停止指令 |  | digital
FW.J0GTA31AA002_LP | 4393 | #1絮凝斜板沉淀池8号排泥门 |  | int32
FW.J0GTA31AA002CD | 4394 | #1絮凝斜板沉淀池8号排泥门关 |  | digital
FW.J0GTA31AA002CP | 4395 | #1絮凝斜板沉淀池8号排泥门全关 |  | digital
FW.J0GTA31AA002F | 4396 | #1絮凝斜板沉淀池8号排泥门故障 |  | digital
FW.J0GTA31AA002OD | 4397 | #1絮凝斜板沉淀池8号排泥门打开 |  | digital
FW.J0GTA31AA002OP | 4398 | #1絮凝斜板沉淀池8号排泥门全开 |  | digital
FW.J0GTA31AA002RC | 4399 | #1絮凝斜板沉淀池8号排泥门远方 |  | digital
FW.J0GTA32AA002_LP | 4400 | #1絮凝斜板沉淀池7号排泥门 |  | int32
FW.J0GTA32AA002CD | 4401 | #1絮凝斜板沉淀池7号排泥门关 |  | digital
FW.J0GTA32AA002CP | 4402 | #1絮凝斜板沉淀池7号排泥门全关 |  | digital
FW.J0GTA32AA002F | 4403 | #1絮凝斜板沉淀池7号排泥门故障 |  | digital
FW.J0GTA32AA002OD | 4404 | #1絮凝斜板沉淀池7号排泥门打开 |  | digital
FW.J0GTA32AA002OP | 4405 | #1絮凝斜板沉淀池7号排泥门全开 |  | digital
FW.J0GTA32AA002RC | 4406 | #1絮凝斜板沉淀池7号排泥门远方 |  | digital
FW.J0GTA33AA002_LP | 4407 | #1絮凝斜板沉淀池6号排泥门 |  | int32
FW.J0GTA33AA002CD | 4408 | #1絮凝斜板沉淀池6号排泥门关 |  | digital
FW.J0GTA33AA002CP | 4409 | #1絮凝斜板沉淀池6号排泥门全关 |  | digital
FW.J0GTA33AA002F | 4410 | #1絮凝斜板沉淀池6号排泥门故障 |  | digital
FW.J0GTA33AA002OD | 4411 | #1絮凝斜板沉淀池6号排泥门打开 |  | digital
FW.J0GTA33AA002OP | 4412 | #1絮凝斜板沉淀池6号排泥门全开 |  | digital
FW.J0GTA33AA002RC | 4413 | #1絮凝斜板沉淀池6号排泥门远方 |  | digital
FW.J0GTA34AA002_LP | 4414 | #1絮凝斜板沉淀池5号排泥门 |  | int32
FW.J0GTA34AA002CD | 4415 | #1絮凝斜板沉淀池5号排泥门关 |  | digital
FW.J0GTA34AA002CP | 4416 | #1絮凝斜板沉淀池5号排泥门全关 |  | digital
FW.J0GTA34AA002F | 4417 | #1絮凝斜板沉淀池5号排泥门故障 |  | digital
FW.J0GTA34AA002OD | 4418 | #1絮凝斜板沉淀池5号排泥门打开 |  | digital
FW.J0GTA34AA002OP | 4419 | #1絮凝斜板沉淀池5号排泥门全开 |  | digital
FW.J0GTA34AA002RC | 4420 | #1絮凝斜板沉淀池5号排泥门远方 |  | digital
FW.J0GTA35AA002_LP | 4421 | #1絮凝斜板沉淀池3号排泥门 |  | int32
FW.J0GTA35AA002CD | 4422 | #1絮凝斜板沉淀池3号排泥门关 |  | digital
FW.J0GTA35AA002CP | 4423 | #1絮凝斜板沉淀池3号排泥门全关 |  | digital
FW.J0GTA35AA002F | 4424 | #1絮凝斜板沉淀池3号排泥门故障 |  | digital
FW.J0GTA35AA002OD | 4425 | #1絮凝斜板沉淀池3号排泥门打开 |  | digital
FW.J0GTA35AA002OP | 4426 | #1絮凝斜板沉淀池3号排泥门全开 |  | digital
FW.J0GTA35AA002RC | 4427 | #1絮凝斜板沉淀池3号排泥门远方 |  | digital
FW.J0GTA35AA012_LP | 4428 | #1絮凝斜板沉淀池4号排泥门 |  | int32
FW.J0GTA35AA012CD | 4429 | #1絮凝斜板沉淀池4号排泥门关 |  | digital
FW.J0GTA35AA012CP | 4430 | #1絮凝斜板沉淀池4号排泥门全关 |  | digital
FW.J0GTA35AA012F | 4431 | #1絮凝斜板沉淀池4号排泥门故障 |  | digital
FW.J0GTA35AA012OD | 4432 | #1絮凝斜板沉淀池4号排泥门打开 |  | digital
FW.J0GTA35AA012OP | 4433 | #1絮凝斜板沉淀池4号排泥门全开 |  | digital
FW.J0GTA35AA012RC | 4434 | #1絮凝斜板沉淀池4号排泥门远方 |  | digital
FW.J0GTA36AA002_LP | 4435 | #1絮凝斜板沉淀池1号排泥门 |  | int32
FW.J0GTA36AA002CD | 4436 | #1絮凝斜板沉淀池1号排泥门关 |  | digital
FW.J0GTA36AA002CP | 4437 | #1絮凝斜板沉淀池1号排泥门全关 |  | digital
FW.J0GTA36AA002F | 4438 | #1絮凝斜板沉淀池1号排泥门故障 |  | digital
FW.J0GTA36AA002OD | 4439 | #1絮凝斜板沉淀池1号排泥门打开 |  | digital
FW.J0GTA36AA002OP | 4440 | #1絮凝斜板沉淀池1号排泥门全开 |  | digital
FW.J0GTA36AA002RC | 4441 | #1絮凝斜板沉淀池1号排泥门远方 |  | digital
FW.J0GTA36AA012_LP | 4442 | #1絮凝斜板沉淀池2号排泥门 |  | int32
FW.J0GTA36AA012CD | 4443 | #1絮凝斜板沉淀池2号排泥门关 |  | digital
FW.J0GTA36AA012CP | 4444 | #1絮凝斜板沉淀池2号排泥门全关 |  | digital
FW.J0GTA36AA012F | 4445 | #1絮凝斜板沉淀池2号排泥门故障 |  | digital
FW.J0GTA36AA012OD | 4446 | #1絮凝斜板沉淀池2号排泥门打开 |  | digital
FW.J0GTA36AA012OP | 4447 | #1絮凝斜板沉淀池2号排泥门全开 |  | digital
FW.J0GTA36AA012RC | 4448 | #1絮凝斜板沉淀池2号排泥门远方 |  | digital
FW.J0GTA40AM001_LP | 4449 | 浓缩池刮泥机 |  | int32
FW.J0GTA40AM001PF | 4450 | 浓缩池刮泥机综合故障 |  | digital
FW.J0GTA40AM001RC | 4451 | 浓缩池刮泥机远方控制 |  | digital
FW.J0GTA40AM001RD | 4452 | 浓缩池刮泥机启动指令 |  | digital
FW.J0GTA40AM001RP | 4453 | 浓缩池刮泥机在运行 |  | digital
FW.J0GTA40AM001TD | 4454 | 浓缩池刮泥机停止指令 |  | digital
FW.J0GTA40CL101 | 4455 | 浓缩池泥位 | m | float32
FW.J0GTA41AA002_LP | 4456 | #2絮凝斜板沉淀池8号排泥门 |  | int32
FW.J0GTA41AA002CD | 4457 | #2絮凝斜板沉淀池8号排泥门关 |  | digital
FW.J0GTA41AA002CP | 4458 | #2絮凝斜板沉淀池8号排泥门全关 |  | digital
FW.J0GTA41AA002F | 4459 | #2絮凝斜板沉淀池8号排泥门故障 |  | digital
FW.J0GTA41AA002OD | 4460 | #2絮凝斜板沉淀池8号排泥门打开 |  | digital
FW.J0GTA41AA002OP | 4461 | #2絮凝斜板沉淀池8号排泥门全开 |  | digital
FW.J0GTA41AA002RC | 4462 | #2絮凝斜板沉淀池8号排泥门远方 |  | digital
FW.J0GTA42AA002_LP | 4463 | #2絮凝斜板沉淀池7号排泥门 |  | int32
FW.J0GTA42AA002CD | 4464 | #2絮凝斜板沉淀池7号排泥门关 |  | digital
FW.J0GTA42AA002CP | 4465 | #2絮凝斜板沉淀池7号排泥门全关 |  | digital
FW.J0GTA42AA002F | 4466 | #2絮凝斜板沉淀池7号排泥门故障 |  | digital
FW.J0GTA42AA002OD | 4467 | #2絮凝斜板沉淀池7号排泥门打开 |  | digital
FW.J0GTA42AA002OP | 4468 | #2絮凝斜板沉淀池7号排泥门全开 |  | digital
FW.J0GTA42AA002RC | 4469 | #2絮凝斜板沉淀池7号排泥门远方 |  | digital
FW.J0GTA43AA002_LP | 4470 | #2絮凝斜板沉淀池6号排泥门 |  | int32
FW.J0GTA43AA002CD | 4471 | #2絮凝斜板沉淀池6号排泥门关 |  | digital
FW.J0GTA43AA002CP | 4472 | #2絮凝斜板沉淀池6号排泥门全关 |  | digital
FW.J0GTA43AA002F | 4473 | #2絮凝斜板沉淀池6号排泥门故障 |  | digital
FW.J0GTA43AA002OD | 4474 | #2絮凝斜板沉淀池6号排泥门打开 |  | digital
FW.J0GTA43AA002OP | 4475 | #2絮凝斜板沉淀池6号排泥门全开 |  | digital
FW.J0GTA43AA002RC | 4476 | #2絮凝斜板沉淀池6号排泥门远方 |  | digital
FW.J0GTA44AA002_LP | 4477 | #2絮凝斜板沉淀池5号排泥门 |  | int32
FW.J0GTA44AA002CD | 4478 | #2絮凝斜板沉淀池5号排泥门关 |  | digital
FW.J0GTA44AA002CP | 4479 | #2絮凝斜板沉淀池5号排泥门全关 |  | digital
FW.J0GTA44AA002F | 4480 | #2絮凝斜板沉淀池5号排泥门故障 |  | digital
FW.J0GTA44AA002OD | 4481 | #2絮凝斜板沉淀池5号排泥门打开 |  | digital
FW.J0GTA44AA002OP | 4482 | #2絮凝斜板沉淀池5号排泥门全开 |  | digital
FW.J0GTA44AA002RC | 4483 | #2絮凝斜板沉淀池5号排泥门远方 |  | digital
FW.J0GTA45AA002_LP | 4484 | #2絮凝斜板沉淀池3号排泥门 |  | int32
FW.J0GTA45AA002CD | 4485 | #2絮凝斜板沉淀池3号排泥门关 |  | digital
FW.J0GTA45AA002CP | 4486 | #2絮凝斜板沉淀池3号排泥门全关 |  | digital
FW.J0GTA45AA002F | 4487 | #2絮凝斜板沉淀池3号排泥门故障 |  | digital
FW.J0GTA45AA002OD | 4488 | #2絮凝斜板沉淀池3号排泥门打开 |  | digital
FW.J0GTA45AA002OP | 4489 | #2絮凝斜板沉淀池3号排泥门全开 |  | digital
FW.J0GTA45AA002RC | 4490 | #2絮凝斜板沉淀池3号排泥门远方 |  | digital
FW.J0GTA45AA012_LP | 4491 | #2絮凝斜板沉淀池4号排泥门 |  | int32
FW.J0GTA45AA012CD | 4492 | #2絮凝斜板沉淀池4号排泥门关 |  | digital
FW.J0GTA45AA012CP | 4493 | #2絮凝斜板沉淀池4号排泥门全关 |  | digital
FW.J0GTA45AA012F | 4494 | #2絮凝斜板沉淀池4号排泥门故障 |  | digital
FW.J0GTA45AA012OD | 4495 | #2絮凝斜板沉淀池4号排泥门打开 |  | digital
FW.J0GTA45AA012OP | 4496 | #2絮凝斜板沉淀池4号排泥门全开 |  | digital
FW.J0GTA45AA012RC | 4497 | #2絮凝斜板沉淀池4号排泥门远方 |  | digital
FW.J0GTA46AA002_LP | 4498 | #2絮凝斜板沉淀池1号排泥门 |  | int32
FW.J0GTA46AA002CD | 4499 | #2絮凝斜板沉淀池1号排泥门关 |  | digital
FW.J0GTA46AA002CP | 4500 | #2絮凝斜板沉淀池1号排泥门全关 |  | digital
FW.J0GTA46AA002F | 4501 | #2絮凝斜板沉淀池1号排泥门故障 |  | digital
FW.J0GTA46AA002OD | 4502 | #2絮凝斜板沉淀池1号排泥门打开 |  | digital
FW.J0GTA46AA002OP | 4503 | #2絮凝斜板沉淀池1号排泥门全开 |  | digital
FW.J0GTA46AA002RC | 4504 | #2絮凝斜板沉淀池1号排泥门远方 |  | digital
FW.J0GTA46AA012_LP | 4505 | #2絮凝斜板沉淀池2号排泥门 |  | int32
FW.J0GTA46AA012CD | 4506 | #2絮凝斜板沉淀池2号排泥门关 |  | digital
FW.J0GTA46AA012CP | 4507 | #2絮凝斜板沉淀池2号排泥门全关 |  | digital
FW.J0GTA46AA012F | 4508 | #2絮凝斜板沉淀池2号排泥门故障 |  | digital
FW.J0GTA46AA012OD | 4509 | #2絮凝斜板沉淀池2号排泥门打开 |  | digital
FW.J0GTA46AA012OP | 4510 | #2絮凝斜板沉淀池2号排泥门全开 |  | digital
FW.J0GTA46AA012RC | 4511 | #2絮凝斜板沉淀池2号排泥门远方 |  | digital
FW.J0GTA61AP001_CHOOSE | 4512 | #1污泥泵选择 |  | digital
FW.J0GTA61AP001_LP | 4513 | #1污泥泵 |  | int32
FW.J0GTA61AP001PF | 4514 | #1污泥泵综合故障 |  | digital
FW.J0GTA61AP001RC | 4515 | #1污泥泵远方控制 |  | digital
FW.J0GTA61AP001RD | 4516 | #1污泥泵启动指令 |  | digital
FW.J0GTA61AP001RP | 4517 | #1污泥泵在运行 |  | digital
FW.J0GTA61AP001TD | 4518 | #1污泥泵停止指令 |  | digital
FW.J0GTA62AP001_CHOOSE | 4519 | #2污泥泵选择 |  | digital
FW.J0GTA62AP001_LP | 4520 | #2污泥泵 |  | int32
FW.J0GTA62AP001PF | 4521 | #2污泥泵综合故障 |  | digital
FW.J0GTA62AP001RC | 4522 | #2污泥泵远方控制 |  | digital
FW.J0GTA62AP001RD | 4523 | #2污泥泵启动指令 |  | digital
FW.J0GTA62AP001RP | 4524 | #2污泥泵在运行 |  | digital
FW.J0GTA62AP001TD | 4525 | #2污泥泵停止指令 |  | digital
FW.J0GTA62CP101 | 4526 | 污泥泵出口压力 | Mpa | float32
FW.J0GTA75AP001_CHOOSE | 4527 | #1中间水池提升泵选择 |  | digital
FW.J0GTA75AP001_LP | 4528 | #1中间水池提升泵 |  | int32
FW.J0GTA75AP001PF | 4529 | #1中间水池提升泵综合故障 |  | digital
FW.J0GTA75AP001RC | 4530 | #1中间水池提升泵远方控制 |  | digital
FW.J0GTA75AP001RD | 4531 | #1中间水池提升泵启动指令 |  | digital
FW.J0GTA75AP001RP | 4532 | #1中间水池提升泵在运行 |  | digital
FW.J0GTA75AP001TD | 4533 | #1中间水池提升泵停止指令 |  | digital
FW.J0GTA76AP001_CHOOSE | 4534 | #2中间水池提升泵选择 |  | digital
FW.J0GTA76AP001_LP | 4535 | #2中间水池提升泵 |  | int32
FW.J0GTA76AP001PF | 4536 | #2中间水池提升泵综合故障 |  | digital
FW.J0GTA76AP001RC | 4537 | #2中间水池提升泵远方控制 |  | digital
FW.J0GTA76AP001RD | 4538 | #2中间水池提升泵启动指令 |  | digital
FW.J0GTA76AP001RP | 4539 | #2中间水池提升泵在运行 |  | digital
FW.J0GTA76AP001TD | 4540 | #2中间水池提升泵停止指令 |  | digital
FW.J0GTA76CL101 | 4541 | 中间水池液位 | m | float32
FW.J0GTA76CP101 | 4542 | 中间水池出口压力 | Mpa | float32
FW.J0GUC21GH001 | 4543 | #1燃机主变电缆头坑极水坑液位高 |  | digital
FW.J0GUC23GH001 | 4544 | #2燃机主变电缆头坑极水坑液位高 |  | digital
FW.J0GUC25GH001 | 4545 | #1汽机主变电缆头坑极水坑液位高 |  | digital
FW.J0GUC27GH001 | 4546 | #2汽机主变电缆头坑极水坑液位高 |  | digital
FW.J0GUC29GH001 | 4547 | 高备变电缆头坑集水坑液位高 |  | digital
FW.J0QCE11AM001_LP | 4548 | #1稳定剂溶液箱搅拌器 |  | int32
FW.J0QCE11AM001F | 4549 | #1稳定剂溶液箱搅拌器故障 |  | digital
FW.J0QCE11AM001RC | 4550 | #1稳定剂溶液箱搅拌器就地/远程 |  | digital
FW.J0QCE11AM001RD | 4551 | #1稳定剂溶液箱搅拌器启动指令 |  | digital
FW.J0QCE11AM001RP | 4552 | #1稳定剂溶液箱搅拌器在运行 |  | digital
FW.J0QCE11AM001TD | 4553 | #1稳定剂溶液箱搅拌器停止指令 |  | digital
FW.J0QCE11CL101 | 4554 | #1稳定剂溶液箱液位 | m | float32
FW.J0QCE12AM001_LP | 4555 | #2稳定剂溶液箱搅拌器 |  | int32
FW.J0QCE12AM001F | 4556 | #2稳定剂溶液箱搅拌器故障 |  | digital
FW.J0QCE12AM001RC | 4557 | #2稳定剂溶液箱搅拌器就地/远程 |  | digital
FW.J0QCE12AM001RD | 4558 | #2稳定剂溶液箱搅拌器启动指令 |  | digital
FW.J0QCE12AM001RP | 4559 | #2稳定剂溶液箱搅拌器在运行 |  | digital
FW.J0QCE12AM001TD | 4560 | #2稳定剂溶液箱搅拌器停止指令 |  | digital
FW.J0QCE12CL101 | 4561 | #2稳定剂溶液箱液位 | m | float32
FW.J0QCE21AP001_LP | 4562 | #1稳定剂加药计量泵 |  | int32
FW.J0QCE21AP001F | 4563 | #1稳定剂加药计量泵故障 |  | digital
FW.J0QCE21AP001RC | 4564 | #1稳定剂加药计量泵就地/远程 |  | digital
FW.J0QCE21AP001RD | 4565 | #1稳定剂加药计量泵启动指令 |  | digital
FW.J0QCE21AP001RP | 4566 | #1稳定剂加药计量泵在运行 |  | digital
FW.J0QCE21AP001TD | 4567 | #1稳定剂加药计量泵停止指令 |  | digital
FW.J0QCE22AP001_LP | 4568 | #2稳定剂加药计量泵 |  | int32
FW.J0QCE22AP001F | 4569 | #2稳定剂加药计量泵故障 |  | digital
FW.J0QCE22AP001RC | 4570 | #2稳定剂加药计量泵就地/远程 |  | digital
FW.J0QCE22AP001RD | 4571 | #2稳定剂加药计量泵启动指令 |  | digital
FW.J0QCE22AP001RP | 4572 | #2稳定剂加药计量泵在运行 |  | digital
FW.J0QCE22AP001TD | 4573 | #2稳定剂加药计量泵停止指令 |  | digital
FW.J0QCE23AP001_LP | 4574 | #3稳定剂加药计量泵 |  | int32
FW.J0QCE23AP001F | 4575 | #3稳定剂加药计量泵故障 |  | digital
FW.J0QCE23AP001RC | 4576 | #3稳定剂加药计量泵就地/远程 |  | digital
FW.J0QCE23AP001RD | 4577 | #3稳定剂加药计量泵启动指令 |  | digital
FW.J0QCE23AP001RP | 4578 | #3稳定剂加药计量泵在运行 |  | digital
FW.J0QCE23AP001TD | 4579 | #3稳定剂加药计量泵停止指令 |  | digital
FW.J0QCL11CL101 | 4580 | #1次氯酸钠卸药储罐液位 | m | float32
FW.J0QCL12CL101 | 4581 | #2次氯酸钠卸药储罐液位 | m | float32
FW.J0QCL21AP001_LP | 4582 | #1次氯酸钠加药计量泵 |  | int32
FW.J0QCL21AP001F | 4583 | #1次氯酸钠加药计量泵故障 |  | digital
FW.J0QCL21AP001RC | 4584 | #1次氯酸钠加药计量泵就地/远程 |  | digital
FW.J0QCL21AP001RD | 4585 | #1次氯酸钠加药计量泵启动指令 |  | digital
FW.J0QCL21AP001RP | 4586 | #1次氯酸钠加药计量泵在运行 |  | digital
FW.J0QCL21AP001TD | 4587 | #1次氯酸钠加药计量泵停止指令 |  | digital
FW.J0QCL22AP001_LP | 4588 | #2次氯酸钠加药计量泵 |  | int32
FW.J0QCL22AP001F | 4589 | #2次氯酸钠加药计量泵故障 |  | digital
FW.J0QCL22AP001RC | 4590 | #2次氯酸钠加药计量泵就地/远程 |  | digital
FW.J0QCL22AP001RD | 4591 | #2次氯酸钠加药计量泵启动指令 |  | digital
FW.J0QCL22AP001RP | 4592 | #2次氯酸钠加药计量泵在运行 |  | digital
FW.J0QCL22AP001TD | 4593 | #2次氯酸钠加药计量泵停止指令 |  | digital
FW.J0QJA00CQ001 | 4594 | 1#在线漏氢检测报警（汇流排间） |  | digital
FW.J0QJA00CQ002 | 4595 | 2#在线漏氢检测报警（实瓶间） |  | digital
FW.J0QJA00CQ003 | 4596 | 3#在线漏氢检测报警（实瓶间） |  | digital
FW.J0QJA00CQ004 | 4597 | 4#在线漏氢检测报警（实瓶间） |  | digital
FW.J0QJA00CQ005 | 4598 | 5#在线漏氢检测报警（实瓶间） |  | digital
FW.J0QJA00CQ006 | 4599 | 6#在线漏氢检测报警（实瓶间） |  | digital
FW.J0QJA00CQ007 | 4600 | 7#在线漏氢检测报警（实瓶间） |  | digital
FW.J0QJA21CM101 | 4601 | 供氢系统A侧氢气露点 |  | float32
FW.J0QJA21CP101 | 4602 | 供氢系统A侧高压母管氢气压力 | Mpa | float32
FW.J0QJA21CP102 | 4603 | 供氢系统A侧低压母管氢气压力 | Mpa | float32
FW.J0QJA21CQ101 | 4604 | 供氢系统A侧氢气纯度 |  | float32
FW.J0QJA22CM101 | 4605 | 供氢系统B侧氢气露点 |  | float32
FW.J0QJA22CP101 | 4606 | 供氢系统B侧高压母管氢气压力 | Mpa | float32
FW.J0QJA22CP102 | 4607 | 供氢系统B侧低压母管氢气压力 | Mpa | float32
FW.J0QJA22CQ101 | 4608 | 供氢系统B侧氢气纯度 |  | float32
FW.J0SGA11CT301 | 4609 | 电动消防泵电机轴承温度 | ℃ | float32
FW.J0SGA11CT302 | 4610 | 电动消防泵电机轴承温度 | ℃ | float32
FW.J0SGA11CT303 | 4611 | 电动消防泵电机U相定子绕组温度1 | ℃ | float32
FW.J0SGA11CT304 | 4612 | 电动消防泵电机U相定子绕组温度2 | ℃ | float32
FW.J0SGA11CT305 | 4613 | 电动消防泵电机V相定子绕组温度1 | ℃ | float32
FW.J0SGA11CT306 | 4614 | 电动消防泵电机V相定子绕组温度2 | ℃ | float32
FW.J0SGA11CT307 | 4615 | 电动消防泵电机W相定子绕组温度1 | ℃ | float32
FW.J0SGA11CT308 | 4616 | 电动消防泵电机W相定子绕组温度2 | ℃ | float32
FW.J0SGA11CT309 | 4617 | 电动消防泵轴承温度 | ℃ | float32
FW.J0SGA11CT310 | 4618 | 电动消防泵轴承温度 | ℃ | float32
FW.J0SGA14CT301 | 4619 | 柴油机消防水泵轴承温度 | ℃ | float32
FW.J0SGA14CT302 | 4620 | 柴油机消防水泵轴承温度 | ℃ | float32
FW.J0SGA14CT303 | 4621 | 柴油消防泵电机U相定子绕组温度1 | ℃ | float32
FW.J0SGA14CT304 | 4622 | 柴油消防泵电机U相定子绕组温度2 | ℃ | float32
FW.J0SGA14CT305 | 4623 | 柴油消防泵电机V相定子绕组温度1 | ℃ | float32
FW.J0SGA14CT306 | 4624 | 柴油消防泵电机V相定子绕组温度2 | ℃ | float32
FW.J0SGA14CT307 | 4625 | 柴油消防泵电机W相定子绕组温度1 | ℃ | float32
FW.J0SGA14CT308 | 4626 | 柴油消防泵电机W相定子绕组温度2 | ℃ | float32
FW.J0SGA23CF101 | 4627 | 消防泵出口母管回水流量 | t/h | float32
FW.J0SGA23CP101 | 4628 | 消防泵出口母管压力 | Mpa | float32
FW.JFYHSJJ_J0GCB40AP001CP | 4629 | 反渗透冲洗水泵顺控停2 |  | digital
FW.JFYHSJJ_J0GCB40AP001OP | 4630 | 反渗透冲洗水泵顺控启2 |  | digital
FW.JFYHSJJ_J0GCF31AA005CP | 4631 | #1一级反渗透进冲洗水阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF31AA005OP | 4632 | #1一级反渗透进冲洗水阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF31AA055CP | 4633 | #1一级反渗透产水排放阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF31AA055OP | 4634 | #1一级反渗透产水排放阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF31AA402CP | 4635 | #1一级反渗透浓水排放阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF31AA402OP | 4636 | #1一级反渗透浓水排放阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF32AA005CP | 4637 | #2一级反渗透进冲洗水阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF32AA005OP | 4638 | #2一级反渗透进冲洗水阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF32AA055CP | 4639 | #2一级反渗透产水排放阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF32AA055OP | 4640 | #2一级反渗透产水排放阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF32AA402CP | 4641 | #2一级反渗透浓水排放阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF32AA402OP | 4642 | #2一级反渗透浓水排放阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF33AA005CP | 4643 | #3一级反渗透进冲洗水阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF33AA005OP | 4644 | #3一级反渗透进冲洗水阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF33AA055CP | 4645 | #3一级反渗透产水排放阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF33AA055OP | 4646 | #3一级反渗透产水排放阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF33AA402CP | 4647 | #3一级反渗透浓水排放阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF33AA402OP | 4648 | #3一级反渗透浓水排放阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF34AA005CP | 4649 | #4一级反渗透进冲洗水阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF34AA005OP | 4650 | #4一级反渗透进冲洗水阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF34AA055CP | 4651 | #4一级反渗透产水排放阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF34AA055OP | 4652 | #4一级反渗透产水排放阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCF34AA402CP | 4653 | #4一级反渗透浓水排放阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCF34AA402OP | 4654 | #4一级反渗透浓水排放阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCK21AP001CP | 4655 | #1一级反渗透给水泵顺控停2 |  | digital
FW.JFYHSJJ_J0GCK21AP001OP | 4656 | #1一级反渗透给水泵顺控启2 |  | digital
FW.JFYHSJJ_J0GCK22AP001CP | 4657 | #2一级反渗透给水泵顺控停2 |  | digital
FW.JFYHSJJ_J0GCK22AP001OP | 4658 | #2一级反渗透给水泵顺控启2 |  | digital
FW.JFYHSJJ_J0GCK23AP001CP | 4659 | #3一级反渗透给水泵顺控停2 |  | digital
FW.JFYHSJJ_J0GCK23AP001OP | 4660 | #3一级反渗透给水泵顺控启2 |  | digital
FW.JFYHSJJ_J0GCK24AP001CP | 4661 | #4一级反渗透给水泵顺控停2 |  | digital
FW.JFYHSJJ_J0GCK24AP001OP | 4662 | #4一级反渗透给水泵顺控启2 |  | digital
FW.JFYHSJJ_J0GCK31AA002CP | 4663 | #1一级反渗透进水阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCK31AA002OP | 4664 | #1一级反渗透进水阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCK32AA002CP | 4665 | #2一级反渗透进水阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCK32AA002OP | 4666 | #2一级反渗透进水阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCK33AA002CP | 4667 | #3一级反渗透进水阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCK33AA002OP | 4668 | #3一级反渗透进水阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCK34AA002CP | 4669 | #4一级反渗透进水阀顺控关2 |  | digital
FW.JFYHSJJ_J0GCK34AA002OP | 4670 | #4一级反渗透进水阀顺控开2 |  | digital
FW.JFYHSJJ_J0GCQ61AP001CP | 4671 | 加非氧化性杀菌剂计量泵顺控停 |  | digital
FW.JFYHSJJ_J0GCQ61AP001OP | 4672 | 加非氧化性杀菌剂计量泵顺控启 |  | digital
FW.JFYHSJJFX_PD | 4673 | Ovation Control Builder |  | float32
FW.JFYHSJJFXJT | 4674 | 加非氧化性杀菌剂急停 |  | digital
FW.JFYHSJJTIME1 | 4675 | #1加非氧化性杀菌剂步序排队时间 |  | float32
FW.JFYHSJJTIME2 | 4676 | #2加非氧化性杀菌剂步序排队时间 |  | float32
FW.JFYHSJJTIME3 | 4677 | #3加非氧化性杀菌剂步序排队时间 |  | float32
FW.JFYHSJJTIME4 | 4678 | #4加非氧化性杀菌剂步序排队时间 |  | float32
FW.JJBLSQ | 4679 | #2加碱泵联锁启 |  | digital
FW.JJBLSQ3 | 4680 | #3加碱泵联锁启 |  | digital
FW.JJLXQYX | 4681 | #1碱溶液泵启允许 |  | digital
FW.JJLXQYX2 | 4682 | #2/3碱溶液泵启允许 |  | digital
FW.JOGNB10AA001_LP | 4683 | pH值调整池入口门 |  | int32
FW.JOGNB10AA001CD | 4684 | pH值调整池入口门关闭 |  | digital
FW.JOGNB10AA001CP | 4685 | pH值调整池入口门关到位 |  | digital
FW.JOGNB10AA001OD | 4686 | pH值调整池入口门开启 |  | digital
FW.JOGNB10AA001OP | 4687 | pH值调整池入口门开到位 |  | digital
FW.JOGNB10AA001RC | 4688 | pH值调整池入口门远控信号 |  | digital
FW.JOGNB10AA002_LP | 4689 | pH值调整池进碱门 |  | int32
FW.JOGNB10AA002CD | 4690 | pH值调整池进碱门关闭 |  | digital
FW.JOGNB10AA002CP | 4691 | pH值调整池进碱门关到位 |  | digital
FW.JOGNB10AA002OD | 4692 | pH值调整池进碱门开启 |  | digital
FW.JOGNB10AA002OP | 4693 | pH值调整池进碱门开到位 |  | digital
FW.JOGNB10AA002RC | 4694 | pH值调整池进碱门远控信号 |  | digital
FW.JOGNB10AA003_LP | 4695 | pH值调整池进酸门 |  | int32
FW.JOGNB10AA003CD | 4696 | pH值调整池进酸门关闭 |  | digital
FW.JOGNB10AA003CP | 4697 | pH值调整池进酸门关到位 |  | digital
FW.JOGNB10AA003OD | 4698 | pH值调整池进酸门开启 |  | digital
FW.JOGNB10AA003OP | 4699 | pH值调整池进酸门开到位 |  | digital
FW.JOGNB10AA003RC | 4700 | pH值调整池进酸门远控信号 |  | digital
FW.JOGNB20AA001_LP | 4701 | 废水反应池加凝聚剂门 |  | int32
FW.JOGNB20AA001CD | 4702 | 反应池加混凝剂门关闭 |  | digital
FW.JOGNB20AA001CP | 4703 | 反应池加混凝剂门关到位 |  | digital
FW.JOGNB20AA001OD | 4704 | 反应池加混凝剂门开启 |  | digital
FW.JOGNB20AA001OP | 4705 | 反应池加混凝剂门开到位 |  | digital
FW.JOGNB20AA001RC | 4706 | 反应池加混凝剂门远控信号 |  | digital
FW.JOGNB30AA001_LP | 4707 | 废水絮凝池加PAM门 |  | int32
FW.JOGNB30AA001CD | 4708 | 絮凝池加PAM门关闭 |  | digital
FW.JOGNB30AA001CP | 4709 | 絮凝池加PAM门关到位 |  | digital
FW.JOGNB30AA001OD | 4710 | 絮凝池加PAM门开启 |  | digital
FW.JOGNB30AA001OP | 4711 | 絮凝池加PAM门开到位 |  | digital
FW.JOGNB30AA001RC | 4712 | 絮凝池加PAM门远控信号 |  | digital
FW.JOGNB40AA001_LP | 4713 | 废水斜板澄清器排污门 |  | int32
FW.JOGNB40AA001CD | 4714 | 斜板澄清器排污门关闭 |  | digital
FW.JOGNB40AA001CP | 4715 | 斜板澄清器排污门关到位 |  | digital
FW.JOGNB40AA001OD | 4716 | 斜板澄清器排污门开启 |  | digital
FW.JOGNB40AA001OP | 4717 | 斜板澄清器排污门开到位 |  | digital
FW.JOGNB40AA001RC | 4718 | 斜板澄清器排污门远控信号 |  | digital
FW.JOGNC20AA501_LP | 4719 | 废水风机母管排空门 |  | int32
FW.JOGNC20AA501CD | 4720 | 风机母管排空门关闭 |  | digital
FW.JOGNC20AA501CP | 4721 | 风机母管排空门关到位 |  | digital
FW.JOGNC20AA501OD | 4722 | 风机母管排空门开启 |  | digital
FW.JOGNC20AA501OP | 4723 | 风机母管排空门开到位 |  | digital
FW.JOGNC20AA501RC | 4724 | 风机母管排空门远控信号 |  | digital
FW.JOGNL11AA001_LP | 4725 | 非经常性废水收集池曝气门 |  | int32
FW.JOGNL11AA001CD | 4726 | 非经常性废水收集池曝气门关闭 |  | digital
FW.JOGNL11AA001CP | 4727 | 非经常性废水收集池曝气门关到位 |  | digital
FW.JOGNL11AA001OD | 4728 | 非经常性废水收集池曝气门开启 |  | digital
FW.JOGNL11AA001OP | 4729 | 非经常性废水收集池曝气门开到位 |  | digital
FW.JOGNL11AA001RC | 4730 | 非经常性废水收集池曝气门远控 |  | digital
FW.JOGNL11AA004_LP | 4731 | 非经常性废水收集池进碱门 |  | int32
FW.JOGNL11AA004CD | 4732 | 非经常性废水收集池进碱门关闭 |  | digital
FW.JOGNL11AA004CP | 4733 | 非经常性废水收集池进碱门关到位 |  | digital
FW.JOGNL11AA004OD | 4734 | 非经常性废水收集池进碱门开启 |  | digital
FW.JOGNL11AA004OP | 4735 | 非经常性废水收集池进碱门开到位 |  | digital
FW.JOGNL11AA004RC | 4736 | 非经常性废水收集池进碱门远控 |  | digital
FW.JOGNL11AA005_LP | 4737 | 非经常性废水收集池废水入口门 |  | int32
FW.JOGNL11AA005CD | 4738 | 非经常性废水收集池废水入口门关 |  | digital
FW.JOGNL11AA005CP | 4739 | 非经常废水收集池废水入口门已关 |  | digital
FW.JOGNL11AA005OD | 4740 | 非经常性废水收集池废水入口门开 |  | digital
FW.JOGNL11AA005OP | 4741 | 非经常废水收集池废水入口门已开 |  | digital
FW.JOGNL11AA005RC | 4742 | 非经常废水收集池废水入口门远控 |  | digital
FW.JOGNL12AA001_LP | 4743 | 经常性废水收集池曝气门 |  | int32
FW.JOGNL12AA001CD | 4744 | 经常性废水收集池曝气门关闭 |  | digital
FW.JOGNL12AA001CP | 4745 | 经常性废水收集池曝气门关到位 |  | digital
FW.JOGNL12AA001OD | 4746 | 经常性废水收集池曝气门开启 |  | digital
FW.JOGNL12AA001OP | 4747 | 经常性废水收集池曝气门开到位 |  | digital
FW.JOGNL12AA001RC | 4748 | 经常性废水收集池曝气门远控信号 |  | digital
FW.JOGNL12AA004_LP | 4749 | 经常性废水收集池进碱门 |  | int32
FW.JOGNL12AA004CD | 4750 | 经常性废水收集池进碱门关闭 |  | digital
FW.JOGNL12AA004CP | 4751 | 经常性废水收集池进碱门关到位 |  | digital
FW.JOGNL12AA004OD | 4752 | 经常性废水收集池进碱门开启 |  | digital
FW.JOGNL12AA004OP | 4753 | 经常性废水收集池进碱门开到位 |  | digital
FW.JOGNL12AA004RC | 4754 | 经常性废水收集池进碱门远控信号 |  | digital
FW.JOGNL12AA005_LP | 4755 | 经常性废水收集池废水入口门 |  | int32
FW.JOGNL12AA005CD | 4756 | 经常性废水收集池废水入口门关闭 |  | digital
FW.JOGNL12AA005CP | 4757 | 经常性废水收集池废水入口门已关 |  | digital
FW.JOGNL12AA005OD | 4758 | 经常性废水收集池废水入口门开启 |  | digital
FW.JOGNL12AA005OP | 4759 | 经常性废水收集池废水入口门已开 |  | digital
FW.JOGNL12AA005RC | 4760 | 经常性废水收集池废水入口门远控 |  | digital
FW.JOGNL40AA001_LP | 4761 | 清水泵出口母管总门 |  | int32
FW.JOGNL40AA001CD | 4762 | 清水泵出口母管总门关闭 |  | digital
FW.JOGNL40AA001CP | 4763 | 清水泵出口母管总门关到位 |  | digital
FW.JOGNL40AA001OD | 4764 | 清水泵出口母管总门开启 |  | digital
FW.JOGNL40AA001OP | 4765 | 清水泵出口母管总门开到位 |  | digital
FW.JOGNL40AA001RC | 4766 | 清水泵出口母管总门远控信号 |  | digital
FW.JOGNL40AA002_LP | 4767 | 清水泵出口母管回流门 |  | int32
FW.JOGNL40AA002CD | 4768 | 清水泵出口母管回流门关闭 |  | digital
FW.JOGNL40AA002CP | 4769 | 清水泵出口母管回流门关到位 |  | digital
FW.JOGNL40AA002OD | 4770 | 清水泵出口母管回流门开启 |  | digital
FW.JOGNL40AA002OP | 4771 | 清水泵出口母管回流门开到位 |  | digital
FW.JOGNL40AA002RC | 4772 | 清水泵出口母管回流门远控信号 |  | digital
FW.JOGNL40AA003_LP | 4773 | 外排水门 |  | int32
FW.JOGNL40AA003CD | 4774 | 外排水门关闭 |  | digital
FW.JOGNL40AA003CP | 4775 | 外排水门关到位 |  | digital
FW.JOGNL40AA003OD | 4776 | 外排水门开启 |  | digital
FW.JOGNL40AA003OP | 4777 | 外排水门开到位 |  | digital
FW.JOGNL40AA003RC | 4778 | 外排水门远控信号 |  | digital
FW.JOGNN31AA001_LP | 4779 | #1废水酸溶液箱进口门 |  | int32
FW.JOGNN31AA001CD | 4780 | #1酸溶液箱进口门关闭 |  | digital
FW.JOGNN31AA001CP | 4781 | #1酸溶液箱进口门关到位 |  | digital
FW.JOGNN31AA001OD | 4782 | #1酸溶液箱进口门开启 |  | digital
FW.JOGNN31AA001OP | 4783 | #1酸溶液箱进口门开到位 |  | digital
FW.JOGNN31AA001RC | 4784 | #1酸溶液箱进口门远控信号 |  | digital
FW.JOGNN32AA001_LP | 4785 | #2废水酸溶液箱进口门 |  | int32
FW.JOGNN32AA001CD | 4786 | #2酸溶液箱进口门关闭 |  | digital
FW.JOGNN32AA001CP | 4787 | #2酸溶液箱进口门关到位 |  | digital
FW.JOGNN32AA001OD | 4788 | #2酸溶液箱进口门开启 |  | digital
FW.JOGNN32AA001OP | 4789 | #2酸溶液箱进口门开到位 |  | digital
FW.JOGNN32AA001RC | 4790 | #2酸溶液箱进口门远控信号 |  | digital
FW.JOGNN51AA001_LP | 4791 | #1废水碱溶液箱进口门 |  | int32
FW.JOGNN51AA001CD | 4792 | #1碱溶液箱进口门关闭 |  | digital
FW.JOGNN51AA001CP | 4793 | #1碱溶液箱进口门关到位 |  | digital
FW.JOGNN51AA001OD | 4794 | #1碱溶液箱进口门开启 |  | digital
FW.JOGNN51AA001OP | 4795 | #1碱溶液箱进口门开到位 |  | digital
FW.JOGNN51AA001RC | 4796 | #1碱溶液箱进口门远控信号 |  | digital
FW.JOGNN52AA001_LP | 4797 | #2废水碱溶液箱进口门 |  | int32
FW.JOGNN52AA001CD | 4798 | #2碱溶液箱进口门关闭 |  | digital
FW.JOGNN52AA001CP | 4799 | #2碱溶液箱进口门关到位 |  | digital
FW.JOGNN52AA001OD | 4800 | #2碱溶液箱进口门开启 |  | digital
FW.JOGNN52AA001OP | 4801 | #2碱溶液箱进口门开到位 |  | digital
FW.JOGNN52AA001RC | 4802 | #2碱溶液箱进口门远控信号 |  | digital
FW.JOGNP60AA001_LP | 4803 | 工业废水PAM进水门 |  | int32
FW.JOGNP60AA001CD | 4804 | PAM进水门关闭 |  | digital
FW.JOGNP60AA001CP | 4805 | PAM进水门关到位 |  | digital
FW.JOGNP60AA001OD | 4806 | PAM进水门开启 |  | digital
FW.JOGNP60AA001OP | 4807 | PAM进水门开到位 |  | digital
FW.JOGNP60AA001RC | 4808 | PAM进水门远控信号 |  | digital
FW.JOGNR10AA002_LP | 4809 | 最终中和池进酸门 |  | int32
FW.JOGNR10AA002CD | 4810 | 最终中和池进酸门关闭 |  | digital
FW.JOGNR10AA002CP | 4811 | 最终中和池进酸门关到位 |  | digital
FW.JOGNR10AA002OD | 4812 | 最终中和池进酸门开启 |  | digital
FW.JOGNR10AA002OP | 4813 | 最终中和池进酸门开到位 |  | digital
FW.JOGNR10AA002RC | 4814 | 最终中和池进酸门远控信号 |  | digital
FW.JOGNR10AA003_LP | 4815 | 最终中和池进碱门 |  | int32
FW.JOGNR10AA003CD | 4816 | 最终中和池进碱门关闭 |  | digital
FW.JOGNR10AA003CP | 4817 | 最终中和池进碱门关到位 |  | digital
FW.JOGNR10AA003OD | 4818 | 最终中和池进碱门开启 |  | digital
FW.JOGNR10AA003OP | 4819 | 最终中和池进碱门开到位 |  | digital
FW.JOGNR10AA003RC | 4820 | 最终中和池进碱门远控信号 |  | digital
FW.JSZGN_CHOOSE | 4821 | 净水站刮泥选择 |  | digital
FW.JT_J0GCQ61AP001 | 4822 | Ovation Control Builder |  | digital
FW.JYBQG | 4823 | 加药泵全关 |  | digital
FW.JYDW | 4824 | 增强反洗加药到位 |  | digital
FW.LCFJ_LSOPEN | 4825 | 罗茨风机联锁启动 |  | digital
FW.P1B2S6_A1/A2 | 4826 | EXT2-1-A1/A2卡件电源故障 |  | digital
FW.P1B2S6_A3/A4 | 4827 | EXT2-1-A3/A4卡件电源故障 |  | digital
FW.P1B2S6_B1/B2 | 4828 | EXT2-1-B1/B2卡件电源故障 |  | digital
FW.P1B2S7_B3/B4 | 4829 | EXT2-1-B3/B4卡件电源故障 |  | digital
FW.P1B2S7_C1/C2 | 4830 | EXT2-1-C1/C2卡件电源故障 |  | digital
FW.P1B2S7_C3 | 4831 | EXT2-1-C3卡件电源故障 |  | digital
FW.PST1 | 4832 | #1超滤给水泵保护停 |  | digital
FW.PST10 | 4833 | #4一级反渗透给水泵保护停 |  | digital
FW.PST11 | 4834 | #1一级反渗透高压泵保护停 |  | digital
FW.PST12 | 4835 | #2一级反渗透高压泵保护停 |  | digital
FW.PST13 | 4836 | #3一级反渗透高压泵保护停 |  | digital
FW.PST14 | 4837 | #4一级反渗透高压泵保护停 |  | digital
FW.PST15 | 4838 | 反渗透冲洗水泵保护停 |  | digital
FW.PST16 | 4839 | #1二级反渗透高压泵保护停 |  | digital
FW.PST17 | 4840 | #2二级反渗透高压泵保护停 |  | digital
FW.PST18 | 4841 | #3二级反渗透高压泵保护停 |  | digital
FW.PST19 | 4842 | #4二级反渗透高压泵保护停 |  | digital
FW.PST2 | 4843 | #2超滤给水泵保护停 |  | digital
FW.PST20 | 4844 | #1EDI给水泵保护停 |  | digital
FW.PST21 | 4845 | #2EDI给水泵保护停 |  | digital
FW.PST22 | 4846 | #3EDI给水泵保护停 |  | digital
FW.PST23 | 4847 | #4EDI给水泵保护停 |  | digital
FW.PST24 | 4848 | #1除盐水泵保护停 |  | digital
FW.PST25 | 4849 | #2除盐水泵保护停 |  | digital
FW.PST26 | 4850 | #3除盐水泵保护停 |  | digital
FW.PST27 | 4851 | #4除盐水泵保护停 |  | digital
FW.PST28 | 4852 | #1阻垢剂计量泵保护停 |  | digital
FW.PST29 | 4853 | #2阻垢剂计量泵保护停 |  | digital
FW.PST3 | 4854 | #3超滤给水泵保护停 |  | digital
FW.PST30 | 4855 | #1还原剂计量泵保护停 |  | digital
FW.PST31 | 4856 | #2还原剂计量泵保护停 |  | digital
FW.PST32 | 4857 | #1超滤反洗加碱计量泵保护停 |  | digital
FW.PST33 | 4858 | #2超滤反洗加碱计量泵保护停 |  | digital
FW.PST34 | 4859 | #1二级反渗透加碱计量泵保护停 |  | digital
FW.PST35 | 4860 | #2二级反渗透加碱计量泵保护停 |  | digital
FW.PST36 | 4861 | #1加酸计量泵保护停 |  | digital
FW.PST37 | 4862 | #2加酸计量泵保护停 |  | digital
FW.PST38 | 4863 | #1杀菌剂计量泵保护停 |  | digital
FW.PST39 | 4864 | #2杀菌剂计量泵保护停 |  | digital
FW.PST4 | 4865 | #4超滤给水泵保护停 |  | digital
FW.PST40 | 4866 | #1回收水泵保护停 |  | digital
FW.PST41 | 4867 | #2回收水泵保护停 |  | digital
FW.PST5 | 4868 | #1超滤反洗泵保护停 |  | digital
FW.PST6 | 4869 | #2超滤反洗泵保护停 |  | digital
FW.PST7 | 4870 | #1一级反渗透给水泵保护停 |  | digital
FW.PST8 | 4871 | #2一级反渗透给水泵保护停 |  | digital
FW.PST9 | 4872 | #3一级反渗透给水泵保护停 |  | digital
FW.SHSXTXM | 4873 | 生活污水系统休眠信号 |  | digital
FW.SXTSBLSTR | 4874 | 水处理设备联锁投入 |  | digital
FW.TEST1 | 4875 | Ovation Control Builder |  | digital
FW.TGYB1 | 4876 | Ovation Control Builder |  | digital
FW.TGYB2 | 4877 | Ovation Control Builder |  | digital
FW.TGYB3 | 4878 | Ovation Control Builder |  | digital
FW.TGYB4 | 4879 | Ovation Control Builder |  | digital
FW.TJSCYWTJ | 4880 | 调节池液位连续72h低于2 |  | digital
FW.TSJL | 4881 | 同时加碱氯 |  | digital
FW.TYTZ1 | 4882 | #1超滤投运停止 |  | digital
FW.TYTZ2 | 4883 | #2超滤投运停止 |  | digital
FW.TYTZ3 | 4884 | #3超滤投运停止 |  | digital
FW.TYTZ4 | 4885 | #4超滤投运停止 |  | digital
FW.WNSBLSTR | 4886 | 污泥设备联锁投入 |  | digital
FW.XNCDC_DPN | 4887 | 絮凝池排泥大排泥 |  | digital
FW.XNCDC_DPNFW | 4888 | 大排泥复位 |  | digital
FW.XNCDC_DPNTZ | 4889 | 絮凝池排泥大排泥停止 |  | digital
FW.XNCDC_QD | 4890 | 絮凝池排泥启动 |  | digital
FW.XNCDC_QDTZ | 4891 | 絮凝池排泥停止 |  | digital
FW.XNCDC_QDTZFW | 4892 | 排泥复位 |  | digital
FW.XNCDCLL1 | 4893 | 一号沉淀池流量 |  | float32
FW.XNCDCLL2 | 4894 | 二号沉淀池流量 |  | float32
FW.XNCDPNTIME | 4895 | Ovation Control Builder |  | float32
FW.XNCDPNTIME2 | 4896 | Ovation Control Builder |  | float32
FW.XNCDPNTIMESPO | 4897 | Ovation Control Builder |  | float32
FW.XNCDPNTIMESPO2 | 4898 | Ovation Control Builder |  | float32
FW.XWQFXTZ | 4899 | 过滤器反洗停止 |  | digital
FW.XWQGLQYX_AUTOM | 4900 | 过滤器运行步序自动状态 |  | digital
FW.XWQGLQYX_DONE | 4901 | 过滤器运行步序结束 |  | digital
FW.XWQGLQYX_FB3 | 4902 | 过滤器运行步序反馈3 |  | digital
FW.XWQGLQYX_FB3TIME | 4903 | 过滤器运行反馈3时间 |  | float32
FW.XWQGLQYX_FB3TIMESPO | 4904 | Ovation Control Builder |  | float32
FW.XWQGLQYX_FB4 | 4905 | 过滤器运行步序反馈4 |  | digital
FW.XWQGLQYX_FB4TIME | 4906 | 过滤器运行反馈4时间 |  | float32
FW.XWQGLQYX_FB4TIMESPO | 4907 | Ovation Control Builder |  | float32
FW.XWQGLQYX_FB5 | 4908 | 过滤器运行步序反馈5 |  | digital
FW.XWQGLQYX_FB5TIME | 4909 | 过滤器运行反馈5时间 |  | float32
FW.XWQGLQYX_FB5TIMESPO | 4910 | Ovation Control Builder |  | float32
FW.XWQGLQYX_FB6 | 4911 | 过滤器运行步序反馈6 |  | digital
FW.XWQGLQYX_FB6TIME | 4912 | Ovation Control Builder |  | float32
FW.XWQGLQYX_FB6TIMESPO | 4913 | Ovation Control Builder |  | float32
FW.XWQGLQYX_LP | 4914 | 过滤器运行步序 |  | int32
FW.XWQGLQYX_MANM | 4915 | 过滤器运行步序手动状态 |  | digital
FW.XWQGLQYX_READY | 4916 | Ovation Control Builder |  | digital
FW.XWQGLQYX_SEQ3 | 4917 | 过滤器运行STEP3单独水冲洗 |  | digital
FW.XWQGLQYX_SEQ4 | 4918 | 过滤器运行STEP4气水混合洗 |  | digital
FW.XWQGLQYX_SEQ5 | 4919 | 过滤器运行STEP5单独水冲洗 |  | digital
FW.XWQGLQYX_SEQ6 | 4920 | 过滤器运行STEP6停止运行 |  | digital
FW.XWQGLQYX_SEQGO | 4921 | 过滤器运行步序启动 |  | digital
FW.XWQGLQYX_SEQNUM | 4922 | 过滤器运行当前步序 |  | float32
FW.Y0CRP74PF | 4923 | 净水站DCS电源故障报警 |  | digital
FW.Y0CRP74PF1 | 4924 | 净水站DCS厂用电电源故障报警 |  | digital
FW.Y0CRP74PF2 | 4925 | 净水站DCS保安电源故障报警 |  | digital
FW.Y0CRP74PF3 | 4926 | 净水站DCS仪表电源故障报警 |  | digital
FW.Y0CST01PF | 4927 | 配电柜母线电源故障 |  | digital
FW.Y0GAA11AA001_LP | 4928 | #1补给水泵进口电动门 |  | int32
FW.Y0GAA11AA001CD | 4929 | 1号补给水泵进口电动阀关闭指令 |  | digital
FW.Y0GAA11AA001CP | 4930 | 1号补给水泵进口电动阀全关位置 |  | digital
FW.Y0GAA11AA001F | 4931 | 1号补给水泵进口电动阀综合故障 |  | digital
FW.Y0GAA11AA001OD | 4932 | 1号补给水泵进口电动阀打开指令 |  | digital
FW.Y0GAA11AA001OP | 4933 | 1号补给水泵进口电动阀全开位置 |  | digital
FW.Y0GAA11AA001RC | 4934 | 1号补给水泵进口电动阀在远控 |  | digital
FW.Y0GAA11AA003_LP | 4935 | #1补给水泵出口电动门 |  | int32
FW.Y0GAA11AA003CD | 4936 | 1号补给水泵出口电动阀关闭指令 |  | digital
FW.Y0GAA11AA003CP | 4937 | 1号补给水泵出口电动阀全关位置 |  | digital
FW.Y0GAA11AA003F | 4938 | 1号补给水泵出口电动阀综合故障 |  | digital
FW.Y0GAA11AA003OD | 4939 | 1号补给水泵出口电动阀打开指令 |  | digital
FW.Y0GAA11AA003OP | 4940 | 1号补给水泵出口电动阀全开位置 |  | digital
FW.Y0GAA11AA003RC | 4941 | 1号补给水泵出口电动阀在远控 |  | digital
FW.Y0GAA11AP001_LP | 4942 | #1补给水泵 |  | int32
FW.Y0GAA11AP001_PMT | 4943 | 1号补给水泵启动允许 |  | digital
FW.Y0GAA11AP001I | 4944 | 1号补给水泵电流 | A | float32
FW.Y0GAA11AP001PF | 4945 | 1号补给水泵综合故障 |  | digital
FW.Y0GAA11AP001RC | 4946 | 1号补给水泵远方控制 |  | digital
FW.Y0GAA11AP001RD | 4947 | 1号补给水泵启动指令 |  | digital
FW.Y0GAA11AP001RP | 4948 | 1号补给水泵在运行 |  | digital
FW.Y0GAA11AP001TD | 4949 | 1号补给水泵停止指令 |  | digital
FW.Y0GAA11AP001TP | 4950 | 1号补给水泵已停止 |  | digital
FW.Y0GAA11APTM_STP | 4951 | #1补水泵温度高保护跳泵 |  | digital
FW.Y0GAA11AT002_LP | 4952 | Ovation Control Builder |  | int32
FW.Y0GAA11AT002CD | 4953 | 1号旋转滤网急停指令 |  | digital
FW.Y0GAA11AT002CP1 | 4954 | 1号旋转滤网冲洗水电动阀关 |  | digital
FW.Y0GAA11AT002CP2 | 4955 | 旋转滤网冲渣沟冲洗水电动阀关 |  | digital
FW.Y0GAA11AT002D_LP | 4956 | #1旋转滤网低速电机 |  | int32
FW.Y0GAA11AT002DSQD | 4957 | 1号旋转滤网低速定时启动 |  | digital
FW.Y0GAA11AT002F | 4958 | 1号旋转滤网故障 |  | digital
FW.Y0GAA11AT002G_LP | 4959 | #1旋转滤网高速电机 |  | int32
FW.Y0GAA11AT002JT | 4960 | 1号旋转滤网已急停 |  | digital
FW.Y0GAA11AT002LC | 4961 | 1号旋转滤网本地模式 |  | digital
FW.Y0GAA11AT002OP1 | 4962 | 1号旋转滤网冲洗水电动阀开 |  | digital
FW.Y0GAA11AT002OP2 | 4963 | 旋转滤网冲渣沟冲洗水电动阀开 |  | digital
FW.Y0GAA11AT002QZ | 4964 | 1号旋转滤网轻载 |  | digital
FW.Y0GAA11AT002RC | 4965 | 1号旋转滤网在远控 |  | digital
FW.Y0GAA11AT002RD1 | 4966 | 1号旋转滤网低速启动指令 |  | digital
FW.Y0GAA11AT002RD2 | 4967 | 1号旋转滤网高速启动指令 |  | digital
FW.Y0GAA11AT002RP | 4968 | 1号旋转滤网运行 |  | digital
FW.Y0GAA11AT002RP1 | 4969 | 1号旋转滤网低速运行 |  | digital
FW.Y0GAA11AT002RP2 | 4970 | 1号旋转滤网高速运行 |  | digital
FW.Y0GAA11AT002SL1 | 4971 | 1号旋转滤网松链1 |  | digital
FW.Y0GAA11AT002SL2 | 4972 | 1号旋转滤网松链2 |  | digital
FW.Y0GAA11AT002SLD1 | 4973 | 1号旋转滤网松链1 |  | digital
FW.Y0GAA11AT002SLD2 | 4974 | 1号旋转滤网松链2 |  | digital
FW.Y0GAA11AT002ZZ | 4975 | 1号旋转滤网重载 |  | digital
FW.Y0GAA11CL101 | 4976 | 1号旋转滤网前液位 | Hz | float32
FW.Y0GAA11CL102 | 4977 | 1号旋转滤网后液位 | Hz | float32
FW.Y0GAA11CL107 | 4978 | #1旋转滤网前后液位差值 |  | float32
FW.Y0GAA11CT301 | 4979 | 1号补给水泵电机线圈温度1 | ℃ | float32
FW.Y0GAA11CT302 | 4980 | 1号补给水泵电机线圈温度2 | ℃ | float32
FW.Y0GAA11CT303 | 4981 | 1号补给水泵电机线圈温度3 | ℃ | float32
FW.Y0GAA11CT304 | 4982 | 1号补给水泵电机线圈温度4 | ℃ | float32
FW.Y0GAA11CT305 | 4983 | 1号补给水泵电机线圈温度5 | ℃ | float32
FW.Y0GAA11CT306 | 4984 | 1号补给水泵电机线圈温度6 | ℃ | float32
FW.Y0GAA11CT307 | 4985 | 1号补给水泵轴伸端轴承温度 | ℃ | float32
FW.Y0GAA11CT308 | 4986 | 1号补给水泵非轴伸端轴承温度 | ℃ | float32
FW.Y0GAA11CT309 | 4987 | 1号补给水泵轴承温度1 | ℃ | float32
FW.Y0GAA11CT310 | 4988 | 1号补给水泵轴承温度2 | ℃ | float32
FW.Y0GAA12AA001_LP | 4989 | #2补给水泵进口电动门 |  | int32
FW.Y0GAA12AA001CD | 4990 | 2号补给水泵进口电动阀关闭指令 |  | digital
FW.Y0GAA12AA001CP | 4991 | 2号补给水泵进口电动阀全关位置 |  | digital
FW.Y0GAA12AA001F | 4992 | 2号补给水泵进口电动阀综合故障 |  | digital
FW.Y0GAA12AA001OD | 4993 | 2号补给水泵进口电动阀打开指令 |  | digital
FW.Y0GAA12AA001OP | 4994 | 2号补给水泵进口电动阀全开位置 |  | digital
FW.Y0GAA12AA001RC | 4995 | 2号补给水泵进口电动阀在远控 |  | digital
FW.Y0GAA12AA003_LP | 4996 | #2补给水泵出口电动门 |  | int32
FW.Y0GAA12AA003CD | 4997 | 2号补给水泵出口电动阀关闭指令 |  | digital
FW.Y0GAA12AA003CP | 4998 | 2号补给水泵出口电动阀全关位置 |  | digital
FW.Y0GAA12AA003F | 4999 | 2号补给水泵出口电动阀综合故障 |  | digital
FW.Y0GAA12AA003OD | 5000 | 2号补给水泵出口电动阀打开指令 |  | digital
FW.Y0GAA12AA003OP | 5001 | 2号补给水泵出口电动阀全开位置 |  | digital
FW.Y0GAA12AA003RC | 5002 | 2号补给水泵出口电动阀在远控 |  | digital
FW.Y0GAA12AP001_LP | 5003 | #2补给水泵 |  | int32
FW.Y0GAA12AP001_PMT | 5004 | 2号补给水泵启动允许条件 |  | digital
FW.Y0GAA12AP001I | 5005 | 2号补给水泵电流 | A | float32
FW.Y0GAA12AP001PF | 5006 | 2号补给水泵综合故障 |  | digital
FW.Y0GAA12AP001RC | 5007 | 2号补给水泵远方控制 |  | digital
FW.Y0GAA12AP001RD | 5008 | 2号补给水泵启动指令 |  | digital
FW.Y0GAA12AP001RP | 5009 | 2号补给水泵在运行 |  | digital
FW.Y0GAA12AP001TD | 5010 | 2号补给水泵停止指令 |  | digital
FW.Y0GAA12APTM_STP | 5011 | 2号补水泵温度保护跳泵 |  | digital
FW.Y0GAA12AT002CD | 5012 | 2号旋转滤网急停指令 |  | digital
FW.Y0GAA12AT002CP1 | 5013 | 2号旋转滤网冲洗水电动阀关 |  | digital
FW.Y0GAA12AT002D_LP | 5014 | #2旋转滤网低速电机 |  | int32
FW.Y0GAA12AT002DSQD | 5015 | 2号旋转滤网低速定时启动 |  | digital
FW.Y0GAA12AT002F | 5016 | 2号旋转滤网故障 |  | digital
FW.Y0GAA12AT002G_LP | 5017 | #2旋转滤网高速电机 |  | int32
FW.Y0GAA12AT002JT | 5018 | 2号旋转滤网已急停 |  | digital
FW.Y0GAA12AT002LC | 5019 | 2号旋转滤网本地模式 |  | digital
FW.Y0GAA12AT002OP1 | 5020 | 2号旋转滤网冲洗水电动阀开 |  | digital
FW.Y0GAA12AT002QZ | 5021 | 2号旋转滤网轻载 |  | digital
FW.Y0GAA12AT002RC | 5022 | 2号旋转滤网在远控 |  | digital
FW.Y0GAA12AT002RD1 | 5023 | 2号旋转滤网低速启动指令 |  | digital
FW.Y0GAA12AT002RD2 | 5024 | 2号旋转滤网高速启动指令 |  | digital
FW.Y0GAA12AT002RP | 5025 | 2号旋转滤网运行 |  | digital
FW.Y0GAA12AT002RP1 | 5026 | 2号旋转滤网低速运行 |  | digital
FW.Y0GAA12AT002RP2 | 5027 | 2号旋转滤网高速运行 |  | digital
FW.Y0GAA12AT002SL1 | 5028 | 2号旋转滤网松链1 |  | digital
FW.Y0GAA12AT002SL2 | 5029 | 2号旋转滤网松链2 |  | digital
FW.Y0GAA12AT002SLD1 | 5030 | 2号旋转滤网松链1 |  | digital
FW.Y0GAA12AT002SLD2 | 5031 | 2号旋转滤网松链2 |  | digital
FW.Y0GAA12AT002ZZ | 5032 | 2号旋转滤网重载 |  | digital
FW.Y0GAA12CL101 | 5033 | 2号旋转滤网前液位 | Hz | float32
FW.Y0GAA12CL102 | 5034 | 2号旋转滤网后液位 | Hz | float32
FW.Y0GAA12CL107 | 5035 | #2旋转滤网前后液位差值 |  | float32
FW.Y0GAA12CT301 | 5036 | 2号补给水泵电机线圈温度1 | ℃ | float32
FW.Y0GAA12CT302 | 5037 | 2号补给水泵电机线圈温度2 | ℃ | float32
FW.Y0GAA12CT303 | 5038 | 2号补给水泵电机线圈温度3 | ℃ | float32
FW.Y0GAA12CT304 | 5039 | 2号补给水泵电机线圈温度4 | ℃ | float32
FW.Y0GAA12CT305 | 5040 | 2号补给水泵电机线圈温度5 | ℃ | float32
FW.Y0GAA12CT306 | 5041 | 2号补给水泵电机线圈温度6 | ℃ | float32
FW.Y0GAA12CT307 | 5042 | 2号补给水泵电机轴伸端轴承温度 | ℃ | float32
FW.Y0GAA12CT308 | 5043 | #2补给水泵电机非轴伸端轴承温度 | ℃ | float32
FW.Y0GAA12CT309 | 5044 | 2号补给水泵轴承温度1 | ℃ | float32
FW.Y0GAA12CT310 | 5045 | 2号补给水泵轴承温度2 | ℃ | float32
FW.Y0GAA16AA001_LP | 5046 | #6补给水泵进口电动门 |  | int32
FW.Y0GAA16AA001CD | 5047 | 6号补给水泵进口电动阀关闭指令 |  | digital
FW.Y0GAA16AA001CP | 5048 | 6号补给水泵进口电动阀全关位置 |  | digital
FW.Y0GAA16AA001F | 5049 | 6号补给水泵进口电动阀综合故障 |  | digital
FW.Y0GAA16AA001OD | 5050 | 6号补给水泵进口电动阀打开指令 |  | digital
FW.Y0GAA16AA001OP | 5051 | 6号补给水泵进口电动阀全开位置 |  | digital
FW.Y0GAA16AA001RC | 5052 | 6号补给水泵进口电动阀在远控 |  | digital
FW.Y0GAA16AA003_LP | 5053 | #6补给水泵出口电动门 |  | int32
FW.Y0GAA16AA003CD | 5054 | 6号补给水泵出口电动阀关闭指令 |  | digital
FW.Y0GAA16AA003CP | 5055 | 6号补给水泵出口电动阀全关位置 |  | digital
FW.Y0GAA16AA003F | 5056 | 6号补给水泵出口电动阀综合故障 |  | digital
FW.Y0GAA16AA003OD | 5057 | 6号补给水泵出口电动阀打开指令 |  | digital
FW.Y0GAA16AA003OP | 5058 | 6号补给水泵出口电动阀全开位置 |  | digital
FW.Y0GAA16AA003RC | 5059 | 6号补给水泵出口电动阀在远控 |  | digital
FW.Y0GAA16AP001_LP | 5060 | #6补给水泵 |  | int32
FW.Y0GAA16AP001_PMT | 5061 | 6号补给水泵启动允许条件 |  | digital
FW.Y0GAA16AP001I | 5062 | 6号补给水泵电流 | A | float32
FW.Y0GAA16AP001PF | 5063 | 6号补给水泵综合故障 |  | digital
FW.Y0GAA16AP001RC | 5064 | 6号补给水泵远方控制 |  | digital
FW.Y0GAA16AP001RD | 5065 | 6号补给水泵启动指令 |  | digital
FW.Y0GAA16AP001RP | 5066 | 6号补给水泵在运行 |  | digital
FW.Y0GAA16AP001TD | 5067 | 6号补给水泵停止指令 |  | digital
FW.Y0GAA16APTM_STP | 5068 | 6号补水泵温度保护跳泵 |  | digital
FW.Y0GAA16CT301 | 5069 | 6号补给水泵电机线圈温度1 | ℃ | float32
FW.Y0GAA16CT302 | 5070 | 6号补给水泵电机线圈温度2 | ℃ | float32
FW.Y0GAA16CT303 | 5071 | 6号补给水泵电机线圈温度3 | ℃ | float32
FW.Y0GAA16CT304 | 5072 | 6号补给水泵电机线圈温度4 | ℃ | float32
FW.Y0GAA16CT305 | 5073 | 6号补给水泵电机线圈温度5 | ℃ | float32
FW.Y0GAA16CT306 | 5074 | 6号补给水泵电机线圈温度6 | ℃ | float32
FW.Y0GAA16CT307 | 5075 | 6号补给水泵轴伸端轴承温度 | ℃ | float32
FW.Y0GAA16CT308 | 5076 | 6号补给水泵非轴伸端轴承温度 | ℃ | float32
FW.Y0GAA16CT309 | 5077 | 6号补给水泵轴承温度1 | ℃ | float32
FW.Y0GAA16CT310 | 5078 | 6号补给水泵轴承温度2 | ℃ | float32
FW.Y0GAA20AA001_LP | 5079 | 补给水出口母管联络电动门 |  | int32
FW.Y0GAA20AA001CD | 5080 | 补给水出口母管联络阀关指令 |  | digital
FW.Y0GAA20AA001CP | 5081 | 补给水出口母管联络阀全关 |  | digital
FW.Y0GAA20AA001F | 5082 | 补给水出口母管联络阀故障 |  | digital
FW.Y0GAA20AA001OD | 5083 | 补给水出口母管联络阀打开指令 |  | digital
FW.Y0GAA20AA001OP | 5084 | 补给水出口母管联络阀全开 |  | digital
FW.Y0GAA20AA001RC | 5085 | 补给水出口母管联络电动阀在远控 |  | digital
FW.Y0GAA20CP101 | 5086 | 补给水泵出口母管压力1 | Hz | float32
FW.Y0GAA20CP102 | 5087 | 补给水泵出口母管压力2 | MPa | float32
FW.Y0GAA21AA001_LP | 5088 | 补给水母管电动门1 |  | int32
FW.Y0GAA21AA001CD | 5089 | 补给水母管电动阀1关闭指令 |  | digital
FW.Y0GAA21AA001CP | 5090 | 补给水母管电动阀1全关位置 |  | digital
FW.Y0GAA21AA001F | 5091 | 补给水母管电动阀1综合故障 |  | digital
FW.Y0GAA21AA001OD | 5092 | 补给水母管电动阀1打开指令 |  | digital
FW.Y0GAA21AA001OP | 5093 | 补给水母管电动阀1全开位置 |  | digital
FW.Y0GAA21AA001RC | 5094 | 补给水母管电动阀1在远控 |  | digital
FW.Y0GAA21CF101 | 5095 | 补给水泵出口母管流量1 | t/h | float32
FW.Y0GAA21CF101L | 5096 | 补给水泵出口母管流量1累计 |  | float32
FW.Y0GAA21CF101LL | 5097 | 补给水计算后出口流量1 |  | float32
FW.Y0GAA22AA001_LP | 5098 | 补给水母管电动门2 |  | int32
FW.Y0GAA22AA001CD | 5099 | 补给水母管电动阀2关闭指令 |  | digital
FW.Y0GAA22AA001CP | 5100 | 补给水母管电动阀2全关位置 |  | digital
FW.Y0GAA22AA001F | 5101 | 补给水母管电动阀2综合故障 |  | digital
FW.Y0GAA22AA001OD | 5102 | 补给水母管电动阀2打开指令 |  | digital
FW.Y0GAA22AA001OP | 5103 | 补给水母管电动阀2全开位置 |  | digital
FW.Y0GAA22AA001RC | 5104 | 补给水母管电动阀2在远控 |  | digital
FW.Y0GAA22CF101 | 5105 | 补给水泵出口母管流量2 | t/h | float32
FW.Y0GAA22CF101L | 5106 | 补给水泵出口母管流量2累计 |  | float32
FW.Y0GAA22CF101LL | 5107 | 补给水计算后出口流量2 |  | float32
FW.Y0GAC21AA002_LP | 5108 | 原水补给水管电动蝶门1 |  | int32
FW.Y0GAC21AA002CD | 5109 | 原水补给水管电动门1关闭指令 |  | digital
FW.Y0GAC21AA002CP | 5110 | 原水补给水管电动门1全关位置 |  | digital
FW.Y0GAC21AA002F | 5111 | 原水补给水管电动门1综合故障 |  | digital
FW.Y0GAC21AA002OD | 5112 | 原水补给水管电动门1打开指令 |  | digital
FW.Y0GAC21AA002OP | 5113 | 原水补给水管电动门1全开位置 |  | digital
FW.Y0GAC21AA002RC | 5114 | 原水补给水管电动门1在远控 |  | digital
FW.Y0GAC22AA002_LP | 5115 | 原水补给水管电动蝶门2 |  | int32
FW.Y0GAC22AA002CD | 5116 | 原水补给水管电动门2关闭指令 |  | digital
FW.Y0GAC22AA002CP | 5117 | 原水补给水管电动门2全关位置 |  | digital
FW.Y0GAC22AA002F | 5118 | 原水补给水管电动门2综合故障 |  | digital
FW.Y0GAC22AA002OD | 5119 | 原水补给水管电动门2打开指令 |  | digital
FW.Y0GAC22AA002OP | 5120 | 原水补给水管电动门2全开位置 |  | digital
FW.Y0GAC22AA002RC | 5121 | 原水补给水管电动门2在远控 |  | digital
FW.Y0GAC23AA001_LP | 5122 | 原水补给水管联络管电动门1 |  | int32
FW.Y0GAC23AA001CD | 5123 | 原水补给水管联络管门1关指令 |  | digital
FW.Y0GAC23AA001CP | 5124 | 原水补给水管联络管门1全关 |  | digital
FW.Y0GAC23AA001F | 5125 | 原水补给水管联络管门1故障 |  | digital
FW.Y0GAC23AA001OD | 5126 | 原水补给水管联络管门1打开 |  | digital
FW.Y0GAC23AA001OP | 5127 | 原水补给水管联络管门1全开 |  | digital
FW.Y0GAC23AA001RC | 5128 | 原水补给水管联络管门1在远控 |  | digital
FW.Y0GAC23AA002_LP | 5129 | 原水补给水管联络管电动门2 |  | int32
FW.Y0GAC23AA002CD | 5130 | 原水补给水管联络管门2关指令 |  | digital
FW.Y0GAC23AA002CP | 5131 | 原水补给水管联络管门2全关 |  | digital
FW.Y0GAC23AA002F | 5132 | 原水补给水管联络管门2故障 |  | digital
FW.Y0GAC23AA002OD | 5133 | 原水补给水管联络管门2打开 |  | digital
FW.Y0GAC23AA002OP | 5134 | 原水补给水管联络管门2全开 |  | digital
FW.Y0GAC23AA002RC | 5135 | 原水补给水管联络管门2在远控 |  | digital
FW.Y0GAP11AA001_LP | 5136 | #1自动滤水器进口电动门 |  | int32
FW.Y0GAP11AA001CD | 5137 | 1号自动滤水器进口阀关指令 |  | digital
FW.Y0GAP11AA001CP | 5138 | 1号自动滤水器进口阀全关 |  | digital
FW.Y0GAP11AA001F | 5139 | 1号自动滤水器进口阀故障 |  | digital
FW.Y0GAP11AA001OD | 5140 | 1号自动滤水器进口阀打开指令 |  | digital
FW.Y0GAP11AA001OP | 5141 | 1号自动滤水器进口阀全开 |  | digital
FW.Y0GAP11AA001RC | 5142 | 1号自动滤水器进口电动阀在远控 |  | digital
FW.Y0GAP11CP101 | 5143 | 1号自动滤水器进出口差压 | KPa | float32
FW.Y0GAP11GH501_LP | 5144 | #1自动滤水器 |  | int32
FW.Y0GAP11GH501CD | 5145 | 1号自动滤水器停止反冲洗指令 |  | digital
FW.Y0GAP11GH501CP | 5146 | 1号自动滤水器排污阀门全关位置 |  | digital
FW.Y0GAP11GH501F | 5147 | 1号自动滤水器滤水器电机故障 |  | digital
FW.Y0GAP11GH501OD | 5148 | 1号自动滤水器启动反冲洗指令 |  | digital
FW.Y0GAP11GH501OP | 5149 | 1号自动滤水器排污阀门全开位置 |  | digital
FW.Y0GAP11GH501PF | 5150 | 1号自动滤水器电源消失 |  | digital
FW.Y0GAP11GH501RC | 5151 | 1号自动滤水器在远控 |  | digital
FW.Y0GAP11GH501W | 5152 | 1号自动滤水器反冲洗进行中 |  | digital
FW.Y0GAP12AA001_LP | 5153 | #2自动滤水器进口电动门 |  | int32
FW.Y0GAP12AA001CD | 5154 | 2号自动滤水器进口阀关指令 |  | digital
FW.Y0GAP12AA001CP | 5155 | 2号自动滤水器进口阀全关 |  | digital
FW.Y0GAP12AA001F | 5156 | 2号自动滤水器进口阀故障 |  | digital
FW.Y0GAP12AA001OD | 5157 | 2号自动滤水器进口阀打开指令 |  | digital
FW.Y0GAP12AA001OP | 5158 | 2号自动滤水器进口阀全开 |  | digital
FW.Y0GAP12AA001RC | 5159 | 2号自动滤水器进口电动阀在远控 |  | digital
FW.Y0GAP12CP101 | 5160 | 2号自动滤水器进出口差压 | KPa | float32
FW.Y0GAP12GH501_LP | 5161 | #2自动滤水器 |  | int32
FW.Y0GAP12GH501CD | 5162 | 2号自动滤水器停止反冲洗指令 |  | digital
FW.Y0GAP12GH501CP | 5163 | 2号自动滤水器排污阀门全关位置 |  | digital
FW.Y0GAP12GH501F | 5164 | 2号自动滤水器滤水器电机故障 |  | digital
FW.Y0GAP12GH501OD | 5165 | 2号自动滤水器启动反冲洗指令 |  | digital
FW.Y0GAP12GH501OP | 5166 | 2号自动滤水器排污阀门全开位置 |  | digital
FW.Y0GAP12GH501PF | 5167 | 2号自动滤水器电源消失 |  | digital
FW.Y0GAP12GH501RC | 5168 | 2号自动滤水器在远控 |  | digital
FW.Y0GAP12GH501W | 5169 | 2号自动滤水器反冲洗进行中 |  | digital
FW.Y0GAP21AA001_LP | 5170 | #1旋转滤网冲洗水门 |  | int32
FW.Y0GAP21AA001CP | 5171 | 1号旋转滤网冲洗水阀全关 |  | digital
FW.Y0GAP21AA001F | 5172 | 1号旋转滤网冲洗水阀故障 |  | digital
FW.Y0GAP21AA001OP | 5173 | 1号旋转滤网冲洗水阀全开 |  | digital
FW.Y0GAP22AA001_LP | 5174 | #2旋转滤网冲洗水门 |  | int32
FW.Y0GAP22AA001CP | 5175 | 2号旋转滤网冲洗水阀全关 |  | digital
FW.Y0GAP22AA001F | 5176 | 2号旋转滤网冲洗水阀故障 |  | digital
FW.Y0GAP22AA001OP | 5177 | 2号旋转滤网冲洗水阀全开 |  | digital
FW.Y0GCB11CP101 | 5178 | #1超滤装置进水压力 | kPa | float32
FW.Y0GCB11CP101L | 5179 | #1超滤装置进水压力 |  | float32
FW.Y0GCB11CP102 | 5180 | #1超滤装置出水压力 | Hz | float32
FW.Y0GCB11CP102L | 5181 | #1超滤装置出水压力 |  | float32
FW.Y0GCB12CP101 | 5182 | #2超滤装置进水压力 | kPa | float32
FW.Y0GCB12CP101L | 5183 | #2超滤装置进水压力 |  | float32
FW.Y0GCB12CP102 | 5184 | #2超滤装置出水压力 | Hz | float32
FW.Y0GCB12CP102L | 5185 | #2超滤装置出水压力 |  | float32
FW.Y0GCB13CP101 | 5186 | #3超滤装置进水压力 | kPa | float32
FW.Y0GCB13CP101L | 5187 | #3超滤装置进水压力 |  | float32
FW.Y0GCB13CP102 | 5188 | #3超滤装置出水压力 | Hz | float32
FW.Y0GCB13CP102L | 5189 | #3超滤装置出水压力 |  | float32
FW.Y0GCB14CP101 | 5190 | #4超滤装置进水压力 | kPa | float32
FW.Y0GCB14CP101L | 5191 | #4超滤装置进水压力 |  | float32
FW.Y0GCB14CP102 | 5192 | #4超滤装置出水压力 | Hz | float32
FW.Y0GCB14CP102L | 5193 | #4超滤装置出水压力 |  | float32
FW.Y0GCK60CL101 | 5194 | #1除盐水箱液位 | Hz | float32
FW.Y0GCK60CL102 | 5195 | #2除盐水箱液位 | Hz | float32
FW.Y0GQB20GH001PF | 5196 | #1厂区生活污水井液位报警 |  | digital
FW.Y0GQB23GH001PF | 5197 | #4厂区生活污水井液位报警 |  | digital
FW.Y0GRB10AA001_LP | 5198 | 纤维球过滤器入口蝶门 |  | int32
FW.Y0GRB10AA001CD | 5199 | 纤维球过滤器入口门关指令 |  | digital
FW.Y0GRB10AA001CP | 5200 | 纤维球过滤器入口门全关 |  | digital
FW.Y0GRB10AA001OD | 5201 | 纤维球过滤器入口门打开指令 |  | digital
FW.Y0GRB10AA001OP | 5202 | 纤维球过滤器入口门全开 |  | digital
FW.Y0GRB10AA001PF | 5203 | 纤维球过滤器入口门故障 |  | digital
FW.Y0GRB10AA002_LP | 5204 | 纤维球过滤器出口蝶门 |  | int32
FW.Y0GRB10AA002CD | 5205 | 纤维球过滤器出口门关指令 |  | digital
FW.Y0GRB10AA002CP | 5206 | 纤维球过滤器出口门全关 |  | digital
FW.Y0GRB10AA002OD | 5207 | 纤维球过滤器出口门打开指令 |  | digital
FW.Y0GRB10AA002OP | 5208 | 纤维球过滤器出口门全开 |  | digital
FW.Y0GRB10AA002PF | 5209 | 纤维球过滤器出口门故障 |  | digital
FW.Y0GRB10AA003_LP | 5210 | 纤维过滤器反洗进水门 |  | int32
FW.Y0GRB10AA003CD | 5211 | 纤维过滤器反洗进水门关指令 |  | digital
FW.Y0GRB10AA003CP | 5212 | 纤维过滤器反洗进水门全关 |  | digital
FW.Y0GRB10AA003OD | 5213 | 纤维过滤器反洗进水门打开指令 |  | digital
FW.Y0GRB10AA003OP | 5214 | 纤维过滤器反洗进水门全开 |  | digital
FW.Y0GRB10AA003PF | 5215 | 纤维过滤器反洗进水门故障 |  | digital
FW.Y0GRB10AA004_LP | 5216 | 纤维过滤器进气电动门 |  | int32
FW.Y0GRB10AA004CD | 5217 | 纤维过滤器进气电动门关闭指令 |  | digital
FW.Y0GRB10AA004CP | 5218 | 纤维过滤器进气电动门全关位置 |  | digital
FW.Y0GRB10AA004OD | 5219 | 纤维过滤器进气电动门打开指令 |  | digital
FW.Y0GRB10AA004OP | 5220 | 纤维过滤器进气电动门全开位置 |  | digital
FW.Y0GRB10AA004PF | 5221 | 纤维过滤器进气电动门综合故障 |  | digital
FW.Y0GRB10AA401_LP | 5222 | 纤维过滤器反洗排污门 |  | int32
FW.Y0GRB10AA401CD | 5223 | 纤维过滤器反洗排污门关指令 |  | digital
FW.Y0GRB10AA401CP | 5224 | 纤维过滤器反洗排污门全关 |  | digital
FW.Y0GRB10AA401OD | 5225 | 纤维过滤器反洗排污门打开指令 |  | digital
FW.Y0GRB10AA401OP | 5226 | 纤维过滤器反洗排污门全开 |  | digital
FW.Y0GRB10AA401PF | 5227 | 纤维过滤器反洗排污门故障 |  | digital
FW.Y0GRB10CP103 | 5228 | 纤维球过滤器进出口差压 | Mpa | float32
FW.Y0GRC11AN001_CHOOSE | 5229 | #1曝气风机备用选择 |  | digital
FW.Y0GRC11AN001_LP | 5230 | #1生活污水曝气风机 |  | int32
FW.Y0GRC11AN001PF | 5231 | #1曝气风机综合故障 |  | digital
FW.Y0GRC11AN001RC | 5232 | #1曝气风机远方控制 |  | digital
FW.Y0GRC11AN001RD | 5233 | #1曝气风机启动指令 |  | digital
FW.Y0GRC11AN001RP | 5234 | #1曝气风机在运行 |  | digital
FW.Y0GRC11AN001TD | 5235 | #1曝气风机停止指令 |  | digital
FW.Y0GRC12AN001_CHOOSE | 5236 | #2曝气风机备用选择 |  | digital
FW.Y0GRC12AN001_LP | 5237 | #2生活污水曝气风机 |  | int32
FW.Y0GRC12AN001PF | 5238 | #2曝气风机综合故障 |  | digital
FW.Y0GRC12AN001RC | 5239 | #2曝气风机远方控制 |  | digital
FW.Y0GRC12AN001RD | 5240 | #2曝气风机启动指令 |  | digital
FW.Y0GRC12AN001RP | 5241 | #2曝气风机在运行 |  | digital
FW.Y0GRC12AN001TD | 5242 | #2曝气风机停止指令 |  | digital
FW.Y0GRC13AN001_CHOOSE | 5243 | #3曝气风机备用选择 |  | digital
FW.Y0GRC13AN001_LP | 5244 | #3生活污水曝气风机 |  | int32
FW.Y0GRC13AN001PF | 5245 | #3曝气风机综合故障 |  | digital
FW.Y0GRC13AN001RC | 5246 | #3曝气风机远方控制 |  | digital
FW.Y0GRC13AN001RD | 5247 | #3曝气风机启动指令 |  | digital
FW.Y0GRC13AN001RP | 5248 | #3曝气风机在运行 |  | digital
FW.Y0GRC13AN001TD | 5249 | #3曝气风机停止指令 |  | digital
FW.Y0GRC14CP101 | 5250 | 曝气风机出口母管压力 | Mpa | float32
FW.Y0GRK10AP001_LP | 5251 | 生活污水机械格栅电机 |  | int32
FW.Y0GRK10AP001_LXYX | 5252 | 机械格栅电机自动运行 |  | digital
FW.Y0GRK10AP001PF | 5253 | 机械格栅电机综合故障 |  | digital
FW.Y0GRK10AP001RC | 5254 | 机械格栅电机远方控制 |  | digital
FW.Y0GRK10AP001RD | 5255 | 机械格栅电机启动指令 |  | digital
FW.Y0GRK10AP001RP | 5256 | 机械格栅电机在运行 |  | digital
FW.Y0GRK10AP001TD | 5257 | 机械格栅电机停止指令 |  | digital
FW.Y0GRK10CL101 | 5258 | 生活污水调节池液位 | m | float32
FW.Y0GRK11AP001_CHOOSE | 5259 | #1生活污水提升泵联锁投入 |  | digital
FW.Y0GRK11AP001_LP | 5260 | #1生活污水提升泵 |  | int32
FW.Y0GRK11AP001PF | 5261 | #1生活污水提升泵综合故障 |  | digital
FW.Y0GRK11AP001RC | 5262 | #1生活污水提升泵远方控制 |  | digital
FW.Y0GRK11AP001RD | 5263 | #1生活污水提升泵启动指令 |  | digital
FW.Y0GRK11AP001RP | 5264 | #1生活污水提升泵在运行 |  | digital
FW.Y0GRK11AP001TD | 5265 | #1生活污水提升泵停止指令 |  | digital
FW.Y0GRK11CF101 | 5266 | 生活污水提升泵出口母管流量 | t/h | float32
FW.Y0GRK11CP101 | 5267 | 生活污水提升泵出口母管压力 | Mpa | float32
FW.Y0GRK12AP001_CHOOSE | 5268 | #2生活污水提升泵联锁投入 |  | digital
FW.Y0GRK12AP001_LP | 5269 | #2生活污水提升泵 |  | int32
FW.Y0GRK12AP001PF | 5270 | #2生活污水提升泵综合故障 |  | digital
FW.Y0GRK12AP001RC | 5271 | #2生活污水提升泵远方控制 |  | digital
FW.Y0GRK12AP001RD | 5272 | #2生活污水提升泵启动指令 |  | digital
FW.Y0GRK12AP001RP | 5273 | #2生活污水提升泵在运行 |  | digital
FW.Y0GRK12AP001TD | 5274 | #2生活污水提升泵停止指令 |  | digital
FW.Y0GRK13AP001_CHOOSE | 5275 | #3生活污水提升泵联锁投入 |  | digital
FW.Y0GRK13AP001_LP | 5276 | #3生活污水提升泵 |  | int32
FW.Y0GRK13AP001PF | 5277 | #3生活污水提升泵综合故障 |  | digital
FW.Y0GRK13AP001RC | 5278 | #3生活污水提升泵远方控制 |  | digital
FW.Y0GRK13AP001RD | 5279 | #3生活污水提升泵启动指令 |  | digital
FW.Y0GRK13AP001RP | 5280 | #3生活污水提升泵在运行 |  | digital
FW.Y0GRK13AP001TD | 5281 | #3生活污水提升泵停止指令 |  | digital
FW.Y0GRK20CL101 | 5282 | 中间水池液位 | m | float32
FW.Y0GRK30CL101 | 5283 | 回用水池液位 | m | float32
FW.Y0GRK30CQ101 | 5284 | 回水出口母管浊度 | NTU | float32
FW.Y0GRK31AP001_LP | 5285 | #1中间水池提升泵 |  | int32
FW.Y0GRK31AP001PF | 5286 | #1中间水池提升泵综合故障 |  | digital
FW.Y0GRK31AP001RC | 5287 | #1中间水池提升泵远方控制 |  | digital
FW.Y0GRK31AP001RD | 5288 | #1中间水池提升泵启动指令 |  | digital
FW.Y0GRK31AP001RP | 5289 | #1中间水池提升泵在运行 |  | digital
FW.Y0GRK31AP001TD | 5290 | #1中间水池提升泵停止指令 |  | digital
FW.Y0GRK31CP101 | 5291 | 中间水池提升泵出口母管压力 | Mpa | float32
FW.Y0GRK32AP001_LP | 5292 | #2中间水池提升泵 |  | int32
FW.Y0GRK32AP001PF | 5293 | #2中间水池提升泵综合故障 |  | digital
FW.Y0GRK32AP001RC | 5294 | #2中间水池提升泵远方控制 |  | digital
FW.Y0GRK32AP001RD | 5295 | #2中间水池提升泵启动指令 |  | digital
FW.Y0GRK32AP001RP | 5296 | #2中间水池提升泵在运行 |  | digital
FW.Y0GRK32AP001TD | 5297 | #2中间水池提升泵停止指令 |  | digital
FW.Y0GRK41AP001_LP | 5298 | #1回用水池提升泵 |  | int32
FW.Y0GRK41AP001PF | 5299 | #1回用水池提升泵综合故障 |  | digital
FW.Y0GRK41AP001RC | 5300 | #1回用水池提升泵远方控制 |  | digital
FW.Y0GRK41AP001RD | 5301 | #1回用水池提升泵启动指令 |  | digital
FW.Y0GRK41AP001RP | 5302 | #1回用水池提升泵在运行 |  | digital
FW.Y0GRK41AP001TD | 5303 | #1回用水池提升泵停止指令 |  | digital
FW.Y0GRK42AP001_LP | 5304 | #2回用水池提升泵 |  | int32
FW.Y0GRK42AP001PF | 5305 | #2回用水池提升泵综合故障 |  | digital
FW.Y0GRK42AP001RC | 5306 | #2回用水池提升泵远方控制 |  | digital
FW.Y0GRK42AP001RD | 5307 | #2回用水池提升泵启动指令 |  | digital
FW.Y0GRK42AP001RP | 5308 | #2回用水池提升泵在运行 |  | digital
FW.Y0GRK42AP001TD | 5309 | #2回用水池提升泵停止指令 |  | digital
FW.Y0GRK50AT001_LP | 5310 | 紫外线消毒器 |  | int32
FW.Y0GRK50AT001PF | 5311 | 紫外线消毒器综合故障 |  | digital
FW.Y0GRK50AT001RC | 5312 | 紫外线消毒器远方控制 |  | digital
FW.Y0GRK50AT001RD | 5313 | 紫外线消毒器启动指令 |  | digital
FW.Y0GRK50AT001RP | 5314 | 紫外线消毒器在运行 |  | digital
FW.Y0GRK50AT001TD | 5315 | 紫外线消毒器停止指令 |  | digital
FW.Y0GRK50CP101 | 5316 | 回用水池提升泵出口母管压力 | Mpa | float32
FW.Y0GRK51CF101 | 5317 | 厂区绿化用水流量 | t/h | float32
FW.Y0GTQ11AP001_LP | 5318 | #1集水坑排污泵 |  | int32
FW.Y0GTQ11AP001PF | 5319 | 集水坑1号排污泵综合故障 |  | digital
FW.Y0GTQ11AP001RC | 5320 | 集水坑1号排污泵远方控制 |  | digital
FW.Y0GTQ11AP001RD | 5321 | 集水坑1号排污泵启动指令 |  | digital
FW.Y0GTQ11AP001RP | 5322 | 集水坑1号排污泵在运行 |  | digital
FW.Y0GTQ11AP001TD | 5323 | 集水坑1号排污泵停止指令 |  | digital
FW.Y0GTQ11AP001TP | 5324 | 集水坑1号排污泵已停止 |  | digital
FW.Y0GTQ12AP001_LP | 5325 | #2集水坑排污泵 |  | int32
FW.Y0GTQ12AP001PF | 5326 | 集水坑2号排污泵综合故障 |  | digital
FW.Y0GTQ12AP001RC | 5327 | 集水坑2号排污泵远方控制 |  | digital
FW.Y0GTQ12AP001RD | 5328 | 集水坑2号排污泵启动指令 |  | digital
FW.Y0GTQ12AP001RP | 5329 | 集水坑2号排污泵在运行 |  | digital
FW.Y0GTQ12AP001TD | 5330 | 集水坑2号排污泵停止指令 |  | digital
FW.Y0GTQ12AP001TP | 5331 | 2号补给水泵已停止 |  | digital
FW.Y0GTQ12CL101 | 5332 | 集水坑液位 | m | float32
FW.Y0GTQ16AP001TP | 5333 | 6号补给水泵已停止 |  | digital
FW.Y0GUC10CL101 | 5334 | 雨水收集池液位 | m | float32
FW.Y0GUC10CL101H1 | 5335 | 雨水收集池液位高1 |  | digital
FW.Y0GUC10CL101H2 | 5336 | 雨水收集池液位高2 |  | digital
FW.Y0GUC10CL101L | 5337 | 雨水集水池液位低 |  | digital
FW.Y0GUC11AP001_LP | 5338 | 1A号雨水提升泵 |  | int32
FW.Y0GUC11AP001I | 5339 | 1A雨水提升泵电流 |  | float32
FW.Y0GUC11AP001PF | 5340 | 1A号雨水提升泵综合故障 |  | digital
FW.Y0GUC11AP001PS | 5341 | 1A号雨水提升泵电气保护动作 |  | digital
FW.Y0GUC11AP001RC | 5342 | 1A雨水提升泵远方控制 |  | digital
FW.Y0GUC11AP001RD | 5343 | 1A雨水提升泵启动指令 |  | digital
FW.Y0GUC11AP001RP | 5344 | 1A号雨水提升泵在运行 |  | digital
FW.Y0GUC11AP001SW | 5345 | 1A雨水提升泵试验位置 |  | digital
FW.Y0GUC11AP001TD | 5346 | 1A号雨水提升泵停止指令 |  | digital
FW.Y0GUC11AP001TP | 5347 | 1A雨水提升泵已停止 |  | digital
FW.Y0GUC11AP001YW | 5348 | 1A雨水提升泵工作位置 |  | digital
FW.Y0GUC11CL001 | 5349 | 1A雨水提升泵电机腔漏水 |  | digital
FW.Y0GUC11CL002 | 5350 | 1A雨水提升泵油室漏水 |  | digital
FW.Y0GUC11CT301 | 5351 | 1A雨水提升泵电机线圈温度1 | DEG | float32
FW.Y0GUC11CT302 | 5352 | 1A雨水提升泵电机线圈温度2 | DEG | float32
FW.Y0GUC11CT303 | 5353 | 1A雨水提升泵电机线圈温度3 | DEG | float32
FW.Y0GUC11CT304 | 5354 | 1A雨水提升泵电机轴承温度 | DEG | float32
FW.Y0GUC12AP001_LP | 5355 | 1B雨水提升泵 |  | int32
FW.Y0GUC12AP001I | 5356 | 1B雨水提升泵电流 |  | float32
FW.Y0GUC12AP001PF | 5357 | 1B雨水提升泵综合故障 |  | digital
FW.Y0GUC12AP001PS | 5358 | 1B雨水提升泵电气保护动作 |  | digital
FW.Y0GUC12AP001RC | 5359 | 1B雨水提升泵远方控制 |  | digital
FW.Y0GUC12AP001RD | 5360 | 1B雨水提升泵启动指令 |  | digital
FW.Y0GUC12AP001RP | 5361 | 1B雨水提升泵在运行 |  | digital
FW.Y0GUC12AP001SW | 5362 | 2A雨水提升泵试验位置 |  | digital
FW.Y0GUC12AP001TD | 5363 | 1B雨水提升泵停止指令 |  | digital
FW.Y0GUC12AP001TP | 5364 | 1B号雨水提升泵已停止 |  | digital
FW.Y0GUC12AP001YW | 5365 | 2A雨水提升泵工作位置 |  | digital
FW.Y0GUC12CL001 | 5366 | 1B雨水提升泵电机腔漏水 |  | digital
FW.Y0GUC12CL002 | 5367 | 1B雨水提升泵油室漏水 |  | digital
FW.Y0GUC12CT301 | 5368 | 1B雨水提升泵电机线圈温度1 | DEG | float32
FW.Y0GUC12CT302 | 5369 | 1B雨水提升泵电机线圈温度2 | DEG | float32
FW.Y0GUC12CT303 | 5370 | 1B雨水提升泵电机线圈温度3 | DEG | float32
FW.Y0GUC12CT304 | 5371 | 1B雨水提升泵电机轴承温度 | DEG | float32
FW.Y0GUC13AP001_LP | 5372 | 2A雨水提升泵 |  | int32
FW.Y0GUC13AP001I | 5373 | 2A雨水提升泵电流 |  | float32
FW.Y0GUC13AP001PF | 5374 | 2A雨水提升泵综合故障 |  | digital
FW.Y0GUC13AP001RC | 5375 | 2A雨水提升泵远方控制 |  | digital
FW.Y0GUC13AP001RD | 5376 | 2A雨水提升泵启动指令 |  | digital
FW.Y0GUC13AP001RP | 5377 | 2A号雨水提升泵在运行 |  | digital
FW.Y0GUC13AP001TD | 5378 | 2A雨水提升泵停止指令 |  | digital
FW.Y0GUC13AP001TP | 5379 | 2A雨水提升泵已停止 |  | digital
FW.Y0GUC13CL001 | 5380 | 2A雨水提升泵电机腔漏水 |  | digital
FW.Y0GUC13CL002 | 5381 | 2A雨水提升泵油室漏水 |  | digital
FW.Y0GUC13CT301 | 5382 | 2A雨水提升泵电机线圈温度1 | DEG | float32
FW.Y0GUC13CT302 | 5383 | 2A雨水提升泵电机线圈温度2 | DEG | float32
FW.Y0GUC13CT303 | 5384 | 2A雨水提升泵电机线圈温度3 | DEG | float32
FW.Y0GUC13CT304 | 5385 | 2A雨水提升泵电机轴承温度 | DEG | float32
FW.Y0GUC14AP001_LP | 5386 | 2B雨水提升泵 |  | int32
FW.Y0GUC14AP001I | 5387 | 2B雨水提升泵电流 |  | float32
FW.Y0GUC14AP001PF | 5388 | 2B雨水提升泵综合故障 |  | digital
FW.Y0GUC14AP001RC | 5389 | 2B雨水提升泵远方控制 |  | digital
FW.Y0GUC14AP001RD | 5390 | 2B雨水提升泵启动指令 |  | digital
FW.Y0GUC14AP001RP | 5391 | 2B雨水提升泵在运行 |  | digital
FW.Y0GUC14AP001TD | 5392 | 2B号雨水提升泵停止指令 |  | digital
FW.Y0GUC14AP001TP | 5393 | 2B雨水提升泵已停止 |  | digital
FW.Y0GUC14CL001 | 5394 | 2B雨水提升泵电机腔漏水 |  | digital
FW.Y0GUC14CL002 | 5395 | 2B雨水提升泵油室漏水 |  | digital
FW.Y0GUC14CT301 | 5396 | 2B雨水提升泵电机线圈温度1 | DEG | float32
FW.Y0GUC14CT302 | 5397 | 2B雨水提升泵电机线圈温度2 | DEG | float32
FW.Y0GUC14CT303 | 5398 | 2B雨水提升泵电机线圈温度3 | DEG | float32
FW.Y0GUC14CT304 | 5399 | 2B雨水提升泵电机轴承温度 | DEG | float32
FW.Y0GUC21GH001 | 5400 | 雨水泵房雨水收集池液位高报警 |  | digital
FW.Y0PAR23AA001_LP | 5401 | 旋转滤网冲渣沟冲洗水门 |  | int32
FW.Y0PAR23AA001CP | 5402 | 旋转滤网冲渣沟冲洗水阀全关 |  | digital
FW.Y0PAR23AA001F | 5403 | 旋转滤网冲渣沟冲洗水阀故障 |  | digital
FW.Y0PAR23AA001OP | 5404 | 旋转滤网冲渣沟冲洗水阀全开 |  | digital
FW.YCG1 | 5405 | #1超滤压差高 |  | digital
FW.YCG2 | 5406 | #2超滤压差高 |  | digital
FW.YCG3 | 5407 | #3超滤压差高 |  | digital
FW.YCG4 | 5408 | #4超滤压差高 |  | digital
FW.YJFST_GJJ | 5409 | Ovation Control Builder |  | digital
FW.YJFST_GZG/HY | 5410 | Ovation Control Builder |  | digital
FW.YJFST_J0GCB40AP001CP | 5411 | 一级反渗透冲洗水泵顺控停 |  | digital
FW.YJFST_J0GCB40AP001OP | 5412 | 一级反渗透冲洗水泵顺控启 |  | digital
FW.YJFST_J0GCF31AA005CP | 5413 | #1一级反渗透进冲洗水门顺控关 |  | digital
FW.YJFST_J0GCF31AA005OP | 5414 | #1一级反渗透进冲洗水门顺控开 |  | digital
FW.YJFST_J0GCF31AA055CP | 5415 | #1一级反渗透产水排放门顺控关 |  | digital
FW.YJFST_J0GCF31AA055OP | 5416 | #1一级反渗透产水排放门顺控开 |  | digital
FW.YJFST_J0GCF31AA402CP | 5417 | #1一级反渗透浓水排放门顺控关 |  | digital
FW.YJFST_J0GCF31AA402OP | 5418 | #1一级反渗透浓水排放门顺控开 |  | digital
FW.YJFST_J0GCF32AA005CP | 5419 | #2一级反渗透进冲洗水门顺控关 |  | digital
FW.YJFST_J0GCF32AA005OP | 5420 | #2一级反渗透进冲洗水门顺控开 |  | digital
FW.YJFST_J0GCF32AA055CP | 5421 | #2一级反渗透产水排放门顺控关 |  | digital
FW.YJFST_J0GCF32AA055OP | 5422 | #2一级反渗透产水排放门顺控开 |  | digital
FW.YJFST_J0GCF32AA402CP | 5423 | #2一级反渗透浓水排放门顺控关 |  | digital
FW.YJFST_J0GCF32AA402OP | 5424 | #2一级反渗透浓水排放门顺控开 |  | digital
FW.YJFST_J0GCF33AA005CP | 5425 | #3一级反渗透进冲洗水门顺控关 |  | digital
FW.YJFST_J0GCF33AA005OP | 5426 | #3一级反渗透进冲洗水门顺控开 |  | digital
FW.YJFST_J0GCF33AA055CP | 5427 | #3一级反渗透产水排放门顺控关 |  | digital
FW.YJFST_J0GCF33AA055OP | 5428 | #3一级反渗透产水排放门顺控开 |  | digital
FW.YJFST_J0GCF33AA402CP | 5429 | #3一级反渗透浓水排放门顺控关 |  | digital
FW.YJFST_J0GCF33AA402OP | 5430 | #3一级反渗透浓水排放门顺控开 |  | digital
FW.YJFST_J0GCF34AA005CP | 5431 | #4一级反渗透进冲洗水门顺控关 |  | digital
FW.YJFST_J0GCF34AA005OP | 5432 | #4一级反渗透进冲洗水门顺控开 |  | digital
FW.YJFST_J0GCF34AA055CP | 5433 | #4一级反渗透产水排放门顺控关 |  | digital
FW.YJFST_J0GCF34AA055OP | 5434 | #4一级反渗透产水排放门顺控开 |  | digital
FW.YJFST_J0GCF34AA402CP | 5435 | #4一级反渗透浓水排放门顺控关 |  | digital
FW.YJFST_J0GCF34AA402OP | 5436 | #4一级反渗透浓水排放门顺控开 |  | digital
FW.YJFST_J0GCK21AP001CP | 5437 | #1一级反渗透给水泵顺控停 |  | digital
FW.YJFST_J0GCK21AP001OP | 5438 | #1一级反渗透给水泵顺控启 |  | digital
FW.YJFST_J0GCK22AP001CP | 5439 | #2一级反渗透给水泵顺控停 |  | digital
FW.YJFST_J0GCK22AP001OP | 5440 | #2一级反渗透给水泵顺控启 |  | digital
FW.YJFST_J0GCK23AP001CP | 5441 | #3一级反渗透给水泵顺控停 |  | digital
FW.YJFST_J0GCK23AP001OP | 5442 | #3一级反渗透给水泵顺控启 |  | digital
FW.YJFST_J0GCK24AP001CP | 5443 | #4一级反渗透给水泵顺控停 |  | digital
FW.YJFST_J0GCK24AP001OP | 5444 | #4一级反渗透给水泵顺控启 |  | digital
FW.YJFST_J0GCK31AA002CP | 5445 | #1一级反渗透进水门顺控关 |  | digital
FW.YJFST_J0GCK31AA002OP | 5446 | #1一级反渗透进水门顺控开 |  | digital
FW.YJFST_J0GCK31AP001CP | 5447 | #1一级反渗透高压泵顺控停 |  | digital
FW.YJFST_J0GCK31AP001OP | 5448 | #1一级反渗透高压泵顺控启 |  | digital
FW.YJFST_J0GCK32AA002CP | 5449 | #2一级反渗透进水门顺控关 |  | digital
FW.YJFST_J0GCK32AA002OP | 5450 | #2一级反渗透进水门顺控开 |  | digital
FW.YJFST_J0GCK32AP001CP | 5451 | #2一级反渗透高压泵顺控停 |  | digital
FW.YJFST_J0GCK32AP001OP | 5452 | #2一级反渗透高压泵顺控启 |  | digital
FW.YJFST_J0GCK33AA002CP | 5453 | #3一级反渗透进水门顺控关 |  | digital
FW.YJFST_J0GCK33AA002OP | 5454 | #3一级反渗透进水门顺控开 |  | digital
FW.YJFST_J0GCK33AP001CP | 5455 | #3一级反渗透高压泵顺控停 |  | digital
FW.YJFST_J0GCK33AP001OP | 5456 | #3一级反渗透高压泵顺控启 |  | digital
FW.YJFST_J0GCK34AA002CP | 5457 | #4一级反渗透进水门顺控关 |  | digital
FW.YJFST_J0GCK34AA002OP | 5458 | #4一级反渗透进水门顺控开 |  | digital
FW.YJFST_J0GCK34AP001CP | 5459 | #4一级反渗透高压泵顺控停 |  | digital
FW.YJFST_J0GCK34AP001OP | 5460 | #4一级反渗透高压泵顺控启 |  | digital
FW.YJFST_J0GCQ31AP001CP | 5461 | 一级反渗透阻垢剂泵顺控停 |  | digital
FW.YJFST_J0GCQ31AP001OP | 5462 | 一级反渗透阻垢剂泵顺控启 |  | digital
FW.YJFST_J0GCQ41AP001CP | 5463 | 一级反渗透还原剂泵顺控停 |  | digital
FW.YJFST_J0GCQ41AP001OP | 5464 | 一级反渗透还原剂泵顺控启 |  | digital
FW.YJFST_J0GCQ51AP003CP | 5465 | 一级反渗透加碱泵顺控停 |  | digital
FW.YJFST_J0GCQ51AP003OP | 5466 | 一级反渗透加碱泵顺控启 |  | digital
FW.YJFSTFX_PD | 5467 | Ovation Control Builder |  | float32
FW.YJFSTFXJT | 5468 | Ovation Control Builder |  | digital
FW.YJFSTTIME1 | 5469 | #1一级反渗透排队时间 |  | float32
FW.YJFSTTIME2 | 5470 | #2一级反渗透排队时间 |  | float32
FW.YJFSTTIME3 | 5471 | #3一级反渗透排队时间 |  | float32
FW.YJFSTTIME4 | 5472 | #4一级反渗透排队时间 |  | float32
FW.YJFSTYX2 | 5473 | Ovation Control Builder |  | digital
FW.YJFSTYX3 | 5474 | Ovation Control Builder |  | digital
FW.YJFSTYX4 | 5475 | Ovation Control Builder |  | digital
FW.ZJSCTSB1 | 5476 | #1中间水池提升泵选择 |  | digital
FW.ZJSCTSB2 | 5477 | #2中间水池提升泵选择 |  | digital
N2DCS.20AGCLOADMAX | 5478 | 第二套机组总负荷上限值 | % | float32
N2DCS.20AGCLOADMIN | 5479 | 第二套机组总负荷下限值 | % | float32
N2DCS.20AGCLOADP2 | 5480 | 第二套机组实际总负荷 | % | float32
N2DCS.20AGCLOADSP | 5481 | AGC总负荷指令 | % | float32
N2DCS.20AGCLOADTP | 5482 | AGC目标定值返回值 | % | float32
N2DCS.20AGCLOADVR | 5483 | 第二套机组总负荷响应速率 | % | float32
N2DCS.20CJA01DE002 | 5484 | EXTERNAL LOAD R | % | float32
N2DCS.20CJA01DE002XQ01 | 5485 | EXTERNAL LOAD REFERENCE - RAMP |  | float32
N2DCS.20CJA01DE003XQ01 | 5486 | EXTERNAL LOAD REFERENCE |  | float32
N2DCS.20CJA01DP100 | 5487 | 高压主蒸汽压力设定值 |  | float32
N2DCS.20CJA01DP200 | 5488 | 再热主蒸汽压力设定值 |  | float32
N2DCS.20LBA10CP101 | 5489 | 高压主蒸汽压力1 | MPa | float32
N2DCS.20LBA10CP102 | 5490 | 高压主蒸汽压力2 | MPa | float32
N2DCS.20LBA10CP103 | 5491 | 高压主蒸汽压力3 | MPa | float32
N2DCS.20LBA10CPX3 | 5492 | 高压主蒸汽压力（3选后） |  | float32
N2DCS.20LBA10CT301 | 5493 | 高压主蒸汽温度 | ℃ | float32
N2DCS.20LBA10CT302 | 5494 | 高压主汽母管疏水气动门1前温度 | ℃ | float32
N2DCS.20LBA10CT303 | 5495 | 高压主汽母管疏水气动门2前温度 | ℃ | float32
N2DCS.20LBA10CT304 | 5496 | 高压主汽母管疏水气动门2后温度 | ℃ | float32
N2DCS.20LBA10CT305 | 5497 | 高压主汽母管疏水气动门1后温度 | ℃ | float32
N2DCS.20LBA20CP101 | 5498 | 低压主蒸汽母管压力1 | MPa | float32
N2DCS.20LBA20CP102 | 5499 | 低压主蒸汽母管压力2 | MPa | float32
N2DCS.20LBA20CPX2 | 5500 | 低压主蒸汽母管压力（2选后） |  | float32
N2DCS.20LBA20CT301 | 5501 | 低压主汽母管温度 | ℃ | float32
N2DCS.20LBA20CT302 | 5502 | 低压主汽母管疏水门前壁温 | ℃ | float32
N2DCS.20LBA20CT303 | 5503 | 低压主汽母管疏水门后壁温 | ℃ | float32
N2DCS.20LBA20CT304 | 5504 | 低压主汽门前疏水门前壁温 | ℃ | float32
N2DCS.20LBA20CT305 | 5505 | 低压主汽门前疏水门后壁温 | ℃ | float32
N2DCS.20LBB10CP101 | 5506 | 高温再热蒸汽压力1 | MPa | float32
N2DCS.20LBB10CP102 | 5507 | 高温再热蒸汽压力2 | MPa | float32
N2DCS.20LBB10CPX2 | 5508 | 高温再热蒸汽压力（2选后） |  | float32
N2DCS.20LBB10CT301 | 5509 | 高温再热蒸汽温度 | ℃ | float32
N2DCS.20LBB10CT302 | 5510 | 中旁阀前疏水气动门前温度 | ℃ | float32
N2DCS.20LBB10CT303 | 5511 | 中旁阀前疏水气动门后温度 | ℃ | float32
N2DCS.20LBB10CT304 | 5512 | 高温再热蒸汽母管疏水门前温度 | ℃ | float32
N2DCS.20LBB10CT305 | 5513 | 高温再热蒸汽母管疏水门后温度 | ℃ | float32
N2DCS.20LBC10CP104 | 5514 | 高压缸排汽压力 | MPa | float32
N2DCS.20LBC10CP105 | 5515 | 冷再母管蒸汽压力 | MPa | float32
N2DCS.20LBC10CT | 5516 | 高压排气管壁温 |  | float32
N2DCS.20LBC10CT303 | 5517 | 高压缸排汽管垂直管壁温 | ℃ | float32
N2DCS.20LBC10CT304 | 5518 | 冷再母管蒸汽温度 | ℃ | float32
N2DCS.20LBC10CT306 | 5519 | 高压缸排汽管下壁温 | ℃ | float32
N2DCS.20LBC10CT307 | 5520 | 高排逆止门后疏水门后管温度 | ℃ | float32
N2DCS.20LBC10CT308 | 5521 | 冷再冷段疏水门后管温度 | ℃ | float32
N2DCS.20LBH10CT301 | 5522 | 高排通风阀前疏水门后管温度 | ℃ | float32
N2DCS.20LEDA002 | 5523 | 汽机转速 |  | float32
N2DCS.20LEDAO01 | 5524 | 炉侧主汽温度 | % | float32
N2DCS.20LEDAO02 | 5525 | #3机转速 | % | float32
N2DCS.20LEDAO03 | 5526 | 无功功率 | % | float32
N2DCS.20LEDAO04 | 5527 | 机组负荷 | % | float32
N2DCS.20LEDAO05 | 5528 | 炉侧主汽压力 | % | float32
N2DCS.20MAL11CT301 | 5529 | 高压主汽门后疏水门前管壁温 | ℃ | float32
N2DCS.20MAL11CT302 | 5530 | 高压主汽门后疏水门后管壁温 | ℃ | float32
N2DCS.20MAL23CT301 | 5531 | 中压主汽门滤网疏水门后温度 |  | float32
N2DCS.20MAL26CT301 | 5532 | 中压调门疏水门后温度 |  | float32
N2DCS.20MAL65CT305 | 5533 | 高排逆止门前疏水门后管温度 | ℃ | float32
N2DCS.20MAN10AA101C | 5534 | 高旁阀阀位控制指令 | % | float32
N2DCS.20MAN10AA101P | 5535 | 高旁阀阀位反馈 | % | float32
N2DCS.20MAN10AA101SP | 5536 | 高旁压力设定偏置值 |  | float32
N2DCS.20MAN10AA101SP1 | 5537 | Ovation Control Builder |  | float32
N2DCS.20MAN10AA102_FF | 5538 | 高压旁路减温水调阀FF |  | float32
N2DCS.20MAN10AA102C | 5539 | 高旁减温水调节阀阀位控制指令 | % | float32
N2DCS.20MAN10AA102P | 5540 | 高旁减温水调节阀阀位反馈 | % | float32
N2DCS.20MAN10AA102SP | 5541 | Ovation Control Builder |  | float32
N2DCS.20MAN10CP101 | 5542 | 高旁阀后蒸汽压力1 | MPa | float32
N2DCS.20MAN10CP102 | 5543 | 高旁阀后蒸汽压力2 | MPa | float32
N2DCS.20MAN10CP103 | 5544 | 高旁减温水压力 | MPa | float32
N2DCS.20MAN10CPX2 | 5545 | 高旁阀后蒸汽压力（2选后） |  | float32
N2DCS.20MAN10CT301 | 5546 | 高旁阀后蒸汽温度1 | ℃ | float32
N2DCS.20MAN10CT302 | 5547 | 高旁阀后蒸汽温度2 | ℃ | float32
N2DCS.20MAN10CTX2 | 5548 | 高旁阀后蒸汽温度（2选后） |  | float32
N2DCS.20MAN10GH001PT | 5549 | 高旁阀油站油压 | MPa | float32
N2DCS.20MAN20AA101C | 5550 | 中旁阀阀位控制指令 | % | float32
N2DCS.20MAN20AA101P | 5551 | 中旁阀阀位反馈 | % | float32
N2DCS.20MAN20AA101SP | 5552 | 中旁压力设定偏置值 |  | float32
N2DCS.20MAN20AA101SP1 | 5553 | Ovation Control Builder |  | float32
N2DCS.20MAN20CP101 | 5554 | 中旁阀后蒸汽压力1 | MPa | float32
N2DCS.20MAN20CP102 | 5555 | 中旁阀后蒸汽压力2 | MPa | float32
N2DCS.20MAN20CPX2 | 5556 | 中旁阀后蒸汽压力（2选后） |  | float32
N2DCS.20MAN20CT301 | 5557 | 中旁阀后蒸汽温度1 | ℃ | float32
N2DCS.20MAN20CT302 | 5558 | 中旁阀后蒸汽温度2 | ℃ | float32
N2DCS.20MAN20CTX2 | 5559 | 中旁阀后蒸汽温度（2选后） |  | float32
N2DCS.20MAN20GH001PT | 5560 | 中旁阀油站油压 | MPa | float32
N2DCS.20MAP10AA101C | 5561 | 低旁阀阀位控制指令 | % | float32
N2DCS.20MAP10AA101P | 5562 | 低旁阀阀位反馈 | % | float32
N2DCS.20MAP10AA101SP | 5563 | 低旁压力设定偏置值 |  | float32
N2DCS.20MAP10AA101SP1 | 5564 | Ovation Control Builder |  | float32
N2DCS.20MAP10CP101 | 5565 | 低旁阀后蒸汽压力1 | MPa | float32
N2DCS.20MAP10CP102 | 5566 | 低旁阀后蒸汽压力2 |  | float32
N2DCS.20MAP10CPX2 | 5567 | 低旁阀后蒸汽压力（2选后） |  | float32
N2DCS.20MAP10CT301 | 5568 | 低旁阀前疏水门前温度 | ℃ | float32
N2DCS.20MAP10CT302 | 5569 | 低旁阀前疏水门后温度 | ℃ | float32
N2DCS.20MAP10CT303 | 5570 | 低旁阀后蒸汽温度1 | ℃ | float32
N2DCS.20MAP10CT304 | 5571 | 低旁阀后蒸汽温度2 | ℃ | float32
N2DCS.20MAP10CTX2 | 5572 | 低旁阀后蒸汽温度（2选后） |  | float32
N2DCS.20MBY10CE901YQ01 | 5573 | #4机实际负荷-ACTIVE POWER |  | float32
N2DCS.20MBY10CS901YQ01 | 5574 | #4机实际转速 | Hz | float32
N2DCS.20MBY10DE010YQ01 | 5575 | #4机负荷设定值 |  | float32
N2DCS.20MBY10DE010YQ02 | 5576 | #4机负荷设定参考 |  | float32
N2DCS.20MBY10DS010 | 5577 | DELTA FREQUENCY |  | float32
N2DCS.20MBY10DS010YQ01 | 5578 | #4机频率偏差 |  | float32
N2DCS.20MBY10DT040 | 5579 | IGV POSITION |  | float32
N2DCS.20MBY10DT040YQ01 | 5580 | IGV实际开度 |  | float32
N2DCS.20MBY10DU050YQ01 | 5581 | #2调频前修正指令 |  | float32
N2DCS.20MBY10DU062 | 5582 | #4机燃烧负荷设定 |  | float32
N2DCS.20MBY10FT010YQ01 | 5583 | #4机透平排气温度TETC（计算值） |  | float32
N2DCS.20MBY10FT010YQ02 | 5584 | 燃机压气机进口温度 |  | float32
N2DCS.20MKA02CE901 | 5585 | #3发电机实际功率 | % | float32
N2DCS.20MKA10FA103 | 5586 | #3机频率偏差 |  | float32
N2DCS.20MYA01CS118 | 5587 | #3机实际转速 |  | float32
N2DCS.20MYA01CS901C | 5588 | #3机实际转速 | rpm | float32
N2DCS.D1P1B1L1C9 | 5589 | TC温度补偿点 | C | float32
N2DCS.D1P1B2L8C9 | 5590 | TC温度补偿点 | C | float32
N2DCS.D1P1B3L1C9 | 5591 | TC温度补偿点 | C | float32
N2DCS.D1P1B4L8C9 | 5592 | TC温度补偿点 | C | float32
N2DCS.GT_LAOD_PCT | 5593 | 燃机-有功功率-百分比 |  | float32
N2DCS.GT_LOAD | 5594 | 燃机-有功功率 |  | float32
N2DCS.GT_LOAD_PCT | 5595 | 燃机功率百分比 |  | float32
N2DCS.GTLOAD | 5596 | #4机实际负荷-ACTIVE POWER |  | float32
N2DCS.GTRPM | 5597 | 燃机转速 |  | float32
N2DCS.HIGBYPSPRSSET | 5598 | 高旁压力设定值 |  | float32
N2DCS.HIGBYPSPRSSET_TOUT | 5599 | 高旁压力设定值跟踪值 |  | float32
N2DCS.HIGBYPSPRSSET1 | 5600 | 高旁压力设定值1 |  | float32
N2DCS.HIGBYPSPRSSET2 | 5601 | 高旁压力设定值2 |  | float32
N2DCS.HPDSHTEMSP | 5602 | 高旁温度设定值 |  | float32
N2DCS.HPFORCESET | 5603 | 高旁压力强制设定值 |  | float32
N2DCS.HPPIDHL | 5604 | 高旁压力调节输出上限 |  | float32
N2DCS.HPPIDLL | 5605 | 高旁压力调节输出下限 |  | float32
N2DCS.INTBYPSPRSSET | 5606 | 中旁压力设定值 |  | float32
N2DCS.INTBYPSPRSSET_TOUT | 5607 | 中旁压力设定跟踪值值 |  | float32
N2DCS.INTBYPSPRSSET1 | 5608 | 中旁压力设定值1 |  | float32
N2DCS.INTBYPSPRSSET2 | 5609 | 中旁压力设定值2 |  | float32
N2DCS.IPFORCESET | 5610 | 中旁压力强制设定值 |  | float32
N2DCS.IPPIDHL | 5611 | 中旁压力调节输出上限 |  | float32
N2DCS.IPPIDLL | 5612 | 中旁压力调节输出下限 |  | float32
N2DCS.J0LBG10CP102_AI | 5613 | 辅汽母管压力2送二号机 |  | float32
N2DCS.J0LBG10CT302_AI | 5614 | 辅汽母管温度2送二号机 |  | float32
N2DCS.J0LBG22CP101_AI | 5615 | 启动锅炉供辅汽母管压力送二号机 |  | float32
N2DCS.J0LBG22CT301_AI | 5616 | 启动锅炉供辅汽温度送二号机 |  | float32
N2DCS.LOWBYPSPRSSET | 5617 | 低旁压力设定值 |  | float32
N2DCS.LOWBYPSPRSSET_TOUT | 5618 | 低旁设定值跟踪 |  | float32
N2DCS.LOWBYPSPRSSET1 | 5619 | 低旁压力设定1 |  | float32
N2DCS.LOWBYPSPRSSET2 | 5620 | 低旁压力设定值2 |  | float32
N2DCS.LPFORCESET | 5621 | 低旁压力强制设定值 |  | float32
N2DCS.LPPIDHL | 5622 | 低旁压力调节输出上限 |  | float32
N2DCS.LPPIDLL | 5623 | 低旁压力调节输出下限 |  | float32
N2DCS.STLOAD | 5624 | #3机实际负荷 |  | float32
N2DCS.TOTALMW | 5625 | 第二套机组实际总负荷 |  | float32
N2DCS.UNIT_RPM | 5626 | 燃机转速 |  | float32
N2DCS.20LBA70CF | 5627 | Ovation Control Builder |  | float32
N2DCS.20LBA80CF | 5628 | Ovation Control Builder |  | float32
N2DCS.20LBA90CF | 5629 | Ovation Control Builder |  | float32
N2DCS.20MBY10CE901YQ01_SUM | 5630 | #4机当月启动时间 |  | float32
N2DCS.20MBY10CE901YQ01_SUM2 | 5631 | #4机年启动时间 |  | float32
N2DCS.20MBY10CE901YQ01_SUM3 | 5632 | #4机单次启动时间 |  | float32
N2DCS.20MKA01CE903_PEL_SUM | 5633 | #3机月启动时间 |  | float32
N2DCS.20MKA01CE903_PEL_SUM2 | 5634 | #3机年启动时间 |  | float32
N2DCS.20MKA01CE903_PEL_SUM3 | 5635 | #3机单次启动时间 |  | float32
N2DCS.ACTLOADDMD1 | 5636 | 第二套机组总负荷设定值 |  | float32
N2DCS.ACTLOADDMDT | 5637 | 第二套机组总负荷设定值跟踪值 |  | float32
N2DCS.AGCLOADDMD | 5638 | Ovation Control Builder |  | float32
N2DCS.AVC11 | 5639 | Ovation Control Builder |  | float32
N2DCS.AVC12 | 5640 | Ovation Control Builder |  | float32
N2DCS.AVC13 | 5641 | Ovation Control Builder |  | float32
N2DCS.CPRESSINTEM | 5642 | 燃机压气机进口温度 |  | float32
N2DCS.DCS_HPFLOW1 | 5643 | 高压主蒸汽流量（计算后） |  | float32
N2DCS.DCS_IPFLOW1 | 5644 | 中压主蒸汽流量（计算后） |  | float32
N2DCS.DCS_IP_BP_D_PRESS1 | 5645 | 中旁阀后蒸汽压力（2选后） |  | float32
N2DCS.DCS_IP_BP_POS1 | 5646 | 中旁阀阀位反馈 |  | float32
N2DCS.DCS_IP_BP_U_PRESS1 | 5647 | 高温再热蒸汽压力（2选后） |  | float32
N2DCS.GEN_NUM | 5648 | #3机月启动次数 |  | float32
N2DCS.GEN_NUM2 | 5649 | #3机年启动次数 |  | float32
N2DCS.GT_NUM | 5650 | #4机月启动次数 |  | float32
N2DCS.GT_NUM2 | 5651 | #4机年启动次数 |  | float32
N2DCS.GTALRFB | 5652 | #4机负荷设定参考 |  | float32
N2DCS.GTFREQ | 5653 | Ovation Control Builder |  | float32
N2DCS.GTFRQ | 5654 | #4机频率偏差 |  | float32
N2DCS.GTGENLOAD1 | 5655 | #4发电机有功功率 |  | float32
N2DCS.GTLOADDMD1 | 5656 | #4机负荷设定值 |  | float32
N2DCS.GTLOADMAX | 5657 | #4机负荷设定上限值 |  | float32
N2DCS.GTLOADMAX1 | 5658 | #4机负荷设定上限值 |  | float32
N2DCS.GTLOADMIN | 5659 | #4机负荷设定下限值 |  | float32
N2DCS.GTLOADMIN1 | 5660 | #4机负荷设定下限值 |  | float32
N2DCS.GTLOADP1 | 5661 | #4机负荷百分比 |  | float32
N2DCS.GTLOADSET | 5662 | #4机实际负荷设定值 |  | float32
N2DCS.GTLOADSP1 | 5663 | Ovation Control Builder |  | float32
N2DCS.GTRATE | 5664 | Ovation Control Builder |  | float32
N2DCS.GTSPEED1 | 5665 | #4机实际转速 |  | float32
N2DCS.GTTETC | 5666 | #4机透平排气温度TETC（计算值） |  | float32
N2DCS.HIGBYPS | 5667 | Ovation Control Builder |  | float32
N2DCS.HPBT_SPO | 5668 | Ovation Control Builder |  | float32
N2DCS.HPBTBIAS | 5669 | Ovation Control Builder |  | float32
N2DCS.IGVPOS | 5670 | IGV阀位反馈 |  | float32
N2DCS.KDELTAF | 5671 | #4机调频修正前指令 |  | float32
N2DCS.LOADMAX1 | 5672 | 第二套机组总负荷设定上限值 |  | float32
N2DCS.LOADMIN1 | 5673 | 第二套机组总负荷设定下限值 |  | float32
N2DCS.LOADRATE_DCS | 5674 | 第二套机组总负荷变化率 |  | float32
N2DCS.LOADSP1 | 5675 | Ovation Control Builder |  | float32
N2DCS.RB_TPFO | 5676 | 燃机RB首出 |  | float32
N2DCS.STTRIPFO | 5677 | 汽机跳闸首出(对应打包点的位号) |  | float32
N2DCS.TEST_AO | 5678 | Ovation Control Builder |  | float32
N2DCS.TEST_SS | 5679 | Ovation Control Builder |  | float32
N2DCS.TEST_ZZ | 5680 | Ovation Control Builder |  | float32
N2DCS.TEST1_BS | 5681 | Ovation Control Builder |  | float32
N2DCS.TEST1_PV | 5682 | Ovation Control Builder |  | float32
N2DCS.TEST1_SO | 5683 | Ovation Control Builder |  | float32
N2DCS.TEST1_SP | 5684 | Ovation Control Builder |  | float32
N2DCS.TEST1_SPO | 5685 | Ovation Control Builder |  | float32
N2DCS.TEST2_BS | 5686 | Ovation Control Builder |  | float32
N2DCS.TEST2_PV | 5687 | Ovation Control Builder |  | float32
N2DCS.TEST2_SO | 5688 | Ovation Control Builder |  | float32
N2DCS.TEST2_SP | 5689 | Ovation Control Builder |  | float32
N2DCS.TEST2_SPO | 5690 | Ovation Control Builder |  | float32
N2DCS.TOTALSTMFLW | 5691 | #2机组过热器出口蒸汽总流量 |  | float32
N2DCS.TURBLOAD | 5692 | #3发电机有功功率 |  | float32
N2DCS.TURBSPEED | 5693 | #3机实际转速 |  | float32
N2DCS.WKWH_TODAY_0 | 5694 | Ovation Control Builder |  | float32
N2DCS.WKWH_TODAY_1 | 5695 | Ovation Control Builder |  | float32
N2DCS.WKWH_TODAY_2 | 5696 | Ovation Control Builder |  | float32
N2DCS.WKWH_TODAY_3 | 5697 | Ovation Control Builder |  | float32
N2DCS.20CJA06DU001 | 5698 | 遥控目标负荷设定1 |  | float32
N2DCS.20LBD20AC001C | 5699 | 冷再供热减温减压器阀位控制指令 | % | float32
N2DCS.20LBD20AC001P | 5700 | 冷再供热减温减压器阀位反馈 | % | float32
N2DCS.20LBD20AC001SP | 5701 | 冷再供热减温减压器压力设定值 |  | float32
N2DCS.20LBD20CP101 | 5702 | 冷再供热蒸汽压力 | MPa | float32
N2DCS.20LBD20CP103 | 5703 | 冷再供热减温减压器后蒸汽压力 | MPa | float32
N2DCS.20LBD20CT301 | 5704 | 冷再供热蒸汽温度 | ℃ | float32
N2DCS.20LBD20CT302 | 5705 | 冷再供热气动疏水门后温度 | ℃ | float32
N2DCS.20LBD20CT303 | 5706 | 冷再供热减温减压器后蒸汽温度 | ℃ | float32
N2DCS.20LBD40AC001C | 5707 | 热再供热减温减压器阀位控制指令 | % | float32
N2DCS.20LBD40AC001P | 5708 | 热再供热减温减压器阀位反馈 | % | float32
N2DCS.20LBD40AC001SP | 5709 | 热再供热减温减压器压力设定值 |  | float32
N2DCS.20LBD40CP101 | 5710 | 热再供热蒸汽压力 | MPa | float32
N2DCS.20LBD40CP105 | 5711 | 热再供热减温减压器后蒸汽压力 | MPa | float32
N2DCS.20LBD40CT301 | 5712 | 热再供热蒸汽温度 | ℃ | float32
N2DCS.20LBD40CT302 | 5713 | 热再供热气动疏水门后温度 | ℃ | float32
N2DCS.20LBD40CT303 | 5714 | 热再供热减温减压器后蒸汽温度 | ℃ | float32
N2DCS.20LBD60CF101 | 5715 | #2机组抽汽供热母管蒸汽流量 | kPa | float32
N2DCS.20LBD60CP101 | 5716 | 第2套机组抽汽供热母管蒸汽压力 | MPa | float32
N2DCS.20LBD60CT301 | 5717 | 第2套机组抽汽供热母管蒸汽温度 | ℃ | float32
N2DCS.20LBD80CT301 | 5718 | 冷再抽汽至预留中压管疏水门后温 | ℃ | float32
N2DCS.20LBG11AC001C | 5719 | 高排至辅汽母管减压器控制指令 | % | float32
N2DCS.20LBG11AC001P | 5720 | 高排至辅汽母管减压器阀位反馈 | % | float32
N2DCS.20LBG11AC001SP | 5721 | 高排至辅汽母管减压器压力设定值 |  | float32
N2DCS.20LCE11AA101C | 5722 | 凝结水至辅汽减温水调阀控制指令 | % | float32
N2DCS.20LCE11AA101P | 5723 | 凝结水至辅汽减温水调阀阀位指令 | % | float32
N2DCS.20LCE11AA101SP | 5724 | 凝结水至辅汽减温水调阀温度设定 |  | float32
N2DCS.20LCE12AA101_FF | 5725 | 低压旁路阀减温水调阀FF |  | float32
N2DCS.20LCE12AA101C | 5726 | 低旁减温水调阀阀位控制指令 | % | float32
N2DCS.20LCE12AA101P | 5727 | 低旁减温水调阀阀位反馈 | % | float32
N2DCS.20LCE12AA101SP | 5728 | 低旁减温水调阀温度设定值 |  | float32
N2DCS.20LCE12CP101 | 5729 | 低旁减温水压力 | MPa | float32
N2DCS.20LCE13AA101C | 5730 | 凝结水至热再减温水调阀控制指令 | % | float32
N2DCS.20LCE13AA101P | 5731 | 凝结水至热再减温水调阀阀位指令 | % | float32
N2DCS.20LCE13AA101SP | 5732 | 凝结水至热再减温水调阀温度设定 |  | float32
N2DCS.20LCE15AA101_FF | 5733 | 中压旁路喷水调阀FF |  | float32
N2DCS.20LCE15AA101C | 5734 | 中旁减温水调阀阀位控制指令 | % | float32
N2DCS.20LCE15AA101P | 5735 | 中旁减温水调阀阀位反馈 | % | float32
N2DCS.20LCE15AA101SP | 5736 | 中旁减温水调阀温度设定值 |  | float32
N2DCS.20LCE15CP101 | 5737 | 中旁减温水压力 | MPa | float32
N2DCS.20LCE17AA101C | 5738 | 凝结水至冷再减温水调阀控制指令 | % | float32
N2DCS.20LCE17AA101P | 5739 | 凝结水至冷再减温水调阀阀位反馈 | % | float32
N2DCS.20LCE17AA101SP | 5740 | 凝结水至冷再减温水调阀温度设定 |  | float32
N2DCS.20LCE18AA152C | 5741 | 凝结水至轴封减温水调阀控制指令 | % | float32
N2DCS.20LCE18AA152P | 5742 | 凝结水至轴封减温水调阀阀位反馈 | % | float32
N2DCS.20LCE18AA152SP | 5743 | 凝结水至轴封减温水调阀温度设定 |  | float32
N2DCS.20LCE19AA101C | 5744 | 凝汽器水幕喷水调节阀控制指令 | % | float32
N2DCS.20LCE19AA101P | 5745 | 凝汽器水幕喷水调节阀阀位反馈 | % | float32
N2DCS.20LCE19AA101SP | 5746 | 凝汽器水幕喷水调节阀温度设定 |  | float32
N2DCS.20LCE20AA101C | 5747 | 疏水扩容器喷水调节阀控制指令 | % | float32
N2DCS.20LCE20AA101P | 5748 | 疏水扩容器喷水调节阀阀位反馈 | % | float32
N2DCS.20LCE20AA101SP | 5749 | 疏水扩容器喷水调节阀温度设定 |  | float32
N2DCS.20LCM40CL101 | 5750 | 疏水扩容器导波雷达液位 | mm | float32
N2DCS.20LCM40CT301 | 5751 | 疏水扩容器温度 | ℃ | float32
N2DCS.20MAC10CP104 | 5752 | 中压排汽压力 | MPa | float32
N2DCS.20MAL22CT301 | 5753 | 高压缸气动疏水门1后温度 | ℃ | float32
N2DCS.20MAL22CT303 | 5754 | 高压缸气动疏水门2后温度 | ℃ | float32
N2DCS.20MAL22CT304 | 5755 | 高压缸气动疏水门3后温度 | ℃ | float32
N2DCS.20MAL35CT301 | 5756 | 中压缸气动疏水门1后温度 | ℃ | float32
N2DCS.20MAL36CT301 | 5757 | 中压缸气动疏水门2后温度 | ℃ | float32
N2DCS.20MAL50CT301 | 5758 | 低压缸气动疏水门后温度 | ℃ | float32
N2DCS.20MAW10AA151C | 5759 | 辅汽至高中压轴封调阀控制指令 | % | float32
N2DCS.20MAW10AA151P | 5760 | 辅汽至高中压轴封调阀阀位反馈 | % | float32
N2DCS.20MAW10AA151SP | 5761 | 辅汽至高中压轴封调阀压力设定值 |  | float32
N2DCS.20MAW13AA151C | 5762 | 辅汽至低压轴封调阀控制指令 | % | float32
N2DCS.20MAW13AA151P | 5763 | 辅汽至低压轴封调阀阀位反馈 | % | float32
N2DCS.20MAW13AA151SP | 5764 | 辅汽至低压轴封调阀压力设定值 |  | float32
N2DCS.20MAW20CP101 | 5765 | 高中压轴封供汽母管压力1 | MPa | float32
N2DCS.20MAW20CP102 | 5766 | 高中压轴封供汽母管压力2 | MPa | float32
N2DCS.20MAW20CT301 | 5767 | 高中压轴封供汽母管高压侧温度 | ℃ | float32
N2DCS.20MAW20CT303 | 5768 | 高中压轴封供汽母管中压侧温度 | ℃ | float32
N2DCS.20MAW24CP101 | 5769 | 低压轴封供汽母管压力1 | MPa | float32
N2DCS.20MAW24CP102 | 5770 | 低压轴封供汽母管压力2 | MPa | float32
N2DCS.20MAW24CT301 | 5771 | 低压轴封供汽母管温度1 | ℃ | float32
N2DCS.20MAW24CT302 | 5772 | 低压轴封供汽母管温度2 | ℃ | float32
N2DCS.20MAW50AA151C | 5773 | 轴封供汽溢流气动调节阀控制指令 | % | float32
N2DCS.20MAW50AA151P | 5774 | 轴封供汽溢流气动调节阀阀位反馈 | % | float32
N2DCS.20MAW50AA151SP | 5775 | 轴封供汽溢流调节阀压力设定值 |  | float32
N2DCS.20MAW65CT301 | 5776 | 高压缸轴封漏汽温度 | ℃ | float32
N2DCS.20MAW80CP101 | 5777 | 轴封冷却器蒸汽进口压力 | KPa | float32
N2DCS.20MBY10DU061 | 5778 | #4机燃烧负荷设定2 |  | float32
N2DCS.20MKA10FA102 | 5779 | 协调控制负荷设定3 |  | float32
N2DCS.20MYA01DG010C | 5780 | 负荷参考 |  | float32
N2DCS.AUXSTMSYS_SEQSTSTEP | 5781 | 辅汽系统启顺控步号 |  | float32
N2DCS.AUXSTMSYS_SEQSTTIME1 | 5782 | 辅汽系统启顺控第1步剩余时间 |  | float32
N2DCS.AUXSTMSYS_SEQSTTIME2 | 5783 | 辅汽系统启顺控第2步剩余时间 |  | float32
N2DCS.AUXSTMSYS_SEQSTTIME3 | 5784 | 辅汽系统启顺控第3步剩余时间 |  | float32
N2DCS.D2P1B1L3C9 | 5785 | TC温度补偿点 | C | float32
N2DCS.D2P1B2L6C9 | 5786 | TC温度补偿点 | C | float32
N2DCS.D2P1B3L3C9 | 5787 | TC温度补偿点 |  | float32
N2DCS.GLDSTMSYS_SEQSPSTEP | 5788 | 轴封系统停顺控步号 |  | float32
N2DCS.GLDSTMSYS_SEQSPTIME1 | 5789 | 轴封系统停顺控第1步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSPTIME2 | 5790 | 轴封系统停顺控第2步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSPTIME3 | 5791 | 轴封系统停顺控第3步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSPTIME4 | 5792 | 轴封系统停顺控第4步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSPTIME5 | 5793 | 轴封系统停顺控第5步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSTSTEP | 5794 | 轴封系统启顺控步号 |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME1 | 5795 | 轴封系统启顺控第1步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME2 | 5796 | 轴封系统启顺控第2步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME3 | 5797 | 轴封系统启顺控第3步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME4 | 5798 | 轴封系统启顺控第4步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME5 | 5799 | 轴封系统启顺控第5步剩余时间 |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME6 | 5800 | Ovation Control Builder |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME7 | 5801 | Ovation Control Builder |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME8 | 5802 | Ovation Control Builder |  | float32
N2DCS.GLDSTMSYS_SEQSTTIME9 | 5803 | Ovation Control Builder |  | float32
N2DCS.HGLDHDRPRS | 5804 | 高中压轴封供汽母管压力(2选后） |  | float32
N2DCS.HGLDHDRTEM | 5805 | 高中压轴封供汽母管温度(2选后） |  | float32
N2DCS.IPBTBIAS | 5806 | Ovation Control Builder |  | float32
N2DCS.J0LBG10CPX2 | 5807 | 辅汽母管压力 |  | float32
N2DCS.J0LBG10CTX2 | 5808 | 辅汽母管温度 |  | float32
N2DCS.LOWGLDSPLPRS | 5809 | 低压轴封供汽母管压力(2选后） |  | float32
N2DCS.LOWGLDSPLTEM | 5810 | 低压轴封供汽母管温度(2选后） |  | float32
N2DCS.LPBTBIAS | 5811 | 低旁出口温度偏值值 |  | float32
N2DCS.20MAA50CT | 5812 | 高压缸金属温度(50%)(2选后) |  | float32
N2DCS.20MAB50CT | 5813 | 中压缸金属温度(50%)(2选后) |  | float32
N2DCS.20MAY01EP144 | 5814 | 高压转子温度(3选后) |  | float32
N2DCS.20MAY01EP145 | 5815 | 中压转子温度(3选后) |  | float32
N2DCS.IPBT_SPO | 5816 | Ovation Control Builder |  | float32
N2DCS.LPBT_SP | 5817 | Ovation Control Builder |  | float32
N2DCS.20LCA11CP101 | 5818 | #1凝结水泵进口滤网差压 | KPa | float32
N2DCS.20LCA11CT301 | 5819 | #1凝结水泵进口温度 | ℃ | float32
N2DCS.20LCA11CY101 | 5820 | #1凝结水泵轴承振动（X方向） |  | float32
N2DCS.20LCA11CY102 | 5821 | #1凝结水泵轴承振动（Y方向） |  | float32
N2DCS.20LCA20CF101 | 5822 | 凝结水泵出口母管流量 | t/h | float32
N2DCS.20LCA20CF101_CAL | 5823 | 凝结水泵出口母管流量（计算后) |  | float32
N2DCS.20LCA20CF102 | 5824 | 凝结水泵供余热锅炉流量 | t/h | float32
N2DCS.20LCA20CP101 | 5825 | 凝结水泵出口母管压力 | MPa | float32
N2DCS.20LCA20CP102 | 5826 | #3机除铁过滤器出口母管压力 | MPa | float32
N2DCS.20LCA20CP103 | 5827 | #3机轴封冷却器出口压力（水侧） | MPa | float32
N2DCS.20LCA20CT301 | 5828 | 凝结水泵出口母管温度 | ℃ | float32
N2DCS.20LCA20CT302 | 5829 | #3机轴封冷却器出口温度（水侧） | ℃ | float32
N2DCS.20LCA30AA101C | 5830 | 凝结水再循环气动调节阀控制指令 | % | float32
N2DCS.20LCA30AA101P | 5831 | 凝结水再循环气动调节阀阀位反馈 | % | float32
N2DCS.20LCA30AA101SP | 5832 | 凝结水再循环气动调节阀设定值 |  | float32
N2DCS.20LCB11AP001I | 5833 | #1凝结水泵电机电流 | A | float32
N2DCS.20LCB11CT301 | 5834 | #1凝结水泵电机线圈温度1 | ℃ | float32
N2DCS.20LCB11CT302 | 5835 | #1凝结水泵电机线圈温度2 | ℃ | float32
N2DCS.20LCB11CT303 | 5836 | #1凝结水泵电机线圈温度3 | ℃ | float32
N2DCS.20LCB11CT304 | 5837 | #1凝结水泵电机线圈温度4 | ℃ | float32
N2DCS.20LCB11CT305 | 5838 | #1凝结水泵电机线圈温度5 | ℃ | float32
N2DCS.20LCB11CT306 | 5839 | #1凝结水泵电机线圈温度6 | ℃ | float32
N2DCS.20LCB11CT307 | 5840 | #1凝结水泵电机下轴承温度 | ℃ | float32
N2DCS.20LCB11CT308 | 5841 | #1凝结水泵电机上轴承温度 | ℃ | float32
N2DCS.20LCB11CT309 | 5842 | #1凝结水泵轴承温度 | ℃ | float32
N2DCS.20LCB11GH001C | 5843 | #1凝结水泵永磁调速器控制指令 | % | float32
N2DCS.20LCB11GH001FT | 5844 | #1凝结水泵冷却水流量 |  | float32
N2DCS.20LCB11GH001P | 5845 | #1凝结水泵永磁控制器阀位反馈 | % | float32
N2DCS.20LCB11GH001S | 5846 | #1凝结水泵转速 |  | float32
N2DCS.20LCB11GH001SP | 5847 | #1凝结水泵永磁调速器压力设定值 |  | float32
N2DCS.20LCB11GH001T1 | 5848 | #1凝结水泵输出端轴承温度 |  | float32
N2DCS.20LCB11GH001T2 | 5849 | #1凝结水泵轴承油箱温度 |  | float32
N2DCS.20LCB11GH001T3 | 5850 | #1凝结水泵冷却水回水温度 |  | float32
N2DCS.20LCE16AA101C | 5851 | 闭式水箱补水电动调节阀控制指令 | % | float32
N2DCS.20LCE16AA101P | 5852 | 闭式水箱补水电动调节阀阀位反馈 | % | float32
N2DCS.20LCE16CF101 | 5853 | 闭式水箱正常补水流量 | t/h | float32
N2DCS.20LCR10AA101C | 5854 | 凝汽器正常补水调节阀控制指令 | % | float32
N2DCS.20LCR10AA101P | 5855 | 凝汽器正常补水调节阀阀位反馈 | % | float32
N2DCS.20LCR10AA101SP | 5856 | 凝汽器正常补水调节阀液位设定值 |  | float32
N2DCS.20LCR10AA102C | 5857 | 凝汽器启动补水调节阀控制指令 | % | float32
N2DCS.20LCR10AA102P | 5858 | 凝汽器启动补水调节阀阀位反馈 | % | float32
N2DCS.20LCR10AA102SP | 5859 | 凝汽器启动补水调节阀液位设定值 |  | float32
N2DCS.20LCR10CF101 | 5860 | 凝汽器补水流量 | t/h | float32
N2DCS.20LCR10CP101 | 5861 | 凝结水补水压力 | MPa | float32
N2DCS.20LDB10CP101 | 5862 | #3机凝结水除铁过滤器进出口差压 | MPa | float32
N2DCS.20LDK10CP101 | 5863 | #3机凝结水除铁过滤器进口压力 |  | float32
N2DCS.20MAC01CP101 | 5864 | 低压缸喷水过滤器差压 | KPa | float32
N2DCS.20MAG10CL101 | 5865 | 凝汽器热井液位1 | mm | float32
N2DCS.20MAG10CL102 | 5866 | 凝汽器热井液位2 | mm | float32
N2DCS.20MAG10CL103 | 5867 | 凝汽器热井液位3 | mm | float32
N2DCS.20PAB11AA001P | 5868 | 凝汽器循环水进水#1电动门门位反 | % | float32
N2DCS.20PAB11AA011P | 5869 | A侧循环水进水电动阀阀位反馈 |  | float32
N2DCS.20PAB11CP101 | 5870 | 凝汽器循环水管#1进水压力 |  | float32
N2DCS.20PAB11CT301 | 5871 | 凝汽器循环水管#1进水温度 | ℃ | float32
N2DCS.20PAB21CP101 | 5872 | 凝汽器循环水管#1出水压力 | MPa | float32
N2DCS.20PAB21CT301 | 5873 | 凝汽器循环水管#1出水温度 | ℃ | float32
N2DCS.20PAB40CL101 | 5874 | 凝泵坑液位 | mm | float32
N2DCS.20PAH11CP101 | 5875 | #1收球网进出口差压 | KPa | float32
N2DCS.20PCB10CP101 | 5876 | 开式水电动过滤器进出口差压 | kPa | float32
N2DCS.20PCB11AP001I | 5877 | #1开式冷却水泵电机电流 | A | float32
N2DCS.20PCB11CP101 | 5878 | 开式冷却水泵出口母管压力 | Mpa | float32
N2DCS.20PCB11CT301 | 5879 | #1开式水泵电机定子线圈温度1 | ℃ | float32
N2DCS.20PCB11CT302 | 5880 | #1开式水泵电机定子线圈温度2 | ℃ | float32
N2DCS.20PCB11CT303 | 5881 | #1开式水泵电机定子线圈温度3 | ℃ | float32
N2DCS.20PCB11CT304 | 5882 | #1开式水泵电机定子线圈温度4 | ℃ | float32
N2DCS.20PCB11CT305 | 5883 | #1开式水泵电机定子线圈温度5 | ℃ | float32
N2DCS.20PCB11CT306 | 5884 | #1开式水泵电机定子线圈温度6 | ℃ | float32
N2DCS.20PCB11CT307 | 5885 | #1开式水泵电机驱动端轴承温度 | ℃ | float32
N2DCS.20PCB11CT308 | 5886 | #1开式水泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20PCB11CT309 | 5887 | #1开式水泵驱动端轴承温度 | ℃ | float32
N2DCS.20PCB11CT310 | 5888 | #1开式水泵非驱动端轴承温度 | ℃ | float32
N2DCS.20PCB21CT301 | 5889 | #1热交换器开式冷却水进口温度 | ℃ | float32
N2DCS.20PCB31AA001P | 5890 | #1热交换器开式水出口门门位反馈 | % | float32
N2DCS.20PCB31CT302 | 5891 | #1热交换器开式冷却水出口温度 | ℃ | float32
N2DCS.20PGA10CL101SP | 5892 | 闭式水箱补水电动调阀液位设定值 |  | float32
N2DCS.20PGA11AP001I | 5893 | #1闭式水泵电机电流 | A | float32
N2DCS.20PGA11CP101 | 5894 | #1闭式水泵进口滤网差压 | kPa | float32
N2DCS.20PGA11CT301 | 5895 | #1闭式水泵电机定子线圈温度1 | ℃ | float32
N2DCS.20PGA11CT302 | 5896 | #1闭式水泵电机定子线圈温度2 | ℃ | float32
N2DCS.20PGA11CT303 | 5897 | #1闭式水泵电机定子线圈温度3 | ℃ | float32
N2DCS.20PGA11CT304 | 5898 | #1闭式水泵电机定子线圈温度4 | ℃ | float32
N2DCS.20PGA11CT305 | 5899 | #1闭式水泵电机定子线圈温度5 | ℃ | float32
N2DCS.20PGA11CT306 | 5900 | #1闭式水泵电机定子线圈温度6 | ℃ | float32
N2DCS.20PGA11CT307 | 5901 | #1闭式水泵电机驱动端轴承温度 | ℃ | float32
N2DCS.20PGA11CT308 | 5902 | #1闭式水泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20PGA11CT311 | 5903 | #1闭式水泵驱动端轴承温度 | ℃ | float32
N2DCS.20PGA11CT312 | 5904 | #1闭式水泵非驱动端轴承温度 | ℃ | float32
N2DCS.20PGA21CT302 | 5905 | #1热交换器闭式冷却水出水温度 | ℃ | float32
N2DCS.CIRWTR_SEQSTSTEP | 5906 | 开式水系统启顺控步号 |  | float32
N2DCS.CIRWTR_SEQSTTIME1 | 5907 | 开式水系统启顺控第1步剩余时间 |  | float32
N2DCS.CIRWTR_SEQSTTIME2 | 5908 | 开式水系统启顺控第2步剩余时间 |  | float32
N2DCS.CIRWTR_SEQSTTIME3 | 5909 | 开式水系统启顺控第3步剩余时间 |  | float32
N2DCS.CLCLGPMPA_SEQSPSTEP | 5910 | #1闭式水泵停顺控步号 |  | float32
N2DCS.CLCLGPMPA_SEQSPTIME1 | 5911 | #1闭式水泵停顺控第1步剩余时间 |  | float32
N2DCS.CLCLGPMPA_SEQSPTIME2 | 5912 | #1闭式水泵停顺控第2步剩余时间 |  | float32
N2DCS.CLCLGPMPA_SEQSPTIME3 | 5913 | #1闭式水泵停顺控第3步剩余时间 |  | float32
N2DCS.CLCLGPMPA_SEQSPTIME4 | 5914 | Ovation Control Builder |  | float32
N2DCS.CLCLGPMPA_SEQSTSTEP | 5915 | #1闭式水泵启顺控步号 |  | float32
N2DCS.CLCLGPMPA_SEQSTTIME1 | 5916 | #1闭式水泵启顺控第1步剩余时间 |  | float32
N2DCS.CLCLGPMPA_SEQSTTIME2 | 5917 | #1闭式水泵启顺控第2步剩余时间 |  | float32
N2DCS.CLCLGPMPA_SEQSTTIME3 | 5918 | #1闭式水泵启顺控第3步剩余时间 |  | float32
N2DCS.CLCLGPMPA_SEQSTTIME4 | 5919 | #1闭式水泵启顺控第4步剩余时间 |  | float32
N2DCS.CLCLGPMPA_SEQSTTIME5 | 5920 | #1闭式水泵启顺控第5步剩余时间 |  | float32
N2DCS.CLCLGPMPA_TPFO | 5921 | #1闭式水泵跳闸首出(打包点位号 |  | float32
N2DCS.CLCLGWTR_SEQSTSTEP | 5922 | 闭式水系统启顺控步号 |  | float32
N2DCS.CLCLGWTR_SEQSTTIME1 | 5923 | 闭式水系统启顺控第1步剩余时间 |  | float32
N2DCS.CLCLGWTR_SEQSTTIME2 | 5924 | 闭式水系统启顺控第2步剩余时间 |  | float32
N2DCS.CLCLGWTR_SEQSTTIME3 | 5925 | 闭式水系统启顺控第3步剩余时间 |  | float32
N2DCS.CLCLGWTR_SEQSTTIME4 | 5926 | 闭式水系统启顺控第4步剩余时间 |  | float32
N2DCS.CLCLGWTR_SEQSTTIME5 | 5927 | 闭式水系统启顺控第5步剩余时间 |  | float32
N2DCS.CLCLGWTR_SEQSTTIME6 | 5928 | 闭式水系统启顺控第6步剩余时间 |  | float32
N2DCS.CLCLGWTR_SEQSTTIME7 | 5929 | 闭式水系统启顺控第7步剩余时间 |  | float32
N2DCS.CNDHWLVL | 5930 | 凝汽器热井液位（3选后） |  | float32
N2DCS.CNDPA_SEQSPTIME1 | 5931 | #1凝结水泵停顺控第1步剩余时间 |  | float32
N2DCS.CNDPA_SEQSPTIME2 | 5932 | #1凝结水泵停顺控第2步剩余时间 |  | float32
N2DCS.CNDPA_SEQSPTIME3 | 5933 | #1凝结水泵停顺控第3步剩余时间 |  | float32
N2DCS.CNDPA_SEQSPTIME4 | 5934 | Ovation Control Builder |  | float32
N2DCS.CNDPA_SEQSTTIME1 | 5935 | #1凝结水泵启顺控第1步剩余时间 |  | float32
N2DCS.CNDPA_SEQSTTIME2 | 5936 | #1凝结水泵启顺控第2步剩余时间 |  | float32
N2DCS.CNDPA_SEQSTTIME3 | 5937 | #1凝结水泵启顺控第3步剩余时间 |  | float32
N2DCS.CNDPA_SEQSTTIME4 | 5938 | Ovation Control Builder |  | float32
N2DCS.CNDPAPA_SEQSPSTEP | 5939 | #1凝结水泵停顺控步号 |  | float32
N2DCS.CNDPAPA_SEQSTSTEP | 5940 | #1凝结水泵启顺控步号 |  | float32
N2DCS.CNDPMPA_TPFO | 5941 | #1凝结水泵跳闸首出(打包点位号 |  | float32
N2DCS.CNDWTRSYS_SEQSTREYSTEP | 5942 | 凝结水系统准备顺控步号 |  | float32
N2DCS.CNDWTRSYS_SEQSTREYTIME1 | 5943 | 凝结水系统准备顺控1步剩余时间 |  | float32
N2DCS.CNDWTRSYS_SEQSTREYTIME2 | 5944 | 凝结水系统准备顺控2步剩余时间 |  | float32
N2DCS.CNDWTRSYS_SEQSTREYTIME3 | 5945 | 凝结水系统准备顺控3步剩余时间 |  | float32
N2DCS.CNDWTRSYS_SEQSTREYTIME4 | 5946 | 凝结水系统准备顺控4步剩余时间 |  | float32
N2DCS.CNDWTRSYS_SEQSTREYTIME5 | 5947 | 凝结水系统准备顺控5步剩余时间 |  | float32
N2DCS.CNDWTRSYS_SEQSTREYTIME6 | 5948 | Ovation Control Builder |  | float32
N2DCS.CNDWTRSYS_SEQSTSTEP | 5949 | 凝结水系统启顺控步号 |  | float32
N2DCS.CNDWTRSYS_SEQSTTIME1 | 5950 | 凝结水系统启顺控第1步剩余时间 |  | float32
N2DCS.CNDWTRSYS_SEQSTTIME2 | 5951 | 凝结水系统启顺控第2步剩余时间 |  | float32
N2DCS.CNDWTRSYS_SEQSTTIME3 | 5952 | 凝结水系统启顺控第3步剩余时间 |  | float32
N2DCS.CNDWTRSYS_SEQSTTIME4 | 5953 | 凝结水系统启顺控第4步剩余时间 |  | float32
N2DCS.CNSRHOTWLVL | 5954 | 选择后凝汽器热井液位 |  | float32
N2DCS.CNSRLVL | 5955 | 凝汽器热井液位（3选后） |  | float32
N2DCS.L0LCB10CT311 | 5956 | Ovation Control Builder |  | float32
N2DCS.L0LCB10CT312 | 5957 | Ovation Control Builder |  | float32
N2DCS.L0LCB10CT314 | 5958 | Ovation Control Builder |  | float32
N2DCS.OPNCIRPMPA_SEQSPSTEP | 5959 | #1开式水泵停顺控步号 |  | float32
N2DCS.OPNCIRPMPA_SEQSPTIME1 | 5960 | #1开式水泵停顺控第1步剩余时间 |  | float32
N2DCS.OPNCIRPMPA_SEQSPTIME2 | 5961 | #1开式水泵停顺控第2步剩余时间 |  | float32
N2DCS.OPNCIRPMPA_SEQSPTIME3 | 5962 | Ovation Control Builder |  | float32
N2DCS.OPNCIRPMPA_SEQSTSTEP | 5963 | #1开式水泵启顺控步号 |  | float32
N2DCS.OPNCIRPMPA_SEQSTTIME1 | 5964 | #1开式水泵启顺控第1步剩余时间 |  | float32
N2DCS.OPNCIRPMPA_SEQSTTIME2 | 5965 | #1开式水泵启顺控第2步剩余时间 |  | float32
N2DCS.OPNCIRPMPA_SEQSTTIME3 | 5966 | #1开式水泵启顺控第3步剩余时间 |  | float32
N2DCS.OPNCIRPMPA_TPFO | 5967 | #1开式水泵跳闸首出(打包点位号 |  | float32
N2DCS.OPNCIRWTR_SEQSTSTEP | 5968 | 开式水系统启顺控步号 |  | float32
N2DCS.OPNCIRWTR_SEQSTTIME1 | 5969 | 开式水系统启顺控第1步剩余时间 |  | float32
N2DCS.OPNCIRWTR_SEQSTTIME2 | 5970 | 开式水系统启顺控第2步剩余时间 |  | float32
N2DCS.OPNCIRWTR_SEQSTTIME3 | 5971 | 开式水系统启顺控第3步剩余时间 |  | float32
N2DCS.OPNCIRWTR_SEQSTTIME4 | 5972 | 开式水系统启顺控第4步剩余时间 |  | float32
N2DCS.RBBRBALLA_SEQSPSTEP | 5973 | 凝汽器#1胶球收球顺控步号 |  | float32
N2DCS.RBBRBALLA_SEQSPTIME1 | 5974 | #1胶球收球顺控第1步剩余时间 |  | float32
N2DCS.RBBRBALLA_SEQSPTIME2 | 5975 | #1胶球收球顺控第2步剩余时间 |  | float32
N2DCS.RBBRBALLA_SEQSPTIME3 | 5976 | #1胶球收球顺控第3步剩余时间 |  | float32
N2DCS.RBBRBALLA_SEQSPTIME4 | 5977 | #1胶球收球顺控第4步剩余时间 |  | float32
N2DCS.RBBRBALLA_SEQSTSTEP | 5978 | 凝汽器#1胶球投球顺控步号 |  | float32
N2DCS.RBBRBALLA_SEQSTTIME1 | 5979 | #1胶球投球顺控第1步剩余时间 |  | float32
N2DCS.RBBRBALLA_SEQSTTIME2 | 5980 | #1胶球投球顺控第2步剩余时间 |  | float32
N2DCS.RBBRBALLA_SEQSTTIME3 | 5981 | #1胶球投球顺控第3步剩余时间 |  | float32
N2DCS.RBBRBALLA_SEQSTTIME4 | 5982 | #1胶球投球顺控第4步剩余时间 |  | float32
N2DCS.20LCA20CF101_SUM | 5983 | 凝结水泵出口母管流量累计值 |  | float32
N2DCS.20LCA20CF102I | 5984 | 凝结水泵供余热锅炉流量(计算后) |  | float32
N2DCS.20LCR10CF101_SUM | 5985 | 凝汽器补水流量累计值 |  | float32
N2DCS.20PCB10GH501RUN_SV | 5986 | 开式水电动过滤器清洗时间 |  | float32
N2DCS.20PCB10GH501SET_SV | 5987 | 开式水电动过滤器定时时间 |  | float32
N2DCS.20LCA12CP101 | 5988 | #2凝结水泵进口滤网差压 | KPa | float32
N2DCS.20LCA12CT301 | 5989 | #2凝结水泵进口温度 | ℃ | float32
N2DCS.20LCA12CY101 | 5990 | #2凝结水泵轴承振动(X方向) |  | float32
N2DCS.20LCA12CY102 | 5991 | #2凝结水泵轴承振动(Y方向) |  | float32
N2DCS.20LCB12AP002I | 5992 | #2凝结水泵电机电流 | A | float32
N2DCS.20LCB12CT301 | 5993 | #2凝结水泵电机定子线圈温度1 | ℃ | float32
N2DCS.20LCB12CT302 | 5994 | #2凝结水泵电机定子线圈温度2 | ℃ | float32
N2DCS.20LCB12CT303 | 5995 | #2凝结水泵电机定子线圈温度3 | ℃ | float32
N2DCS.20LCB12CT304 | 5996 | #2凝结水泵电机定子线圈温度4 | ℃ | float32
N2DCS.20LCB12CT305 | 5997 | #2凝结水泵电机定子线圈温度5 | ℃ | float32
N2DCS.20LCB12CT306 | 5998 | #2凝结水泵电机定子线圈温度6 | ℃ | float32
N2DCS.20LCB12CT307 | 5999 | #2凝结水泵电机下轴承温度 | ℃ | float32
N2DCS.20LCB12CT308 | 6000 | #2凝结水泵电机上轴承温度 | ℃ | float32
N2DCS.20LCB12CT309 | 6001 | #2凝结水泵轴承温度 | ℃ | float32
N2DCS.20LCB12GH001C | 6002 | #2凝结水泵永磁调速器控制指令 | % | float32
N2DCS.20LCB12GH001FT | 6003 | #2凝结水泵冷却水流量 |  | float32
N2DCS.20LCB12GH001FT2 | 6004 | #2凝结水泵轴承油流量 |  | float32
N2DCS.20LCB12GH001LT | 6005 | #2凝结水泵水箱液位 |  | float32
N2DCS.20LCB12GH001P | 6006 | #2凝结水泵永磁控制器阀位反馈 | % | float32
N2DCS.20LCB12GH001S | 6007 | #2凝结水泵转速 |  | float32
N2DCS.20LCB12GH001T1 | 6008 | #2凝结水泵输出端轴承温度 |  | float32
N2DCS.20LCB12GH001T2 | 6009 | #2凝结水泵轴承油箱温度 |  | float32
N2DCS.20LCB12GH001T3 | 6010 | #2凝结水泵冷却水回水温度 |  | float32
N2DCS.20PAB12AA001P | 6011 | 凝汽器循环水进水#2电动门门位反 | % | float32
N2DCS.20PAB12AA011P | 6012 | 凝汽器B侧循环水进水阀位反馈 |  | float32
N2DCS.20PAB12CP101 | 6013 | 凝汽器循环水管#2进水压力 |  | float32
N2DCS.20PAB12CT301 | 6014 | 凝汽器循环水管#2进水温度 | ℃ | float32
N2DCS.20PAB22CP101 | 6015 | 凝汽器循环水管#2出水压力 | MPa | float32
N2DCS.20PAB22CT301 | 6016 | 凝汽器循环水管#2出水温度 | ℃ | float32
N2DCS.20PAH12CP101 | 6017 | #2收球网进出口差压 | KPa | float32
N2DCS.20PCB11AP002I | 6018 | #2开式冷却水泵电机电流 | A | float32
N2DCS.20PCB11CT311 | 6019 | #2开式水泵电机定子线圈温度1 | ℃ | float32
N2DCS.20PCB11CT312 | 6020 | #2开式水泵电机定子线圈温度2 | ℃ | float32
N2DCS.20PCB11CT313 | 6021 | #2开式水泵电机定子线圈温度3 | ℃ | float32
N2DCS.20PCB11CT314 | 6022 | #2开式水泵电机定子线圈温度4 | ℃ | float32
N2DCS.20PCB11CT315 | 6023 | #2开式水泵电机定子线圈温度5 | ℃ | float32
N2DCS.20PCB11CT316 | 6024 | #2开式水泵电机定子线圈温度6 | ℃ | float32
N2DCS.20PCB11CT317 | 6025 | #2开式水泵电机驱动端轴承温度 | ℃ | float32
N2DCS.20PCB11CT318 | 6026 | #2开式水泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20PCB11CT319 | 6027 | #2开式水泵驱动端轴承温度 | ℃ | float32
N2DCS.20PCB11CT320 | 6028 | #2开式水泵非驱动端轴承温度 | ℃ | float32
N2DCS.20PCB22CT301 | 6029 | #2热交换器开式冷却水进口温度 | ℃ | float32
N2DCS.20PCB32AA001P | 6030 | #2热交换器开式水出口门门位反馈 | % | float32
N2DCS.20PCB32CT302 | 6031 | #2热交换器开式冷却水出口温度 | ℃ | float32
N2DCS.20PGA10CL101 | 6032 | 闭式水箱液位 | mm | float32
N2DCS.20PGA12AP001I | 6033 | #2闭式水泵电机电流 | A | float32
N2DCS.20PGA12CP101 | 6034 | #2闭式水泵进口滤网差压 | kPa | float32
N2DCS.20PGA12CT301 | 6035 | #2闭式水泵电机定子线圈温度1 | ℃ | float32
N2DCS.20PGA12CT302 | 6036 | #2闭式水泵电机定子线圈温度2 | ℃ | float32
N2DCS.20PGA12CT303 | 6037 | #2闭式水泵电机定子线圈温度3 | ℃ | float32
N2DCS.20PGA12CT304 | 6038 | #2闭式水泵电机定子线圈温度4 | ℃ | float32
N2DCS.20PGA12CT305 | 6039 | #2闭式水泵电机定子线圈温度5 | ℃ | float32
N2DCS.20PGA12CT306 | 6040 | #2闭式水泵电机定子线圈温度6 | ℃ | float32
N2DCS.20PGA12CT307 | 6041 | #2闭式水泵电机驱动端轴承温度 | ℃ | float32
N2DCS.20PGA12CT308 | 6042 | #2闭式水泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20PGA12CT311 | 6043 | #2闭式水泵驱动端轴承温度 | ℃ | float32
N2DCS.20PGA12CT312 | 6044 | #2闭式水泵非驱动端轴承温度 | ℃ | float32
N2DCS.20PGA20CP101 | 6045 | 闭式水泵出口母管压力 | Mpa | float32
N2DCS.20PGA20CP102 | 6046 | 热交热器闭式冷却水出口母管压力 | Mpa | float32
N2DCS.20PGA20CT301 | 6047 | 热交换器闭式冷却水进口母管温度 | ℃ | float32
N2DCS.20PGA22CT302 | 6048 | #2热交换器闭式冷却水出水温度 | ℃ | float32
N2DCS.20PGA26AA101C | 6049 | #4发电机定冷水进水调阀控制指令 | % | float32
N2DCS.20PGA26AA101P | 6050 | #4发电机定冷水进水调阀阀位反馈 | % | float32
N2DCS.20PGA26AA101SP | 6051 | #4发电机定冷水进水调阀温度设定 |  | float32
N2DCS.20PGA26AA101TEMP | 6052 | 临时温度测点 |  | float32
N2DCS.20PGA26AA102C | 6053 | #4发电机氢冷器进水调阀控制指令 | % | float32
N2DCS.20PGA26AA102P | 6054 | #4发电机氢冷器进水调阀阀位反馈 | % | float32
N2DCS.20PGA26AA102SP | 6055 | #4发电机氢冷器进水调阀温度设定 |  | float32
N2DCS.20PGA26AA103C | 6056 | #4机滑油冷却器进水调阀控制指令 | % | float32
N2DCS.20PGA26AA103P | 6057 | #4机滑油冷却器进水调阀阀位反馈 | % | float32
N2DCS.20PGA26AA103SP | 6058 | #4机滑油冷却器进水调阀温度设定 |  | float32
N2DCS.20PGA32AA101C | 6059 | #3机EH油冷却器进水调阀控制指令 | % | float32
N2DCS.20PGA32AA101P | 6060 | #3机EH油冷却器进水调阀反馈反馈 | % | float32
N2DCS.20PGA32AA101SP | 6061 | #3机EH油冷却器进水调阀温度设定 |  | float32
N2DCS.20PGA32AA101TEMP | 6062 | 临时温度测点 |  | float32
N2DCS.20PGA33AA101C | 6063 | #3机滑油冷却器进水调阀控制指令 | % | float32
N2DCS.20PGA33AA101P | 6064 | #3机滑油冷却器进水调阀阀位反馈 | % | float32
N2DCS.20PGA33AA101SP | 6065 | #3机滑油冷却器进水调阀温度设定 |  | float32
N2DCS.20PGA34AA101C | 6066 | #3发电机空冷器进水调阀控制指令 | % | float32
N2DCS.20PGA34AA101P | 6067 | #3发电机空冷器进水调阀阀位反馈 | % | float32
N2DCS.20PGA34AA101SP | 6068 | #3发电机空冷器进水调阀温度设定 |  | float32
N2DCS.CLCLGPMPB_SEQSPSTEP | 6069 | #2闭式水泵停顺控步号 |  | float32
N2DCS.CLCLGPMPB_SEQSPTIME1 | 6070 | #2闭式水泵停顺控第1步剩余时间 |  | float32
N2DCS.CLCLGPMPB_SEQSPTIME2 | 6071 | #2闭式水泵停顺控第2步剩余时间 |  | float32
N2DCS.CLCLGPMPB_SEQSTSTEP | 6072 | #2闭式水泵启顺控步号 |  | float32
N2DCS.CLCLGPMPB_SEQSTTIME1 | 6073 | #2闭式水泵启顺控第1步剩余时间 |  | float32
N2DCS.CLCLGPMPB_SEQSTTIME2 | 6074 | #2闭式水泵启顺控第2步剩余时间 |  | float32
N2DCS.CLCLGPMPB_SEQSTTIME3 | 6075 | #2闭式水泵启顺控第3步剩余时间 |  | float32
N2DCS.CLCLGPMPB_TPFO | 6076 | #2闭式水泵跳闸首出(打包点位号 |  | float32
N2DCS.CNDPAPB_SEQSPSTEP | 6077 | #2凝结水泵停顺控步号 |  | float32
N2DCS.CNDPAPB_SEQSTSTEP | 6078 | #2凝结水泵启顺控步号 |  | float32
N2DCS.CNDPB_SEQSPTIME1 | 6079 | #2凝结水泵停顺控第1步剩余时间 |  | float32
N2DCS.CNDPB_SEQSPTIME2 | 6080 | #2凝结水泵停顺控第2步剩余时间 |  | float32
N2DCS.CNDPB_SEQSPTIME3 | 6081 | #2凝结水泵停顺控第3步剩余时间 |  | float32
N2DCS.CNDPB_SEQSPTIME4 | 6082 | Ovation Control Builder |  | float32
N2DCS.CNDPB_SEQSTTIME1 | 6083 | #2凝结水泵启顺控第1步剩余时间 |  | float32
N2DCS.CNDPB_SEQSTTIME2 | 6084 | #2凝结水泵启顺控第2步剩余时间 |  | float32
N2DCS.CNDPB_SEQSTTIME3 | 6085 | #2凝结水泵启顺控第3步剩余时间 |  | float32
N2DCS.CNDPB_SEQSTTIME4 | 6086 | #2凝结水泵启顺控第4步剩余时间 |  | float32
N2DCS.CNDPMPB_TPFO | 6087 | #2凝结水泵跳闸首出(打包点位号 |  | float32
N2DCS.OPNCIRPMPB_SEQSPSTEP | 6088 | #2开式水泵停顺控步号 |  | float32
N2DCS.OPNCIRPMPB_SEQSPTIME1 | 6089 | #2开式水泵停顺控第1步剩余时间 |  | float32
N2DCS.OPNCIRPMPB_SEQSPTIME2 | 6090 | #2开式水泵停顺控第2步剩余时间 |  | float32
N2DCS.OPNCIRPMPB_SEQSTSTEP | 6091 | #2开式水泵启顺控步号 |  | float32
N2DCS.OPNCIRPMPB_SEQSTTIME1 | 6092 | #2开式水泵启顺控第1步剩余时间 |  | float32
N2DCS.OPNCIRPMPB_SEQSTTIME2 | 6093 | #2开式水泵启顺控第2步剩余时间 |  | float32
N2DCS.OPNCIRPMPB_SEQSTTIME3 | 6094 | #2开式水泵启顺控第3步剩余时间 |  | float32
N2DCS.OPNCIRPMPB_TPFO | 6095 | #2开式水泵跳闸首出(打包点位号 |  | float32
N2DCS.RBBRBALLB_SEQSPSTEP | 6096 | 凝汽器#2胶球收球顺控步号 |  | float32
N2DCS.RBBRBALLB_SEQSPTIME1 | 6097 | #2胶球收球顺控第1步剩余时间 |  | float32
N2DCS.RBBRBALLB_SEQSPTIME2 | 6098 | #2胶球收球顺控第2步剩余时间 |  | float32
N2DCS.RBBRBALLB_SEQSPTIME3 | 6099 | #2胶球收球顺控第3步剩余时间 |  | float32
N2DCS.RBBRBALLB_SEQSPTIME4 | 6100 | #2胶球收球顺控第4步剩余时间 |  | float32
N2DCS.RBBRBALLB_SEQSTSTEP | 6101 | 凝汽器#2胶球投球顺控步号 |  | float32
N2DCS.RBBRBALLB_SEQSTTIME1 | 6102 | #2胶球投球顺控第1步剩余时间 |  | float32
N2DCS.RBBRBALLB_SEQSTTIME2 | 6103 | #2胶球投球顺控第2步剩余时间 |  | float32
N2DCS.RBBRBALLB_SEQSTTIME3 | 6104 | #2胶球投球顺控第3步剩余时间 |  | float32
N2DCS.RBBRBALLB_SEQSTTIME4 | 6105 | #2胶球投球顺控第4步剩余时间 |  | float32
N2DCS.20LCB12GH001LTMM | 6106 | #2凝结水泵冷却水箱液位(计算后) |  | float32
N2DCS.20LCB12GH001SP | 6107 | #2凝结水泵永磁调速器压力设定值 |  | float32
N2DCS.20PGA33AA101SPO | 6108 | #3机滑油冷却器进水调阀温度设定 |  | float32
N2DCS.HXCTQ_SEQSPSTEP | 6109 | 除铁过滤器停顺控 |  | float32
N2DCS.HXCTQ_SEQSPTIME1 | 6110 | 除铁过滤器停顺控第1步剩余时间 |  | float32
N2DCS.HXCTQ_SEQSPTIME2 | 6111 | 除铁过滤器停顺控第2步剩余时间 |  | float32
N2DCS.HXCTQ_SEQSPTIME3 | 6112 | 除铁过滤器停顺控第3步剩余时间 |  | float32
N2DCS.HXCTQ_SEQSTSTEP | 6113 | 除铁过滤器启顺控 |  | float32
N2DCS.HXCTQ_SEQSTTIME1 | 6114 | 除铁过滤器启顺控第1步剩余时间 |  | float32
N2DCS.HXCTQ_SEQSTTIME2 | 6115 | 除铁过滤器启顺控第2步剩余时间 |  | float32
N2DCS.HXCTQ_SEQSTTIME3 | 6116 | 除铁过滤器启顺控第3步剩余时间 |  | float32
N2DCS.HXCTQ_SEQSTTIME4 | 6117 | 除铁过滤器启顺控第4步剩余时间 |  | float32
N2DCS.HXCTQ_SEQSTTIME5 | 6118 | 除铁过滤器启顺控第5步剩余时间 |  | float32
N2DCS.HXCTQ_SP1 | 6119 | Ovation Control Builder |  | float32
N2DCS.HXCTQ_SP2 | 6120 | Ovation Control Builder |  | float32
N2DCS.HXCTQCY | 6121 | 凝结水出口母管与除铁器进口压差 |  | float32
N2DCS.20MAG01GH001C | 6122 | 凝汽器电导率 |  | float32
N2DCS.20MAG10CP104 | 6123 | 凝汽器真空4 | KPa | float32
N2DCS.20MAG10CP105 | 6124 | 凝汽器真空5 | KPa | float32
N2DCS.20MAG10CT301 | 6125 | 凝汽器温度 | ℃ | float32
N2DCS.20MAJ21AP001I | 6126 | #1真空泵电机电流 | A | float32
N2DCS.20MAJ21CL501 | 6127 | #1真空泵汽水分离器 | mm | float32
N2DCS.20MAJ21CP101 | 6128 | #1真空泵进口手动门前绝对压力 | KPa | float32
N2DCS.20MAJ21CP102 | 6129 | #1真空泵进口蝶阀前后差压 | KPa | float32
N2DCS.20MAJ21CT301 | 6130 | #1真空泵电机定子线圈温度1 | ℃ | float32
N2DCS.20MAJ21CT302 | 6131 | #1真空泵电机定子线圈温度2 | ℃ | float32
N2DCS.20MAJ21CT303 | 6132 | #1真空泵电机定子线圈温度3 | ℃ | float32
N2DCS.20MAJ21CT304 | 6133 | #1真空泵电机定子线圈温度4 | ℃ | float32
N2DCS.20MAJ21CT305 | 6134 | #1真空泵电机定子线圈温度5 | ℃ | float32
N2DCS.20MAJ21CT306 | 6135 | #1真空泵电机定子线圈温度6 | ℃ | float32
N2DCS.20MAJ21CT307 | 6136 | #1真空泵电机前轴承温度 | ℃ | float32
N2DCS.20MAJ21CT308 | 6137 | #1真空泵电机后轴承温度 | ℃ | float32
N2DCS.20MAJ21CT311 | 6138 | #1真空泵前轴承温度 | ℃ | float32
N2DCS.20MAJ23AA101C | 6139 | 蒸汽喷射装置压力调节阀控制指令 | % | float32
N2DCS.20MAJ23AA101P | 6140 | 蒸汽喷射装置压力调节阀阀位指令 | % | float32
N2DCS.20MAJ23AA101SP | 6141 | 蒸汽喷射装置压力调节阀压力设定 |  | float32
N2DCS.20MAJ23CF101 | 6142 | 蒸汽喷射装置压力调节阀后流量 | kg/h | float32
N2DCS.20MAJ23CP101 | 6143 | 蒸汽喷射装置压力调节阀前压力 | MPa | float32
N2DCS.20MAJ23CP102 | 6144 | 蒸汽喷射装置换热器汽侧出口压力 | MPa | float32
N2DCS.20MAJ23CP103 | 6145 | 蒸汽喷射装置压力调节阀后压力 |  | float32
N2DCS.20MAJ23CT301 | 6146 | 蒸汽喷射装置进口辅汽温度 | ℃ | float32
N2DCS.20MAJ23CT302 | 6147 | 蒸汽喷射装置进气温度 | ℃ | float32
N2DCS.20MAJ23CT303 | 6148 | 蒸汽喷射装置换热器供水温度 | ℃ | float32
N2DCS.20MAJ23CT304 | 6149 | 蒸汽喷射装置换热器回水温度 | ℃ | float32
N2DCS.20MAJ23CT305 | 6150 | 蒸汽喷射装置换热器汽侧出口温度 | ℃ | float32
N2DCS.20MAV21AP021I | 6151 | #1润滑油泵电机电流 | A | float32
N2DCS.20MAV31AP001I | 6152 | #1顶轴油泵电机电流 | A | float32
N2DCS.20MAV31CP101 | 6153 | #1顶轴油泵出口压力 | MPa | float32
N2DCS.20MAV82AN001I | 6154 | #1润滑油风机电流 |  | float32
N2DCS.20MAX01AP001I | 6155 | #1EH油泵电机电流 | A | float32
N2DCS.20MAX01AP011I | 6156 | #1EH油循环泵电机电流 | A | float32
N2DCS.20PAB11AA002CT | 6157 | #3循环水泵出口液控蝶阀油箱油温 | ℃ | float32
N2DCS.20PAB11AA002P1 | 6158 | #3循环水泵出口液控阀蓄能器压力 | MPa | float32
N2DCS.20PAB11AA002P2 | 6159 | #3循环水泵出口液控蝶阀A口油压 | MPa | float32
N2DCS.20PAB11AA002P3 | 6160 | #3循环水泵出口液控蝶阀B口油压 | MPa | float32
N2DCS.20PAB11CL102 | 6161 | #1旋转滤网前水位 | m | float32
N2DCS.20PAB11CL103 | 6162 | #1旋转滤网后水位 | m | float32
N2DCS.20PAB11CP1016 | 6163 | #3循环水泵出口压力 |  | float32
N2DCS.20PAB43CP101 | 6164 | #3循环水泵冷却水进口母管压力 | MPa | float32
N2DCS.20PAC11AP001I | 6165 | #3循环水泵电机电流 |  | float32
N2DCS.20PAC11CP101 | 6166 | #3循环水泵出口压力 |  | float32
N2DCS.20PAC11CS101 | 6167 | #3循环水泵转速 |  | float32
N2DCS.20PAC11CT301 | 6168 | #3循环水泵电机“U”绕组温度1 | ℃ | float32
N2DCS.20PAC11CT302 | 6169 | #3循环水泵电机“U”绕组温度2 | ℃ | float32
N2DCS.20PAC11CT303 | 6170 | #3循环水泵电机“V”绕组温度1 | ℃ | float32
N2DCS.20PAC11CT304 | 6171 | #3循环水泵电机“V”绕组温度2 | ℃ | float32
N2DCS.20PAC11CT305 | 6172 | #3循环水泵电机“W”绕组温度1 | ℃ | float32
N2DCS.20PAC11CT306 | 6173 | #3循环水泵电机“W”绕组温度2 | ℃ | float32
N2DCS.20PAC11CT307 | 6174 | #3循环水泵电机导轴瓦温度1 | ℃ | float32
N2DCS.20PAC11CT308 | 6175 | #3循环水泵电机导轴瓦温度2 | ℃ | float32
N2DCS.20PAC11CT309 | 6176 | #3循环水泵电机推力瓦温度1 | ℃ | float32
N2DCS.20PAC11CT310 | 6177 | #3循环水泵电机推力瓦温度2 | ℃ | float32
N2DCS.20PAC11CT311 | 6178 | #3循环水泵电机下轴承温度 | ℃ | float32
N2DCS.20PAC11CY101 | 6179 | #3循环水泵垂直方向振动 |  | float32
N2DCS.20PAC11CY102 | 6180 | #3循环水泵水平方向振动 |  | float32
N2DCS.20PAC12AP001I | 6181 | #4循环水泵电机电流 |  | float32
N2DCS.ACTUALSPEEDA | 6182 | Ovation Control Builder |  | float32
N2DCS.CIRPMPA_TPFO | 6183 | #3循环水泵跳闸首出(打包点位号) |  | float32
N2DCS.CIRWTRPMPA_SEQSPSTEP | 6184 | #3循环水泵停顺控步号 |  | float32
N2DCS.CIRWTRPMPA_SEQSPTIME1 | 6185 | #3循环水泵停顺控第1步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSPTIME2 | 6186 | #3循环水泵停顺控第2步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSPTIME3 | 6187 | #3循环水泵停顺控第3步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSPTIME4 | 6188 | #3循环水泵停顺控第4步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSPTIME5 | 6189 | Ovation Control Builder |  | float32
N2DCS.CIRWTRPMPA_SEQSTSTEP | 6190 | #3循环水泵启顺控步号 |  | float32
N2DCS.CIRWTRPMPA_SEQSTTIME1 | 6191 | #3循环水泵启顺控第1步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSTTIME2 | 6192 | #3循环水泵启顺控第2步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSTTIME3 | 6193 | #3循环水泵启顺控第3步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSTTIME4 | 6194 | #3循环水泵启顺控第4步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSTTIME5 | 6195 | #3循环水泵启顺控第5步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSTTIME6 | 6196 | #3循环水泵启顺控第6步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSTTIME7 | 6197 | #3循环水泵启顺控第7步剩余时间 |  | float32
N2DCS.CIRWTRPMPA_SEQSTTIME8 | 6198 | Ovation Control Builder |  | float32
N2DCS.CIRWTRPMPAFRMODETIME | 6199 | Ovation Control Builder |  | float32
N2DCS.CIRWTRSYS_SEQSTSTEP | 6200 | 循环水系统启顺控步号 |  | float32
N2DCS.CIRWTRSYS_SEQSTTIME1 | 6201 | 循环水系统启顺控第1步剩余时间 |  | float32
N2DCS.CIRWTRSYS_SEQSTTIME2 | 6202 | 循环水系统启顺控第2步剩余时间 |  | float32
N2DCS.CIRWTRSYS_SEQSTTIME3 | 6203 | 循环水系统启顺控第3步剩余时间 |  | float32
N2DCS.CIRWTRSYS_SEQSTTIME4 | 6204 | 循环水系统启顺控第4步剩余时间 |  | float32
N2DCS.CIRWTRSYS_SEQSTTIME5 | 6205 | Ovation Control Builder |  | float32
N2DCS.CNSRVACM | 6206 | 凝汽器真空（2选后） |  | float32
N2DCS.EHOILSYS_SEQSPSTEP | 6207 | EH油系统停顺控步号 |  | float32
N2DCS.EHOILSYS_SEQSPTIME1 | 6208 | EH油系统停顺控第1步剩余时间 |  | float32
N2DCS.EHOILSYS_SEQSPTIME2 | 6209 | EH油系统停顺控第2步剩余时间 |  | float32
N2DCS.EHOILSYS_SEQSTSTEP | 6210 | EH油系统启顺控步号 |  | float32
N2DCS.EHOILSYS_SEQSTTIME1 | 6211 | EH油系统启顺控第1步剩余时间 |  | float32
N2DCS.EHOILSYS_SEQSTTIME2 | 6212 | EH油系统启顺控第2步剩余时间 |  | float32
N2DCS.EHOILSYS_SEQSTTIME3 | 6213 | EH油系统启顺控第3步剩余时间 |  | float32
N2DCS.EHOILSYS_SEQSTTIME4 | 6214 | Ovation Control Builder |  | float32
N2DCS.EHOILSYS_SEQSTTIME5 | 6215 | Ovation Control Builder |  | float32
N2DCS.LUBOILBOXTEM | 6216 | #3机润滑油箱温度 |  | float32
N2DCS.ROTFLTRA_SEQSTSTEP | 6217 | #1旋转滤网冲洗顺控 |  | float32
N2DCS.ROTFLTRA_SEQSTTIME1 | 6218 | #1旋转滤网冲洗顺控第1步剩余时? |  | float32
N2DCS.ROTFLTRA_SEQSTTIME2 | 6219 | #1旋转滤网冲洗顺控第2步剩余时? |  | float32
N2DCS.ROTFLTRA_SEQSTTIME3 | 6220 | #1旋转滤网冲洗顺控第3步剩余时? |  | float32
N2DCS.ROTFLTRAFRBHDL | 6221 | #1旋转滤网前后液位差 |  | float32
N2DCS.TURBOILSYS_SEQSTSTEP | 6222 | #3机润滑油系统启顺控步号 |  | float32
N2DCS.TURBOILSYS_SEQSTTIME1 | 6223 | #3机滑油系统启顺控1步剩余时间 |  | float32
N2DCS.TURBOILSYS_SEQSTTIME2 | 6224 | #3机滑油系统启顺控2步剩余时间 |  | float32
N2DCS.TURBOILSYS_SEQSTTIME3 | 6225 | #3机滑油系统启顺控3步剩余时间 |  | float32
N2DCS.TURBOILSYS_SEQSTTIME4 | 6226 | #3机滑油系统启顺控4步剩余时间 |  | float32
N2DCS.TURBOILSYS_SEQSTTIME5 | 6227 | #3机滑油系统启顺控5步剩余时间 |  | float32
N2DCS.VACMPMPA_SEQSPSTEP | 6228 | #1真空泵停顺控步号 |  | float32
N2DCS.VACMPMPA_SEQSPTIME1 | 6229 | #1真空泵停顺控第1步剩余时间 |  | float32
N2DCS.VACMPMPA_SEQSPTIME2 | 6230 | #1真空泵停顺控第2步剩余时间 |  | float32
N2DCS.VACMPMPA_SEQSPTIME3 | 6231 | Ovation Control Builder |  | float32
N2DCS.VACMPMPA_SEQSTSTEP | 6232 | #1真空泵启顺控步号 |  | float32
N2DCS.VACMPMPA_SEQSTTIME1 | 6233 | #1真空泵启顺控第1步剩余时间 |  | float32
N2DCS.VACMPMPA_SEQSTTIME2 | 6234 | #1真空泵启顺控第2步剩余时间 |  | float32
N2DCS.VACMPMPA_SEQSTTIME3 | 6235 | #1真空泵启顺控第3步剩余时间 |  | float32
N2DCS.VACMPMPA_SEQSTTIME4 | 6236 | Ovation Control Builder |  | float32
N2DCS.VACMPMPA_SEQSTTIME5 | 6237 | Ovation Control Builder |  | float32
N2DCS.VACMPMPA_TPFO | 6238 | #1真空泵跳闸首出(打包点位号) |  | float32
N2DCS.VACMSYS_SEQSPSTEP | 6239 | 抽真空系统停顺控步号 |  | float32
N2DCS.VACMSYS_SEQSPTIME1 | 6240 | 抽真空系统停顺控第1步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSPTIME2 | 6241 | 抽真空系统停顺控第2步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSPTIME3 | 6242 | 抽真空系统停顺控第3步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSPTIME4 | 6243 | 抽真空系统停顺控第4步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSPTIME5 | 6244 | 抽真空系统停顺控第5步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSTSTEP | 6245 | 抽真空系统启顺控步号 |  | float32
N2DCS.VACMSYS_SEQSTTIME1 | 6246 | 抽真空系统启顺控第1步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSTTIME2 | 6247 | 抽真空系统启顺控第2步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSTTIME3 | 6248 | 抽真空系统启顺控第3步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSTTIME4 | 6249 | 抽真空系统启顺控第4步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSTTIME5 | 6250 | 抽真空系统启顺控第5步剩余时间 |  | float32
N2DCS.VACMSYS_SEQSTTIME6 | 6251 | 抽真空系统启顺控第6步剩余时间 |  | float32
N2DCS.20MAJ21CT312 | 6252 | #1真空泵后轴承温度 |  | float32
N2DCS.RHYCKMGYLBD | 6253 | Ovation Control Builder |  | float32
N2DCS.20MAJ22AP001I | 6254 | #2真空泵电机电流 | A | float32
N2DCS.20MAJ22CL501 | 6255 | #2真空泵汽水分离器 | mm | float32
N2DCS.20MAJ22CP101 | 6256 | #2真空泵进口手动门前绝对压力 | KPa | float32
N2DCS.20MAJ22CP102 | 6257 | #2真空泵进口蝶阀前后差压 | KPa | float32
N2DCS.20MAJ22CT301 | 6258 | #2真空泵电机定子线圈温度1 | ℃ | float32
N2DCS.20MAJ22CT302 | 6259 | #2真空泵电机定子线圈温度2 | ℃ | float32
N2DCS.20MAJ22CT303 | 6260 | #2真空泵电机定子线圈温度3 | ℃ | float32
N2DCS.20MAJ22CT304 | 6261 | #2真空泵电机定子线圈温度4 | ℃ | float32
N2DCS.20MAJ22CT305 | 6262 | #2真空泵电机定子线圈温度5 | ℃ | float32
N2DCS.20MAJ22CT306 | 6263 | #2真空泵电机定子线圈温度6 | ℃ | float32
N2DCS.20MAJ22CT307 | 6264 | #2真空泵电机前轴承温度 | ℃ | float32
N2DCS.20MAJ22CT308 | 6265 | #2真空泵电机后轴承温度 | ℃ | float32
N2DCS.20MAV10CT301 | 6266 | #3机润滑油箱温度 | ℃ | float32
N2DCS.20MAV10CT311 | 6267 | 润滑油箱温度 | ℃ | float32
N2DCS.20MAV21AP022I | 6268 | #2润滑油泵电机电流 | A | float32
N2DCS.20MAV24AP001I | 6269 | 应急滑油泵电机电流 | A | float32
N2DCS.20MAV32AP001I | 6270 | #2顶轴油泵电机电流 | A | float32
N2DCS.20MAV32CP101 | 6271 | #2顶轴油泵出口压力 | MPa | float32
N2DCS.20MAV35CP101 | 6272 | 顶轴油母管压力 | MPa | float32
N2DCS.20MAV35CT301 | 6273 | 顶轴油母管温度 | ℃ | float32
N2DCS.20MAV42CT301 | 6274 | #3机润滑油温控阀后温度 | ℃ | float32
N2DCS.20MAV82AN002I | 6275 | #3机#2润滑油风机电流 |  | float32
N2DCS.20MAV82CP101 | 6276 | #3机润滑油风机进口压力 | MPa | float32
N2DCS.20MAX01AP002I | 6277 | #2EH油泵电机电流 | A | float32
N2DCS.20MAX01AP012I | 6278 | #2EH油循环泵电机电流 | A | float32
N2DCS.20MAX01CL101 | 6279 | #3机EH油箱液位 | mm | float32
N2DCS.20MAX01CP101 | 6280 | EH油供油压力1 | MPa | float32
N2DCS.20MAX01CP102 | 6281 | EH油供油压力2 | MPa | float32
N2DCS.20MAX01CP103 | 6282 | EH油供油压力3 | MPa | float32
N2DCS.20MAX01CT301 | 6283 | #3机EH油箱油温 | ℃ | float32
N2DCS.20MKA10CT301 | 6284 | #3发电机定子线圈温度1(5号槽) | ℃ | float32
N2DCS.20MKA10CT302 | 6285 | #3发电机定子线圈温度2(5号槽) | ℃ | float32
N2DCS.20MKA10CT303 | 6286 | #3发电机定子线圈温度1(6号槽) | ℃ | float32
N2DCS.20MKA10CT304 | 6287 | #3发电机定子线圈温度2(6号槽) | ℃ | float32
N2DCS.20MKA10CT305 | 6288 | #3发电机定子线圈温度1(14号槽) | ℃ | float32
N2DCS.20MKA10CT306 | 6289 | #3发电机定子线圈温度2(14号槽) | ℃ | float32
N2DCS.20MKA10CT307 | 6290 | #3发电机定子线圈温度1(15号槽) | ℃ | float32
N2DCS.20MKA10CT308 | 6291 | #3发电机定子线圈温度2(15号槽) | ℃ | float32
N2DCS.20MKA10CT309 | 6292 | #3发电机定子线圈温度1(23号槽) | ℃ | float32
N2DCS.20MKA10CT310 | 6293 | #3发电机定子线圈温度2(23号槽) | ℃ | float32
N2DCS.20MKA10CT311 | 6294 | #3发电机定子线圈温度1(24号槽) | ℃ | float32
N2DCS.20MKA10CT312 | 6295 | #3发电机定子线圈温度2(24号槽) | ℃ | float32
N2DCS.20MKA10CT313 | 6296 | #3发电机定子线圈温度1(32号槽) | ℃ | float32
N2DCS.20MKA10CT314 | 6297 | #3发电机定子线圈温度2(32号槽) | ℃ | float32
N2DCS.20MKA10CT315 | 6298 | #3发电机定子线圈温度1(33号槽) | ℃ | float32
N2DCS.20MKA10CT316 | 6299 | #3发电机定子线圈温度2(33号槽) | ℃ | float32
N2DCS.20MKA10CT317 | 6300 | #3发电机定子线圈温度1(41号槽) | ℃ | float32
N2DCS.20MKA10CT318 | 6301 | #3发电机定子线圈温度2(41号槽) | ℃ | float32
N2DCS.20MKA10CT319 | 6302 | #3发电机定子线圈温度1(42号槽) | ℃ | float32
N2DCS.20MKA10CT320 | 6303 | #3发电机定子线圈温度2(42号槽) | ℃ | float32
N2DCS.20MKA10CT321 | 6304 | #3发电机定子线圈温度1(50号槽) | ℃ | float32
N2DCS.20MKA10CT322 | 6305 | #3发电机定子线圈温度2(50号槽) | ℃ | float32
N2DCS.20MKA10CT323 | 6306 | #3发电机定子线圈温度1(51号槽) | ℃ | float32
N2DCS.20MKA10CT324 | 6307 | #3发电机定子线圈温度2(51号槽) | ℃ | float32
N2DCS.20MKA20CT301 | 6308 | #3发电机定子轭部温度1(2~3号槽) | ℃ | float32
N2DCS.20MKA20CT302 | 6309 | #3发电机定子轭部温度2(2~3号槽) | ℃ | float32
N2DCS.20MKA20CT303 | 6310 | #3发电机定子齿部温度1(2~3号槽) | ℃ | float32
N2DCS.20MKA20CT304 | 6311 | #3发电机定子齿部温度2(2~3号槽) | ℃ | float32
N2DCS.20MKA20CT305 | 6312 | #3发电机定子轭部温度1(26~27槽) | ℃ | float32
N2DCS.20MKA20CT306 | 6313 | #3发电机定子轭部温度2(26~27槽) | ℃ | float32
N2DCS.20MKA20CT307 | 6314 | #3发电机定子齿部温度1(26~27槽) | ℃ | float32
N2DCS.20MKA20CT308 | 6315 | #3发电机定子齿部温度2(26~27槽) | ℃ | float32
N2DCS.20MKA20CT309 | 6316 | #3发电机定子轭部温度1(44~45槽) | ℃ | float32
N2DCS.20MKA20CT310 | 6317 | #3发电机定子轭部温度2(44~45槽) | ℃ | float32
N2DCS.20MKA20CT311 | 6318 | #3发电机定子齿部温度1(44~45槽) | ℃ | float32
N2DCS.20MKA20CT312 | 6319 | #3发电机定子齿部温度2(44~45槽) | ℃ | float32
N2DCS.20MKA20CT313 | 6320 | #3发电机定子轭部温度3(2~3号槽) | ℃ | float32
N2DCS.20MKA20CT314 | 6321 | #3发电机定子轭部温度4(2~3号槽) | ℃ | float32
N2DCS.20MKA20CT315 | 6322 | #3发电机定子齿部温度3(2~3号槽) | ℃ | float32
N2DCS.20MKA20CT316 | 6323 | #3发电机定子齿部温度4(2~3号槽) | ℃ | float32
N2DCS.20MKA20CT317 | 6324 | #3发电机定子轭部温度3(26~27槽) | ℃ | float32
N2DCS.20MKA20CT318 | 6325 | #3发电机定子轭部温度4(26~27槽) | ℃ | float32
N2DCS.20MKA20CT319 | 6326 | #3发电机定子齿部温度3(26~27槽) | ℃ | float32
N2DCS.20MKA20CT320 | 6327 | #3发电机定子齿部温度4(26~27槽) | ℃ | float32
N2DCS.20MKA20CT321 | 6328 | #3发电机定子轭部温度3(44~45槽) | ℃ | float32
N2DCS.20MKA20CT322 | 6329 | #3发电机定子轭部温度4(44~45槽) | ℃ | float32
N2DCS.20MKA20CT323 | 6330 | #3发电机定子齿部温度3(44~45槽) | ℃ | float32
N2DCS.20MKA20CT324 | 6331 | #3发电机定子齿部温度4(44~45槽) | ℃ | float32
N2DCS.20MKA30CT301 | 6332 | #3发电机励端进风温度1 | ℃ | float32
N2DCS.20MKA30CT302 | 6333 | #3发电机励端进风温度2 | ℃ | float32
N2DCS.20MKA30CT303 | 6334 | #3发电机中部出风温度1 | ℃ | float32
N2DCS.20MKA30CT304 | 6335 | #3发电机中部出风温度2 | ℃ | float32
N2DCS.20MKA30CT305 | 6336 | #3发电机中部出风温度3 | ℃ | float32
N2DCS.20MKA30CT306 | 6337 | #3发电机中部出风温度4 | ℃ | float32
N2DCS.20MKA30CT307 | 6338 | #3发电机中部出风温度5 | ℃ | float32
N2DCS.20MKA30CT308 | 6339 | #3发电机中部出风温度6 | ℃ | float32
N2DCS.20MKA30CT309 | 6340 | #3发电机汽端进风温度1 | ℃ | float32
N2DCS.20MKA30CT310 | 6341 | #3发电机汽端进风温度2 | ℃ | float32
N2DCS.20MKA30CT311 | 6342 | #3发电机励端进风温度3 | ℃ | float32
N2DCS.20MKA30CT312 | 6343 | #3发电机励端进风温度4 | ℃ | float32
N2DCS.20MKA30CT313 | 6344 | #3发电机汽端进风温度3 | ℃ | float32
N2DCS.20MKA30CT314 | 6345 | #3发电机汽端进风温度4 | ℃ | float32
N2DCS.20PAB10CP101 | 6346 | 第二套机组循环水泵出口母管压力 |  | float32
N2DCS.20PAB10CP101AO | 6347 | 循环水泵出口母管压力(至公用) | % | float32
N2DCS.20PAB11CL111AO | 6348 | 旋转滤网前后水位差(至公用) | % | float32
N2DCS.20PAB12AA002CT | 6349 | #4循环水泵出口液控蝶阀油箱油温 | ℃ | float32
N2DCS.20PAB12AA002P1 | 6350 | #4循环水泵出口液控阀蓄能器压力 | MPa | float32
N2DCS.20PAB12AA002P2 | 6351 | #4循环水泵出口液控蝶阀A口油压 | MPa | float32
N2DCS.20PAB12AA002P3 | 6352 | #4循环水泵出口液控蝶阀B口油压 | MPa | float32
N2DCS.20PAB12CL104 | 6353 | #2旋转滤网前水位 | m | float32
N2DCS.20PAB12CL105 | 6354 | #2旋转滤网后水位 | m | float32
N2DCS.20PAB12CP1016 | 6355 | #4循环水泵出口母管压力 |  | float32
N2DCS.20PAB53CP101 | 6356 | #4循环水泵冷却水进口母管压力 | MPa | float32
N2DCS.20PAC12CP101 | 6357 | #4循环水泵出口压力 |  | float32
N2DCS.20PAC12CS101 | 6358 | #4循环水泵转速 |  | float32
N2DCS.20PAC12CT301 | 6359 | #4循环水泵电机“U”绕组温度1 | ℃ | float32
N2DCS.20PAC12CT302 | 6360 | #4循环水泵电机“U”绕组温度2 | ℃ | float32
N2DCS.20PAC12CT303 | 6361 | #4循环水泵电机“V”绕组温度1 | ℃ | float32
N2DCS.20PAC12CT304 | 6362 | #4循环水泵电机“V”绕组温度2 | ℃ | float32
N2DCS.20PAC12CT305 | 6363 | #4循环水泵电机“W”绕组温度1 | ℃ | float32
N2DCS.20PAC12CT306 | 6364 | #4循环水泵电机“W”绕组温度2 | ℃ | float32
N2DCS.20PAC12CT307 | 6365 | #4循环水泵电机导轴瓦温度1 | ℃ | float32
N2DCS.20PAC12CT308 | 6366 | #4循环水泵电机导轴瓦温度2 | ℃ | float32
N2DCS.20PAC12CT309 | 6367 | #4循环水泵电机推力瓦温度1 | ℃ | float32
N2DCS.20PAC12CT310 | 6368 | #4循环水泵电机推力瓦温度2 | ℃ | float32
N2DCS.20PAC12CT311 | 6369 | #4循环水泵电机下轴承温度 | ℃ | float32
N2DCS.20PAC12CY101 | 6370 | #4循环水泵垂直方向振动 |  | float32
N2DCS.20PAC12CY102 | 6371 | #4循环水泵水平方向振动 |  | float32
N2DCS.20PAR01AA002C | 6372 | #2冷却塔进水流量调节阀控制指令 | % | float32
N2DCS.20PAR01AA002P | 6373 | #2冷却塔进水流量调节阀阀位反馈 | % | float32
N2DCS.20PAR01AA002SP | 6374 | #2冷却塔进水流量调节阀流量设定 |  | float32
N2DCS.20PAR01CF101 | 6375 | #2冷却塔进口流量 | kpa | float32
N2DCS.20PSA01CF101 | 6376 | #2冷却塔排水池出口流量 | kpa | float32
N2DCS.20PSA01CL101 | 6377 | #2冷却塔排水池液位 | m | float32
N2DCS.CIRPMPB_TPFO | 6378 | #4循环水泵跳闸首出(打包点位号) |  | float32
N2DCS.CIRWTRPMPB_SEQSPSTEP | 6379 | #4循环水泵停顺控步号 |  | float32
N2DCS.CIRWTRPMPB_SEQSPTIME1 | 6380 | #4循环水泵停顺控第1步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSPTIME2 | 6381 | #4循环水泵停顺控第2步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSPTIME3 | 6382 | #4循环水泵停顺控第3步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSPTIME4 | 6383 | #4循环水泵停顺控第4步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSPTIME5 | 6384 | Ovation Control Builder |  | float32
N2DCS.CIRWTRPMPB_SEQSTSTEP | 6385 | #4循环水泵启顺控步号 |  | float32
N2DCS.CIRWTRPMPB_SEQSTTIME1 | 6386 | #4循环水泵启顺控第1步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSTTIME2 | 6387 | #4循环水泵启顺控第2步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSTTIME3 | 6388 | #4循环水泵启顺控第3步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSTTIME4 | 6389 | #4循环水泵启顺控第4步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSTTIME5 | 6390 | #4循环水泵启顺控第5步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSTTIME6 | 6391 | #4循环水泵启顺控第6步剩余时间 |  | float32
N2DCS.CIRWTRPMPB_SEQSTTIME7 | 6392 | #4循环水泵启顺控第7步剩余时间 |  | float32
N2DCS.CIRWTRPMPBFRMODETIME | 6393 | Ovation Control Builder |  | float32
N2DCS.CLEANOILBOXLVL | 6394 | 第二套机组净油箱液位（2选后） |  | float32
N2DCS.EHOILSPLPRS | 6395 | #3机EH油泵供油压力 |  | float32
N2DCS.J0MAV30CL101 | 6396 | 第二套机组净油箱液位1 | mm | float32
N2DCS.J0MAV30CL102 | 6397 | 第二套机组净油箱液位2 | mm | float32
N2DCS.J0MAV30CL111 | 6398 | 第二套机组污油箱液位1 | mm | float32
N2DCS.J0MAV30CL112 | 6399 | 第二套机组污油箱液位2 | mm | float32
N2DCS.LQTBSLL | 6400 | #2冷却塔进口流量（计算后） | t/h | float32
N2DCS.LQTPSLL | 6401 | #2冷却塔排水池出口流量(计算后) | t/h | float32
N2DCS.ROTFLTRB_SEQSTSTEP | 6402 | #2旋转滤网冲洗顺控 |  | float32
N2DCS.ROTFLTRB_SEQSTTIME1 | 6403 | #2旋转滤网冲洗顺控第1步剩余时? |  | float32
N2DCS.ROTFLTRB_SEQSTTIME2 | 6404 | #2旋转滤网冲洗顺控第2步剩余时? |  | float32
N2DCS.ROTFLTRB_SEQSTTIME3 | 6405 | #2旋转滤网冲洗顺控第3步剩余时? |  | float32
N2DCS.RSTA30015 | 6406 |  |  | float32
N2DCS.SPINFLTRBFRBHDL | 6407 | #2旋转滤网前后液位差 |  | float32
N2DCS.VACMPMPB_SEQSPSTEP | 6408 | #2真空泵停顺控步号 |  | float32
N2DCS.VACMPMPB_SEQSPTIME1 | 6409 | #2真空泵停顺控第1步剩余时间 |  | float32
N2DCS.VACMPMPB_SEQSPTIME2 | 6410 | #2真空泵停顺控第2步剩余时间 |  | float32
N2DCS.VACMPMPB_SEQSPTIME3 | 6411 | Ovation Control Builder |  | float32
N2DCS.VACMPMPB_SEQSTSTEP | 6412 | #2真空泵启顺控步号 |  | float32
N2DCS.VACMPMPB_SEQSTTIME1 | 6413 | #2真空泵启顺控第1步剩余时间 |  | float32
N2DCS.VACMPMPB_SEQSTTIME2 | 6414 | #2真空泵启顺控第2步剩余时间 |  | float32
N2DCS.VACMPMPB_SEQSTTIME3 | 6415 | #2真空泵启顺控第3步剩余时间 |  | float32
N2DCS.VACMPMPB_TPFO | 6416 | #2真空泵跳闸首出(打包点位号) |  | float32
N2DCS.20MAJ22CT311 | 6417 | #2真空泵前轴承温度 | ℃ | float32
N2DCS.20MAJ22CT312 | 6418 | #2真空泵后轴承温度 | ℃ | float32
N2DCS.20MYA01CS901CA | 6419 | #4机实际转速 |  | float32
N2DCS.20HAD70CL001 | 6420 | 低压汽包左电接点液位 |  | float32
N2DCS.20HAD70CL002 | 6421 | 低压汽包右电接点液位 |  | float32
N2DCS.20HAD70CL101 | 6422 | 低压汽包液位1 | KPa | float32
N2DCS.20HAD70CL102 | 6423 | 低压汽包液位2 | mmH2O | float32
N2DCS.20HAD70CL103 | 6424 | 低压汽包液位3 | mmH2O | float32
N2DCS.20HAD70CP101 | 6425 | 低压汽包压力1 | MPa | float32
N2DCS.20HAD70CP102 | 6426 | 低压汽包压力2 | MPa | float32
N2DCS.20HAD70CP103 | 6427 | 低压汽包压力3 | MPa | float32
N2DCS.20HAD70CT301 | 6428 | 低压汽包上壁温1 | ℃ | float32
N2DCS.20HAD70CT302 | 6429 | 低压汽包上壁温2 | ℃ | float32
N2DCS.20HAD70CT303 | 6430 | 低压汽包上壁温3 | ℃ | float32
N2DCS.20HAD70CT304 | 6431 | 低压汽包下壁温1 | ℃ | float32
N2DCS.20HAD70CT305 | 6432 | 低压汽包下壁温2 | ℃ | float32
N2DCS.20HAD70CT306 | 6433 | 低压汽包下壁温3 | ℃ | float32
N2DCS.20HAD74AA401P | 6434 | 低压蒸发器排污至定排门门位开度 |  | float32
N2DCS.20HAD75AA101C | 6435 | 低压汽包连排电动调节门阀位指令 | % | float32
N2DCS.20HAD75AA101P | 6436 | 低压汽包连排电动调节门阀位反馈 |  | float32
N2DCS.20HAD76AA001P | 6437 | 低压汽包启动放水电动门门位反馈 |  | float32
N2DCS.20HAD76AA002P | 6438 | 低压汽包启动放水调节阀阀位反馈 |  | float32
N2DCS.20HAJ81CT301 | 6439 | 一级再热器减温器后温度1 | ℃ | float32
N2DCS.20HAJ81CT302 | 6440 | 一级再热器减温器后温度2 | ℃ | float32
N2DCS.20HAJ81CT303 | 6441 | 一级再热器减温器后温度3 | ℃ | float32
N2DCS.20HAJ81CT304 | 6442 | 一级再热器减温器前温度 | ℃ | float32
N2DCS.20HNA70CP101 | 6443 | HRSG进口烟气压力 | KPa | float32
N2DCS.20HNA80CP103 | 6444 | 低压省煤器出口烟气压力 | KPa | float32
N2DCS.20HNA80CT303 | 6445 | 一级再热器进口烟气温度1 | ℃ | float32
N2DCS.20HNA80CT304 | 6446 | 一级再热器进口烟气温度2 | ℃ | float32
N2DCS.20LAA70AA501P | 6447 | #3炉除氧头放空电动门 |  | float32
N2DCS.20LAA70CP101 | 6448 | 除氧头压力 | MPa | float32
N2DCS.20LAB70AA101C | 6449 | 低压给水调节阀阀位控制指令 | % | float32
N2DCS.20LAB70AA101P | 6450 | 低压给水调节阀阀位反馈 |  | float32
N2DCS.20LAB70CF101 | 6451 | 低压汽包给水流量1 | KPa | float32
N2DCS.20LAB70CF102 | 6452 | 低压汽包给水流量2 | KPa | float32
N2DCS.20LAB70CF103 | 6453 | 低压汽包给水流量3 | KPa | float32
N2DCS.20LAB70CP101 | 6454 | 低压省煤器出口压力 | MPa | float32
N2DCS.20LAB70CT301 | 6455 | 低压省煤器出口温度1 | ℃ | float32
N2DCS.20LAB70CT302 | 6456 | 低压省煤器出口温度2 | ℃ | float32
N2DCS.20LAB70CT303 | 6457 | 低压省煤器出口温度3 | ℃ | float32
N2DCS.20LAF80AA101_SPO | 6458 | Ovation Control Builder |  | float32
N2DCS.20LAF80AA101C | 6459 | 一级再热器减温水调节阀控制指令 | % | float32
N2DCS.20LAF80AA101P | 6460 | 一级再热器减温水调节阀阀位反馈 |  | float32
N2DCS.20LAF80AA102_SPO | 6461 | Ovation Control Builder |  | float32
N2DCS.20LAF80AA102C | 6462 | 二级再热器减温水调节阀控制指令 | % | float32
N2DCS.20LAF80AA102P | 6463 | 二级再热器减温水调节阀阀位反馈 |  | float32
N2DCS.20LAF80CF101 | 6464 | 再热器减温水流量 | KPa | float32
N2DCS.20LBA70AA502P | 6465 | 低压过热器启动排汽门阀位反馈 |  | float32
N2DCS.20LBA70CF101 | 6466 | 低压主蒸汽蒸汽流量1 | KPa | float32
N2DCS.20LBA70CF102 | 6467 | 低压主蒸汽蒸汽流量2 | KPa | float32
N2DCS.20LBA70CF103 | 6468 | 低压主蒸汽蒸汽流量3 | KPa | float32
N2DCS.20LBA70CP101 | 6469 | 低压主蒸汽压力1 | MPa | float32
N2DCS.20LBA70CP102 | 6470 | 低压主蒸汽压力2 | MPa | float32
N2DCS.20LBA70CP103 | 6471 | 低压主蒸汽压力3 | MPa | float32
N2DCS.20LBA70CT301 | 6472 | 低压主蒸汽温度1 | ℃ | float32
N2DCS.20LBA70CT302 | 6473 | 低压主蒸汽温度2 | ℃ | float32
N2DCS.20LBA70CT303 | 6474 | 低压主蒸汽温度3 | ℃ | float32
N2DCS.20LBB80AA502P | 6475 | 热再主蒸汽启动排汽门阀位反馈 |  | float32
N2DCS.20LBB80CP101 | 6476 | 热再主蒸汽压力1 | MPa | float32
N2DCS.20LBB80CP102 | 6477 | 热再主蒸汽压力2 | MPa | float32
N2DCS.20LBB80CP103 | 6478 | 热再主蒸汽压力3 | MPa | float32
N2DCS.20LBB80CT301 | 6479 | 热再主蒸汽温度1 | ℃ | float32
N2DCS.20LBB80CT302 | 6480 | 热再主蒸汽温度2 | ℃ | float32
N2DCS.20LBB80CT303 | 6481 | 热再主蒸汽温度3 | ℃ | float32
N2DCS.20LBC80CP101 | 6482 | 高排至冷再进口蒸汽压力 | MPa | float32
N2DCS.20LBC80CP102 | 6483 | 一级再热器进口压力 | MPa | float32
N2DCS.20LBC80CT301 | 6484 | 高排至冷再进口蒸汽温度 | ℃ | float32
N2DCS.20LBC80CT302 | 6485 | 一级再热器进口蒸汽温度 | ℃ | float32
N2DCS.20LBG70AA101_SPO | 6486 | Ovation Control Builder |  | float32
N2DCS.20LBG70AA101C | 6487 | 辅汽至#3炉除氧头调节阀控制指令 | % | float32
N2DCS.20LBG70AA101P | 6488 | 辅汽至#3炉除氧头调节阀阀位反馈 |  | float32
N2DCS.20LBG70CP101 | 6489 | 辅汽至#3炉除氧头进口压力 | MPa | float32
N2DCS.20LBG70CT301 | 6490 | 辅汽至#3炉除氧头进口温度 | ℃ | float32
N2DCS.20LCA70CP101 | 6491 | 低压省煤器给水压力（混合前） | MPa | float32
N2DCS.20LCA70CP102 | 6492 | 低压省煤器进口压力（混合后） | MPa | float32
N2DCS.20LCA70CT301 | 6493 | 低压省煤器给水温度（混合前） | ℃ | float32
N2DCS.20LCA70CT302 | 6494 | 低压省煤器进口温度（混合后） | ℃ | float32
N2DCS.20LCC71AA101_SPO | 6495 | Ovation Control Builder |  | float32
N2DCS.20LCC71AA101C | 6496 | 低省再循环泵出口调阀控制指令 | % | float32
N2DCS.20LCC71AA101P | 6497 | 低省再循环泵出口调阀阀位反馈 |  | float32
N2DCS.20LCC72AP001I | 6498 | 低压省煤器#1再循环泵电流 |  | float32
N2DCS.20LCC72CP101 | 6499 | 低压省煤器#1再循环泵出口压力 | MPa | float32
N2DCS.20LCC72CT301 | 6500 | #1再循环泵电机驱动端轴承温度 | ℃ | float32
N2DCS.20LCC72CT302 | 6501 | #1再循环泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20LCC72CT303 | 6502 | #1再循环泵电机“W”绕组温度1 | ℃ | float32
N2DCS.20LCC72CT304 | 6503 | #1再循环泵电机“W”绕组温度2 | ℃ | float32
N2DCS.20LCC72CT305 | 6504 | #1再循环泵电机“V”绕组温度1 | ℃ | float32
N2DCS.20LCC72CT306 | 6505 | #1再循环泵电机“V”绕组温度2 | ℃ | float32
N2DCS.20LCC72CT307 | 6506 | #1再循环泵电机“U”绕组温度1 | ℃ | float32
N2DCS.20LCC72CT308 | 6507 | #1再循环泵电机“U”绕组温度2 | ℃ | float32
N2DCS.20LCC72DP101 | 6508 | #1再循环泵进口过滤器前后差压 | KPa | float32
N2DCS.20LCC73AP001I | 6509 | 低压省煤器#2再循环泵电流 |  | float32
N2DCS.20LCC73CP101 | 6510 | 低压省煤器#2再循环泵出口压力 | MPa | float32
N2DCS.20LCC73CT301 | 6511 | #2再循环泵电机驱动端轴承温度 | ℃ | float32
N2DCS.20LCC73CT302 | 6512 | #2再循环泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20LCC73CT303 | 6513 | #2再循环泵电机“W”绕组温度1 | ℃ | float32
N2DCS.20LCC73CT304 | 6514 | #2再循环泵电机“W”绕组温度2 | ℃ | float32
N2DCS.20LCC73CT305 | 6515 | #2再循环泵电机“V”绕组温度1 | ℃ | float32
N2DCS.20LCC73CT306 | 6516 | #2再循环泵电机“V”绕组温度2 | ℃ | float32
N2DCS.20LCC73CT307 | 6517 | #2再循环泵电机“U”绕组温度1 | ℃ | float32
N2DCS.20LCC73CT308 | 6518 | #2再循环泵电机“U”绕组温度2 | ℃ | float32
N2DCS.20LCC73DP101 | 6519 | #2再循环泵进口过滤器前后差压 | KPa | float32
N2DCS.20LCQ74AA101_SPO | 6520 | Ovation Control Builder |  | float32
N2DCS.20LCQ74AA101C | 6521 | 连排至定排气动调节阀控制指令 | % | float32
N2DCS.20LCQ74AA101P | 6522 | 连排至定排气动调节阀阀位反馈 |  | float32
N2DCS.D7P1B1L3C9 | 6523 | TC温度补偿点 | C | float32
N2DCS.D7P1B2L6C9 | 6524 | TC温度补偿点 | C | float32
N2DCS.LPDRUMCP | 6525 | 低压汽包压力（3选后） |  | float32
N2DCS.LPDRUMCTD | 6526 | 低压汽包下壁温（3选后） |  | float32
N2DCS.LPDRUMCTU | 6527 | 低压汽包上壁温（3选后） |  | float32
N2DCS.LPDRUMLVL | 6528 | 低压汽包液位(计算后) |  | float32
N2DCS.LPDRUMLVL_A | 6529 | 低压汽包液位1(计算后) |  | float32
N2DCS.LPDRUMLVL_B | 6530 | 低压汽包液位2(计算后) |  | float32
N2DCS.LPDRUMLVL_C | 6531 | 低压汽包液位3(计算后) |  | float32
N2DCS.LPDRUMLVL_DIF | 6532 | 低压汽包液位(计算后) |  | float32
N2DCS.LPDRUMLVL_SP | 6533 | 低压汽包液位最终设定值 |  | float32
N2DCS.LPDRUMLVL_SP1 | 6534 | 低压汽包液位设定值 |  | float32
N2DCS.LPDSTCF | 6535 | 低压主蒸汽蒸汽流量（3选后） |  | float32
N2DCS.LPDSTCF_A | 6536 | 低压主蒸汽蒸汽流量1（计算后） |  | float32
N2DCS.LPDSTCF_B | 6537 | 低压主蒸汽蒸汽流量2（计算后） |  | float32
N2DCS.LPDSTCF_C | 6538 | 低压主蒸汽蒸汽流量3（计算后） |  | float32
N2DCS.LPDSTCP | 6539 | 低压主蒸汽压力（3选后） |  | float32
N2DCS.LPDSTCT | 6540 | 低压主蒸汽温度（3选后） |  | float32
N2DCS.LPDWTCF | 6541 | 低压汽包给水流量（3选后） |  | float32
N2DCS.LPDWTCF_A | 6542 | 低压汽包给水流量1（计算后） |  | float32
N2DCS.LPDWTCF_B | 6543 | 低压汽包给水流量2（计算后） |  | float32
N2DCS.LPDWTCF_C | 6544 | 低压汽包给水流量3（计算后） |  | float32
N2DCS.LPDWTCT | 6545 | 低压省煤器出口温度（计算后） |  | float32
N2DCS.LPECON_SEQSTSTEP | 6546 | 再循环泵功能组启顺控步号 |  | float32
N2DCS.LPECON_SEQSTTIME1 | 6547 | 再循环泵启顺控第1步剩余时间 |  | float32
N2DCS.LPECON_SEQSTTIME2 | 6548 | 再循环泵启顺控第2步剩余时间 |  | float32
N2DCS.LPECON_SEQSTTIME3 | 6549 | 再循环泵启顺控第3步剩余时间 |  | float32
N2DCS.LPECONPA_SEQSPSTEP | 6550 | #1再循环泵停顺控步号 |  | float32
N2DCS.LPECONPA_SEQSPTIME1 | 6551 | #1再循环泵停顺控第1步剩余时间 |  | float32
N2DCS.LPECONPA_SEQSPTIME2 | 6552 | #1再循环泵停顺控第2步剩余时间 |  | float32
N2DCS.LPECONPA_SEQSTSTEP | 6553 | #1再循环泵启顺控步号 |  | float32
N2DCS.LPECONPA_SEQSTTIME1 | 6554 | #1再循环泵启顺控第1步剩余时间 |  | float32
N2DCS.LPECONPA_SEQSTTIME2 | 6555 | #1再循环泵启顺控第2步剩余时间 |  | float32
N2DCS.LPECONPA_SEQSTTIME3 | 6556 | #1再循环泵启顺控第3步剩余时间 |  | float32
N2DCS.LPECONPA_TPFO | 6557 | #1再循环泵跳闸首出(打包点位号) |  | float32
N2DCS.LPECONPB_SEQSPSTEP | 6558 | #2再循环泵停顺控步号 |  | float32
N2DCS.LPECONPB_SEQSPTIME1 | 6559 | #2再循环泵停顺控第1步剩余时间 |  | float32
N2DCS.LPECONPB_SEQSPTIME2 | 6560 | #2再循环泵停顺控第2步剩余时间 |  | float32
N2DCS.LPECONPB_SEQSTSTEP | 6561 | #2再循环泵启顺控步号 |  | float32
N2DCS.LPECONPB_SEQSTTIME1 | 6562 | #2再循环泵启顺控第1步剩余时间 |  | float32
N2DCS.LPECONPB_SEQSTTIME2 | 6563 | #2再循环泵启顺控第2步剩余时间 |  | float32
N2DCS.LPECONPB_SEQSTTIME3 | 6564 | #2再循环泵启顺控第3步剩余时间 |  | float32
N2DCS.LPECONPB_TPFO | 6565 | #2再循环泵跳闸首出(打包点位号) |  | float32
N2DCS.LPFW_BIASO | 6566 | Ovation Control Builder |  | float32
N2DCS.LPFW_SEQSTSTEP | 6567 | 低压汽包上水顺控步号 |  | float32
N2DCS.LPFW_SEQSTTIME1 | 6568 | 低压汽包上水顺控第1步剩余时间 |  | float32
N2DCS.LPFW_SEQSTTIME2 | 6569 | 低压汽包上水顺控第2步剩余时间 |  | float32
N2DCS.LPFW_SEQSTTIME3 | 6570 | 低压汽包上水顺控第3步剩余时间 |  | float32
N2DCS.LPFW_SEQSTTIME4 | 6571 | 低压汽包上水顺控第4步剩余时间 |  | float32
N2DCS.LPFW_SEQSTTIME5 | 6572 | 低压汽包上水顺控第5步剩余时间 |  | float32
N2DCS.LPMS_SEQSTSTEP | 6573 | 低压主汽升温升压顺控步号 |  | float32
N2DCS.LPMS_SEQSTTIME1 | 6574 | 低压主汽升温升压顺控1步剩时间 |  | float32
N2DCS.LPMS_SEQSTTIME2 | 6575 | 低压主汽升温升压顺控2步剩时间 |  | float32
N2DCS.LPMS_SEQSTTIME3 | 6576 | 低压主汽升温升压顺控3步剩时间 |  | float32
N2DCS.LPMS_SEQSTTIME4 | 6577 | 低压主汽升温升压顺控4步剩时间 |  | float32
N2DCS.LPMS_SEQSTTIME5 | 6578 | 低压主汽升温升压顺控5步剩时间 |  | float32
N2DCS.LPMS_SEQSTTIME6 | 6579 | 低压主汽升温升压顺控6步剩时间 |  | float32
N2DCS.LPMS_SEQSTTIME7 | 6580 | 低压主汽升温升压顺控7步剩时间 |  | float32
N2DCS.RH2INSTCT | 6581 | 一级再热器减温器后温度（3选后) |  | float32
N2DCS.RH2OUTSTCP | 6582 | 热再主蒸汽压力(3选后） |  | float32
N2DCS.RH2OUTSTCT | 6583 | 热再主蒸汽温度(3选后） |  | float32
N2DCS.SEQTEST_SEQSTSTEP | 6584 | Ovation Control Builder |  | float32
N2DCS.SEQTEST_SEQSTTIME1 | 6585 | Ovation Control Builder |  | float32
N2DCS.SEQTEST_SEQSTTIME2 | 6586 | Ovation Control Builder |  | float32
N2DCS.SEQTEST_SEQSTTIME3 | 6587 | Ovation Control Builder |  | float32
N2DCS.SEQTEST_SEQSTTIME4 | 6588 | Ovation Control Builder |  | float32
N2DCS.SEQTEST_SEQSTTIME5 | 6589 | Ovation Control Builder |  | float32
N2DCS.SEQTEST_SEQSTTIME6 | 6590 | Ovation Control Builder |  | float32
N2DCS.SEQTEST_SEQSTTIME7 | 6591 | Ovation Control Builder |  | float32
N2DCS.SEQTEST_SEQSTTIME8 | 6592 | Ovation Control Builder |  | float32
N2DCS.20LAF80AA101_BIAS | 6593 | Ovation Control Builder |  | float32
N2DCS.20LAF80AA101_SP1 | 6594 | 一级再热器减温调阀最终温度设定 |  | float32
N2DCS.20LAF80AA101_SPB | 6595 | 一级再热器减温水调阀温度设定值 |  | float32
N2DCS.20LAF80AA102_BIAS | 6596 | Ovation Control Builder |  | float32
N2DCS.20LAF80AA102_SP1 | 6597 | 二级再热器减温调阀最终温度设定 |  | float32
N2DCS.20LAF80AA102_SPB | 6598 | 二级再热器减温水调阀温度设定值 |  | float32
N2DCS.20LAF80CF101I | 6599 | 再热器减温水流量（计算后） |  | float32
N2DCS.DYCGXS | 6600 | 低压汽包吹管系数 |  | float32
N2DCS.GYCGXS | 6601 | 高压汽包吹管系数 |  | float32
N2DCS.LPDRUMLVL_TRKN | 6602 | Ovation Control Builder |  | float32
N2DCS.LPDWTCF_SUM | 6603 | 低压汽包给水累计流量 |  | float32
N2DCS.ZYCGXS | 6604 | 中压汽包吹管系数 |  | float32
N2DCS.20CFE40CF101 | 6605 | 烟囱出口烟气流速差压 | Nm3/h | float32
N2DCS.20CFE40CM101 | 6606 | 烟囱出口湿氧 | % | float32
N2DCS.20CFE40CP101 | 6607 | 烟囱出口烟气压力 | Pa | float32
N2DCS.20CFE40CQ101 | 6608 | 烟囱出口NO含量 | mg/Nm3 | float32
N2DCS.20CFE40CQ102 | 6609 | 烟囱出口干氧 | % | float32
N2DCS.20CFE40CQ103 | 6610 | 烟囱出口SO2含量 | ppm | float32
N2DCS.20CFE40CQ104 | 6611 | 烟囱出口CO含量 | mg/Nm3 | float32
N2DCS.20CFE40CQ106 | 6612 | 烟囱出口粉尘含量 | % | float32
N2DCS.20CFE40CT101 | 6613 | 烟囱出口烟气温度 | ℃ | float32
N2DCS.20HAD80CL001 | 6614 | 中压汽包左电接点液位 |  | float32
N2DCS.20HAD80CL002 | 6615 | 中压汽包右电接点液位 |  | float32
N2DCS.20HAD80CL101 | 6616 | 中压汽包液位1 | mmH2O | float32
N2DCS.20HAD80CL102 | 6617 | 中压汽包液位2 | KPa | float32
N2DCS.20HAD80CL103 | 6618 | 中压汽包液位3 | mmH2O | float32
N2DCS.20HAD80CP101 | 6619 | 中压汽包压力1 | MPa | float32
N2DCS.20HAD80CP102 | 6620 | 中压汽包压力2 | MPa | float32
N2DCS.20HAD80CP103 | 6621 | 中压汽包压力3 | MPa | float32
N2DCS.20HAD80CT301 | 6622 | 中压汽包上壁温1 | ℃ | float32
N2DCS.20HAD80CT302 | 6623 | 中压汽包上壁温2 | ℃ | float32
N2DCS.20HAD80CT303 | 6624 | 中压汽包上壁温3 | ℃ | float32
N2DCS.20HAD80CT304 | 6625 | 中压汽包下壁温1 | ℃ | float32
N2DCS.20HAD80CT305 | 6626 | 中压汽包下壁温2 | ℃ | float32
N2DCS.20HAD80CT306 | 6627 | 中压汽包下壁温3 | ℃ | float32
N2DCS.20HAD84AA401P | 6628 | 中压蒸发器排污至定排门门位开度 |  | float32
N2DCS.20HAD85AA101C | 6629 | 中压汽包连排电动调节门阀位指令 | % | float32
N2DCS.20HAD85AA101P | 6630 | 中压汽包连排电动调节门阀位反馈 |  | float32
N2DCS.20HAD86AA001P | 6631 | 中压汽包启动放水电动门门位反馈 |  | float32
N2DCS.20HAD86AA002P | 6632 | 中压汽包启动放水调节阀阀位反馈 |  | float32
N2DCS.20HNA80CT307 | 6633 | 中压过热器进口烟气温度1 | ℃ | float32
N2DCS.20HNA80CT308 | 6634 | 中压过热器进口烟气温度2 | ℃ | float32
N2DCS.20HNA80CT311 | 6635 | 低压省煤器进口烟气温度1 | ℃ | float32
N2DCS.20HNA80CT312 | 6636 | 低压省煤器进口烟气温度2 | ℃ | float32
N2DCS.20HNA80CT313 | 6637 | 低压省煤器出口烟气温度1 | ℃ | float32
N2DCS.20HNA80CT314 | 6638 | 低压省煤器出口烟气温度2 | ℃ | float32
N2DCS.20HNE70CP101 | 6639 | 烟囱出口烟气压力 | KPa | float32
N2DCS.20LAB72CP101 | 6640 | #1中压给水泵进口压力 | MPa | float32
N2DCS.20LAB72DP101 | 6641 | #1中压给水泵进口过滤器差压 | KPa | float32
N2DCS.20LAB74CP101 | 6642 | #1高压给水泵进口压力 | MPa | float32
N2DCS.20LAB74DP101 | 6643 | #1高压给水泵进口过滤器差压 | KPa | float32
N2DCS.20LAB80CF101 | 6644 | 中压给水省煤器进口流量1 | KPa | float32
N2DCS.20LAB80CF102 | 6645 | 中压给水省煤器进口流量2 | KPa | float32
N2DCS.20LAB80CF103 | 6646 | 中压给水省煤器进口流量3 | KPa | float32
N2DCS.20LAB80CT301 | 6647 | 中压给水省煤器进口温度1 | ℃ | float32
N2DCS.20LAB80CT302 | 6648 | 中压给水省煤器进口温度2 | ℃ | float32
N2DCS.20LAB80CT303 | 6649 | 中压给水省煤器进口温度3 | ℃ | float32
N2DCS.20LAB81AP001I | 6650 | #1中压给水泵电流 |  | float32
N2DCS.20LAB81CP102 | 6651 | #1中压给水泵出口压力 | MPa | float32
N2DCS.20LAB81CT301 | 6652 | #1中给泵非驱动端径向轴承温度 | ℃ | float32
N2DCS.20LAB81CT302 | 6653 | #1中压给水泵驱动端径向轴承温度 | ℃ | float32
N2DCS.20LAB81CT303 | 6654 | #1中给泵电机驱动端径向轴承温度 | ℃ | float32
N2DCS.20LAB81CT304 | 6655 | #1中给泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20LAB81CT305 | 6656 | #1中压给水泵电机“W”绕组温度1 | ℃ | float32
N2DCS.20LAB81CT306 | 6657 | #1中压给水泵电机“W”绕组温度2 | ℃ | float32
N2DCS.20LAB81CT307 | 6658 | #1中压给水泵电机“V”绕组温度1 | ℃ | float32
N2DCS.20LAB81CT308 | 6659 | #1中压给水泵电机“V”绕组温度2 | ℃ | float32
N2DCS.20LAB81CT309 | 6660 | #1中压给水泵电机“U”绕组温度1 | ℃ | float32
N2DCS.20LAB81CT310 | 6661 | #1中压给水泵电机“U”绕组温度2 | ℃ | float32
N2DCS.20LAB81CT311 | 6662 | #1中给泵轴承冷却水回水温度1 | ℃ | float32
N2DCS.20LAB81CT312 | 6663 | #1中给泵轴承冷却水回水温度2 | ℃ | float32
N2DCS.20LAB81CT313 | 6664 | #1中给泵机密封冷却水回水温度1 | ℃ | float32
N2DCS.20LAB81CT314 | 6665 | #1中给泵机密封冷却水回水温度2 | ℃ | float32
N2DCS.20LAB81CT315 | 6666 | #1中给泵机密封冷却水回水温度3 | ℃ | float32
N2DCS.20LAB81CT316 | 6667 | #1中给泵机密封冷却水回水温度4 | ℃ | float32
N2DCS.20LAB81CY101 | 6668 | #1中给泵非驱动端轴承座振动(X向 |  | float32
N2DCS.20LAB81CY102 | 6669 | #1中给泵非驱动端轴承座振动(Y向 |  | float32
N2DCS.20LAB81CY103 | 6670 | #1中给泵驱动端轴承座振动（X向 |  | float32
N2DCS.20LAB81CY104 | 6671 | #1中给泵驱动端轴承座振动（Y向 |  | float32
N2DCS.20LAB83AA101_DM | 6672 | 中压给水调节阀指令（中间） |  | float32
N2DCS.20LAB83AA101_DMTK | 6673 | 中压给水调节阀指令（中间） |  | float32
N2DCS.20LAB83AA101C | 6674 | 中压给水调节阀控制指令 | % | float32
N2DCS.20LAB83AA101P | 6675 | 中压给水调节阀开度反馈 |  | float32
N2DCS.20LAB83CP101 | 6676 | 中压省煤器出口压力 | MPa | float32
N2DCS.20LAB83CT301 | 6677 | 中压省煤器出口温度 | ℃ | float32
N2DCS.20LAB91AP001I | 6678 | #1高压给水泵电流 |  | float32
N2DCS.20LAB91CP102 | 6679 | #1高压给水泵出口压力 | MPa | float32
N2DCS.20LAB91CS101 | 6680 | #1高压给水泵转速 | rpm | float32
N2DCS.20LAB91CT301 | 6681 | #1高给泵进水端径向轴承轴瓦温度 | ℃ | float32
N2DCS.20LAB91CT302 | 6682 | #1高给泵出水端径向轴承轴瓦温度 | ℃ | float32
N2DCS.20LAB91CT303 | 6683 | #1高给泵电机驱动端径向轴承温度 | ℃ | float32
N2DCS.20LAB91CT304 | 6684 | #1高给泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20LAB91CT305 | 6685 | #1高压给水泵电机“W”绕组温度1 | ℃ | float32
N2DCS.20LAB91CT306 | 6686 | #1高压给水泵电机“W”绕组温度2 | ℃ | float32
N2DCS.20LAB91CT307 | 6687 | #1高压给水泵电机“V”绕组温度1 | ℃ | float32
N2DCS.20LAB91CT308 | 6688 | #1高压给水泵电机“V”绕组温度2 | ℃ | float32
N2DCS.20LAB91CT309 | 6689 | #1高压给水泵电机“U”绕组温度1 | ℃ | float32
N2DCS.20LAB91CT310 | 6690 | #1高压给水泵电机“U”绕组温度2 | ℃ | float32
N2DCS.20LAB91CT311 | 6691 | #1高给泵机密封冷却水回水温度1 | ℃ | float32
N2DCS.20LAB91CT312 | 6692 | #1高给泵机密封冷却水回水温度2 | ℃ | float32
N2DCS.20LAB91CT313 | 6693 | #1高给泵机密封冷却水回水温度3 | ℃ | float32
N2DCS.20LAB91CT314 | 6694 | #1高给泵机密封冷却水回水温度4 | ℃ | float32
N2DCS.20LAB91CY101 | 6695 | #1高给泵非驱动端轴承座振动(X向 | mm/s | float32
N2DCS.20LAB91CY102 | 6696 | #1高给泵非驱动端轴承座振动(Y向 | mm/s | float32
N2DCS.20LAB91CY103 | 6697 | #1高给泵驱动端轴承座振动(X向 | mm/s | float32
N2DCS.20LAB91CY104 | 6698 | #1高给泵驱动端轴承座振动(Y向 | mm/s | float32
N2DCS.20LBA80AA502P | 6699 | 中压主蒸汽启动排汽门门位反馈 |  | float32
N2DCS.20LBA80CF101 | 6700 | 中压主蒸汽流量1 | KPa | float32
N2DCS.20LBA80CF102 | 6701 | 中压主蒸汽流量2 | KPa | float32
N2DCS.20LBA80CF103 | 6702 | 中压主蒸汽流量3 | KPa | float32
N2DCS.20LBA80CP101 | 6703 | 中压主蒸汽压力1 | MPa | float32
N2DCS.20LBA80CP102 | 6704 | 中压主蒸汽压力2 | MPa | float32
N2DCS.20LBA80CP103 | 6705 | 中压主蒸汽压力3 | MPa | float32
N2DCS.20LBA80CT301 | 6706 | 中压主蒸汽温度1 | ℃ | float32
N2DCS.20LBA80CT302 | 6707 | 中压主蒸汽温度2 | ℃ | float32
N2DCS.20LBA80CT303 | 6708 | 中压主蒸汽温度3 | ℃ | float32
N2DCS.20LCQ70CL101 | 6709 | 连排扩容器液位 | KPa | float32
N2DCS.20LCQ70CP101 | 6710 | 连排扩容器压力 | MPa | float32
N2DCS.20LCQ75CL101 | 6711 | 定排扩容器液位 | KPa | float32
N2DCS.20LCQ75CP101 | 6712 | 定排扩容器压力 | MPa | float32
N2DCS.20LCQ75CT301 | 6713 | 定排扩容器温度 | ℃ | float32
N2DCS.20XAV91CP101 | 6714 | #1高压给水泵稀油站供油母管压力 |  | float32
N2DCS.20XAV91CT301 | 6715 | #1高压给水泵稀油站油箱温度 | ℃ | float32
N2DCS.20XAV91CT302 | 6716 | #1高压给水泵稀油站供油母管温度 | ℃ | float32
N2DCS.20XAV91CT303 | 6717 | #1高压给水泵稀油站回油温度 | ℃ | float32
N2DCS.D8P1B1L3C9 | 6718 | TC温度补偿点 | C | float32
N2DCS.D8P1B2L6C9 | 6719 | TC温度补偿点 | C | float32
N2DCS.D8P1B3L3C9 | 6720 | TC温度补偿点 | C | float32
N2DCS.HPFWPA_SEQSPSTEP | 6721 | #1高压给水泵停顺控步号 |  | float32
N2DCS.HPFWPA_SEQSPTIME1 | 6722 | #1高给泵停顺控第1步剩余时间 |  | float32
N2DCS.HPFWPA_SEQSPTIME2 | 6723 | #1高给泵停顺控第2步剩余时间 |  | float32
N2DCS.HPFWPA_SEQSPTIME3 | 6724 | Ovation Control Builder |  | float32
N2DCS.HPFWPA_SEQSPTIME4 | 6725 | Ovation Control Builder |  | float32
N2DCS.HPFWPA_SEQSTSTEP | 6726 | #1高压给水泵启顺控步号 |  | float32
N2DCS.HPFWPA_SEQSTTIME1 | 6727 | #1高给泵启顺控第1步剩余时间 |  | float32
N2DCS.HPFWPA_SEQSTTIME2 | 6728 | #1高给泵启顺控第2步剩余时间 |  | float32
N2DCS.HPFWPA_SEQSTTIME3 | 6729 | #1高给泵启顺控第3步剩余时间 |  | float32
N2DCS.HPFWPA_SEQSTTIME4 | 6730 | #1高给泵启顺控第4步剩余时间 |  | float32
N2DCS.HPFWPA_TPFO | 6731 | #1高给泵跳闸首出(打包点位号 |  | float32
N2DCS.IPDRUMCP | 6732 | 中压汽包压力（3选后） |  | float32
N2DCS.IPDRUMCTD | 6733 | 中压汽包下外壁温（3选后） |  | float32
N2DCS.IPDRUMCTU | 6734 | 中压汽包上外壁温（3选后） |  | float32
N2DCS.IPDRUMLVL | 6735 | 中压汽包液位（3选后） |  | float32
N2DCS.IPDRUMLVL_A | 6736 | 中压汽包液位1（计算后） |  | float32
N2DCS.IPDRUMLVL_B | 6737 | 中压汽包液位2（计算后） |  | float32
N2DCS.IPDRUMLVL_C | 6738 | 中压汽包液位3（计算后） |  | float32
N2DCS.IPDRUMLVL_DIF | 6739 | 中压汽包液位（3选后） |  | float32
N2DCS.IPDRUMLVLBIAS | 6740 | Ovation Control Builder |  | float32
N2DCS.IPDRUMLVLSP | 6741 | 中压汽包液位最终设定值 |  | float32
N2DCS.IPDRUMLVLSP1 | 6742 | 中压汽包液位设定值 |  | float32
N2DCS.IPDSTCF | 6743 | 中压主蒸汽流量（3选后） |  | float32
N2DCS.IPDSTCF_A | 6744 | 中压主蒸汽流量1（计算后） |  | float32
N2DCS.IPDSTCF_B | 6745 | 中压主蒸汽流量2（计算后） |  | float32
N2DCS.IPDSTCF_C | 6746 | 中压主蒸汽流量3（计算后） |  | float32
N2DCS.IPDSTCP | 6747 | 中压主蒸汽压力（3选后） |  | float32
N2DCS.IPDSTCT | 6748 | 中压主蒸汽温度（3选后） |  | float32
N2DCS.IPDWTCF | 6749 | 中压汽包给水流量（3选后） |  | float32
N2DCS.IPDWTCF_A | 6750 | 中压汽包给水流量1（计算后） |  | float32
N2DCS.IPDWTCF_B | 6751 | 中压汽包给水流量2（计算后） |  | float32
N2DCS.IPDWTCF_C | 6752 | 中压汽包给水流量3（计算后） |  | float32
N2DCS.IPDWTCT | 6753 | 中压给水省煤器进口温度（3选后) |  | float32
N2DCS.IPFW_SEQSTSTEP | 6754 | 中压汽包上水顺控步号 |  | float32
N2DCS.IPFW_SEQSTTIME1 | 6755 | 中压汽包上水顺控第1步剩余时间 |  | float32
N2DCS.IPFW_SEQSTTIME2 | 6756 | 中压汽包上水顺控第2步剩余时间 |  | float32
N2DCS.IPFW_SEQSTTIME3 | 6757 | 中压汽包上水顺控第3步剩余时间 |  | float32
N2DCS.IPFW_SEQSTTIME4 | 6758 | 中压汽包上水顺控第4步剩余时间 |  | float32
N2DCS.IPFW_SEQSTTIME5 | 6759 | 中压汽包上水顺控第5步剩余时间 |  | float32
N2DCS.IPFW_SEQSTTIME6 | 6760 | 中压汽包上水顺控第6步剩余时间 |  | float32
N2DCS.IPFWPA_SEQSPSTEP | 6761 | #1中压给水泵停顺控步号 |  | float32
N2DCS.IPFWPA_SEQSPTIME1 | 6762 | #1中给泵停顺控第1步剩余时间 |  | float32
N2DCS.IPFWPA_SEQSPTIME2 | 6763 | #1中给泵停顺控第2步剩余时间 |  | float32
N2DCS.IPFWPA_SEQSPTIME3 | 6764 | 中压给水泵A程控停止第3步时间 |  | float32
N2DCS.IPFWPA_SEQSTSTEP | 6765 | #1中压给水泵启顺控步号 |  | float32
N2DCS.IPFWPA_SEQSTTIME1 | 6766 | #1中给泵启顺控第1步剩余时间 |  | float32
N2DCS.IPFWPA_SEQSTTIME2 | 6767 | #1中给泵启顺控第2步剩余时间 |  | float32
N2DCS.IPFWPA_SEQSTTIME3 | 6768 | #1中给泵启顺控第3步剩余时间 |  | float32
N2DCS.IPFWPA_TPFO | 6769 | #1中给泵跳闸首出(打包点位号 |  | float32
N2DCS.IPMS_SEQSTSTEP | 6770 | 中压主蒸汽升温升压顺控步号 |  | float32
N2DCS.IPMS_SEQSTTIME1 | 6771 | 中压主汽升温升压顺控1步剩时间 |  | float32
N2DCS.IPMS_SEQSTTIME2 | 6772 | 中压主汽升温升压顺控2步剩时间 |  | float32
N2DCS.IPMS_SEQSTTIME3 | 6773 | 中压主汽升温升压顺控3步剩时间 |  | float32
N2DCS.IPMS_SEQSTTIME4 | 6774 | 中压主汽升温升压顺控4步剩时间 |  | float32
N2DCS.IPMS_SEQSTTIME5 | 6775 | 中压主汽升温升压顺控5步剩时间 |  | float32
N2DCS.IPMS_SEQSTTIME6 | 6776 | 中压主汽升温升压顺控6步剩时间 |  | float32
N2DCS.IPMS_SEQSTTIME7 | 6777 | 中压主汽升温升压顺控7步剩时间 |  | float32
N2DCS.20CFE40CQ101I | 6778 | 烟囱出口NOX折算值 |  | float32
N2DCS.20CFE40CQ103I | 6779 | 烟囱出口SO2折算值 | mg/m3 | float32
N2DCS.20CFE40CQ106I | 6780 | 烟囱出口粉尘折算值 |  | float32
N2DCS.HPFWPA_SEQBPSTSTEP | 6781 | #1高压给水泵变频启顺控步号 |  | float32
N2DCS.HPFWPA_SEQBPSTTIME1 | 6782 | #1高给泵变频启顺控1步剩余时间 |  | float32
N2DCS.HPFWPA_SEQBPSTTIME2 | 6783 | #1高给泵变频启顺控2步剩余时间 |  | float32
N2DCS.HPFWPA_SEQBPSTTIME3 | 6784 | #1高给泵变频启顺控3步剩余时间 |  | float32
N2DCS.HPFWPA_SEQBPSTTIME4 | 6785 | #1高给泵变频启顺控4步剩余时间 |  | float32
N2DCS.IPDWTCF_SUM | 6786 | 中压汽包给水累计流量 |  | float32
N2DCS.IPMS_SEQSTTIME8 | 6787 | 中压主汽升温升压顺控8步剩时间 |  | float32
N2DCS.20HAD90CL001 | 6788 | 高压汽包左电接点液位 |  | float32
N2DCS.20HAD90CL002 | 6789 | 高压汽包右电接点液位 |  | float32
N2DCS.20HAD90CL101 | 6790 | 高压汽包液位1 | mmH2O | float32
N2DCS.20HAD90CL102 | 6791 | 高压汽包液位2 | mmH2O | float32
N2DCS.20HAD90CL103 | 6792 | 高压汽包液位3 | KPa | float32
N2DCS.20HAD90CP101 | 6793 | 高压汽包压力1 | MPa | float32
N2DCS.20HAD90CP102 | 6794 | 高压汽包压力2 | MPa | float32
N2DCS.20HAD90CP103 | 6795 | 高压汽包压力3 | MPa | float32
N2DCS.20HAD90CT301 | 6796 | 高压汽包上内壁温1 | ℃ | float32
N2DCS.20HAD90CT302 | 6797 | 高压汽包上内壁温2 | ℃ | float32
N2DCS.20HAD90CT303 | 6798 | 高压汽包上内壁温3 | ℃ | float32
N2DCS.20HAD90CT304 | 6799 | 高压汽包上外壁温1 | ℃ | float32
N2DCS.20HAD90CT305 | 6800 | 高压汽包上外壁温2 | ℃ | float32
N2DCS.20HAD90CT306 | 6801 | 高压汽包上外壁温3 | ℃ | float32
N2DCS.20HAD90CT307 | 6802 | 高压汽包下外壁温1 | ℃ | float32
N2DCS.20HAD90CT308 | 6803 | 高压汽包下外壁温2 | ℃ | float32
N2DCS.20HAD90CT309 | 6804 | 高压汽包下外壁温3 | ℃ | float32
N2DCS.20HAD91AA405P | 6805 | 高压蒸发器排污至定排门阀位反馈 |  | float32
N2DCS.20HAD95AA101C | 6806 | 高压汽包连排气动调节阀控制指令 | % | float32
N2DCS.20HAD95AA101P | 6807 | 高压汽包连排气动调节阀阀位反馈 |  | float32
N2DCS.20HAD96AA001P | 6808 | 高压汽包启动放水电动门阀位反馈 |  | float32
N2DCS.20HAD96AA002P | 6809 | 高压汽包启动放水调门阀位反馈 |  | float32
N2DCS.20HAH90CT301 | 6810 | 高压三级过热器进口温度1 | ℃ | float32
N2DCS.20HAH90CT302 | 6811 | 高压三级过热器进口温度2 | ℃ | float32
N2DCS.20HAH90CT303 | 6812 | 高压三级过热器进口温度3 | ℃ | float32
N2DCS.20HAH90CT304 | 6813 | 高压二级过热器出口温度 | ℃ | float32
N2DCS.20HNA80CP101 | 6814 | 高压三级过热器进口烟气压力1 | KPa | float32
N2DCS.20HNA80CP102 | 6815 | 高压三级过热器进口烟气压力2 | KPa | float32
N2DCS.20HNA80CT301 | 6816 | 高压三级过热器进口烟气温度1 | ℃ | float32
N2DCS.20HNA80CT302 | 6817 | 高压三级过热器进口烟气温度2 | ℃ | float32
N2DCS.20HNA80CT305 | 6818 | 高压蒸发器进口烟气温度1 | ℃ | float32
N2DCS.20HNA80CT306 | 6819 | 高压蒸发器进口烟气温度2 | ℃ | float32
N2DCS.20HNA80CT309 | 6820 | 高压二级省煤器进口烟气温度1 | ℃ | float32
N2DCS.20HNA80CT310 | 6821 | 高压二级省煤器进口烟气温度2 | ℃ | float32
N2DCS.20LAB73CP101 | 6822 | #2中压给水泵进口压力 | MPa | float32
N2DCS.20LAB73DP101 | 6823 | #2中压给水泵进口过滤器差压 | KPa | float32
N2DCS.20LAB75CP101 | 6824 | #2高压给水泵进口压力 | MPa | float32
N2DCS.20LAB75DP101 | 6825 | #2高压给水泵进口过滤器差压 | KPa | float32
N2DCS.20LAB82AP001I | 6826 | #2中压给水泵电流 |  | float32
N2DCS.20LAB82CP102 | 6827 | #2中压给水泵出口压力 | MPa | float32
N2DCS.20LAB82CT301 | 6828 | #2中给泵非驱动端径向轴承温度 | ℃ | float32
N2DCS.20LAB82CT302 | 6829 | #2中压给水泵驱动端径向轴承温度 | ℃ | float32
N2DCS.20LAB82CT303 | 6830 | #2中给泵电机驱动端径向轴承温度 | ℃ | float32
N2DCS.20LAB82CT304 | 6831 | #2中给泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20LAB82CT305 | 6832 | #2中压给水泵电机“W”绕组温度1 | ℃ | float32
N2DCS.20LAB82CT306 | 6833 | #2中压给水泵电机“W”绕组温度2 | ℃ | float32
N2DCS.20LAB82CT307 | 6834 | #2中压给水泵电机“V”绕组温度1 | ℃ | float32
N2DCS.20LAB82CT308 | 6835 | #2中压给水泵电机“V”绕组温度2 | ℃ | float32
N2DCS.20LAB82CT309 | 6836 | #2中压给水泵电机“U”绕组温度1 | ℃ | float32
N2DCS.20LAB82CT310 | 6837 | #2中压给水泵电机“U”绕组温度2 | ℃ | float32
N2DCS.20LAB82CT311 | 6838 | #2中给泵轴承冷却水回水温度1 | ℃ | float32
N2DCS.20LAB82CT312 | 6839 | #2中给泵轴承冷却水回水温度2 | ℃ | float32
N2DCS.20LAB82CT313 | 6840 | #2中给泵机密封冷却水回水温度1 | ℃ | float32
N2DCS.20LAB82CT314 | 6841 | #2中给泵机密封冷却水回水温度2 | ℃ | float32
N2DCS.20LAB82CT315 | 6842 | #2中给泵机密封冷却水回水温度3 | ℃ | float32
N2DCS.20LAB82CT316 | 6843 | #2中给泵机密封冷却水回水温度4 | ℃ | float32
N2DCS.20LAB82CY101 | 6844 | #2中给泵非驱动端轴承座振动(X向 |  | float32
N2DCS.20LAB82CY102 | 6845 | #2中给泵非驱动端轴承座振动(Y向 |  | float32
N2DCS.20LAB82CY103 | 6846 | #2中给泵驱动端轴承座振动（X向 |  | float32
N2DCS.20LAB82CY104 | 6847 | #2中给泵驱动端轴承座振动（Y向 |  | float32
N2DCS.20LAB90AA101_BIAS | 6848 | Ovation Control Builder |  | float32
N2DCS.20LAB90AA101_SP | 6849 | Ovation Control Builder |  | float32
N2DCS.20LAB90AA101_SPTK | 6850 | Ovation Control Builder |  | float32
N2DCS.20LAB90AA101C | 6851 | 高压给水气动调节阀控制指令 | % | float32
N2DCS.20LAB90AA101P | 6852 | 高压给水气动调节阀阀位反馈 |  | float32
N2DCS.20LAB90CF101 | 6853 | 高压给水流量1 | KPa | float32
N2DCS.20LAB90CF102 | 6854 | 高压给水流量2 | KPa | float32
N2DCS.20LAB90CF103 | 6855 | 高压给水流量3 | KPa | float32
N2DCS.20LAB90CP101 | 6856 | 高压给水调节阀前压力 | MPa | float32
N2DCS.20LAB90CP102 | 6857 | 高压给水调节阀后压力 | MPa | float32
N2DCS.20LAB90CT301 | 6858 | 高压给水温度1 | ℃ | float32
N2DCS.20LAB90CT302 | 6859 | 高压给水温度2 | ℃ | float32
N2DCS.20LAB90CT303 | 6860 | 高压给水温度3 | ℃ | float32
N2DCS.20LAB90GX001_BIAS | 6861 | Ovation Control Builder |  | float32
N2DCS.20LAB90GX001_SP1 | 6862 | Ovation Control Builder |  | float32
N2DCS.20LAB92AP001I | 6863 | #2高压给水泵电流 |  | float32
N2DCS.20LAB92CP102 | 6864 | #2高压给水泵出口压力 | MPa | float32
N2DCS.20LAB92CS101 | 6865 | #2高压给水泵转速 | rpm | float32
N2DCS.20LAB92CT301 | 6866 | #2高给泵进水端径向轴承轴瓦温度 | ℃ | float32
N2DCS.20LAB92CT302 | 6867 | #2高给泵出水端径向轴承轴瓦温度 | ℃ | float32
N2DCS.20LAB92CT303 | 6868 | #2高给泵电机驱动端径向轴承温度 | ℃ | float32
N2DCS.20LAB92CT304 | 6869 | #2高给泵电机非驱动端轴承温度 | ℃ | float32
N2DCS.20LAB92CT305 | 6870 | #2高压给水泵电机“W”绕组温度1 | ℃ | float32
N2DCS.20LAB92CT306 | 6871 | #2高压给水泵电机“W”绕组温度2 | ℃ | float32
N2DCS.20LAB92CT307 | 6872 | #2高压给水泵电机“V”绕组温度1 | ℃ | float32
N2DCS.20LAB92CT308 | 6873 | #2高压给水泵电机“V”绕组温度2 | ℃ | float32
N2DCS.20LAB92CT309 | 6874 | #2高压给水泵电机“U”绕组温度1 | ℃ | float32
N2DCS.20LAB92CT310 | 6875 | #2高压给水泵电机“U”绕组温度2 | ℃ | float32
N2DCS.20LAB92CT311 | 6876 | #2高给泵机密封冷却水回水温度1 | ℃ | float32
N2DCS.20LAB92CT312 | 6877 | #2高给泵机密封冷却水回水温度2 | ℃ | float32
N2DCS.20LAB92CT313 | 6878 | #2高给泵机密封冷却水回水温度3 | ℃ | float32
N2DCS.20LAB92CT314 | 6879 | #2高给泵机密封冷却水回水温度4 | ℃ | float32
N2DCS.20LAB92CY101 | 6880 | #2高给泵非驱动端轴承座振动(X向 | mm/s | float32
N2DCS.20LAB92CY102 | 6881 | #2高给泵非驱动端轴承座振动(Y向 | mm/s | float32
N2DCS.20LAB92CY103 | 6882 | #2高给泵驱动端轴承座振动(X向 | mm/s | float32
N2DCS.20LAB92CY104 | 6883 | #2高给泵驱动端轴承座振动(Y向 | mm/s | float32
N2DCS.20LAB93CP101 | 6884 | 高压省煤器出口压力 | MPa | float32
N2DCS.20LAB93CT301 | 6885 | 高压省煤器出口温度 | ℃ | float32
N2DCS.20LAC91G10001C | 6886 | 高压给水泵变频器转速给定 |  | float32
N2DCS.20LAC91G10001F | 6887 | 高压给水泵变频器频率反馈 |  | float32
N2DCS.20LAC91G10001I | 6888 | 高压给水泵变频器电流反馈 |  | float32
N2DCS.20LAC91GX0001_BIAS | 6889 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001_LVL | 6890 | 高压给水泵变频器液位设定值 |  | float32
N2DCS.20LAC91GX0001_LVLT | 6891 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001_PID | 6892 | 高压给水泵变频器PID输出 |  | float32
N2DCS.20LAC91GX0001_PIDT | 6893 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001_SP | 6894 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001_SP1 | 6895 | 高压给水泵变频器压力设定值 |  | float32
N2DCS.20LAC91GX0001_SPBIAS | 6896 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001C | 6897 | 高压给水泵变频器频率指令 | % | float32
N2DCS.20LAC91GX0001F | 6898 | 高压给水泵变频器频率反馈 |  | float32
N2DCS.20LAC91GX0001I | 6899 | 高压给水泵变频器电流反馈 |  | float32
N2DCS.20LAE90AA101_BIAS | 6900 | 高压过热器一级减温水气动调节阀 |  | float32
N2DCS.20LAE90AA101_SPO | 6901 | 高压二级过热器减温调阀温度设定 |  | float32
N2DCS.20LAE90AA101C | 6902 | 高压二级过热器减温调阀控制指令 | % | float32
N2DCS.20LAE90AA101P | 6903 | 高压二级过热器减温调阀阀位反馈 |  | float32
N2DCS.20LAE90AA102_BIAS | 6904 | Ovation Control Builder |  | float32
N2DCS.20LAE90AA102_SPO | 6905 | 高压主蒸汽减温水调节阀温度设定 |  | float32
N2DCS.20LAE90AA102C | 6906 | 高压主蒸汽减温水调节阀控制指令 | % | float32
N2DCS.20LAE90AA102P | 6907 | 高压主蒸汽减温水调节阀阀位反馈 |  | float32
N2DCS.20LAE90CF101 | 6908 | 高压过热器减温水流量 | KPa | float32
N2DCS.20LAE91AA101_BIAS | 6909 | 高压省煤器旁路调节阀偏置 |  | float32
N2DCS.20LAE91AA101_SP | 6910 | Ovation Control Builder |  | float32
N2DCS.20LAE91AA101_SV | 6911 | Ovation Control Builder |  | float32
N2DCS.20LAE91AA101C | 6912 | 高压省煤器旁路调节阀控制指令 | % | float32
N2DCS.20LAE91AA101P | 6913 | 高压省煤器旁路调节阀阀位反馈 |  | float32
N2DCS.20LBA90AA502P | 6914 | 高压主蒸汽启动排汽门阀位反馈 |  | float32
N2DCS.20LBA90CF101 | 6915 | 高压主蒸汽流量1 | KPa | float32
N2DCS.20LBA90CF102 | 6916 | 高压主蒸汽流量2 | KPa | float32
N2DCS.20LBA90CF103 | 6917 | 高压主蒸汽流量3 | KPa | float32
N2DCS.20LBA90CP101 | 6918 | 高压主蒸汽压力1 | MPa | float32
N2DCS.20LBA90CP102 | 6919 | 高压主蒸汽压力2 | MPa | float32
N2DCS.20LBA90CP103 | 6920 | 高压主蒸汽压力3 | MPa | float32
N2DCS.20LBA90CT301 | 6921 | 高压主蒸汽温度1 | ℃ | float32
N2DCS.20LBA90CT302 | 6922 | 高压主蒸汽温度2 | ℃ | float32
N2DCS.20LBA90CT303 | 6923 | 高压主蒸汽温度3 | ℃ | float32
N2DCS.20XAV92CP101 | 6924 | #2高压给水泵稀油站供油母管压力 |  | float32
N2DCS.20XAV92CT301 | 6925 | #2高压给水泵稀油站油箱温度 | ℃ | float32
N2DCS.20XAV92CT302 | 6926 | #2高压给水泵稀油站供油母管温度 | ℃ | float32
N2DCS.20XAV92CT303 | 6927 | #2高压给水泵稀油站回油温度 | ℃ | float32
N2DCS.D9P1B1L3C9 | 6928 | TC温度补偿点 | C | float32
N2DCS.D9P1B2L6C9 | 6929 | TC温度补偿点 | C | float32
N2DCS.D9P1B2L7C9 | 6930 | TC温度补偿点 | C | float32
N2DCS.D9P1B3L2C9 | 6931 | TC温度补偿点 | C | float32
N2DCS.D9P1B3L3C9 | 6932 | TC温度补偿点 | C | float32
N2DCS.GYSJGRQJKWD | 6933 | 高压三级过热器进口温度（3选后) |  | float32
N2DCS.H1HPDRUMLVLSP | 6934 | Ovation Control Builder |  | float32
N2DCS.H1HPDRUMLVLSP1 | 6935 | Ovation Control Builder |  | float32
N2DCS.H1HPFW_BIAS | 6936 | Ovation Control Builder |  | float32
N2DCS.HPDRUMCP | 6937 | 高压汽包压力(3选后) |  | float32
N2DCS.HPDRUMCTD | 6938 | 高压汽包下外壁温(3选后) |  | float32
N2DCS.HPDRUMCTU | 6939 | 高压汽包上外壁温(3选后) |  | float32
N2DCS.HPDRUMCTU2 | 6940 | 高压汽包上内壁温(3选后) |  | float32
N2DCS.HPDRUMLVL | 6941 | 高压汽包液位(3选后) |  | float32
N2DCS.HPDRUMLVL_A | 6942 | 高压汽包液位(计算后） |  | float32
N2DCS.HPDRUMLVL_B | 6943 | 高压汽包液位(计算后） |  | float32
N2DCS.HPDRUMLVL_C | 6944 | 高压汽包液位(计算后） |  | float32
N2DCS.HPDRUMLVL_DIF | 6945 | 高压汽包液位(3选后) |  | float32
N2DCS.HPDRUMLVLPIDOUT | 6946 | Ovation Control Builder |  | float32
N2DCS.HPDRUMLVLPIDTOUT | 6947 | Ovation Control Builder |  | float32
N2DCS.HPDRUMLVLSP | 6948 | 高压汽包液位偏置值-250mm |  | float32
N2DCS.HPDRUMLVLSP1 | 6949 | 高压汽包液位基本设定值 |  | float32
N2DCS.HPDRUMLVLSP2 | 6950 | 高压汽包液位最终设定值 |  | float32
N2DCS.HPDSTCF | 6951 | 高压主蒸汽流量（3选后） |  | float32
N2DCS.HPDSTCF_A | 6952 | 高压主蒸汽流量1（计算后） |  | float32
N2DCS.HPDSTCF_B | 6953 | 高压主蒸汽流量2（计算后） |  | float32
N2DCS.HPDSTCF_C | 6954 | 高压主蒸汽流量3（计算后） |  | float32
N2DCS.HPDSTCP | 6955 | 高压主蒸汽压力（3选后） |  | float32
N2DCS.HPDSTCT | 6956 | 高压主蒸汽温度（3选后） |  | float32
N2DCS.HPDWTCF | 6957 | 高压汽包给水流量(3选后) |  | float32
N2DCS.HPDWTCF_A | 6958 | 高压汽包给水流量1(计算后) |  | float32
N2DCS.HPDWTCF_B | 6959 | 高压汽包给水流量2(计算后) |  | float32
N2DCS.HPDWTCF_C | 6960 | 高压汽包给水流量3(计算后) |  | float32
N2DCS.HPDWTCT | 6961 | 高压汽包给水温度(3选后) |  | float32
N2DCS.HPFW_SEQSTSTEP | 6962 | 高压汽包上水顺控步号 |  | float32
N2DCS.HPFW_SEQSTTIME1 | 6963 | 高压汽包上水顺控第1步剩余时间 |  | float32
N2DCS.HPFW_SEQSTTIME2 | 6964 | 高压汽包上水顺控第2步剩余时间 |  | float32
N2DCS.HPFW_SEQSTTIME3 | 6965 | 高压汽包上水顺控第3步剩余时间 |  | float32
N2DCS.HPFW_SEQSTTIME4 | 6966 | 高压汽包上水顺控第4步剩余时间 |  | float32
N2DCS.HPFW_SEQSTTIME5 | 6967 | 高压汽包上水顺控第5步剩余时间 |  | float32
N2DCS.HPFW_SEQSTTIME6 | 6968 | 高压汽包上水顺控第6步剩余时间 |  | float32
N2DCS.HPFWPB_SEQSPSTEP | 6969 | #2高压给水泵停顺控步号 |  | float32
N2DCS.HPFWPB_SEQSPTIME1 | 6970 | #2高给泵停顺控第1步剩余时间 |  | float32
N2DCS.HPFWPB_SEQSPTIME2 | 6971 | #2高给泵停顺控第2步剩余时间 |  | float32
N2DCS.HPFWPB_SEQSPTIME3 | 6972 | Ovation Control Builder |  | float32
N2DCS.HPFWPB_SEQSPTIME4 | 6973 | Ovation Control Builder |  | float32
N2DCS.HPFWPB_SEQSTSTEP | 6974 | #2高压给水泵启顺控步号 |  | float32
N2DCS.HPFWPB_SEQSTTIME1 | 6975 | #2高给泵启顺控第1步剩余时间 |  | float32
N2DCS.HPFWPB_SEQSTTIME2 | 6976 | #2高给泵启顺控第2步剩余时间 |  | float32
N2DCS.HPFWPB_SEQSTTIME3 | 6977 | #2高给泵启顺控第3步剩余时间 |  | float32
N2DCS.HPFWPB_SEQSTTIME4 | 6978 | #2高给泵启顺控第4步剩余时间 |  | float32
N2DCS.HPFWPB_TPFO | 6979 | #2高给泵跳闸首出(打包点位号 |  | float32
N2DCS.HPMS_SEQSTSTEP | 6980 | 高压主蒸汽升温升压顺控步号 |  | float32
N2DCS.HPMS_SEQSTTIME1 | 6981 | 高压主汽升温升压顺控1步剩时间 |  | float32
N2DCS.HPMS_SEQSTTIME2 | 6982 | 高压主汽升温升压顺控2步剩时间 |  | float32
N2DCS.HPMS_SEQSTTIME3 | 6983 | 高压主汽升温升压顺控3步剩时间 |  | float32
N2DCS.HPMS_SEQSTTIME4 | 6984 | 高压主汽升温升压顺控4步剩时间 |  | float32
N2DCS.IPFWPB_SEQSPSTEP | 6985 | Ovation Control Builder |  | float32
N2DCS.IPFWPB_SEQSPTIME1 | 6986 | Ovation Control Builder |  | float32
N2DCS.IPFWPB_SEQSPTIME2 | 6987 | Ovation Control Builder |  | float32
N2DCS.IPFWPB_SEQSTSTEP | 6988 | Ovation Control Builder |  | float32
N2DCS.IPFWPB_SEQSTTIME1 | 6989 | Ovation Control Builder |  | float32
N2DCS.IPFWPB_SEQSTTIME2 | 6990 | Ovation Control Builder |  | float32
N2DCS.IPFWPB_SEQSTTIME3 | 6991 | Ovation Control Builder |  | float32
N2DCS.IPFWPB_TPFO | 6992 | #2中压给水泵跳闸首出 |  | float32
N2DCS.20LAB93CT301A | 6993 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001_1BIAS | 6994 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001_2BIAS | 6995 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001_SP2 | 6996 | Ovation Control Builder |  | float32
N2DCS.20LAC91GX0001I_SP | 6997 | Ovation Control Builder |  | float32
N2DCS.20LAE90AA101_SPO1 | 6998 | Ovation Control Builder |  | float32
N2DCS.20LAE90AA102_SP1 | 6999 | Ovation Control Builder |  | float32
N2DCS.20LAE90CF101I | 7000 | Ovation Control Builder |  | float32
N2DCS.GYBPSD | 7001 | Ovation Control Builder |  | float32
N2DCS.HPDRUMCT | 7002 | Ovation Control Builder |  | float32
N2DCS.HPDRUMLVLPIDOUT1 | 7003 | Ovation Control Builder |  | float32
N2DCS.HPDWTCF_SUM | 7004 | 高压汽包给水流量(累计) |  | float32
N2DCS.HPFWPB_SEQBPSTSTEP | 7005 | Ovation Control Builder |  | float32
N2DCS.HPFWPB_SEQBPSTTIME1 | 7006 | Ovation Control Builder |  | float32
N2DCS.HPFWPB_SEQBPSTTIME2 | 7007 | Ovation Control Builder |  | float32
N2DCS.HPFWPB_SEQBPSTTIME3 | 7008 | Ovation Control Builder |  | float32
N2DCS.HPFWPB_SEQBPSTTIME4 | 7009 | Ovation Control Builder |  | float32
N2DCS.HPMS_SEQSTTIME5 | 7010 | Ovation Control Builder |  | float32
N2DCS.HRSGFO | 7011 | 余热锅炉保护跳闸首出 |  | float32
N2DCS.SCLSWSD | 7012 | Ovation Control Builder |  | float32
N2DCS.20BBA00CE001 | 7013 | 6KV IIA段母线AC线电压 |  | float32
N2DCS.20BBA00CE101 | 7014 | 6KV IIA段工作电源进线电压 |  | float32
N2DCS.20BBA00GS001I | 7015 | 6KV IIA段工作电源进线开关电流 |  | float32
N2DCS.20BBB00CE203 | 7016 | 6KV IIA段备用电源进线电压 |  | float32
N2DCS.20BBB00GS002I | 7017 | 6KV IIA段备用电源进线开关电流 |  | float32
N2DCS.20BBB13GS001I | 7018 | #3机隔离变馈开关器电流 |  | float32
N2DCS.20BFA00CE201 | 7019 | 380V机组工作PC IIA段AC线电压 |  | float32
N2DCS.20BFA00GS001I | 7020 | 380V机组工作段分段开关电流 |  | float32
N2DCS.20BFA00GS103I | 7021 | 380V工作PC IIA至保安段开关电流 |  | float32
N2DCS.20BFA00GS201I | 7022 | 工作PC IIA至保安段开关电流 |  | float32
N2DCS.20BFB00GS001I | 7023 | 380V机组工作PC段分段开关电流 |  | float32
N2DCS.20BFT10GS101I | 7024 | 工作IIA变6kV侧开关电流 |  | float32
N2DCS.20BFT10GS102I | 7025 | 工作IIA变380V侧开关电流 |  | float32
N2DCS.20BJA00GS201I | 7026 | 工作PC 2A段至汽机MCCA开关电流 |  | float32
N2DCS.20BJB00GS201I | 7027 | 工作PC IIA段至汽机MCC B开关电? |  | float32
N2DCS.20BJC00GS201I | 7028 | 工作PC 2A段至余炉MCC开关电流 |  | float32
N2DCS.20BJD00GS201I | 7029 | 工作IP 2A段至燃机MCCA开关电流 |  | float32
N2DCS.20BJE00GS201I | 7030 | 工作PC 2A段至燃机MCCB开关电流 |  | float32
N2DCS.20BNA00GS201I | 7031 | 保安段至燃机EMCC段电源开关电流 |  | float32
N2DCS.22BAT01CE101 | 7032 | #3主变高压侧电流 | A | float32
N2DCS.22BAT01CE201 | 7033 | #3汽机主变油温1 | ℃ | float32
N2DCS.22BAT01CE202 | 7034 | #3汽机主变油温2 | ℃ | float32
N2DCS.22BAT01CE203 | 7035 | #3汽机主变绕组温度 | ℃ | float32
N2DCS.22BAT01CE301 | 7036 | #3汽机主变有功功率 | MW | float32
N2DCS.22BAT01CE302 | 7037 | #3汽机主变无功功率 | MVAR | float32
N2DCS.22BAT01CE501 | 7038 | #3汽机主变主表有功电度 | kWh | float32
N2DCS.22BAT01CE502 | 7039 | #3汽机主变主表无功电度 | kWh | float32
N2DCS.22BAT01CE503 | 7040 | #3汽机主变副表有功电度 | kWh | float32
N2DCS.22BAT01CE504 | 7041 | #3汽机主变副表无功电度 | kWh | float32
N2DCS.22MKA01CE001 | 7042 | #4发电机励磁电压 |  | float32
N2DCS.22MKA01CE002 | 7043 | #4发电机励磁电流 |  | float32
N2DCS.22MKA01CE101 | 7044 | #3发电机A相电流 | A | float32
N2DCS.22MKA01CE102 | 7045 | #3发电机B相电流 | A | float32
N2DCS.22MKA01CE103 | 7046 | #3发电机C相电流 | A | float32
N2DCS.22MKA01CE201 | 7047 | #3发电机定子电压(A-C） | V | float32
N2DCS.22MKA01CE202 | 7048 | #3发电机定子电压(A-B） | V | float32
N2DCS.22MKA01CE203 | 7049 | #3发电机定子电压(B-C） | V | float32
N2DCS.22MKA01CE204 | 7050 | #3发电机零序电压 | V | float32
N2DCS.22MKA01CE304 | 7051 | #3发电机有功功率 | MW | float32
N2DCS.22MKA01CE305 | 7052 | #3发电机无功功率 | MVAR | float32
N2DCS.22MKA01CE401 | 7053 | #3发电机频率 | Hz | float32
N2DCS.22MKA01CE402 | 7054 | #3发电机功率因数 |  | float32
N2DCS.22MKA01CE402_CAL | 7055 | #3发电机功率因数 |  | float32
N2DCS.22MKA01CE501 | 7056 | #3发电机有功电度 | kWh | float32
N2DCS.22MKA01CE502 | 7057 | #3发电机无功电度 | kWh | float32
N2DCS.22MKC01CE001 | 7058 | #3汽机励磁电压 |  | float32
N2DCS.22MKC01CE002 | 7059 | #3汽机励磁电流 |  | float32
N2DCS.22MKC01CE101 | 7060 | #4发电机励磁变电流 |  | float32
N2DCS.22MKC01CE102 | 7061 | #3励磁变高压侧电流 |  | float32
N2DCS.22MKC01CE301 | 7062 | #3励磁变有功功率 |  | float32
N2DCS.22MKC01CE302 | 7063 | #3励磁变无功功率 |  | float32
N2DCS.22MKC01CE501 | 7064 | #3汽机励磁变有功电度 |  | float32
N2DCS.22MKC01CE502 | 7065 | #3汽机励磁变无功电度 |  | float32
N2DCS.22BAT01CE501CI | 7066 | #3汽机主变主表有功电度 |  | float32
N2DCS.22BAT01CE502CI | 7067 | #3汽机主变主表无功电度 |  | float32
N2DCS.22BAT01CE503CI | 7068 | #3汽机主变副表有功电度 |  | float32
N2DCS.22BAT01CE504CI | 7069 | #3汽机主变副表无功电度 |  | float32
N2DCS.22MKA01CE501CI | 7070 | #3发电机有功电度 |  | float32
N2DCS.22MKA01CE502CI | 7071 | #3发电机无功电度 |  | float32
N2DCS.22MKC01CE301CI | 7072 | #3励磁变有功功率 |  | float32
N2DCS.22MKC01CE302CI | 7073 | #3励磁变无功功率 |  | float32
N2DCS.22MKC01CE501CI | 7074 | #3汽机励磁变有功电度 |  | float32
N2DCS.22MKC01CE502CI | 7075 | #3汽机励磁变无功电度 |  | float32
N2DCS.QJBW_SEQSTSTEP | 7076 | Ovation Control Builder |  | float32
N2DCS.QJBW_SEQSTTIME1 | 7077 | Ovation Control Builder |  | float32
N2DCS.QJBW_SEQSTTIME2 | 7078 | Ovation Control Builder |  | float32
N2DCS.QJBW_SEQSTTIME3 | 7079 | Ovation Control Builder |  | float32
N2DCS.QJBW_SEQSTTIME4 | 7080 | Ovation Control Builder |  | float32
N2DCS.QJBW_SEQSTTIME5 | 7081 | Ovation Control Builder |  | float32
N2DCS.20BBA00CE203 | 7082 | 6KV IIA段备用电源进线电压 |  | float32
N2DCS.20BBA00GS002I | 7083 | 6KV IIA段备用电源进线开关电流 |  | float32
N2DCS.20BBB00CE001 | 7084 | 6KV IIB段母线AC线电压 |  | float32
N2DCS.20BBB00CE101 | 7085 | 6kV IIB段工作电源进线电压 |  | float32
N2DCS.20BBB00GS001I | 7086 | 6KV IIB段工作进线开关电流 |  | float32
N2DCS.20BBT01CE101 | 7087 | #3高厂变油面温度1 | ℃ | float32
N2DCS.20BBT01CE102 | 7088 | #3高厂变油面温度2 | ℃ | float32
N2DCS.20BBT01CE103 | 7089 | #3高厂变绕组温度 | ℃ | float32
N2DCS.20BBT01CE301 | 7090 | #3高厂变有功功率 | MW | float32
N2DCS.20BBT01CE302 | 7091 | #3高厂变高压侧电流 | A | float32
N2DCS.20BBT01CE501 | 7092 | #3高厂变有功电度 | kWh | float32
N2DCS.20BBT01CE502 | 7093 | #3高厂变无功电度 | kWh | float32
N2DCS.20BFB00CE201 | 7094 | 380V工作PC IIB段母线AC线电压 |  | float32
N2DCS.20BFB00GS103I | 7095 | 工作PC IIB至保安段电源开关电流 |  | float32
N2DCS.20BFB00GS201I | 7096 | 工作PC IIB至保安段开关电流 |  | float32
N2DCS.20BFT20GS101I | 7097 | 工作IIB变6kV侧开关电流 |  | float32
N2DCS.20BFT20GS102I | 7098 | 工作IIB变380V侧开关电流 |  | float32
N2DCS.20BJA00GS202I | 7099 | 工作PC 2B段至汽机MCCA开关电流 |  | float32
N2DCS.20BJB00GS202I | 7100 | 工作PC 2B段至汽机MCCB开关电流 |  | float32
N2DCS.20BJC00GS202I | 7101 | 工作PC 2B段至余炉MCC段开关电流 |  | float32
N2DCS.20BJD00GS202I | 7102 | 工作PC 2B段至燃机MCCA开关电流 |  | float32
N2DCS.20BJE00GS202I | 7103 | 工作PC 2B段至燃机MCC开关电流 |  | float32
N2DCS.20BMA00CE201 | 7104 | 380V保安段母线AC线电压 |  | float32
N2DCS.20BMA00GS001I | 7105 | 保安段柴油发电机进线K1开关电流 |  | float32
N2DCS.20BMA00GS002I | 7106 | 保安段工作电源进线K2开关电流 |  | float32
N2DCS.20BMA00GS003I | 7107 | 保安段工作电源进线K3开关电流 |  | float32
N2DCS.20BNA00GS202I | 7108 | 工作PC IIB段至燃机EMCC开关电流 |  | float32
N2DCS.20BRU03CE101 | 7109 | #4机组UPS系统进线电流 |  | float32
N2DCS.20BRU03CE201 | 7110 | #4机组UPS系统母线电压 |  | float32
N2DCS.20BRU03CE401 | 7111 | #4机组UPS系统母线频率 |  | float32
N2DCS.20BTB01CE101 | 7112 | #4机组110V直流电池组1输出电流 |  | float32
N2DCS.20BTB01CE102 | 7113 | #4机组110V直流电池组1输出电压 |  | float32
N2DCS.20BTB01EH001 | 7114 | #3机110V直流#1电池组熔断 |  | digital
N2DCS.20BTB02CE101 | 7115 | #4机组110V直流电池组2输出电流 |  | float32
N2DCS.20BTB02CE102 | 7116 | #4机组110V直流电池组2输出电压 |  | float32
N2DCS.20BTB02EH001 | 7117 | #3机110V直流#2电池组熔断 |  | digital
N2DCS.20BTL01CE101 | 7118 | #3机220V直流系统整流输出电流 |  | float32
N2DCS.20BTL01CE102 | 7119 | #3机220V直流系统整流输出电压 |  | float32
N2DCS.20BTM01CE101 | 7120 | #4机组110V直流A段整流输出电流 |  | float32
N2DCS.20BTM01CE102 | 7121 | #4机组110V直流A段整流输出电压 |  | float32
N2DCS.20BTM01CE201 | 7122 | #4机组110V直流A段直流母线电压 |  | float32
N2DCS.20BTM02CE101 | 7123 | #4机组110V直流B段整流输出电流 |  | float32
N2DCS.20BTM02CE102 | 7124 | #4机组110V直流B段整流输出电压 |  | float32
N2DCS.20BTM02CE201 | 7125 | #4机组110V直流B段直流母线电压 |  | float32
N2DCS.20BUA02CE101 | 7126 | #3机220V直流系统电池输出电流 |  | float32
N2DCS.20BUA02CE102 | 7127 | #3机220V直流系统电池输出电压 |  | float32
N2DCS.20BUA02CE201 | 7128 | #3机220V直流B段直流母线电压 |  | float32
N2DCS.20MJA01CE102 | 7129 | #4机组柴油发电机B相电流 |  | float32
N2DCS.20MJA01CE203 | 7130 | #4机组柴油发电机AC相线电压 |  | float32
N2DCS.20MJA01CE501 | 7131 | #4机组柴油发电机有功功率 |  | float32
N2DCS.21BAT01CE101 | 7132 | #4主变高压侧电流 | A | float32
N2DCS.21BAT01CE102 | 7133 | #4主变高压侧电压(A-C） | V | float32
N2DCS.21BAT01CE103 | 7134 | #4主变220kV侧系统频 | Hz | float32
N2DCS.21BAT01CE201 | 7135 | #4主变油温1 | ℃ | float32
N2DCS.21BAT01CE202 | 7136 | #4主变油温2 | ℃ | float32
N2DCS.21BAT01CE203 | 7137 | #4主变绕组温度 | ℃ | float32
N2DCS.21BAT01CE301 | 7138 | #4主变有功功率 | MW | float32
N2DCS.21BAT01CE302 | 7139 | #4主变无功功率 | MVAR | float32
N2DCS.21BAT01CE501 | 7140 | #4主变主表有功电度 | kWh | float32
N2DCS.21BAT01CE502 | 7141 | #4主变主表无功电度 | kWh | float32
N2DCS.21BAT01CE503 | 7142 | #4主变副表有功电度 | kWh | float32
N2DCS.21BAT01CE504 | 7143 | #4主变副表无功电度 | kWh | float32
N2DCS.21MKA01CE501 | 7144 | #4发电机有功电度 | kWh | float32
N2DCS.21MKA01CE501CI | 7145 | #4发电机有功电度 |  | float32
N2DCS.21MKA01CE502 | 7146 | #4发电机无功电度 | kWh | float32
N2DCS.21MKA01CE502CI | 7147 | #4发电机无功电度 |  | float32
N2DCS.21MKC01CE501 | 7148 | #4发电机励磁变有功电度 | kWh | float32
N2DCS.21MKC01CE501CI | 7149 | #4发电机励磁变有功电度 |  | float32
N2DCS.21MKC01CE502 | 7150 | #4发电机励磁变无功电度 | kWh | float32
N2DCS.21MKC01CE502CI | 7151 | #4发电机励磁变无功电度 |  | float32
N2DCS.20BBT01CE501CI | 7152 | #3高厂变有功电度 |  | float32
N2DCS.20BBT01CE502CI | 7153 | #3高厂变无功电度 |  | float32
N2DCS.21BAT01CE501CI | 7154 | #4主变主表有功电度 |  | float32
N2DCS.21BAT01CE502CI | 7155 | #4主变主表无功电度 |  | float32
N2DCS.21BAT01CE503CI | 7156 | #4主变副表有功电度 |  | float32
N2DCS.21BAT01CE504CI | 7157 | #4主变副表无功电度 |  | float32
N2DCS.APSSPBP1_SEQSTEP | 7158 | 降负荷断点步号 |  | float32
N2DCS.APSSPBP1_SEQTIME1 | 7159 | 降负荷断点第1步时间 |  | float32
N2DCS.APSSPBP1_SEQTIME2 | 7160 | 降负荷断点第2步时间 |  | float32
N2DCS.APSSPBP1_SEQTIME3 | 7161 | 降负荷断点第3步时间 |  | float32
N2DCS.APSSPBP1_SEQTIME4 | 7162 | 降负荷断点第4步时间 |  | float32
N2DCS.APSSPBP1_SEQTIME5 | 7163 | 降负荷断点第5步时间 |  | float32
N2DCS.APSSPBP1_SEQTIME6 | 7164 | 降负荷断点第6步时间 |  | float32
N2DCS.APSSPBP1_SEQTIME7 | 7165 | 降负荷断点第7步时间 |  | float32
N2DCS.APSSPBP1_SEQTIME8 | 7166 | 降负荷断点第8步时间 |  | float32
N2DCS.APSSPBP2_SEQSTEP | 7167 | 燃机打闸断点步号 |  | float32
N2DCS.APSSPBP2_SEQTIME1 | 7168 | 燃机打闸断点第1步时间 |  | float32
N2DCS.APSSPBP2_SEQTIME2 | 7169 | 燃机打闸断点第2步时间 |  | float32
N2DCS.APSSPBP2_SEQTIME3 | 7170 | 燃机打闸断点第3步时间 |  | float32
N2DCS.APSSPBP2_SEQTIME4 | 7171 | 燃机打闸断点第4步时间 |  | float32
N2DCS.APSSPBP2_SEQTIME5 | 7172 | 燃机打闸断点第5步时间 |  | float32
N2DCS.APSSPBP2_SEQTIME6 | 7173 | 燃机打闸断点第6步时间 |  | float32
N2DCS.APSSPBP2_SEQTIME7 | 7174 | 燃机打闸断点第7步时间 |  | float32
N2DCS.APSSPBP2_SEQTIME8 | 7175 | 燃机打闸断点第8步时间 |  | float32
N2DCS.APSSPBP3_SEQSTEP | 7176 | 余热锅炉停止断点步号 |  | float32
N2DCS.APSSPBP3_SEQTIME1 | 7177 | 余热锅炉停止断点第1步时间 |  | float32
N2DCS.APSSPBP3_SEQTIME2 | 7178 | 余热锅炉停止断点第2步时间 |  | float32
N2DCS.APSSPBP3_SEQTIME3 | 7179 | 余热锅炉停止断点第3步时间 |  | float32
N2DCS.APSSPBP3_SEQTIME4 | 7180 | 余热锅炉停止断点第4步时间 |  | float32
N2DCS.APSSPBP3_SEQTIME5 | 7181 | 余热锅炉停止断点第5步时间 |  | float32
N2DCS.APSSPBP3_SEQTIME6 | 7182 | 余热锅炉停止断点第6步时间 |  | float32
N2DCS.APSSPBP3_SEQTIME7 | 7183 | 余热锅炉停止断点第7步时间 |  | float32
N2DCS.APSSPBP3_SEQTIME8 | 7184 | 余热锅炉停止断点第8步时间 |  | float32
N2DCS.APSSPBP4_SEQSTEP | 7185 | 机组停运断点步号 |  | float32
N2DCS.APSSPBP4_SEQTIME1 | 7186 | 机组停运断点第1步时间 |  | float32
N2DCS.APSSPBP4_SEQTIME2 | 7187 | 机组停运断点第2步时间 |  | float32
N2DCS.APSSPBP4_SEQTIME3 | 7188 | 机组停运断点第3步时间 |  | float32
N2DCS.APSSPBP4_SEQTIME4 | 7189 | 机组停运断点第4步时间 |  | float32
N2DCS.APSSPBP4_SEQTIME5 | 7190 | 机组停运断点第5步时间 |  | float32
N2DCS.APSSPBP4_SEQTIME6 | 7191 | 机组停运断点第6步时间 |  | float32
N2DCS.APSSPBP4_SEQTIME7 | 7192 | 机组停运断点第7步时间 |  | float32
N2DCS.APSSPBP4_SEQTIME8 | 7193 | 机组停运断点第8步时间 |  | float32
N2DCS.APSSTBP1_SEQSTEP | 7194 | 系统准备断点步号 |  | float32
N2DCS.APSSTBP1_SEQTIME1 | 7195 | 系统准备断点第1步时间 |  | float32
N2DCS.APSSTBP1_SEQTIME2 | 7196 | 系统准备断点第2步时间 |  | float32
N2DCS.APSSTBP1_SEQTIME3 | 7197 | 系统准备断点第3步时间 |  | float32
N2DCS.APSSTBP1_SEQTIME4 | 7198 | 系统准备断点第4步时间 |  | float32
N2DCS.APSSTBP1_SEQTIME5 | 7199 | 系统准备断点第5步时间 |  | float32
N2DCS.APSSTBP1_SEQTIME6 | 7200 | 系统准备断点第6步时间 |  | float32
N2DCS.APSSTBP1_SEQTIME7 | 7201 | 系统准备断点第7步时间 |  | float32
N2DCS.APSSTBP1_SEQTIME8 | 7202 | 系统准备断点第8步时间 |  | float32
N2DCS.APSSTBP2_SEQSTEP | 7203 | 机组上水断点步号 |  | float32
N2DCS.APSSTBP2_SEQTIME1 | 7204 | 机组上水断点第1步时间 |  | float32
N2DCS.APSSTBP2_SEQTIME2 | 7205 | 机组上水断点第2步时间 |  | float32
N2DCS.APSSTBP2_SEQTIME3 | 7206 | 机组上水断点第3步时间 |  | float32
N2DCS.APSSTBP2_SEQTIME4 | 7207 | 机组上水断点第4步时间 |  | float32
N2DCS.APSSTBP2_SEQTIME5 | 7208 | 机组上水断点第5步时间 |  | float32
N2DCS.APSSTBP2_SEQTIME6 | 7209 | 机组上水断点第6步时间 |  | float32
N2DCS.APSSTBP2_SEQTIME7 | 7210 | 机组上水断点第7步时间 |  | float32
N2DCS.APSSTBP2_SEQTIME8 | 7211 | 机组上水断点第8步时间 |  | float32
N2DCS.APSSTBP3_SEQSTEP | 7212 | 燃机点火断点步号 |  | float32
N2DCS.APSSTBP3_SEQTIME1 | 7213 | 燃机点火断点第1步时间 |  | float32
N2DCS.APSSTBP3_SEQTIME2 | 7214 | 燃机点火断点第2步时间 |  | float32
N2DCS.APSSTBP3_SEQTIME3 | 7215 | 燃机点火断点第3步时间 |  | float32
N2DCS.APSSTBP3_SEQTIME4 | 7216 | 燃机点火断点第4步时间 |  | float32
N2DCS.APSSTBP3_SEQTIME5 | 7217 | 燃机点火断点第5步时间 |  | float32
N2DCS.APSSTBP3_SEQTIME6 | 7218 | 燃机点火断点第6步时间 |  | float32
N2DCS.APSSTBP3_SEQTIME7 | 7219 | 燃机点火断点第7步时间 |  | float32
N2DCS.APSSTBP3_SEQTIME8 | 7220 | 燃机点火断点第8步时间 |  | float32
N2DCS.APSSTBP4_SEQSTEP | 7221 | 汽机并网断点步号 |  | float32
N2DCS.APSSTBP4_SEQTIME1 | 7222 | 汽机并网断点第1步时间 |  | float32
N2DCS.APSSTBP4_SEQTIME2 | 7223 | 汽机并网断点第2步时间 |  | float32
N2DCS.APSSTBP4_SEQTIME3 | 7224 | 汽机并网断点第3步时间 |  | float32
N2DCS.APSSTBP4_SEQTIME4 | 7225 | 汽机并网断点第4步时间 |  | float32
N2DCS.APSSTBP4_SEQTIME5 | 7226 | 汽机并网断点第5步时间 |  | float32
N2DCS.APSSTBP4_SEQTIME6 | 7227 | 汽机并网断点第6步时间 |  | float32
N2DCS.APSSTBP4_SEQTIME7 | 7228 | 汽机并网断点第7步时间 |  | float32
N2DCS.APSSTBP4_SEQTIME8 | 7229 | 汽机并网断点第8步时间 |  | float32
N2DCS.APSSTBP5_SEQSTEP | 7230 | 升负荷断点步号 |  | float32
N2DCS.APSSTBP5_SEQTIME1 | 7231 | 升负荷断点第1步时间 |  | float32
N2DCS.APSSTBP5_SEQTIME2 | 7232 | 升负荷断点第2步时间 |  | float32
N2DCS.APSSTBP5_SEQTIME3 | 7233 | 升负荷断点第3步时间 |  | float32
N2DCS.APSSTBP5_SEQTIME4 | 7234 | 升负荷断点第4步时间 |  | float32
N2DCS.APSSTBP5_SEQTIME5 | 7235 | 升负荷断点第5步时间 |  | float32
N2DCS.APSSTBP5_SEQTIME6 | 7236 | 升负荷断点第6步时间 |  | float32
N2DCS.APSSTBP5_SEQTIME7 | 7237 | 升负荷断点第7步时间 |  | float32
N2DCS.APSSTBP5_SEQTIME8 | 7238 | 升负荷断点第8步时间 |  | float32
N2DCS.AUXSYS_SEQSTSTEP | 7239 | Ovation Control Builder |  | float32
N2DCS.AUXSYS_SEQSTTIME1 | 7240 | Ovation Control Builder |  | float32
N2DCS.AUXSYS_SEQSTTIME2 | 7241 | Ovation Control Builder |  | float32
N2DCS.AUXSYS_SEQSTTIME3 | 7242 | Ovation Control Builder |  | float32
N2DCS.AUXSYS_SEQSTTIME4 | 7243 | Ovation Control Builder |  | float32
N2DCS.AUXSYS_SEQSTTIME5 | 7244 | Ovation Control Builder |  | float32
N2DCS.AUXSYS_SEQSTTIME6 | 7245 | Ovation Control Builder |  | float32
N2DCS.AUXSYS_SEQSTTIME7 | 7246 | Ovation Control Builder |  | float32
N2DCS.HRSGFW_SEQSTSTEP | 7247 | 余热锅炉上水程控步号 |  | float32
N2DCS.HRSGFW_SEQSTTIME1 | 7248 | 余热锅炉上水程控第1步时间 |  | float32
N2DCS.HRSGFW_SEQSTTIME2 | 7249 | 余热锅炉上水程控第2步时间 |  | float32
N2DCS.HRSGFW_SEQSTTIME3 | 7250 | 余热锅炉上水程控第3步时间 |  | float32
N2DCS.HRSGFW_SEQSTTIME4 | 7251 | 余热锅炉上水程控第4步时间 |  | float32
N2DCS.HRSGFW_SEQSTTIME5 | 7252 | 余热锅炉上水程控第5步时间 |  | float32
N2DCS.J0QFA40CP101 | 7253 |  |  | float32
N2DCS.LOADSP | 7254 |  |  | float32
N2DCS.TURBWARMTIME | 7255 | Ovation Control Builder |  | float32
N2DCS.APSSPBP1_SEQTIME10 | 7256 | Ovation Control Builder |  | float32
N2DCS.APSSPBP1_SEQTIME9 | 7257 | Ovation Control Builder |  | float32
N2DCS.APSSPBP3_SEQTIME10 | 7258 | Ovation Control Builder |  | float32
N2DCS.APSSPBP3_SEQTIME9 | 7259 | Ovation Control Builder |  | float32
N2DCS.APSSPBP4_SEQTIME10 | 7260 | Ovation Control Builder |  | float32
N2DCS.APSSPBP4_SEQTIME9 | 7261 | Ovation Control Builder |  | float32
N2DCS.APSSTBP4_SEQTIME10 | 7262 | Ovation Control Builder |  | float32
N2DCS.APSSTBP4_SEQTIME9 | 7263 | Ovation Control Builder |  | float32
N2DCS.APSSTBP5_SEQTIME10 | 7264 | Ovation Control Builder |  | float32
N2DCS.APSSTBP5_SEQTIME9 | 7265 | Ovation Control Builder |  | float32
N2DCS.20MAA50CP111 | 7266 | 高压缸前后压差#1 | MPa | float32
N2DCS.20MAA50CP112 | 7267 | 高压缸前后压差#2 | MPa | float32
N2DCS.20MAA50CP113 | 7268 | 高压缸前后压差#3 | MPa | float32
N2DCS.20MAA50CT121A | 7269 | 高压排汽蒸汽温度 1# | ℃ | float32
N2DCS.20MAA50CT122A | 7270 | 高压排汽蒸汽温度 2# | ℃ | float32
N2DCS.20MAA50CT123A | 7271 | 高压排汽蒸汽温度 3# | ℃ | float32
N2DCS.20MAA50CT321 | 7272 | 高压排汽蒸汽温度 1# |  | float32
N2DCS.20MAA50CT322 | 7273 | 高压排汽蒸汽温度 2# | ℃ | float32
N2DCS.20MAA50CT323 | 7274 | 高压排汽蒸汽温度 3# |  | float32
N2DCS.20MAA50CT621A_XQ01 | 7275 | Ovation Control Builder |  | float32
N2DCS.20MAA50CT622A_XQ01 | 7276 | Ovation Control Builder |  | float32
N2DCS.20MAA50CT623A_XQ01 | 7277 | Ovation Control Builder |  | float32
N2DCS.20MAA50FT621_XQ01 | 7278 | 高压排汽蒸汽温度（3选后） |  | float32
N2DCS.20MAB50CT121A | 7279 | 中压排汽蒸汽温度 1# | ℃ | float32
N2DCS.20MAB50CT122A | 7280 | 中压排汽蒸汽温度 2# | ℃ | float32
N2DCS.20MAB50CT321 | 7281 | 中压排汽蒸汽温度 1# | ℃ | float32
N2DCS.20MAB50CT322 | 7282 | 中压排汽蒸汽温度 2# | ℃ | float32
N2DCS.20MAB50FT621_XQ01 | 7283 | Ovation Control Builder |  | float32
N2DCS.20MAC10CT671_XQ01 | 7284 | Ovation Control Builder |  | float32
N2DCS.20MAC10CT672_XQ01 | 7285 | Ovation Control Builder |  | float32
N2DCS.20MAC10CT673_XQ01 | 7286 | Ovation Control Builder |  | float32
N2DCS.20MAC10FT611A_XQ01 | 7287 | 低压缸末级叶片温度(2选后) |  | float32
N2DCS.20MAC10FT671_XQ01 | 7288 | Ovation Control Builder |  | float32
N2DCS.20MAD11CT114A | 7289 | #1支持轴承前右下温度A | ℃ | float32
N2DCS.20MAD11CT114B | 7290 | #1支持轴承前右下温度B | ℃ | float32
N2DCS.20MAD11CT114C | 7291 | #1支持轴承前右下温度C | ℃ | float32
N2DCS.20MAD11CT118A | 7292 | #1支持轴承后右下温度A | ℃ | float32
N2DCS.20MAD11CT118B | 7293 | #1支持轴承后右下温度B | ℃ | float32
N2DCS.20MAD11CT118C | 7294 | #1支持轴承后右下温度C | ℃ | float32
N2DCS.20MAD11CT314A | 7295 | #1支持轴承前右下温度A | ℃ | float32
N2DCS.20MAD11CT314B | 7296 | #1支持轴承前右下温度B | ℃ | float32
N2DCS.20MAD11CT314C | 7297 | #1支持轴承前右下温度C | ℃ | float32
N2DCS.20MAD11CT318A | 7298 | #1支持轴承后右下温度A | ℃ | float32
N2DCS.20MAD11CT318B | 7299 | #1支持轴承后右下温度B | ℃ | float32
N2DCS.20MAD11CT318C | 7300 | #1支持轴承后右下温度C | ℃ | float32
N2DCS.20MAD11CY121 | 7301 | #1径向轴承壳振1 | mm/s | float32
N2DCS.20MAD11CY122 | 7302 | #1径向轴承壳振2 | mm/s | float32
N2DCS.20MAD12CT111A | 7303 | #2支持轴承前左上温度A | ℃ | float32
N2DCS.20MAD12CT111B | 7304 | #2支持轴承前左上温度B | ℃ | float32
N2DCS.20MAD12CT111C | 7305 | #2支持轴承前左上温度C | ℃ | float32
N2DCS.20MAD12CT112A | 7306 | #2支持轴承前右上温度A | ℃ | float32
N2DCS.20MAD12CT112B | 7307 | #2支持轴承前右上温度B | ℃ | float32
N2DCS.20MAD12CT112C | 7308 | #2支持轴承前右上温度C | ℃ | float32
N2DCS.20MAD12CT113A | 7309 | #2支持轴承前左下温度A | ℃ | float32
N2DCS.20MAD12CT113B | 7310 | #2支持轴承前左下温度B | ℃ | float32
N2DCS.20MAD12CT113C | 7311 | #2支持轴承前左下温度C | ℃ | float32
N2DCS.20MAD12CT114A | 7312 | #2支持轴承前右下温度A | ℃ | float32
N2DCS.20MAD12CT114B | 7313 | #2支持轴承前右下温度B | ℃ | float32
N2DCS.20MAD12CT114C | 7314 | #2支持轴承前右下温度C | ℃ | float32
N2DCS.20MAD12CT131A | 7315 | 推力轴承前左上温度A | ℃ | float32
N2DCS.20MAD12CT131B | 7316 | 推力轴承前左上温度B | ℃ | float32
N2DCS.20MAD12CT131C | 7317 | 推力轴承前左上温度C | ℃ | float32
N2DCS.20MAD12CT132A | 7318 | 推力轴承前右上温度A | ℃ | float32
N2DCS.20MAD12CT132B | 7319 | 推力轴承前右上温度B | ℃ | float32
N2DCS.20MAD12CT132C | 7320 | 推力轴承前右上温度C | ℃ | float32
N2DCS.20MAD12CT133A | 7321 | 推力轴承前左下温度A | ℃ | float32
N2DCS.20MAD12CT133B | 7322 | 推力轴承前左下温度B | ℃ | float32
N2DCS.20MAD12CT133C | 7323 | 推力轴承前左下温度C | ℃ | float32
N2DCS.20MAD12CT134A | 7324 | 推力轴承前右下温度A | ℃ | float32
N2DCS.20MAD12CT134B | 7325 | 推力轴承前右下温度B | ℃ | float32
N2DCS.20MAD12CT134C | 7326 | 推力轴承前右下温度C | ℃ | float32
N2DCS.20MAD12CT311A | 7327 | #2支持轴承前左上温度A | ℃ | float32
N2DCS.20MAD12CT311B | 7328 | #2支持轴承前左上温度B | ℃ | float32
N2DCS.20MAD12CT311C | 7329 | #2支持轴承前左上温度C | ℃ | float32
N2DCS.20MAD12CT312A | 7330 | #2支持轴承前右上温度A | ℃ | float32
N2DCS.20MAD12CT312B | 7331 | #2支持轴承前右上温度B | ℃ | float32
N2DCS.20MAD12CT312C | 7332 | #2支持轴承前右上温度C | ℃ | float32
N2DCS.20MAD12CT313A | 7333 | #2支持轴承前左下温度A | ℃ | float32
N2DCS.20MAD12CT313B | 7334 | #2支持轴承前左下温度B | ℃ | float32
N2DCS.20MAD12CT313C | 7335 | #2支持轴承前左下温度C | ℃ | float32
N2DCS.20MAD12CT314A | 7336 | #2支持轴承前右下温度A | ℃ | float32
N2DCS.20MAD12CT314B | 7337 | #2支持轴承前右下温度B | ℃ | float32
N2DCS.20MAD12CT314C | 7338 | #2支持轴承前右下温度C | ℃ | float32
N2DCS.20MAD12CT331A | 7339 | 推力轴承前左上温度A | ℃ | float32
N2DCS.20MAD12CT331B | 7340 | 推力轴承前左上温度B | ℃ | float32
N2DCS.20MAD12CT331C | 7341 | 推力轴承前左上温度C | ℃ | float32
N2DCS.20MAD12CT332A | 7342 | 推力轴承前右上温度A | ℃ | float32
N2DCS.20MAD12CT332B | 7343 | 推力轴承前右上温度B | ℃ | float32
N2DCS.20MAD12CT332C | 7344 | 推力轴承前右上温度C | ℃ | float32
N2DCS.20MAD12CT333A | 7345 | 推力轴承前左下温度A | ℃ | float32
N2DCS.20MAD12CT333B | 7346 | 推力轴承前左下温度B | ℃ | float32
N2DCS.20MAD12CT333C | 7347 | 推力轴承前左下温度C | ℃ | float32
N2DCS.20MAD12CT334A | 7348 | 推力轴承前右下温度A | ℃ | float32
N2DCS.20MAD12CT334B | 7349 | 推力轴承前右下温度B | ℃ | float32
N2DCS.20MAD12CT334C | 7350 | 推力轴承前右下温度C | ℃ | float32
N2DCS.20MAD12CY111 | 7351 | 轴向位移1# | mm | float32
N2DCS.20MAD12CY112 | 7352 | 轴向位移2# | mm | float32
N2DCS.20MAD12CY113 | 7353 | 轴向位移3# | mm | float32
N2DCS.20MAD12CY121 | 7354 | #2径向轴承壳振1 | mm/s | float32
N2DCS.20MAD12CY122 | 7355 | #2径向轴承壳振2 | mm/s | float32
N2DCS.20MAD13CT111A | 7356 | #3支持轴承汽轮机侧前左上温度A | ℃ | float32
N2DCS.20MAD13CT111B | 7357 | #3支持轴承汽轮机侧前左上温度B | ℃ | float32
N2DCS.20MAD13CT111C | 7358 | #3支持轴承汽轮机侧前左上温度C | ℃ | float32
N2DCS.20MAD13CT112A | 7359 | #3支持轴承汽轮机侧前右上温度A | ℃ | float32
N2DCS.20MAD13CT112B | 7360 | #3支持轴承汽轮机侧前右上温度B | ℃ | float32
N2DCS.20MAD13CT112C | 7361 | #3支持轴承汽轮机侧前右上温度C | ℃ | float32
N2DCS.20MAD13CT113A | 7362 | #3支持轴承汽轮机侧前左下温度A | ℃ | float32
N2DCS.20MAD13CT113B | 7363 | #3支持轴承汽轮机侧前左下温度B | ℃ | float32
N2DCS.20MAD13CT113C | 7364 | #3支持轴承汽轮机侧前左下温度C | ℃ | float32
N2DCS.20MAD13CT114A | 7365 | #3支持轴承汽轮机侧前右下温度A | ℃ | float32
N2DCS.20MAD13CT114B | 7366 | #3支持轴承汽轮机侧前右下温度B | ℃ | float32
N2DCS.20MAD13CT114C | 7367 | #3支持轴承汽轮机侧前右下温度C | ℃ | float32
N2DCS.20MAD13CT115A | 7368 | #3支持轴承汽轮机侧后右下温度A | ℃ | float32
N2DCS.20MAD13CT115B | 7369 | #3支持轴承汽轮机侧后右下温度B | ℃ | float32
N2DCS.20MAD13CT115C | 7370 | #3支持轴承汽轮机侧后右下温度C | ℃ | float32
N2DCS.20MAD13CT311A | 7371 | #3支持轴承汽轮机侧前左上温度A | ℃ | float32
N2DCS.20MAD13CT311B | 7372 | #3支持轴承汽轮机侧前左上温度B |  | float32
N2DCS.20MAD13CT311C | 7373 | #3支持轴承汽轮机侧前左上温度C |  | float32
N2DCS.20MAD13CT312A | 7374 | #3支持轴承汽轮机侧前右上温度A |  | float32
N2DCS.20MAD13CT312B | 7375 | #3支持轴承汽轮机侧前右上温度B |  | float32
N2DCS.20MAD13CT312C | 7376 | #3支持轴承汽轮机侧前右上温度C |  | float32
N2DCS.20MAD13CT313A | 7377 | #3支持轴承汽轮机侧前左下温度A | ℃ | float32
N2DCS.20MAD13CT313B | 7378 | #3支持轴承汽轮机侧前左下温度B | ℃ | float32
N2DCS.20MAD13CT313C | 7379 | #3支持轴承汽轮机侧前左下温度C | ℃ | float32
N2DCS.20MAD13CT314A | 7380 | #3支持轴承汽轮机侧前右下温度A |  | float32
N2DCS.20MAD13CT314B | 7381 | #3支持轴承汽轮机侧前右下温度B |  | float32
N2DCS.20MAD13CT314C | 7382 | #3支持轴承汽轮机侧前右下温度C |  | float32
N2DCS.20MAD13CT315A | 7383 | #3支持轴承汽轮机侧后右下温度A |  | float32
N2DCS.20MAD13CT315B | 7384 | #3支持轴承汽轮机侧后右下温度B | ℃ | float32
N2DCS.20MAD13CT315C | 7385 | #3支持轴承汽轮机侧后右下温度C | ℃ | float32
N2DCS.20MAD13CY121 | 7386 | #3径向轴承壳振1 | mm/s | float32
N2DCS.20MAD13CY122 | 7387 | #3径向轴承壳振2 | mm/s | float32
N2DCS.20MAG01CP101 | 7388 | 凝汽器真空1# | kPa | float32
N2DCS.20MAG01CP102 | 7389 | 凝汽器真空2# | kPa | float32
N2DCS.20MAG01CP103 | 7390 | 凝汽器真空3# | kPa | float32
N2DCS.20MAG01FP101_XQ01 | 7391 | 凝汽器真空(选择后) |  | float32
N2DCS.20MAV10CL121 | 7392 | 润滑油液位1# | mm | float32
N2DCS.20MAV10CL122 | 7393 | 润滑油液位2# | mm | float32
N2DCS.20MAV10CL123 | 7394 | 润滑油液位3# | mm | float32
N2DCS.20MAV10FL121_XQ01 | 7395 | Ovation Control Builder |  | float32
N2DCS.20MAV42CP116 | 7396 | 润滑油母管压力1# | MPa | float32
N2DCS.20MAV42CP117 | 7397 | 润滑油母管压力2# | MPa | float32
N2DCS.20MAV42CP118 | 7398 | 润滑油母管压力3# | MPa | float32
N2DCS.20MAV42FP116_XQ01 | 7399 | Ovation Control Builder |  | float32
N2DCS.20MAX01CP101_DEH | 7400 | 控制油泵出口压力1# | MPa | float32
N2DCS.20MAX01CP102_DEH | 7401 | 控制油泵出口压力2# | MPa | float32
N2DCS.20MAX01CP103_DEH | 7402 | 控制油泵出口压力3# | MPa | float32
N2DCS.20MAX01FP103_XQ01 | 7403 | Ovation Control Builder |  | float32
N2DCS.20MKD11CT013A | 7404 | #1汽轮发电机轴承左下温度A |  | float32
N2DCS.20MKD11CT013B | 7405 | #1汽轮发电机轴承左下温度B |  | float32
N2DCS.20MKD11CT014A | 7406 | #1汽轮发电机轴承右下温度A |  | float32
N2DCS.20MKD11CT014B | 7407 | #1汽轮发电机轴承右下温度B |  | float32
N2DCS.20MKD11CT113A | 7408 | #1汽轮发电机轴承左下温度A | ℃ | float32
N2DCS.20MKD11CT113B | 7409 | #1汽轮发电机轴承左下温度B | ℃ | float32
N2DCS.20MKD11CT114A | 7410 | #1汽轮发电机轴承右下温度A | ℃ | float32
N2DCS.20MKD11CT114B | 7411 | #1汽轮发电机轴承右下温度B | ℃ | float32
N2DCS.20MKD11CY121 | 7412 | #4轴承壳振1 | mm/s | float32
N2DCS.20MKD11CY122 | 7413 | #4轴承壳振2 | mm/s | float32
N2DCS.20MKD12CT013A | 7414 | #2汽轮发电机轴承左下温度A |  | float32
N2DCS.20MKD12CT013B | 7415 | #2汽轮发电机轴承左下温度B |  | float32
N2DCS.20MKD12CT014A | 7416 | #2汽轮发电机轴承右下温度A |  | float32
N2DCS.20MKD12CT014B | 7417 | #2汽轮发电机轴承右下温度B |  | float32
N2DCS.20MKD12CT113A | 7418 | #2汽轮发电机轴承左下温度A | ℃ | float32
N2DCS.20MKD12CT113B | 7419 | #2汽轮发电机轴承左下温度B | ℃ | float32
N2DCS.20MKD12CT114A | 7420 | #2汽轮发电机轴承右下温度A | ℃ | float32
N2DCS.20MKD12CT114B | 7421 | #2汽轮发电机轴承右下温度B | ℃ | float32
N2DCS.20MKD12CY121 | 7422 | #5轴承壳振1 | mm/s | float32
N2DCS.20MKD12CY122 | 7423 | #5轴承壳振2 | mm/s | float32
N2DCS.20MYA01CS111 | 7424 | 高中压汽轮机转速 1 |  | float32
N2DCS.20MYA01CS112 | 7425 | 高中压汽轮机转速 2 |  | float32
N2DCS.20MYA01CS113 | 7426 | 高中压汽轮机转速 3 |  | float32
N2DCS.20MYA01CS114 | 7427 | 高中压汽轮机转速 4 |  | float32
N2DCS.20MYA01CS115 | 7428 | 高中压汽轮机转速 5 |  | float32
N2DCS.20MYA01CS116 | 7429 | 高中压汽轮机转速 6 |  | float32
N2DCS.D41P1B1L5C9 | 7430 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D41P1B1L6C9 | 7431 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D41P1B1L7C9 | 7432 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D41P1B3L4C9 | 7433 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D41P1B3L5C9 | 7434 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D41P1B3L6C9 | 7435 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D41P1B3L7C9 | 7436 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D41P1B4L1C9 | 7437 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D41P1B4L2C9 | 7438 | TC冷端温度补偿点 | DEGC | float32
N2DCS.20MAD12CY | 7439 | Ovation Control Builder |  | float32
N2DCS.20CJA00DP200_XQ05 | 7440 | Ovation Control Builder |  | float32
N2DCS.20CJA01DP100_DEH | 7441 | 主蒸汽压力设定(1/102) | MPa | float32
N2DCS.20CJA01DP200_DEH | 7442 | 再热蒸汽压力设定 | MPa | float32
N2DCS.20CJA01DP300 | 7443 | 低压蒸汽压力设定 | MPa | float32
N2DCS.20LBA10CP901_PFD | 7444 | 高压主汽门前蒸汽压力（Bar） |  | float32
N2DCS.20LBA10CP901_PFD11 | 7445 | Ovation Control Builder |  | float32
N2DCS.20LBA10CP901_XQ01 | 7446 | 高压主汽门前蒸汽压力（三选中） |  | float32
N2DCS.20LBA20CP104 | 7447 | 高压主汽门前蒸汽压力#1 | MPa | float32
N2DCS.20LBA20CP104_XQ01 | 7448 | 高压主汽门前蒸汽压力#1 |  | float32
N2DCS.20LBA20CP105 | 7449 | 高压主汽门前蒸汽压力#2 | MPa | float32
N2DCS.20LBA20CP105_XQ01 | 7450 | 高压主汽门前蒸汽压力#2 |  | float32
N2DCS.20LBA20CP106 | 7451 | 高压主汽门前蒸汽压力#3 | MPa | float32
N2DCS.20LBA20CP106_XQ01 | 7452 | 高压主汽门前蒸汽压力#3 |  | float32
N2DCS.20LBA90CP104 | 7453 | 低压主汽门前蒸汽压力#1 | MPa | float32
N2DCS.20LBA90CP104_XQ01 | 7454 | 补汽主汽门前压力#1 |  | float32
N2DCS.20LBA90CP105 | 7455 | 低压主汽门前蒸汽压力#2 | MPa | float32
N2DCS.20LBA90CP105_XQ01 | 7456 | 补汽主汽门前压力#2 |  | float32
N2DCS.20LBA90CP106 | 7457 | 低压主汽门前蒸汽压力#3 | MPa | float32
N2DCS.20LBA90CP106_XQ01 | 7458 | 补汽主汽门前压力#3 |  | float32
N2DCS.20LBA90CP901_PZD | 7459 | 低压主汽门前蒸汽压力（Bar） |  | float32
N2DCS.20LBA90CP901_PZD11 | 7460 | Ovation Control Builder |  | float32
N2DCS.20LBA90CP901_XQ01 | 7461 | 低压主汽门前蒸汽压力（选择后） |  | float32
N2DCS.20LBB10CP901_PHZ | 7462 | 中压主汽门前蒸汽压力（Bar） |  | float32
N2DCS.20LBB10CP901_PHZ11 | 7463 | 中压主汽门前蒸汽压力 |  | float32
N2DCS.20LBB10CP901_XQ01 | 7464 | 中压主汽门前蒸汽压力（选择后） |  | float32
N2DCS.20LBB50CP104 | 7465 | 中压主汽前蒸汽压力#1 | MPa | float32
N2DCS.20LBB50CP104_XQ01 | 7466 | 中压主汽门前蒸汽压力#1 |  | float32
N2DCS.20LBB50CP105 | 7467 | 中压主汽门前蒸汽压力#2 | MPa | float32
N2DCS.20LBB50CP105_XQ01 | 7468 | 中压主汽门前蒸汽压力#2 |  | float32
N2DCS.20LBB50CP106 | 7469 | 中压主汽门前蒸汽压力#3 | MPa | float32
N2DCS.20LBB50CP106_XQ01 | 7470 | 中压主汽门前蒸汽压力#3 |  | float32
N2DCS.20LBB51CP901_XQ01 | 7471 | Ovation Control Builder |  | float32
N2DCS.20LBC40CG152 | 7472 | 高排调节阀力矩反馈 | % | float32
N2DCS.20LBC40CP101 | 7473 | 高压排汽蒸汽压力1# | MPa | float32
N2DCS.20LBC40CP101_XQ01 | 7474 | 高压排气蒸汽压力#1 |  | float32
N2DCS.20LBC40CP102 | 7475 | 高压排汽蒸汽压力2# | MPa | float32
N2DCS.20LBC40CP102_XQ01 | 7476 | 高压排气蒸汽压力#2 |  | float32
N2DCS.20LBC40CP103 | 7477 | 高压排汽蒸汽压力3# | MPa | float32
N2DCS.20LBC40CP103_XQ01 | 7478 | 高压排气蒸汽压力#3 |  | float32
N2DCS.20LBC40FP101_XQ01 | 7479 | 高压排汽蒸汽压力（3选中） |  | float32
N2DCS.20LBD20CP102 | 7480 | 冷再抽汽减压阀前压力 | MPa | float32
N2DCS.20LBD40CG151 | 7481 | 中压抽汽快关调节阀阀位反馈 |  | float32
N2DCS.20LBD40CP102 | 7482 | 热再抽汽减压阀前压力 | MPa | float32
N2DCS.20LBS45AA001_SETP | 7483 | Ovation Control Builder |  | float32
N2DCS.20LBS45AA001_XQ02 | 7484 | Ovation Control Builder |  | float32
N2DCS.20LBS45AA012A | 7485 | 中压抽汽快关调节阀控制设定 | % | float32
N2DCS.20LBS45AA101_TRACKV | 7486 | Ovation Control Builder |  | float32
N2DCS.20LBS45AA112A | 7487 | 中压抽汽快关调节阀控制设定 |  | float32
N2DCS.20LBS45CG151 | 7488 | 中压抽汽快关调节阀阀位反馈 | % | float32
N2DCS.20LBS45CG151_XQ01 | 7489 | 中压抽汽快关调节阀阀位反馈 |  | float32
N2DCS.20LBS46AA001_SETP | 7490 | 高排抽汽压力设定值 |  | float32
N2DCS.20LBS46AA001_XQ02 | 7491 | Ovation Control Builder |  | float32
N2DCS.20LBS46AA012A | 7492 | 高压抽汽快关调节阀控制设定 | % | float32
N2DCS.20LBS46AA101_TRACKV | 7493 | Ovation Control Builder |  | float32
N2DCS.20LBS46AA112A | 7494 | 高压抽汽快关调节阀控制设定 |  | float32
N2DCS.20LBS46CG151 | 7495 | 高压抽汽快关调节阀阀位反馈 | % | float32
N2DCS.20LBS46CG151_XQ01 | 7496 | 高压抽气快关调节阀阀位反馈 |  | float32
N2DCS.20MAA11CG051 | 7497 | 高压主汽门阀位 |  | float32
N2DCS.20MAA11CG151 | 7498 | 高压主汽门阀位 | % | float32
N2DCS.20MAA11CG151_XQ01 | 7499 | 高压主汽阀阀位反馈 |  | float32
N2DCS.20MAA12AA012 | 7500 | Ovation Control Builder |  | float32
N2DCS.20MAA12AA012_T | 7501 | Ovation Control Builder |  | float32
N2DCS.20MAA12AA112A | 7502 | 高压调门指令1 |  | float32
N2DCS.20MAA12AA112B | 7503 | 高压调门指令2 |  | float32
N2DCS.20MAA12CG051 | 7504 | 高压调门阀位 |  | float32
N2DCS.20MAA12CG151 | 7505 | 高压调门阀位 |  | float32
N2DCS.20MAA12CG151_XQ01 | 7506 | 高压调阀阀位反馈 |  | float32
N2DCS.20MAA12DG010_BFD | 7507 | 高调门阀限 |  | float32
N2DCS.20MAA12DG010_BFDV | 7508 | 高调门阀限 |  | float32
N2DCS.20MAA12DG010_OUT | 7509 | Ovation Control Builder |  | float32
N2DCS.20MAA12DG010_TRACKV | 7510 | 高调门阀限跟踪 |  | float32
N2DCS.20MAA12DG050_HPCMD | 7511 | Ovation Control Builder |  | float32
N2DCS.20MAA12DG050_YFDR | 7512 | 高调门阀位设定值 |  | float32
N2DCS.20MAA50CP101 | 7513 | 高调门阀后蒸汽压力1# | MPa | float32
N2DCS.20MAA50CP101_XQ01 | 7514 | Ovation Control Builder |  | float32
N2DCS.20MAA50CP102 | 7515 | 高调门阀后蒸汽压力2# | MPa | float32
N2DCS.20MAA50CP102_XQ01 | 7516 | Ovation Control Builder |  | float32
N2DCS.20MAA50CP103 | 7517 | 高调门阀后蒸汽压力3# | MPa | float32
N2DCS.20MAA50CP103_XQ01 | 7518 | Ovation Control Builder |  | float32
N2DCS.20MAA50CP111_XQ01 | 7519 | 高压缸前后压差#1 |  | float32
N2DCS.20MAA50CP112_XQ01 | 7520 | 高压缸前后压差#2 |  | float32
N2DCS.20MAA50CP113_XQ01 | 7521 | 高压缸前后压差#3 |  | float32
N2DCS.20MAA50DP111_XQ01 | 7522 | 高压缸压比 |  | float32
N2DCS.20MAA50FP011_XQ01 | 7523 | 高调门阀后蒸汽压力（3选中） |  | float32
N2DCS.20MAA50FP011_XQ02 | 7524 | 高排抽汽时高排压力低限 |  | float32
N2DCS.20MAA50FP111_XQ01 | 7525 | 高压缸前后压差(3选后) |  | float32
N2DCS.20MAB11AA012_SPT | 7526 | Ovation Control Builder |  | float32
N2DCS.20MAB11CG151 | 7527 | 中压主汽门阀位 | % | float32
N2DCS.20MAB11CG151_XQ01 | 7528 | 中压主汽门阀位反馈 |  | float32
N2DCS.20MAB12AA012 | 7529 | Ovation Control Builder |  | float32
N2DCS.20MAB12AA012_T | 7530 | Ovation Control Builder |  | float32
N2DCS.20MAB12AA112A | 7531 | 中压调门指令1 |  | float32
N2DCS.20MAB12AA112B | 7532 | 中压调门指令2 |  | float32
N2DCS.20MAB12CG051 | 7533 | 中压调门阀位 |  | float32
N2DCS.20MAB12CG151 | 7534 | 中压调门阀位 |  | float32
N2DCS.20MAB12CG151_XQ01 | 7535 | 中压调门阀位反馈 |  | float32
N2DCS.20MAB12DG010_BAF | 7536 | 中调门阀限 |  | float32
N2DCS.20MAB12DG010_BAFV | 7537 | 中调门阀限 |  | float32
N2DCS.20MAB12DG010_OUT | 7538 | Ovation Control Builder |  | float32
N2DCS.20MAB12DG010_TRACKV | 7539 | Ovation Control Builder |  | float32
N2DCS.20MAB12DG050_IPCMD | 7540 | Ovation Control Builder |  | float32
N2DCS.20MAB12DG050_YAFR | 7541 | 中压调门阀位设定 |  | float32
N2DCS.20MAB21CG051 | 7542 | 中压主汽门阀位 |  | float32
N2DCS.20MAB50CP101 | 7543 | 中调门阀后蒸汽压力 | MPa | float32
N2DCS.20MAB50CP101_XQ01 | 7544 | 中压调门后蒸汽压力 |  | float32
N2DCS.20MAB50CP121 | 7545 | 中压缸排汽压力 #1 | MPa | float32
N2DCS.20MAB50CP122 | 7546 | 中压缸排汽压力 #2 | MPa | float32
N2DCS.20MAB50CP123 | 7547 | 中压缸排汽压力 #3 | MPa | float32
N2DCS.20MAC10CP101 | 7548 | 低压缸进汽压力 #1 | MPa | float32
N2DCS.20MAC10CP101_XQ01 | 7549 | 低压缸进汽压力#1 |  | float32
N2DCS.20MAC10CP102 | 7550 | 低压缸进汽压力 #2 | MPa | float32
N2DCS.20MAC10CP102_XQ01 | 7551 | 低压缸进汽压力#2 |  | float32
N2DCS.20MAC10CP103 | 7552 | 低压缸进汽压力 #3 | MPa | float32
N2DCS.20MAC10CP103_XQ01 | 7553 | 低压缸进汽压力#3 |  | float32
N2DCS.20MAC10CP901_XQ01 | 7554 | Ovation Control Builder |  | float32
N2DCS.20MAC10CP901_XQ02 | 7555 | Ovation Control Builder |  | float32
N2DCS.20MAC10CP901_XQ09 | 7556 | Ovation Control Builder |  | float32
N2DCS.20MAC46AA012A | 7557 | 低压补汽调阀控制设定 |  | float32
N2DCS.20MAC46AA112A | 7558 | 低压补汽调阀控制设定 | % | float32
N2DCS.20MAC46CG151 | 7559 | 低压补汽调阀阀位反馈 | % | float32
N2DCS.20MAC46CG151_XQ01 | 7560 | 低压补汽调门阀位反馈 |  | float32
N2DCS.20MAC46DG010_BZD | 7561 | 低调门阀限 |  | float32
N2DCS.20MAC46DG010_BZDV | 7562 | 低调阀阀限 |  | float32
N2DCS.20MAC46DG010_OUT | 7563 | Ovation Control Builder |  | float32
N2DCS.20MAC46DG010_TRACKV | 7564 | Ovation Control Builder |  | float32
N2DCS.20MAC46DG050_LPCMD | 7565 | Ovation Control Builder |  | float32
N2DCS.20MAG01FP101_XQ21 | 7566 | Ovation Control Builder |  | float32
N2DCS.20MAL11AA151T_XQ01 | 7567 | 高压主汽门疏水阀指令 | % | float32
N2DCS.20MAL11CG151_XQ01 | 7568 | 高压调门前疏水阀位反馈 | % | float32
N2DCS.20MAN52CG161_XQ01 | 7569 | Ovation Control Builder |  | float32
N2DCS.20MAN52CP001_XQ01 | 7570 | Ovation Control Builder |  | float32
N2DCS.20MAV10FL121_XQ21 | 7571 | Ovation Control Builder |  | float32
N2DCS.20MAV42FP116_XQ21 | 7572 | Ovation Control Builder |  | float32
N2DCS.20MAX01FP103_XQ21 | 7573 | Ovation Control Builder |  | float32
N2DCS.20MAY01CS118 | 7574 | 汽机实际转速（去电厂LED） | rpm | float32
N2DCS.20MAY10EC001_DNTS | 7575 | 汽机停止顺控步序号 |  | float32
N2DCS.20MAY10EC001_DPT51 | 7576 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DPT52 | 7577 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DPT53 | 7578 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DT54 | 7579 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DT55 | 7580 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DT56 | 7581 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DT57 | 7582 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DT58 | 7583 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DT59 | 7584 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DT60 | 7585 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_DT61 | 7586 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT1 | 7587 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT10 | 7588 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT11 | 7589 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT12 | 7590 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT13 | 7591 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT14 | 7592 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT15 | 7593 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT16 | 7594 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT17 | 7595 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT18 | 7596 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT19 | 7597 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT2 | 7598 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT20 | 7599 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT21 | 7600 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT22 | 7601 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT23 | 7602 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT24 | 7603 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT25 | 7604 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT3 | 7605 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT4 | 7606 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT5 | 7607 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT6 | 7608 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT7 | 7609 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT8 | 7610 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPT9 | 7611 | Ovation Control Builder |  | float32
N2DCS.20MAY10EC001_UPTS | 7612 | 汽机启动顺控步序号 |  | float32
N2DCS.20MAY10FT910_LEFT_TIME | 7613 | 暖机剩余时间 |  | float32
N2DCS.20MKA01CE003A | 7614 | 发电机功率#1 | MW | float32
N2DCS.20MKA01CE003B | 7615 | 发电机功率#2 | MW | float32
N2DCS.20MKA01CE003C | 7616 | 发电机功率#3 | MW | float32
N2DCS.20MKA01CE903_PEL | 7617 | #3机负荷 |  | float32
N2DCS.20MKA01CE903_PELKOR | 7618 | 发电机功率（百分比） |  | float32
N2DCS.20MKA02CE901_DEH | 7619 | 汽轮发电机实际功率 | MW | float32
N2DCS.20MKA10FA101 | 7620 | 协调控制负荷设定#1 | MW | float32
N2DCS.20MKA10FA102_DEH | 7621 | 协调控制负荷设定#2 | MW | float32
N2DCS.20MKA10FA103_DEH | 7622 | 频率偏差 | rpm | float32
N2DCS.20MYA01CS001_XQ01 | 7623 | Ovation Control Builder |  | float32
N2DCS.20MYA01CS001_XQ02 | 7624 | Ovation Control Builder |  | float32
N2DCS.20MYA01CS011C | 7625 | 汽轮机转速 1 | RPM | float32
N2DCS.20MYA01CS012C | 7626 | 汽轮机转速 2 | RPM | float32
N2DCS.20MYA01CS013C | 7627 | 汽轮机转速 3 | RPM | float32
N2DCS.20MYA01CS021C | 7628 | 汽轮机转速 4 | RPM | float32
N2DCS.20MYA01CS022C | 7629 | 汽轮机转速 5 | RPM | float32
N2DCS.20MYA01CS023C | 7630 | 汽轮机转速 6 | RPM | float32
N2DCS.20MYA01CS111C | 7631 | 汽轮机转速 1 | RPM | float32
N2DCS.20MYA01CS112C | 7632 | 汽轮机转速 2 | RPM | float32
N2DCS.20MYA01CS113C | 7633 | 汽轮机转速 3 | RPM | float32
N2DCS.20MYA01CS121C | 7634 | 汽轮机转速 4 | RPM | float32
N2DCS.20MYA01CS122C | 7635 | 汽轮机转速 5 | RPM | float32
N2DCS.20MYA01CS123C | 7636 | 汽轮机转速 6 | RPM | float32
N2DCS.20MYA01CS901_NT | 7637 | 汽轮机转速（HZ） |  | float32
N2DCS.20MYA01CS901_XQ01 | 7638 | 汽轮机转速 |  | float32
N2DCS.20MYA01CS901C_DEH | 7639 | 汽轮机转速(去远动) | rpm | float32
N2DCS.20MYA01DG010_OS | 7640 | 外部负荷设定 |  | float32
N2DCS.20MYA01DG010_OSV | 7641 | 负荷设定参考（百分比） |  | float32
N2DCS.20MYA01DG010_OSV2 | 7642 | 负荷设定参考(MW) |  | float32
N2DCS.20MYA01DG010_OSX | 7643 | 协调控制负荷设定值 |  | float32
N2DCS.20MYA01DG010_OSX2 | 7644 | Ovation Control Builder |  | float32
N2DCS.20MYA01DG010_P100 | 7645 | Ovation Control Builder |  | float32
N2DCS.20MYA01DG010_VGOS | 7646 | 负荷设定 |  | float32
N2DCS.20MYA01DG011_OSGI | 7647 | 内部进汽设定值梯度 |  | float32
N2DCS.20MYA01DG020_XQ01 | 7648 | TABx0.01 |  | float32
N2DCS.20MYA01DG020_XQ02 | 7649 | TAB值 |  | float32
N2DCS.20MYA01DG110C | 7650 | 负荷设定参考 | MW | float32
N2DCS.20MYA01DP010_FDS | 7651 | 实时高压压力设定值 |  | float32
N2DCS.20MYA01DP010_FDSV | 7652 | 延时高压压力设定值 |  | float32
N2DCS.20MYA01DP010_FDSVK | 7653 | 修正的延时高压压力设定值 |  | float32
N2DCS.20MYA01DP010_FDSX | 7654 | 高压压力设定(来自Drop1) |  | float32
N2DCS.20MYA01DP010_FDXW | 7655 | 主蒸汽压力控制偏差 |  | float32
N2DCS.20MYA01DP010_VGFDS | 7656 | 高压压力设定(手动) |  | float32
N2DCS.20MYA01DP011_DGD | 7657 | 压力限制偏置值 |  | float32
N2DCS.20MYA01DP011_DVD | 7658 | 初压模式偏置值 |  | float32
N2DCS.20MYA01DP020_EGVS | 7659 | Ovation Control Builder |  | float32
N2DCS.20MYA01DP020_HZS | 7660 | 实时再热压力设定值bar |  | float32
N2DCS.20MYA01DP020_HZSV | 7661 | 延时再热压力设定值bar |  | float32
N2DCS.20MYA01DP020_HZSX | 7662 | 再热蒸汽压力设定 |  | float32
N2DCS.20MYA01DP020_VGHZS | 7663 | 再热蒸汽压力手动设定值 |  | float32
N2DCS.20MYA01DP020_XQ03 | 7664 | Ovation Control Builder |  | float32
N2DCS.20MYA01DP030_VGZDS | 7665 | 低压压力设定(手动) |  | float32
N2DCS.20MYA01DP030_ZDS | 7666 | 实时低压压力设定值 |  | float32
N2DCS.20MYA01DP030_ZDSV | 7667 | 延时低压压力设定值 |  | float32
N2DCS.20MYA01DP030_ZDSX | 7668 | 低压压力设定值 |  | float32
N2DCS.20MYA01DP050_P120Y | 7669 | 主蒸汽压力输出限值 |  | float32
N2DCS.20MYA01DP050_YFDPR | 7670 | 高压主蒸汽压力控制输出 |  | float32
N2DCS.20MYA01DP060_YHZPR | 7671 | 再热压力控制器输出值 |  | float32
N2DCS.20MYA01DP070_YZDPR | 7672 | 低压压力控制器输出 |  | float32
N2DCS.20MYA01DP090_PIRY | 7673 | Ovation Control Builder |  | float32
N2DCS.20MYA01DP090_YHVDR | 7674 | 高压压比控制器输出 |  | float32
N2DCS.20MYA01DS010_NS | 7675 | Ovation Control Builder |  | float32
N2DCS.20MYA01DS010_NS0 | 7676 | Ovation Control Builder |  | float32
N2DCS.20MYA01DS010_NSV | 7677 | 延时转速设定值 |  | float32
N2DCS.20MYA01DS010_OFBY | 7678 | 转速设定值上升梯度 |  | float32
N2DCS.20MYA01DS010_UFBY | 7679 | 转速设定值下降梯度 |  | float32
N2DCS.20MYA01DS010_VGNS | 7680 | Ovation Control Builder |  | float32
N2DCS.20MYA01DT050_PIRY | 7681 | Ovation Control Builder |  | float32
N2DCS.20MYA01DT050_YHATR | 7682 | 高排温度控制器输出 |  | float32
N2DCS.20MYA01DU011_OFBN | 7683 | 转速设定值梯度上限 |  | float32
N2DCS.20MYA01DU011_OFBO | 7684 | 进汽设定值梯度上限 |  | float32
N2DCS.20MYA01DU011_UFBN | 7685 | 转速设定值梯度下限 |  | float32
N2DCS.20MYA01DU011_UFBO | 7686 | 进汽设定值梯度下限 |  | float32
N2DCS.20MYA01DU011_XQ51 | 7687 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU011_XQ52 | 7688 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU050_DNY | 7689 | 转速控制偏差 |  | float32
N2DCS.20MYA01DU050_FREQT | 7690 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU050_N410 | 7691 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU050_N420 | 7692 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU050_N490 | 7693 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU050_SET | 7694 | 转速/负荷控制偏差 |  | float32
N2DCS.20MYA01DU050_WY | 7695 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU050_YNOR | 7696 | 转速控制器输出值 |  | float32
N2DCS.20MYA01DU050_YNOR2 | 7697 | 负荷控制器输出值 |  | float32
N2DCS.20MYA01DU060_AF14 | 7698 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU060_AFMUS | 7699 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU060_INV | 7700 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU060_OSAF | 7701 | 中压调门进汽设定值 |  | float32
N2DCS.20MYA01DU060_OSFD | 7702 | 高压调门进汽设定值 |  | float32
N2DCS.20MYA01DU060_OSZD | 7703 | 低压调门进汽设定值 |  | float32
N2DCS.20MYA01DU060_PFDFE1 | 7704 | 实际主蒸汽信号 |  | float32
N2DCS.20MYA01DU060_PFDN | 7705 | 高主门前蒸汽压力与额定压力比值 |  | float32
N2DCS.20MYA01DU060_TABS | 7706 | TAB控制器输出 |  | float32
N2DCS.20MYA01DU060_YAF | 7707 | 中压调门阀位控制器设定值 |  | float32
N2DCS.20MYA01DU060_YR | 7708 | 中央小选块输出 |  | float32
N2DCS.20MYA01DU060_YRFD | 7709 | 高压调门阀位控制器设定值 |  | float32
N2DCS.20MYA01DU060_YRKOR | 7710 | 进汽修正 |  | float32
N2DCS.20MYA01DU060_YZD | 7711 | 低压调门阀位控制器设定值 |  | float32
N2DCS.20MYA01EZ400_XQ01 | 7712 | Ovation Control Builder |  | float32
N2DCS.20NAA01CP101 | 7713 | 热网抽汽调阀后压力（高排）#1 | MPa | float32
N2DCS.20NAA01CP101_XQ01 | 7714 | 冷再抽气减压阀前压力 |  | float32
N2DCS.20NAA01CP102 | 7715 | 热网抽汽调阀后压力（高排）#2 | MPa | float32
N2DCS.20NAA01CP102_XQ01 | 7716 | Ovation Control Builder |  | float32
N2DCS.20NAA01CP103 | 7717 | 热网抽汽调阀后压力（高排）#3 | MPa | float32
N2DCS.20NAA01CP103_XQ01 | 7718 | Ovation Control Builder |  | float32
N2DCS.20NAA01FP101_XQ01 | 7719 | 冷再抽汽减压阀前压力（3选中） |  | float32
N2DCS.20NAA02CP101 | 7720 | 中压抽汽蒸汽压力(调阀后)#1 | MPa | float32
N2DCS.20NAA02CP101_XQ01 | 7721 | 热再抽汽减压阀阀前压力 |  | float32
N2DCS.20NAA02CP102 | 7722 | 中压抽汽蒸汽压力(调阀后)#2 | MPa | float32
N2DCS.20NAA02CP102_XQ01 | 7723 | Ovation Control Builder |  | float32
N2DCS.20NAA02CP103 | 7724 | 中压抽汽蒸汽压力(调阀后)#3 | MPa | float32
N2DCS.20NAA02CP103_XQ01 | 7725 | Ovation Control Builder |  | float32
N2DCS.20NAA02FP101_XQ01 | 7726 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_BOILER | 7727 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_FLOW | 7728 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SCVAREA | 7729 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMEXTRA_HP | 7730 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMEXTRA_IP | 7731 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMHPB | 7732 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMHP_EXH_P | 7733 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMIDUP | 7734 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMIPB | 7735 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMLPB | 7736 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMPFD | 7737 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIMPHZ | 7738 | Ovation Control Builder |  | float32
N2DCS.20SIM01EZ001_SIVAREA | 7739 | Ovation Control Builder |  | float32
N2DCS.2_1_7_COIL_1_KSERVO_A | 7740 | Ovation Control Builder |  | float32
N2DCS.2_1_7_COIL_2_KSERVO_A | 7741 | Ovation Control Builder |  | float32
N2DCS.2_1_8_COIL_1_KSERVO_A | 7742 | Ovation Control Builder |  | float32
N2DCS.2_1_8_COIL_2_KSERVO_A | 7743 | Ovation Control Builder |  | float32
N2DCS.AFOB | 7744 | 中压调门阀门进汽起点 |  | float32
N2DCS.AFOE | 7745 | 中压调门阀门进汽终点 |  | float32
N2DCS.BEGME | 7746 | 测量范围上限限值 |  | float32
N2DCS.BONTGT | 7747 | Ovation Control Builder |  | float32
N2DCS.DCS_HPFLOW | 7748 | Ovation Control Builder |  | float32
N2DCS.DCS_IPFLOW | 7749 | Ovation Control Builder |  | float32
N2DCS.DCS_IP_BP_D_PRESS | 7750 | Ovation Control Builder |  | float32
N2DCS.DCS_IP_BP_POS | 7751 | Ovation Control Builder |  | float32
N2DCS.DCS_IP_BP_U_PRESS | 7752 | Ovation Control Builder |  | float32
N2DCS.DGDI | 7753 | Ovation Control Builder |  | float32
N2DCS.DNKUPA | 7754 | Ovation Control Builder |  | float32
N2DCS.DNKUPE | 7755 | Ovation Control Builder |  | float32
N2DCS.ENTGT | 7756 | Ovation Control Builder |  | float32
N2DCS.FBMAX | 7757 | 最大允许裕度 |  | float32
N2DCS.FDNOM | 7758 | Ovation Control Builder |  | float32
N2DCS.FDPRKP | 7759 | 主蒸汽压力控制器比例系数 |  | float32
N2DCS.FDPRTN | 7760 | Ovation Control Builder |  | float32
N2DCS.FDSHMI | 7761 | 实时高压压力设定值（显示） |  | float32
N2DCS.FDSVG | 7762 | 延时主蒸汽压力设定值梯度 |  | float32
N2DCS.FDSVG2 | 7763 | 延时主蒸汽压力设定值梯度2 |  | float32
N2DCS.FDSVHMI | 7764 | 延时高压压力设定值（显示） |  | float32
N2DCS.GDNGD | 7765 | Ovation Control Builder |  | float32
N2DCS.GDNT | 7766 | 转速控制偏差限制值 |  | float32
N2DCS.GNSR | 7767 | Ovation Control Builder |  | float32
N2DCS.GNTGRD | 7768 | Ovation Control Builder |  | float32
N2DCS.GSP1A | 7769 | Ovation Control Builder |  | float32
N2DCS.GSP1E | 7770 | Ovation Control Builder |  | float32
N2DCS.GSP2A | 7771 | Ovation Control Builder |  | float32
N2DCS.GSP2E | 7772 | Ovation Control Builder |  | float32
N2DCS.GTAB | 7773 | Ovation Control Builder |  | float32
N2DCS.GV_1_1_7_COIL1 | 7774 | 1_1_7 COIL1 VOLTAGE |  | float32
N2DCS.GV_1_1_7_COIL2 | 7775 | 1_1_7 COIL2 VOLTAGE |  | float32
N2DCS.GV_COMMAND | 7776 | GV 11CH COMMAND |  | float32
N2DCS.GV_DEMOD | 7777 |  |  | float32
N2DCS.GV_SPO | 7778 | Ovation Control Builder |  | float32
N2DCS.GV_STAT_POINT | 7779 | GV 14CH STAT |  | float32
N2DCS.GWHF | 7780 | Ovation Control Builder |  | float32
N2DCS.GWLF | 7781 | Ovation Control Builder |  | float32
N2DCS.GYRKOR | 7782 | 修正的进汽设定值限制值 |  | float32
N2DCS.HATNOM | 7783 | Ovation Control Builder |  | float32
N2DCS.HATRKP | 7784 | Ovation Control Builder |  | float32
N2DCS.HATRTS | 7785 | Ovation Control Builder |  | float32
N2DCS.HPE_RATE | 7786 | Ovation Control Builder |  | float32
N2DCS.HPETGT | 7787 | Ovation Control Builder |  | float32
N2DCS.HVDNOM | 7788 | Ovation Control Builder |  | float32
N2DCS.HVDRKP | 7789 | Ovation Control Builder |  | float32
N2DCS.HVDRTS | 7790 | Ovation Control Builder |  | float32
N2DCS.HZNOM | 7791 | Ovation Control Builder |  | float32
N2DCS.HZPRKP | 7792 | Ovation Control Builder |  | float32
N2DCS.HZPRTN | 7793 | Ovation Control Builder |  | float32
N2DCS.HZSHMI | 7794 | 实时再热压力设定值显示 |  | float32
N2DCS.HZSVG | 7795 | Ovation Control Builder |  | float32
N2DCS.HZSVG2 | 7796 | Ovation Control Builder |  | float32
N2DCS.HZSVHMI | 7797 | 延时再热压力设定值显示 |  | float32
N2DCS.IPE_RATE | 7798 | Ovation Control Builder |  | float32
N2DCS.IPETGT | 7799 | Ovation Control Builder |  | float32
N2DCS.IV_1_1_8_COIL1 | 7800 | 1_1_8 COIL1 VOLTAGE |  | float32
N2DCS.IV_1_1_8_COIL2 | 7801 | 1_1_8 COIL2 VOLTAGE |  | float32
N2DCS.IV_COMMAND | 7802 | IV 11CH COMMAND |  | float32
N2DCS.IV_DEMOD | 7803 |  |  | float32
N2DCS.IV_SPO | 7804 | Ovation Control Builder |  | float32
N2DCS.IV_STAT_POINT | 7805 | IV 14CH STAT |  | float32
N2DCS.KDN | 7806 | 转速控制器比例前馈 |  | float32
N2DCS.KOS | 7807 | 进汽控制器比例前馈 |  | float32
N2DCS.NNOM | 7808 | 额定转速 |  | float32
N2DCS.NORKP | 7809 | Ovation Control Builder |  | float32
N2DCS.NORTN | 7810 | 转速/进汽控制积分时间 |  | float32
N2DCS.NORTS | 7811 | Ovation Control Builder |  | float32
N2DCS.NORTT | 7812 | Ovation Control Builder |  | float32
N2DCS.NSGP | 7813 | Ovation Control Builder |  | float32
N2DCS.NSOG | 7814 | Ovation Control Builder |  | float32
N2DCS.NSS | 7815 | 超速试验转速设定值 |  | float32
N2DCS.NSUG | 7816 | Ovation Control Builder |  | float32
N2DCS.NSVG | 7817 | Ovation Control Builder |  | float32
N2DCS.NSVGSY | 7818 | 转速设定值同期时的梯度 |  | float32
N2DCS.NSYN | 7819 | 同期转速 |  | float32
N2DCS.NT1 | 7820 | Ovation Control Builder |  | float32
N2DCS.NT2 | 7821 | Ovation Control Builder |  | float32
N2DCS.NT3 | 7822 | Ovation Control Builder |  | float32
N2DCS.NTGTMA | 7823 | Ovation Control Builder |  | float32
N2DCS.NTGTME | 7824 | Ovation Control Builder |  | float32
N2DCS.NTKD | 7825 | Ovation Control Builder |  | float32
N2DCS.NTKG | 7826 | Ovation Control Builder |  | float32
N2DCS.NTTD | 7827 | Ovation Control Builder |  | float32
N2DCS.NTTF | 7828 | Ovation Control Builder |  | float32
N2DCS.NTTG | 7829 | Ovation Control Builder |  | float32
N2DCS.NWART | 7830 | 暖机转速 |  | float32
N2DCS.OSGOG | 7831 | Ovation Control Builder |  | float32
N2DCS.OSGUG | 7832 | Ovation Control Builder |  | float32
N2DCS.OSVG | 7833 | 延时的进汽设定值梯度 |  | float32
N2DCS.PNOM | 7834 | 额定负荷 |  | float32
N2DCS.RVP_1_1_7_KSERVO_ALG_I | 7835 | Ovation Control Builder |  | float32
N2DCS.RVP_1_1_7_KSERVODB_ALG_I | 7836 | Ovation Control Builder |  | float32
N2DCS.RVP_1_1_8_KSERVO_ALG_I | 7837 | Ovation Control Builder |  | float32
N2DCS.RVP_1_1_8_KSERVODB_ALG_I | 7838 | Ovation Control Builder |  | float32
N2DCS.STATHF | 7839 | Ovation Control Builder |  | float32
N2DCS.STATLF | 7840 | Ovation Control Builder |  | float32
N2DCS.STATNR | 7841 | 转速控制不等率 |  | float32
N2DCS.TABMA | 7842 | 汽机启动及升程器允许值起点 |  | float32
N2DCS.TABME | 7843 | 汽机启动及升程器允许值终点 |  | float32
N2DCS.TABSHMI | 7844 | TAB控制器输出百分比 |  | float32
N2DCS.TEST_LA | 7845 | test |  | float32
N2DCS.TWFCH | 7846 | Ovation Control Builder |  | float32
N2DCS.VGBAFV | 7847 | Ovation Control Builder |  | float32
N2DCS.VGBFDV | 7848 | Ovation Control Builder |  | float32
N2DCS.VGBZDV | 7849 | Ovation Control Builder |  | float32
N2DCS.VGFDS1 | 7850 | Ovation Control Builder |  | float32
N2DCS.VGHZS1 | 7851 | Ovation Control Builder |  | float32
N2DCS.VGNS1 | 7852 | Ovation Control Builder |  | float32
N2DCS.VGOS1 | 7853 | Ovation Control Builder |  | float32
N2DCS.VGOSG1 | 7854 | 负荷速率设定 |  | float32
N2DCS.VGSD1 | 7855 | Ovation Control Builder |  | float32
N2DCS.VGZDS1 | 7856 | Ovation Control Builder |  | float32
N2DCS.W150Y | 7857 | Ovation Control Builder |  | float32
N2DCS.W160Y | 7858 | Ovation Control Builder |  | float32
N2DCS.W170Y | 7859 | Ovation Control Builder |  | float32
N2DCS.W180Y | 7860 | Ovation Control Builder |  | float32
N2DCS.W230Y | 7861 | Ovation Control Builder |  | float32
N2DCS.YFDPG1 | 7862 | 主蒸汽压力输出限值1 |  | float32
N2DCS.YFDPG2 | 7863 | 主蒸汽压力输出限值2 |  | float32
N2DCS.YFDPRHMI | 7864 | 高压主蒸汽压力控制输出(百分比) |  | float32
N2DCS.YHATGO | 7865 | Ovation Control Builder |  | float32
N2DCS.YHATGU | 7866 | Ovation Control Builder |  | float32
N2DCS.YHVDGO | 7867 | Ovation Control Builder |  | float32
N2DCS.YHVDGU | 7868 | Ovation Control Builder |  | float32
N2DCS.YHZPG1 | 7869 | 热再压力控制器输出限值1 |  | float32
N2DCS.YHZPG2 | 7870 | 热再压力控制器输出限值2 |  | float32
N2DCS.YNORHMI | 7871 | 转速/负荷控制器输出百分比 |  | float32
N2DCS.YRHMI | 7872 | 中央小选输出百分比 |  | float32
N2DCS.YZDPG1 | 7873 | Ovation Control Builder |  | float32
N2DCS.YZDPG2 | 7874 | Ovation Control Builder |  | float32
N2DCS.ZDNOM | 7875 | Ovation Control Builder |  | float32
N2DCS.ZDPRKP | 7876 | Ovation Control Builder |  | float32
N2DCS.ZDPRTN | 7877 | Ovation Control Builder |  | float32
N2DCS.ZDSHMI | 7878 | 实时低压压力设定值（显示） |  | float32
N2DCS.ZDSVG | 7879 | Ovation Control Builder |  | float32
N2DCS.ZDSVG2 | 7880 | Ovation Control Builder |  | float32
N2DCS.ZDSVHMI | 7881 | 延时低压压力设定值（显示） |  | float32
N2DCS.1_1_7_COIL_1_KSERVO_A | 7882 | Ovation Control Builder |  | float32
N2DCS.1_1_7_COIL_2_KSERVO_A | 7883 | Ovation Control Builder |  | float32
N2DCS.20MYA01CS902_NT | 7884 | Ovation Control Builder |  | float32
N2DCS.20LBA20CT007_TEMP | 7885 | Ovation Control Builder |  | float32
N2DCS.20LBA20CT007_XQ01 | 7886 | 高压主汽门前蒸汽温度 |  | float32
N2DCS.20LBA20CT007_XQ03 | 7887 | Ovation Control Builder |  | float32
N2DCS.20LBA20CT107A | 7888 | 主汽门前蒸汽温度1# | ℃ | float32
N2DCS.20LBA20CT108A | 7889 | 主汽门前蒸汽温度2# | ℃ | float32
N2DCS.20LBA20CT109A | 7890 | 主汽门前蒸汽温度3# | ℃ | float32
N2DCS.20LBA20CT307A | 7891 | 高压主汽门前蒸汽温度1# | ℃ | float32
N2DCS.20LBA20CT308A | 7892 | 主汽门前蒸汽温度2# |  | float32
N2DCS.20LBA20CT309A | 7893 | 主汽门前蒸汽温度3# |  | float32
N2DCS.20LBA20CT901 | 7894 | 高压主汽门前蒸汽温度 |  | float32
N2DCS.20LBA90CT001_XQ01 | 7895 | 低压主汽门前蒸汽温度 |  | float32
N2DCS.20LBA90CT101A | 7896 | 低压主汽门前蒸汽温度 | ℃ | float32
N2DCS.20LBA90CT301A | 7897 | 低压主汽门前蒸汽温度 | ℃ | float32
N2DCS.20LBB50CP111 | 7898 | 中压抽汽调节阀前后差压1 | MPa | float32
N2DCS.20LBB50CP112 | 7899 | 中压抽汽调节阀前后差压2 | MPa | float32
N2DCS.20LBB50CT007_XQ01 | 7900 | 中压主汽门前蒸汽温度（选择后） |  | float32
N2DCS.20LBB50CT007_XQ03 | 7901 | Ovation Control Builder |  | float32
N2DCS.20LBB50CT107A | 7902 | 中压主汽门前蒸汽温度1# | ℃ | float32
N2DCS.20LBB50CT108A | 7903 | 中压主汽门前蒸汽温度2# | ℃ | float32
N2DCS.20LBB50CT109A | 7904 | 再热门阀前蒸汽温度3# | ℃ | float32
N2DCS.20LBB50CT307A | 7905 | 中压主汽门前蒸汽温度1# | ℃ | float32
N2DCS.20LBB50CT308A | 7906 | 中压主汽门前蒸汽温度2# | ℃ | float32
N2DCS.20LBB50CT309A | 7907 | 中压主汽门前蒸汽温度3# | ℃ | float32
N2DCS.20LBB50CT901 | 7908 | 中压主汽门前蒸汽温度 |  | float32
N2DCS.20LBC40CT101 | 7909 | 高排逆止门前蒸汽温度 | ℃ | float32
N2DCS.20LBC40CT301 | 7910 | 高排逆止门前蒸汽温度 | ℃ | float32
N2DCS.20MAA11CT121A | 7911 | 高压主汽门内壁温度A（100%） | ℃ | float32
N2DCS.20MAA11CT121A_XQ01 | 7912 | 高压主汽门内壁温度A（100%） |  | float32
N2DCS.20MAA11CT122A | 7913 | 高压主汽门中壁温度A（50%） | ℃ | float32
N2DCS.20MAA11CT122A_XQ01 | 7914 | 高压主汽门中壁温度A（50%） |  | float32
N2DCS.20MAA11CT321 | 7915 | 高压主汽门内壁温度A（100%） | ℃ | float32
N2DCS.20MAA11CT322 | 7916 | 高压主汽门中壁温度A（50%） | ℃ | float32
N2DCS.20MAA12CT121A | 7917 | 高压调节汽门内壁温度A（100%） | ℃ | float32
N2DCS.20MAA12CT121A_XQ01 | 7918 | Ovation Control Builder |  | float32
N2DCS.20MAA12CT122A | 7919 | 高压调节汽门中壁温度A（50%） | ℃ | float32
N2DCS.20MAA12CT122A_XQ01 | 7920 | 高压调节汽门中壁温度A（50%） |  | float32
N2DCS.20MAA12CT321 | 7921 | 高压调节汽门内壁温度A（100%） | ℃ | float32
N2DCS.20MAA12CT322 | 7922 | 高压调节汽门中壁温度A（50%） | ℃ | float32
N2DCS.20MAA50CT104A | 7923 | 高压调节门后蒸汽温度1 | ℃ | float32
N2DCS.20MAA50CT104A_XQ01 | 7924 | Ovation Control Builder |  | float32
N2DCS.20MAA50CT105A | 7925 | 高压调节门后蒸汽温度2 | ℃ | float32
N2DCS.20MAA50CT105A_XQ01 | 7926 | Ovation Control Builder |  | float32
N2DCS.20MAA50CT106A | 7927 | 高压调节门后蒸汽温度3 | ℃ | float32
N2DCS.20MAA50CT106A_XQ01 | 7928 | Ovation Control Builder |  | float32
N2DCS.20MAA50CT131A | 7929 | 高压缸内壁温度A（100%） | ℃ | float32
N2DCS.20MAA50CT131A_XQ01 | 7930 | 高压缸内壁温度A（100%） |  | float32
N2DCS.20MAA50CT132A | 7931 | 高压缸中壁温度A（50%） | ℃ | float32
N2DCS.20MAA50CT132A_XQ01 | 7932 | 高压缸内壁温度A（50%） |  | float32
N2DCS.20MAA50CT141A | 7933 | 高压缸外壁温（50%） | ℃ | float32
N2DCS.20MAA50CT141A_XQ01 | 7934 | 高压缸外壁温（50%） |  | float32
N2DCS.20MAA50CT142A | 7935 | 高压缸中壁温（50%） | ℃ | float32
N2DCS.20MAA50CT142A_XQ01 | 7936 | Ovation Control Builder |  | float32
N2DCS.20MAA50CT143A | 7937 | 高压缸内壁温（50%） | ℃ | float32
N2DCS.20MAA50CT143A_XQ01 | 7938 | Ovation Control Builder |  | float32
N2DCS.20MAA50CT151A | 7939 | 高压缸上中壁温A | ℃ | float32
N2DCS.20MAA50CT152A | 7940 | 高压缸下中壁温A | ℃ | float32
N2DCS.20MAA50CT304 | 7941 | 高压调节门后蒸汽温度1 | ℃ | float32
N2DCS.20MAA50CT305 | 7942 | 高压调节门后蒸汽温度2 | ℃ | float32
N2DCS.20MAA50CT306 | 7943 | 高压调节门后蒸汽温度3 | ℃ | float32
N2DCS.20MAA50CT322A | 7944 | 高压主汽门中壁温度A（50%） |  | float32
N2DCS.20MAA50CT331 | 7945 | 高压缸内壁温度A（100%） | ℃ | float32
N2DCS.20MAA50CT332 | 7946 | 高压缸中壁温度A（50%） | ℃ | float32
N2DCS.20MAA50CT341 | 7947 | 高压缸外壁温（50%） | ℃ | float32
N2DCS.20MAA50CT342 | 7948 | 高压缸中壁温（50%） | ℃ | float32
N2DCS.20MAA50CT343 | 7949 | 高压缸内壁温（50%） | ℃ | float32
N2DCS.20MAA50CT351 | 7950 | 高压缸上中壁温A | ℃ | float32
N2DCS.20MAA50CT352 | 7951 | 高压缸下中壁温A | ℃ | float32
N2DCS.20MAA50FT004A_XQ01 | 7952 | 高压调节门后蒸汽温度 |  | float32
N2DCS.20MAA50FT051_XQ01 | 7953 | 高压缸左右温差 |  | float32
N2DCS.20MAA50FT051_XQ02 | 7954 | 高压缸上下温差 |  | float32
N2DCS.20MAB50CT111A | 7955 | 中压缸排汽口壁温1 | ℃ | float32
N2DCS.20MAB50CT112A | 7956 | 中压缸排汽口壁温2 | ℃ | float32
N2DCS.20MAB50CT113A | 7957 | 中压缸排汽口壁温3 | ℃ | float32
N2DCS.20MAB50CT151A | 7958 | 中压缸上中壁温度A | ℃ | float32
N2DCS.20MAB50CT152A | 7959 | 中压缸中下壁温度A | ℃ | float32
N2DCS.20MAB50CT311 | 7960 | 中压内缸进汽口壁温1 | ℃ | float32
N2DCS.20MAB50CT312 | 7961 | 中压内缸进汽口壁温2 | ℃ | float32
N2DCS.20MAB50CT313 | 7962 | 中压内缸进汽口壁温3 | ℃ | float32
N2DCS.20MAB50CT351 | 7963 | 中压缸上中壁温度A | ℃ | float32
N2DCS.20MAB50CT352 | 7964 | 中压缸中下壁温度A | ℃ | float32
N2DCS.20MAB50FT011A_XQ01 | 7965 | Ovation Control Builder |  | float32
N2DCS.20MAB50FT011A_XQ02 | 7966 | Ovation Control Builder |  | float32
N2DCS.20MAB50FT011A_XQ03 | 7967 | Ovation Control Builder |  | float32
N2DCS.20MAC10CT111A | 7968 | 末级蒸汽温度1#(静叶环温度) | ℃ | float32
N2DCS.20MAC10CT112A | 7969 | 末级蒸汽温度2#(静叶环温度) | ℃ | float32
N2DCS.20MAC10CT181A | 7970 | 低压后缸支柱壁温上 | ℃ | float32
N2DCS.20MAC10CT181A_XQ01 | 7971 | Ovation Control Builder |  | float32
N2DCS.20MAC10CT182A | 7972 | 低压后缸支柱壁温下 | ℃ | float32
N2DCS.20MAC10CT182A_XQ01 | 7973 | Ovation Control Builder |  | float32
N2DCS.20MAC10CT183A | 7974 | 低压排汽支架温度1#（排汽温度） | ℃ | float32
N2DCS.20MAC10CT184A | 7975 | 低压排汽支架温度2#（排汽温度） | ℃ | float32
N2DCS.20MAC10CT185A | 7976 | 低压排汽支架温度3#（排汽温度） | ℃ | float32
N2DCS.20MAC10CT311 | 7977 | 末级蒸汽温度1#(静叶环温度) | ℃ | float32
N2DCS.20MAC10CT312 | 7978 | 末级蒸汽温度2#(静叶环温度) | ℃ | float32
N2DCS.20MAC10CT381 | 7979 | 低压后缸支柱壁温上 | ℃ | float32
N2DCS.20MAC10CT382 | 7980 | 低压后缸支柱壁温下 | ℃ | float32
N2DCS.20MAC10CT383 | 7981 | 低压排汽支架温度1#（排汽温度） | ℃ | float32
N2DCS.20MAC10CT384A | 7982 | 低压排汽支架温度2#（排汽温度） | ℃ | float32
N2DCS.20MAC10CT385 | 7983 | 低压排汽支架温度3#（排汽温度） | ℃ | float32
N2DCS.20MAD11CY141 | 7984 | #1径向轴承轴振（X） | μm | float32
N2DCS.20MAD11CY142 | 7985 | #1径向轴承轴振（Y） | μm | float32
N2DCS.20MAD12CY141 | 7986 | #2径向轴承轴振（X） | μm | float32
N2DCS.20MAD12CY142 | 7987 | #2径向轴承轴振（Y） | μm | float32
N2DCS.20MAD13CY101 | 7988 | #3径向轴承处转子膨胀 | mm | float32
N2DCS.20MAD13CY141 | 7989 | #3径向轴承轴振（X） | μm | float32
N2DCS.20MAD13CY142 | 7990 | #3径向轴承轴振（Y） | μm | float32
N2DCS.20MAY01EP144_TA | 7991 | 高压转子温度1 |  | float32
N2DCS.20MAY01EP144_TMGR | 7992 | 高压转子温度3 |  | float32
N2DCS.20MAY01EP144_TMSH | 7993 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP144_XQ01 | 7994 | 高压转子温度3(绝对值) |  | float32
N2DCS.20MAY01EP144_XQ02 | 7995 | 高压转子温度2 |  | float32
N2DCS.20MAY01EP144_XQ03 | 7996 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP144_Z1TMGR | 7997 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP144_Z1TMS | 7998 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP145_TA | 7999 | 中压转子温度1 |  | float32
N2DCS.20MAY01EP145_TMGR | 8000 | 中压转子温度3 |  | float32
N2DCS.20MAY01EP145_XQ02 | 8001 | 中压转子温度2 |  | float32
N2DCS.20MAY01EP145_XQ03 | 8002 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP145_Z1TMGR | 8003 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP145_Z1TMS | 8004 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP150_XQ06 | 8005 | 最小上升温度裕度 |  | float32
N2DCS.20MAY01EP150_XQ07 | 8006 | 最小下降温度裕度 |  | float32
N2DCS.20MAY01EP150_XQ16 | 8007 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP151_DT | 8008 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP151_TM | 8009 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP151_XQ06 | 8010 | 高压主汽门上升温度裕度 |  | float32
N2DCS.20MAY01EP151_XQ07 | 8011 | 高压主汽门下降温度裕度 |  | float32
N2DCS.20MAY01EP152_DT | 8012 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP152_TM | 8013 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP152_XQ04 | 8014 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP152_XQ06 | 8015 | 高压调节门上升温度裕度 |  | float32
N2DCS.20MAY01EP152_XQ07 | 8016 | 高压调节门下降温度裕度 |  | float32
N2DCS.20MAY01EP153_DT | 8017 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP153_TM | 8018 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP153_XQ04 | 8019 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP153_XQ06 | 8020 | 高压缸上升温度裕度 |  | float32
N2DCS.20MAY01EP153_XQ07 | 8021 | 高压缸下降温度裕度 |  | float32
N2DCS.20MAY01EP154_DDTUS | 8022 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_DPMUF | 8023 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_DPMUN | 8024 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_DPMUS | 8025 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_DPMUT | 8026 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_DT | 8027 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_TA | 8028 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_TEMP | 8029 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_XQ01 | 8030 | 高压转子温度3 |  | float32
N2DCS.20MAY01EP154_XQ02 | 8031 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_XQ04 | 8032 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_XQ06 | 8033 | 高压转子上升温度裕度 |  | float32
N2DCS.20MAY01EP154_XQ07 | 8034 | 高压转子下降温度裕度 |  | float32
N2DCS.20MAY01EP154_XQ10 | 8035 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP154_XQ14 | 8036 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_DDTUS | 8037 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_DPMUF | 8038 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_DPMUN | 8039 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_DPMUS | 8040 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_DPMUT | 8041 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_DT | 8042 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_XQ01 | 8043 | 中压缸轮毂温度 |  | float32
N2DCS.20MAY01EP155_XQ02 | 8044 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_XQ04 | 8045 | 中压缸转子允许温差 |  | float32
N2DCS.20MAY01EP155_XQ06 | 8046 | 中压转子上升温度裕度 |  | float32
N2DCS.20MAY01EP155_XQ07 | 8047 | 中压转子下降温度裕度 |  | float32
N2DCS.20MAY01EP155_XQ10 | 8048 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP155_XQ14 | 8049 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP181_DE | 8050 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP181_F1 | 8051 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP181_IN | 8052 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP181_MIN | 8053 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP181_RRDOW | 8054 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP181_RRUP | 8055 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP181_SPCINP | 8056 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP181_XQ01 | 8057 | 最佳高压蒸汽参数 |  | float32
N2DCS.20MAY01EP181_XQ02 | 8058 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP182_DE | 8059 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP182_F2 | 8060 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP182_IN | 8061 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP182_RRDOW | 8062 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP182_RRUP | 8063 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP182_SPCINP | 8064 | Ovation Control Builder |  | float32
N2DCS.20MAY01EP182_XQ01 | 8065 | 最佳中压蒸汽参数 |  | float32
N2DCS.20MAY01EP182_XQ04 | 8066 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT001_XQ02 | 8067 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT001_XQ11 | 8068 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT002_XQ02 | 8069 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT002_XQ11 | 8070 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT004_TEMP | 8071 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT004_XQ02 | 8072 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT004_XQ11 | 8073 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT005_XQ02 | 8074 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT005_XQ11 | 8075 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT006_XQ02 | 8076 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT006_XQ11 | 8077 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT007A_XQ11 | 8078 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT007B_XQ11 | 8079 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT008_XQ11 | 8080 | Ovation Control Builder |  | float32
N2DCS.20MAY10FT014_TEMP | 8081 | Ovation Control Builder |  | float32
N2DCS.20MKD11CY141 | 8082 | #4轴承轴振（X） | μm | float32
N2DCS.20MKD11CY142 | 8083 | #4轴承轴振（Y） | μm | float32
N2DCS.20MKD12CY141 | 8084 | #5轴承轴振（X） | μm | float32
N2DCS.20MKD12CY142 | 8085 | #5轴承轴振（Y） | μm | float32
N2DCS.20MYA01EP150_DDTUV | 8086 | Ovation Control Builder |  | float32
N2DCS.D43P1B1L1C9 | 8087 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D43P1B1L2C9 | 8088 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D43P1B2L6C9 | 8089 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D43P1B2L7C9 | 8090 | TC冷端温度补偿点 | DEGC | float32
N2DCS.D43P1B2L8C9 | 8091 | TC冷端温度补偿点 | DEGC | float32
N2DCS.IP_TEMP_TRIP | 8092 | Ovation Control Builder |  | float32
N2DCS.IP_TEMP_WARN | 8093 | Ovation Control Builder |  | float32
N2DCS.20AGC0022 | 8094 | #2机组远方AGC投入状态 |  | digital
N2DCS.20AGC0023 | 8095 | #2机组远方AGC投入允许 |  | digital
N2DCS.20AGC0024 | 8096 | #2机组总负荷增闭锁信号 |  | digital
N2DCS.20AGC0025 | 8097 | #2机组总负荷减闭锁信号 |  | digital
N2DCS.20CAE01EY301XB51 | 8098 | #3炉保护跳闸通道A（至燃机） |  | digital
N2DCS.20CAE01EY302XB51 | 8099 | #3炉保护跳闸通道B（至燃机） |  | digital
N2DCS.20CAE01EY303XB51 | 8100 | #3炉保护跳闸通道C（至燃机） |  | digital
N2DCS.20CBA00FU002 | 8101 | 负荷遥控模式 |  | digital
N2DCS.20CBA00FU003 | 8102 | 开高压疏水阀（1% LOAD关）24VDC |  | digital
N2DCS.20CBA00FU004 | 8103 | 开中压疏水阀（2% LOAD关）24VDC |  | digital
N2DCS.20CJA00EA001DEH1 | 8104 | DCS发出启动#3机启顺控指令 |  | digital
N2DCS.20CJA00EA001DEH2 | 8105 | DCS发出启动#3机停顺控指令 |  | digital
N2DCS.20CJA01EC001 | 8106 | DCS FAST LOAD GRADIENT SELECT |  | digital
N2DCS.20CJA01EC001XB01 | 8107 | GAS SYS READY |  | digital
N2DCS.20CJA01EC001XB07 | 8108 | DCS发出允许#4机同期信号 |  | digital
N2DCS.20CJA01EC001XB09 | 8109 | DCS允许#4机增负荷 |  | digital
N2DCS.20CJA01EC001XB10 | 8110 | DCS一次调频投入 |  | digital
N2DCS.20CJA01EC001XB12 | 8111 | DCS STOP UNLOADING |  | digital
N2DCS.20CJA01EC001XB13 | 8112 | DCS STOP LOADING |  | digital
N2DCS.20CJA01EC001XB14 | 8113 | DCS复位燃机跳闸 |  | digital
N2DCS.20CJA01EC001XB16 | 8114 | DCS投入负荷快速速率 |  | digital
N2DCS.20CJA01EC001YB08 | 8115 | DCS投入负荷正常速率 |  | digital
N2DCS.20CJA06DU001XT | 8116 | 负荷控制协调方式请求 |  | digital
N2DCS.20CRA02T0PMU13 | 8117 | 汽机一次调频信号 |  | digital
N2DCS.20CRA02TOPMU13 | 8118 | #3机一次调频信号 |  | digital
N2DCS.20CSA01PF | 8119 | 机组辅助盘1电源消失 |  | digital
N2DCS.20CSA02PF | 8120 | 机组辅助盘2电源消失 |  | digital
N2DCS.20CSA51PF | 8121 | #3机热力配电柜1电源消失 |  | digital
N2DCS.20CSA52PF | 8122 | #3机热力配电柜2电源消失 |  | digital
N2DCS.20CSC01PF | 8123 | 第二套机组APS电源盘电源消失 |  | digital
N2DCS.20CSC31PF | 8124 | 第二套机组UPS电源盘电源消失 |  | digital
N2DCS.20CZTSOE01 | 8125 | 手动打闸停#3机（SOE） |  | digital
N2DCS.20CZTSOE02 | 8126 | 手动启动#3机#1润滑油泵（SOE） |  | digital
N2DCS.20CZTSOE03 | 8127 | 手动启动#3机#2润滑油泵（SOE） |  | digital
N2DCS.20CZTSOE04 | 8128 | 手动启动#3机柴油发电机（SOE） |  | digital
N2DCS.20CZTSOE05 | 8129 | 手动打闸停#4机（SOE） |  | digital
N2DCS.20CZTSOE06 | 8130 | 手动关闭调压站火警阀（SOE） |  | digital
N2DCS.20CZTSOE07 | 8131 | 手动解列#3发电机（SOE） |  | digital
N2DCS.20CZTSOE08 | 8132 | 手动打开真空破坏气动门（SOE） |  | digital
N2DCS.20CZTSOE09 | 8133 | 手动开高压过热器PCV阀（SOE） |  | digital
N2DCS.20CZTSOE10 | 8134 | 手动开中压过热器排汽门（SOE） |  | digital
N2DCS.20CZTSOE11 | 8135 | 手动开低压过热器排汽门（SOE） |  | digital
N2DCS.20CZTSOE12 | 8136 | 手动启动#3机应急油泵（SOE） |  | digital
N2DCS.20CZTSOE13 | 8137 | 手动启动#4机#1润滑油泵（SOE） |  | digital
N2DCS.20CZTSOE14 | 8138 | 手动启动#4机#2润滑油泵（SOE） |  | digital
N2DCS.20CZTSOE15 | 8139 | 手动启动#4机应急油泵（SOE） |  | digital
N2DCS.20CZTSOE16 | 8140 | 手动解列#4发电机（SOE） |  | digital
N2DCS.20CZTSOE17 | 8141 | 手动打开高包启动放水门（SOE） |  | digital
N2DCS.20CZTSOE18 | 8142 | 手动打开中包启动放水门（SOE） |  | digital
N2DCS.20CZTSOE19 | 8143 | 手动打开低包启动放水门（SOE） |  | digital
N2DCS.20DCSTOTCS01 | 8144 | MAKE GT READY |  | digital
N2DCS.20HYY01EY001ASOE | 8145 | #3炉停机通道1（SOE） |  | digital
N2DCS.20HYY01EY001BDEH | 8146 | #3炉联跳#3机通道2 |  | digital
N2DCS.20HYY01EY001BSOE | 8147 | #3炉停机通道2（SOE） |  | digital
N2DCS.20HYY01EY001CDEH | 8148 | #3炉联跳#3机通道3 |  | digital
N2DCS.20HYY01EY001CSOE | 8149 | #3炉停机通道3（SOE） |  | digital
N2DCS.20LBA10AA402CP | 8150 | 高压主汽母管疏水气动门1全关位 |  | digital
N2DCS.20LBA10AA402F | 8151 | 高压主汽母管疏水气动门1无电源 |  | digital
N2DCS.20LBA10AA402OD/CD | 8152 | 高压主汽母管疏水门1关/开指令 |  | digital
N2DCS.20LBA10AA402OP | 8153 | 高压主汽母管疏水气动门1全开位 |  | digital
N2DCS.20LBA10AA404CP | 8154 | 高压主汽母管疏水气动门2全关位 |  | digital
N2DCS.20LBA10AA404F | 8155 | 高压主汽母管疏水气动门2无电源 |  | digital
N2DCS.20LBA10AA404OD/CD | 8156 | 高压主汽母管疏水门2关/开指令 |  | digital
N2DCS.20LBA10AA404OP | 8157 | 高压主汽母管疏水气动门2全开位 |  | digital
N2DCS.20LBA10CPX3_MRE | 8158 | 高压主汽压力坏点 |  | digital
N2DCS.20LBA20AA402CP | 8159 | 低压主汽门前疏水气动门全关位 |  | digital
N2DCS.20LBA20AA402F | 8160 | 低压主汽门前疏水气动门无电源 |  | digital
N2DCS.20LBA20AA402OD/CD | 8161 | 低压主汽门前疏水门关/开指令 |  | digital
N2DCS.20LBA20AA402OP | 8162 | 低压主汽门前疏水气动门全开位 |  | digital
N2DCS.20LBA20AA406CP | 8163 | 低压主汽母管疏水气动门全关位 |  | digital
N2DCS.20LBA20AA406F | 8164 | 低压主汽母管疏水气动门无电源 |  | digital
N2DCS.20LBA20AA406OD/CD | 8165 | 低压主汽母管疏水门关/开指令 |  | digital
N2DCS.20LBA20AA406OP | 8166 | 低压主汽母管疏水气动门全开位 |  | digital
N2DCS.20LBA20CPX2_MRE | 8167 | 低压蒸汽母管压力坏点 |  | digital
N2DCS.20LBB10AA402CP | 8168 | 高温再热蒸汽母管疏水门全关位 |  | digital
N2DCS.20LBB10AA402F | 8169 | 高温再热蒸汽母管疏水门无电源 |  | digital
N2DCS.20LBB10AA402OD/CD | 8170 | 高温再热汽母管疏水门关/开指令 |  | digital
N2DCS.20LBB10AA402OP | 8171 | 高温再热蒸汽母管疏水门全开位 |  | digital
N2DCS.20LBB10AA404CP | 8172 | 中旁阀前疏水气动门全关位 |  | digital
N2DCS.20LBB10AA404F | 8173 | 中旁阀前疏水气动门无电源 |  | digital
N2DCS.20LBB10AA404OD/CD | 8174 | 中旁阀前疏水气动门关/开指令 |  | digital
N2DCS.20LBB10AA404OP | 8175 | 中旁阀前疏水气动门全开位 |  | digital
N2DCS.20LBB10CPX2_MRE | 8176 | 高温再热蒸汽压力坏点 |  | digital
N2DCS.20LBC10AA001CP | 8177 | 高排逆止门全关位 |  | digital
N2DCS.20LBC10AA001F | 8178 | 高排逆止门无电源 |  | digital
N2DCS.20LBC10AA001OD | 8179 | 高排逆止门打开/关闭指令 |  | digital
N2DCS.20LBC10AA001OP | 8180 | 高排逆止门全开位 |  | digital
N2DCS.20LBC10AA404CP | 8181 | 高排逆止门后疏水气动门全关位 |  | digital
N2DCS.20LBC10AA404F | 8182 | 高排逆止门后疏水气动门无电源 |  | digital
N2DCS.20LBC10AA404OD/CD | 8183 | 高排逆止门后疏水门关/开指令 |  | digital
N2DCS.20LBC10AA404OP | 8184 | 高排逆止门后疏水气动门全开位 |  | digital
N2DCS.20LBC10AA406CP | 8185 | 冷再疏水气动门全关位 |  | digital
N2DCS.20LBC10AA406F | 8186 | 冷再疏水气动门无电源 |  | digital
N2DCS.20LBC10AA406OD/CD | 8187 | 冷再疏水气动门关闭/打开指令 |  | digital
N2DCS.20LBC10AA406OP | 8188 | 冷再疏水气动门全开位 |  | digital
N2DCS.20LBC10CL001HH | 8189 | 高排逆止门前疏水罐液位高高 |  | digital
N2DCS.20LBC10CL002H | 8190 | 高排逆止门前疏水罐液位高 |  | digital
N2DCS.20LBC10CL003HH | 8191 | 高排逆止门后疏水罐液位高高 |  | digital
N2DCS.20LBC10CL004H | 8192 | 高排逆止门后疏水罐液位高 |  | digital
N2DCS.20LBC10CL005HH | 8193 | 冷再冷段疏水罐液位高高 |  | digital
N2DCS.20LBC10CL006H | 8194 | 冷再冷段疏水罐液位高 |  | digital
N2DCS.20LBC10CT_MRE | 8195 | 高压排气管壁温度坏质量 |  | digital
N2DCS.20LBH10AA101CD | 8196 | 高排通风阀快关指令 |  | digital
N2DCS.20LBH10AA101CP | 8197 | 高排通风阀全关位置 |  | digital
N2DCS.20LBH10AA101F | 8198 | 高排通风阀电源消失 |  | digital
N2DCS.20LBH10AA101OD | 8199 | 高排通风阀打开指令 |  | digital
N2DCS.20LBH10AA101OP | 8200 | 高排通风阀全开位置 |  | digital
N2DCS.20LBH10AA402CP | 8201 | 高排通风阀前疏水气动门全关位 |  | digital
N2DCS.20LBH10AA402F | 8202 | 高排通风阀前疏水气动门无电源 |  | digital
N2DCS.20LBH10AA402OD/CD | 8203 | 高排通风阀前疏水门关/开指令 |  | digital
N2DCS.20LBH10AA402OP | 8204 | 高排通风阀前疏水气动门全开位 |  | digital
N2DCS.20LCB11AP001TP1 | 8205 | #1凝结水泵已停止 |  | digital
N2DCS.20LCB12AP002TP1 | 8206 | #2凝结水泵已停止 |  | digital
N2DCS.20LCE12AA001CP | 8207 | 凝结水至低旁减温水气动门全关位 |  | digital
N2DCS.20LCE12AA101CP | 8208 | 凝结水至低旁减温水调节门全关位 |  | digital
N2DCS.20LCE12AA101OP | 8209 | 凝结水至低旁减温水调节门全开位 |  | digital
N2DCS.20LCE15AA001CP | 8210 | 凝结水至中旁减温水气动门全关位 |  | digital
N2DCS.20LCE15AA101CP | 8211 | 凝结水至中旁减温水调节门全关位 |  | digital
N2DCS.20LCE15AA101OP | 8212 | 凝结水至中旁减温水调节门全开位 |  | digital
N2DCS.20MAA11CG051CP | 8213 | 高压主汽门全关位置 |  | digital
N2DCS.20MAA11CG051OP | 8214 | 高压主汽门全开位置 |  | digital
N2DCS.20MAA12CG051CP | 8215 | 高压调节阀全关位置 |  | digital
N2DCS.20MAA12CG051OP | 8216 | 高压调节阀全开位置 |  | digital
N2DCS.20MAA50EZ110SOE | 8217 | #3机高压缸前后差压保护动作 |  | digital
N2DCS.20MAA50EZ120SOE | 8218 | #3机高压主蒸汽温度高保护动作 |  | digital
N2DCS.20MAB11CG051DEH | 8219 | 中压主汽门全关位置 |  | digital
N2DCS.20MAB11CG051OP | 8220 | 中压主汽门全开位置 |  | digital
N2DCS.20MAB12CG051CP | 8221 | 中压调节门全关位置 |  | digital
N2DCS.20MAB12CG051OP | 8222 | 中压调节门全开位置 |  | digital
N2DCS.20MAC10EZ220SOE | 8223 | #3机低排温度高保护动作 |  | digital
N2DCS.20MAC11FF001 | 8224 | 热网故障 |  | digital
N2DCS.20MAD11EZ100SOE | 8225 | #3机轴承金属温度高保护动作 |  | digital
N2DCS.20MAD12EZ310SOE | 8226 | #3机轴向位移大保护动作 |  | digital
N2DCS.20MAG10EZ110SOE | 8227 | #3机凝汽器真空低保护动作 |  | digital
N2DCS.20MAJ21AP001TP1 | 8228 | #1真空泵已停止 |  | digital
N2DCS.20MAJ22AP001TP1 | 8229 | #2真空泵已停止 |  | digital
N2DCS.20MAJ30AA002OP | 8230 | 真空破坏气动门全开位置 |  | digital
N2DCS.20MAL11AA051CP | 8231 | 高压调节阀前疏水气动门全关位 |  | digital
N2DCS.20MAL11AA051F | 8232 | 高压调节阀前疏水气动门无电源 |  | digital
N2DCS.20MAL11AA051OD/CD | 8233 | 高压调节阀前疏水门关/开指令 |  | digital
N2DCS.20MAL11AA051OP | 8234 | 高压调节阀前疏水气动门全开位 |  | digital
N2DCS.20MAL23AA051CP | 8235 | 中压主汽门前疏水门全关位置 |  | digital
N2DCS.20MAL23AA051F | 8236 | 中压主汽门前疏水门电源消失 |  | digital
N2DCS.20MAL23AA051OD/CD | 8237 | 中压主汽门前疏水门关/开指令 |  | digital
N2DCS.20MAL23AA051OP | 8238 | 中压主汽门前疏水门全开位置 |  | digital
N2DCS.20MAL26AA051CP | 8239 | 中压调节阀前疏水门全关位置 |  | digital
N2DCS.20MAL26AA051F | 8240 | 中压调节阀前疏水门电源消失 |  | digital
N2DCS.20MAL26AA051OD/CD | 8241 | 中压调节阀前疏水门关/开指令 |  | digital
N2DCS.20MAL26AA051OP | 8242 | 中压调节阀前疏水门全开位置 |  | digital
N2DCS.20MAL65AA051CP | 8243 | 高排逆止门前疏水气动门全关位 |  | digital
N2DCS.20MAL65AA051F | 8244 | 高排逆止门前疏水门电源消失 |  | digital
N2DCS.20MAL65AA051OD/CD | 8245 | 高排逆止门前疏水门关/开指令 |  | digital
N2DCS.20MAL65AA051OP | 8246 | 高排逆止门前疏水门全开位置 |  | digital
N2DCS.20MAN10AA001CP | 8247 | 凝结水至高旁减温水气动门全关位 |  | digital
N2DCS.20MAN10AA001OD | 8248 | 凝结水至高旁减温水门关/开指令 |  | digital
N2DCS.20MAN10AA001OP | 8249 | 凝结水至高旁减温水气动门全开位 |  | digital
N2DCS.20MAN10AA101AUTO | 8250 | 高旁阀在自动模式 |  | digital
N2DCS.20MAN10AA101CD | 8251 | 高旁阀快关指令 |  | digital
N2DCS.20MAN10AA101CP | 8252 | 高旁阀全关位置 |  | digital
N2DCS.20MAN10AA101F | 8253 | 高旁阀故障 |  | digital
N2DCS.20MAN10AA101OD | 8254 | 高旁阀快开指令 |  | digital
N2DCS.20MAN10AA101OP | 8255 | 高旁阀全开位置 |  | digital
N2DCS.20MAN10AA101PH | 8256 | Ovation Control Builder |  | digital
N2DCS.20MAN10AA101SC | 8257 | 高旁阀安全关指令 |  | digital
N2DCS.20MAN10AA102_OP | 8258 | Ovation Control Builder |  | digital
N2DCS.20MAN10AA102AUTO | 8259 | 高旁减温水调节阀在自动模式 |  | digital
N2DCS.20MAN10AA102CD | 8260 | 高旁减温水调节阀快关指令 |  | digital
N2DCS.20MAN10AA102CP | 8261 | 高旁减温水调节阀全关位置 |  | digital
N2DCS.20MAN10AA102F | 8262 | 高旁减温水调节阀故障 |  | digital
N2DCS.20MAN10AA102OD | 8263 | 高旁减温水调节阀快开指令 |  | digital
N2DCS.20MAN10AA102OP | 8264 | 高旁减温水调节阀全开位置 |  | digital
N2DCS.20MAN10AC101CP | 8265 | 高旁阀全关位置 |  | digital
N2DCS.20MAN10CPX2_MRE | 8266 | 高旁阀后蒸汽压力坏点 |  | digital
N2DCS.20MAN10CTX2_MRE | 8267 | 高旁阀后蒸汽温度坏点 |  | digital
N2DCS.20MAN10GH001FF | 8268 | 高压旁路油站过载 |  | digital
N2DCS.20MAN10GH001LL1 | 8269 | 高压旁路油站油位低 |  | digital
N2DCS.20MAN10GH001LL2 | 8270 | 高压旁路油站油位低低 |  | digital
N2DCS.20MAN10GH001PDH | 8271 | 高压旁路油站过滤器阻塞 |  | digital
N2DCS.20MAN10GH001PF1 | 8272 | 高压旁路油站电源1故障 |  | digital
N2DCS.20MAN10GH001PF2 | 8273 | 高压旁路油站电源2故障 |  | digital
N2DCS.20MAN10GH001PH1 | 8274 | 高压旁路油站油压高 |  | digital
N2DCS.20MAN10GH001PH2 | 8275 | 高压旁路油站油压高高 |  | digital
N2DCS.20MAN10GH001PL1 | 8276 | 高压旁路油站油压低 |  | digital
N2DCS.20MAN10GH001PL2 | 8277 | 高压旁路油站油压低低 |  | digital
N2DCS.20MAN10GH001RD1 | 8278 | 高压旁路油站#1油泵启动指令 |  | digital
N2DCS.20MAN10GH001RD2 | 8279 | 高压旁路油站#2油泵启动指令 |  | digital
N2DCS.20MAN10GH001RP1 | 8280 | 高压旁路油站#1油泵在运行 |  | digital
N2DCS.20MAN10GH001RP2 | 8281 | 高压旁路油站#2油泵在运行 |  | digital
N2DCS.20MAN10GH001TD1 | 8282 | 高压旁路油站#1油泵停止指令 |  | digital
N2DCS.20MAN10GH001TD2 | 8283 | 高压旁路油站#2油泵停止指令 |  | digital
N2DCS.20MAN10GH001TH | 8284 | 高压旁路油站油温高 |  | digital
N2DCS.20MAN10GH001TP1 | 8285 | 高压旁路油站#1油泵已停止 |  | digital
N2DCS.20MAN10GH001TP2 | 8286 | 高压旁路油站#2油泵已停止 |  | digital
N2DCS.20MAN20AA101AUTO | 8287 | 中旁阀在自动模式 |  | digital
N2DCS.20MAN20AA101CD | 8288 | 中旁阀快关指令 |  | digital
N2DCS.20MAN20AA101CP | 8289 | 中旁阀全关位置 |  | digital
N2DCS.20MAN20AA101F | 8290 | 中旁阀故障 |  | digital
N2DCS.20MAN20AA101OD | 8291 | 中旁阀快开指令 |  | digital
N2DCS.20MAN20AA101OP | 8292 | 中旁阀全开位置 |  | digital
N2DCS.20MAN20AA101SC1 | 8293 | 中旁阀安全关指令1 |  | digital
N2DCS.20MAN20AA101SC2 | 8294 | 中旁阀安全关指令2 |  | digital
N2DCS.20MAN20AC101CP | 8295 | 中旁阀全关位置 |  | digital
N2DCS.20MAN20CPX2_MRE | 8296 | 中旁阀后蒸汽压力坏点 |  | digital
N2DCS.20MAN20CTX2_MRE | 8297 | 中旁阀后蒸汽温度坏点 |  | digital
N2DCS.20MAN20GH001FF | 8298 | 中低压旁路油站过载 |  | digital
N2DCS.20MAN20GH001LL1 | 8299 | 中低压旁路油站油位低 |  | digital
N2DCS.20MAN20GH001LL2 | 8300 | 中低压旁路油站油位低低 |  | digital
N2DCS.20MAN20GH001PDH | 8301 | 中低压旁路油站过滤器阻塞 |  | digital
N2DCS.20MAN20GH001PF1 | 8302 | 中低压旁路油站电源1故障 |  | digital
N2DCS.20MAN20GH001PF2 | 8303 | 中低压旁路油站电源2故障 |  | digital
N2DCS.20MAN20GH001PH1 | 8304 | 中低压旁路油站油压高 |  | digital
N2DCS.20MAN20GH001PH2 | 8305 | 中低压旁路油站油压高高 |  | digital
N2DCS.20MAN20GH001PL1 | 8306 | 中低压旁路油站油压低 |  | digital
N2DCS.20MAN20GH001PL2 | 8307 | 中低压旁路油站油压低低 |  | digital
N2DCS.20MAN20GH001RD1 | 8308 | 中低压旁路油站#1油泵启动指令 |  | digital
N2DCS.20MAN20GH001RD2 | 8309 | 中低压旁路油站#2油泵启动指令 |  | digital
N2DCS.20MAN20GH001RP1 | 8310 | 中低压旁路油站#1油泵在运行 |  | digital
N2DCS.20MAN20GH001RP2 | 8311 | 中低压旁路油站#2油泵在运行 |  | digital
N2DCS.20MAN20GH001TD1 | 8312 | 中低压旁路油站#1油泵停止指令 |  | digital
N2DCS.20MAN20GH001TD2 | 8313 | 中低压旁路油站#1油泵停止指令 |  | digital
N2DCS.20MAN20GH001TH | 8314 | 中低压旁路油站油温高 |  | digital
N2DCS.20MAN20GH001TP1 | 8315 | 中低压旁路油站#1油泵已停止 |  | digital
N2DCS.20MAN20GH001TP2 | 8316 | 中低压旁路油站#2油泵已停止 |  | digital
N2DCS.20MAP10AA101AUTO | 8317 | 低旁阀在自动模式 |  | digital
N2DCS.20MAP10AA101CD | 8318 | 低旁阀快关指令 |  | digital
N2DCS.20MAP10AA101CP | 8319 | 低旁阀全关位置 |  | digital
N2DCS.20MAP10AA101F | 8320 | 低旁阀故障 |  | digital
N2DCS.20MAP10AA101OD | 8321 | 低旁阀快开指令 |  | digital
N2DCS.20MAP10AA101OP | 8322 | 低旁阀全开位置 |  | digital
N2DCS.20MAP10AA101SC1 | 8323 | 低旁阀安全关指令1 |  | digital
N2DCS.20MAP10AA101SC2 | 8324 | 低旁阀安全关指令2 |  | digital
N2DCS.20MAP10AA404CP | 8325 | 低旁阀前疏水气动门全关位 |  | digital
N2DCS.20MAP10AA404F | 8326 | 低旁阀前疏水气动门无电源 |  | digital
N2DCS.20MAP10AA404OD/CD | 8327 | 低旁阀前疏水气动门关/开指令 |  | digital
N2DCS.20MAP10AA404OP | 8328 | 低旁阀前疏水气动门全开位 |  | digital
N2DCS.20MAP10CPX2_MRE | 8329 | 低旁阀后蒸汽压力坏点 |  | digital
N2DCS.20MAP10CTX2_MRE | 8330 | 低旁阀后蒸汽温度坏点 |  | digital
N2DCS.20MAY01CG151CP1 | 8331 | 所有主汽门已关闭1-去锅炉主保护 |  | digital
N2DCS.20MAY01CG151CP2 | 8332 | 所有主汽门已关闭2-去锅炉主保护 |  | digital
N2DCS.20MAY01EZ001SOE | 8333 | #3机本体保护动作 |  | digital
N2DCS.20MAY01EZ011SOE | 8334 | #3机超速保护动作 |  | digital
N2DCS.20MAY01EZ020SOE | 8335 | 手动打闸停#3机（SOE） |  | digital
N2DCS.20MAY10EZ011SOE | 8336 | #3机轴承振动大保护动作（SOE） |  | digital
N2DCS.20MBA10CS910 | 8337 | #4机停机(GT STOPPED) |  | digital
N2DCS.20MBY10DE010YB01 | 8338 | #4机负荷控制切至DCS设定 |  | digital
N2DCS.20MBY10DE020XB01 | 8339 | AGC可用 |  | digital
N2DCS.20MBY10DE020YB01 | 8340 | 一次调频投入/退出 |  | digital
N2DCS.20MBY10DE020YB06 | 8341 | #4机在运行 |  | digital
N2DCS.20MBY10DE020YB07 | 8342 | #4机已停止 |  | digital
N2DCS.20MBY10DT040YB01 | 8343 | IGV全开位（慢速速率） |  | digital
N2DCS.20MBY10DT040YB02 | 8344 | IGV全开位 |  | digital
N2DCS.20MBY10DU060YB01 | 8345 | #4机准备同期 |  | digital
N2DCS.20MBY10DU060YB02 | 8346 | #4机在转速控制方式 |  | digital
N2DCS.20MBY10DU060YB03 | 8347 | #4机在负荷控制方式 |  | digital
N2DCS.20MBY10DU060YB04 | 8348 | #4机在最大负荷限制控制方式 |  | digital
N2DCS.20MBY10DU060YB05 | 8349 | #4机在排气温度控制方式 |  | digital
N2DCS.20MBY10EE010 | 8350 | DCS EXT LOAD SET POINT SELECT |  | digital
N2DCS.20MBY10EE010XB02 | 8351 | #4机负荷控制切至DCS设定 |  | digital
N2DCS.20MBY10EE010YB02 | 8352 | DCS外部负荷设定投入 |  | digital
N2DCS.20MKA01DE120 | 8353 | REMOTE SYN REQUEST FROM DCS |  | digital
N2DCS.20MKA01DE120XB02 | 8354 | DCS发出#4机远方同期投入 |  | digital
N2DCS.20MKA01DE120XB03 | 8355 | DCS发出#4机自动同期投入 |  | digital
N2DCS.20MKA01DE120XB04 | 8356 | DCS发出#4机再同期请求 |  | digital
N2DCS.20MKA01DE120YB01 | 8357 | DCS发出#4机远方同期请求 |  | digital
N2DCS.20MKA01DE120YB02 | 8358 | DCS发出#4机自动同期请求 |  | digital
N2DCS.20MKA10CL001 | 8359 | #3发电机漏水1 |  | digital
N2DCS.20MKA10CL002 | 8360 | #3发电机漏水2 |  | digital
N2DCS.20MKA10CL003 | 8361 | #3发电机漏水3 |  | digital
N2DCS.20MKA10CL004 | 8362 | #3发电机漏水4 |  | digital
N2DCS.20MKA10CL005 | 8363 | #3发电机漏水5 |  | digital
N2DCS.20MKA10CL006 | 8364 | #3发电机漏水6 |  | digital
N2DCS.20MYA01CS901H | 8365 | #3机转速大于2951RPM |  | digital
N2DCS.20MYA01CS901L | 8366 | #3机转速大于600RPM |  | digital
N2DCS.20MYA01DG010 | 8367 | 负荷控制投入（协调方式） |  | digital
N2DCS.20MYA01DU010 | 8368 | 负荷控制投入 |  | digital
N2DCS.20MYB01EC001YB01 | 8369 | #4机无火焰通道A |  | digital
N2DCS.20MYB01EC002YB01 | 8370 | #4机无火焰通道A |  | digital
N2DCS.20MYB01EC003YB01 | 8371 | #4机无火焰通道A |  | digital
N2DCS.20MYB01EC051YB01 | 8372 | #4机已停止 |  | digital
N2DCS.20MYB01EC061YB01 | 8373 | #4机盘车已投入通道1 |  | digital
N2DCS.20MYB01EC062YB01 | 8374 | #4机盘车已投入通道2 |  | digital
N2DCS.20MYB01EC063YB01 | 8375 | #4机盘车已投入通道3 |  | digital
N2DCS.20MYB01EC304YB01 | 8376 | #4机甩负荷通道1 |  | digital
N2DCS.20MYB01EC305YB01 | 8377 | #4机甩负荷通道2 |  | digital
N2DCS.20MYB01EC306YB01 | 8378 | #4机甩负荷通道3 |  | digital
N2DCS.20MYB01EU001YB01 | 8379 | #4机跳闸信号（至DCS） |  | digital
N2DCS.20MYB01EU001YB11 | 8380 | #4机跳闸信号（至DCS） |  | digital
N2DCS.20MYB01EU001YB21 | 8381 | #4机跳闸信号（至DCS） |  | digital
N2DCS.20MYB01EU301 | 8382 | #4机跳闸至DCS通道A |  | digital
N2DCS.20MYB01EU302 | 8383 | #4机跳闸至DCS通道B |  | digital
N2DCS.20MYB01EU303 | 8384 | #4机跳闸至DCS通道C |  | digital
N2DCS.20MYB01EZ001YB01 | 8385 | #4机跳闸信号（至SER） |  | digital
N2DCS.20MYB10DE010 | 8386 | GT NOR LOAD GRADIENT SELECTED |  | digital
N2DCS.20MYB10DE010YB01 | 8387 | #4机负荷快速速率投入 |  | digital
N2DCS.20MYB10DE010YB02 | 8388 | #4机负荷正常速率投入 |  | digital
N2DCS.20MYB10EE101XB01 | 8389 | DCS发出停#4机指令 |  | digital
N2DCS.20MYB10EE102XB02 | 8390 | DCS发出启#4机指令 |  | digital
N2DCS.20PFMPUTIN | 8391 | #2机组一次调频投入/退出 |  | digital
N2DCS.20PGA11AP001TP1 | 8392 | #1闭式冷却水泵已停止 |  | digital
N2DCS.20PGA12AP001TP1 | 8393 | #2闭式冷却水泵已停止 |  | digital
N2DCS.20TCSTODCS01 | 8394 | #4机已准备就绪 |  | digital
N2DCS.20TSIDI1 | 8395 | #3机零转速报警 |  | digital
N2DCS.20TSIDI10 | 8396 | #3机偏心大报警1 |  | digital
N2DCS.20TSIDI11 | 8397 | #3机偏心大报警2 |  | digital
N2DCS.20TSIDI12 | 8398 | #3机轴承盖振大报警1 |  | digital
N2DCS.20TSIDI13 | 8399 | #3机轴承盖振大报警2 |  | digital
N2DCS.20TSIDI14 | 8400 | #3机左高压缸热膨胀大报警 |  | digital
N2DCS.20TSIDI15 | 8401 | #3机右高压缸热膨胀大报警 |  | digital
N2DCS.20TSIDI16 | 8402 | #3机装置\OK\"状态" |  | digital
N2DCS.20TSIDI17 | 8403 | #3机主电源失电报警 |  | digital
N2DCS.20TSIDI18 | 8404 | #3机副电源失电报警 |  | digital
N2DCS.20TSIDI19 | 8405 | #3机主、副电源失电报警 |  | digital
N2DCS.20TSIDI2 | 8406 | #3机转速大报警1 |  | digital
N2DCS.20TSIDI20 | 8407 | #3机24VDC失电报警 |  | digital
N2DCS.20TSIDI3 | 8408 | #3机转速大报警2 |  | digital
N2DCS.20TSIDI4 | 8409 | #3机轴振动大报警1 |  | digital
N2DCS.20TSIDI5 | 8410 | #3机轴振动大报警2 |  | digital
N2DCS.20TSIDI6 | 8411 | #3机轴向位移大报警1 |  | digital
N2DCS.20TSIDI7 | 8412 | #3机轴向位移大报警2 |  | digital
N2DCS.20TSIDI8 | 8413 | #3机高压及低压缸胀差大报警1 |  | digital
N2DCS.20TSIDI9 | 8414 | #3机高压及低压缸胀差大报警2 |  | digital
N2DCS.AGCOFF | 8415 | AGC已退出 |  | digital
N2DCS.AGCON | 8416 | AGC已投入 |  | digital
N2DCS.DEHHIPRSCTL | 8417 | 高中压压力控制后备模式 |  | digital
N2DCS.DEHLPRSCTL | 8418 | 低压蒸汽压力控制后备模式 |  | digital
N2DCS.DI | 8419 | 开关量 |  | digital
N2DCS.GT_FIRE | 8420 | #4机在运行 |  | digital
N2DCS.GT_STOP | 8421 | 燃机停止 |  | digital
N2DCS.GT_TRIP | 8422 | 燃机跳闸(TO DCS) |  | digital
N2DCS.HOTBANKTBVFULLCLS | 8423 | 热备用强制全关 |  | digital
N2DCS.HPBCL | 8424 | 高旁阀已关闭 |  | digital
N2DCS.HPBFOLLOW | 8425 | 高旁阀压力控制后备模式 |  | digital
N2DCS.HPBMAN | 8426 | 高旁阀在手动模式 |  | digital
N2DCS.HPBPRATE0 | 8427 | 高旁阀压力设定值下降速率为0 |  | digital
N2DCS.HPBPUPRATEMAX | 8428 | 高旁阀压力设定值上升速率最大 |  | digital
N2DCS.HPBSPYCL | 8429 | 高旁减温水调节阀已关闭 |  | digital
N2DCS.HPBSPYOP | 8430 | 高旁减温水调节阀已打开 |  | digital
N2DCS.HPBYCVFASTCLS | 8431 | 高旁阀快关指令 |  | digital
N2DCS.HPBYCVFASTOP | 8432 | 高旁阀快开指令 |  | digital
N2DCS.HPBYSPYCVCLS | 8433 | 高旁减温水调节阀快关指令 |  | digital
N2DCS.HPBYSPYCVOP | 8434 | 高旁减温水调节阀快开指令 |  | digital
N2DCS.HPIPMINPRSMODE | 8435 | 高中压旁路最小压力模式 |  | digital
N2DCS.HPIPMINPRSSET | 8436 | 高中压旁路最小压力设定 |  | digital
N2DCS.HPIPTBVBACKUP | 8437 | 高中压旁路阀备用模式 |  | digital
N2DCS.HPIPTBVBACKUPTRK | 8438 | 高旁备用压力设定跟踪 |  | digital
N2DCS.HPIPTBVPRSTRK | 8439 | 高中压旁路实际压力跟踪 |  | digital
N2DCS.HPMINPOS | 8440 | 高旁阀最小阀位模式 |  | digital
N2DCS.HPPRSHIGH03 | 8441 | Ovation Control Builder |  | digital
N2DCS.HPPRSHIGH05 | 8442 | 高压主汽压力大于0.5 |  | digital
N2DCS.HPPRSHIGH55 | 8443 | 高压主汽压力大于5.5 |  | digital
N2DCS.HPPVSPERRLOW1 | 8444 | 高旁压力与设定值差<0.02 |  | digital
N2DCS.HPPVSPERRLOW2 | 8445 | 高旁压力与设定值差<0.2 |  | digital
N2DCS.HPPVSVERRHIGH02 | 8446 | 高旁压力与设定值1差>0.02 |  | digital
N2DCS.HPPVSVHIGH02 | 8447 | 高旁压力与设定值2差>0.2 |  | digital
N2DCS.HPPVSVLOW0 | 8448 | 高旁压力与设定值2差<0 |  | digital
N2DCS.HPTARGETSETP | 8449 | 高旁阀后备模式压力设定值高限 |  | digital
N2DCS.HPTBVAUTO | 8450 | 高旁控制自动 |  | digital
N2DCS.HPTBVBACKUPHOLD | 8451 | 高旁备用压力设定保持 |  | digital
N2DCS.HPTBVCTRLON | 8452 | 高旁压力控制投入 |  | digital
N2DCS.HPTBVCUTAUTO | 8453 | 高旁切手动 |  | digital
N2DCS.HPTBVERRLOW | 8454 | Ovation Control Builder |  | digital
N2DCS.HPTBVFLAMETRK | 8455 | 高旁压力跟踪 |  | digital
N2DCS.HPTBVFORCECLS | 8456 | 高旁强制关 |  | digital
N2DCS.HPTBVFORCEOPEN | 8457 | 高旁强制开 |  | digital
N2DCS.HPTBVH0 | 8458 | 高旁调节指令>0% |  | digital
N2DCS.HPTBVH5 | 8459 | 高旁调节指令>5% |  | digital
N2DCS.HPTBVINTPRSTRK | 8460 | 高旁初始压力设定跟踪 |  | digital
N2DCS.HPTBVLOWLIMIT | 8461 | 高旁阀位保持 |  | digital
N2DCS.HPTBVMINCTRLON | 8462 | 高旁最小阀位方式控制 |  | digital
N2DCS.HPTBVPITRK | 8463 | Ovation Control Builder |  | digital
N2DCS.HPTBVPRSPASS | 8464 | 高旁实际压力设定PASS |  | digital
N2DCS.HRSGCOLD | 8465 | #3炉冷态模式启动 |  | digital
N2DCS.HRSGHOT | 8466 | #3炉热态模式启动 |  | digital
N2DCS.HRSGWARM | 8467 | #3炉温态模式启动 |  | digital
N2DCS.IPBCL | 8468 | 中旁阀已关闭 |  | digital
N2DCS.IPBFOLLOW | 8469 | 中旁阀压力控制后备模式 |  | digital
N2DCS.IPBMAN | 8470 | 中旁阀在手动模式 |  | digital
N2DCS.IPBPRATE0 | 8471 | 中旁阀压力设定值下降速率为0 |  | digital
N2DCS.IPBPUPRATEMAX | 8472 | 中旁阀压力设定值上升速率最大 |  | digital
N2DCS.IPBSPYCL | 8473 | 中旁减温水调节阀已关闭 |  | digital
N2DCS.IPBSPYOP | 8474 | 中旁减温水调节阀已打开 |  | digital
N2DCS.IPBYCVFASTCLS | 8475 | 中旁阀快关指令 |  | digital
N2DCS.IPBYCVFASTOP | 8476 | 中旁阀快开指令 |  | digital
N2DCS.IPMINPOS | 8477 | 中旁阀最小阀位模式 |  | digital
N2DCS.IPPRSHIGH01 | 8478 | 中压蒸汽压力>0.1 |  | digital
N2DCS.IPPRSHIGH03 | 8479 | 中压蒸汽压力>0.3 |  | digital
N2DCS.IPPRSHIGH15 | 8480 | 中压蒸汽压力>1.5 |  | digital
N2DCS.IPPVSPERRLOW1 | 8481 | 中旁压力与设定值差<-0.02 |  | digital
N2DCS.IPPVSPERRLOW2 | 8482 | 中旁压力与设定值差<-0.1 |  | digital
N2DCS.IPPVSVERRHIGH02 | 8483 | 中压蒸汽压力与设定值1差>0.02 |  | digital
N2DCS.IPPVSVHIGH02 | 8484 | 中压蒸汽压力与设定值2差>0.2 |  | digital
N2DCS.IPPVSVLOW0 | 8485 | 中压蒸汽压力与设定值2差<0 |  | digital
N2DCS.IPTARGETSETP | 8486 | 中旁阀后备模式压力设定值高限 |  | digital
N2DCS.IPTBVAUTO | 8487 | 中旁控制自动 |  | digital
N2DCS.IPTBVBAKPRSTRK | 8488 | 中压旁路备用跟踪 |  | digital
N2DCS.IPTBVBANKPRSHOLD | 8489 | 中旁备用压力设定保持 |  | digital
N2DCS.IPTBVCTRLON | 8490 | 中旁压力控制投入 |  | digital
N2DCS.IPTBVERRLOW | 8491 | Ovation Control Builder |  | digital
N2DCS.IPTBVFLAMETRK | 8492 | 中旁压力跟踪 |  | digital
N2DCS.IPTBVFORCECLOSE | 8493 | 中旁强制关 |  | digital
N2DCS.IPTBVFORCECLS | 8494 | 中旁强制关 |  | digital
N2DCS.IPTBVFORCEOPEN | 8495 | 中旁强制开 |  | digital
N2DCS.IPTBVH0 | 8496 | 中旁调节指令>0% |  | digital
N2DCS.IPTBVH5 | 8497 | 中旁调节指令>5% |  | digital
N2DCS.IPTBVINTPRSSETTRK | 8498 | 中旁初始压力设定跟踪 |  | digital
N2DCS.IPTBVLOWLIMIT | 8499 | 中旁阀位保持 |  | digital
N2DCS.IPTBVMINCTRLON | 8500 | Ovation Control Builder |  | digital
N2DCS.IPTBVMINPRSSET | 8501 | 中旁最小压力设定 |  | digital
N2DCS.IPTBVPITRK | 8502 | Ovation Control Builder |  | digital
N2DCS.IPTBVPRSRATEPASS | 8503 | Ovation Control Builder |  | digital
N2DCS.J0LBG10AA003CD_DO | 8504 | 二号机关闭启动锅炉至1号机辅汽? |  | digital
N2DCS.J0LBG10AA003CP_DI | 8505 | 启动锅炉至1号机辅汽母管关断阀? |  | digital
N2DCS.J0LBG22AA001CD_DO | 8506 | 二号机关闭启动锅炉至辅汽母管关 |  | digital
N2DCS.J0LBG22AA001CP_DI | 8507 | 启动锅炉至辅汽母管关断阀全关送 |  | digital
N2DCS.J0LBG22AA001OD_DO | 8508 | 二号机打开启动锅炉至辅汽母管关 |  | digital
N2DCS.J0LBG22AA001OP_DI | 8509 | 启动锅炉至辅汽母管关断阀全开送 |  | digital
N2DCS.J0QFB50AP001RD_DI | 8510 | 二号机启动空压机顺控指令 |  | digital
N2DCS.J0QFB50CP101DI | 8511 | 压缩空气母管压力正常 |  | digital
N2DCS.LPBCL | 8512 | 低旁阀已关闭 |  | digital
N2DCS.LPBFOLLOW | 8513 | 低旁阀压力控制后备模式 |  | digital
N2DCS.LPBMAN | 8514 | 低旁阀在手动模式 |  | digital
N2DCS.LPBPRATE0 | 8515 | 低旁阀压力设定值下降速率为0 |  | digital
N2DCS.LPBPUPRATEMAX | 8516 | 低旁阀压力设定值上升速率最大 |  | digital
N2DCS.LPBSPYCL | 8517 | 低旁减温水调节阀已关闭 |  | digital
N2DCS.LPBSPYOP | 8518 | 低旁减温水调节阀已打开 |  | digital
N2DCS.LPBYCVFASTCLS | 8519 | 低旁阀快关指令 |  | digital
N2DCS.LPBYCVFASTOP | 8520 | 低旁阀快开指令 |  | digital
N2DCS.LPMINPOS | 8521 | 低旁阀最小阀位模式 |  | digital
N2DCS.LPMINPRSMODE | 8522 | Ovation Control Builder |  | digital
N2DCS.LPMINPRSSET | 8523 | 低旁最小压力设定 |  | digital
N2DCS.LPPRSHIGH01 | 8524 | 低压蒸汽压力>0.1 |  | digital
N2DCS.LPPRSHIGH015 | 8525 | 低压蒸汽压力>0.15 |  | digital
N2DCS.LPPRSHIGH03 | 8526 | Ovation Control Builder |  | digital
N2DCS.LPPRSHIGH06 | 8527 | 低压蒸汽压力>0.6 |  | digital
N2DCS.LPPVSPERRLOW1 | 8528 | 低旁压力与设定值差小于-0.002 |  | digital
N2DCS.LPPVSPERRLOW2 | 8529 | 低旁压力与设定值差小于-0.03 |  | digital
N2DCS.LPPVSVERRHIGH02 | 8530 | 低压蒸汽压力与设定值1差>0.02 |  | digital
N2DCS.LPPVSVHIGH02 | 8531 | 低压蒸汽压力与设定值2差>0.02 |  | digital
N2DCS.LPPVSVLOW0 | 8532 | 低压蒸汽压力与设定值2差<0 |  | digital
N2DCS.LPTARGETSETP | 8533 | 低旁阀后备模式压力设定值高限 |  | digital
N2DCS.LPTBVAUTO | 8534 | 低旁控制自动 |  | digital
N2DCS.LPTBVBACKUP | 8535 | 低旁备用模式 |  | digital
N2DCS.LPTBVBACKUPHOLD | 8536 | 低旁备用压力设定保持 |  | digital
N2DCS.LPTBVBACKUPTK | 8537 | 低压旁路备用跟踪 |  | digital
N2DCS.LPTBVBACKUPTRK | 8538 | 低旁备用压力设定跟踪 |  | digital
N2DCS.LPTBVCTRLON | 8539 | 低旁压力控制投入 |  | digital
N2DCS.LPTBVERRLOW | 8540 | Ovation Control Builder |  | digital
N2DCS.LPTBVFLAMETRK | 8541 | 低旁压力跟踪 |  | digital
N2DCS.LPTBVFORCECLS | 8542 | 低旁强制关 |  | digital
N2DCS.LPTBVFORCEOPEN | 8543 | 低旁强制开 |  | digital
N2DCS.LPTBVH0 | 8544 | Ovation Control Builder |  | digital
N2DCS.LPTBVH5 | 8545 | 低旁调节指令大于5% |  | digital
N2DCS.LPTBVINTPRSTRK | 8546 | 低旁初始压力设定跟踪 |  | digital
N2DCS.LPTBVLOWLIMIT | 8547 | 低旁阀位保持 |  | digital
N2DCS.LPTBVMINCTRLON | 8548 | 低旁最小阀位控制方式投入 |  | digital
N2DCS.LPTBVPITRK | 8549 | Ovation Control Builder |  | digital
N2DCS.LPTBVPRSPASS | 8550 | 低旁实际压力设定PASS |  | digital
N2DCS.ONE1 | 8551 | 开关量1 |  | digital
N2DCS.OPHIBYPS | 8552 | 停机时开高中压旁路 |  | digital
N2DCS.TRIPCMD1 | 8553 | Ovation Control Builder |  | digital
N2DCS.TSCSALMA | 8554 | 汽机报警A |  | digital
N2DCS.TSCSALMB | 8555 | 汽机报警B |  | digital
N2DCS.TURBDRNHP_CL | 8556 | #3机高压疏水阀组关闭指令 |  | digital
N2DCS.TURBDRNHP_OP | 8557 | #3机高压疏水阀组打开指令 |  | digital
N2DCS.TURBDRNHPCP | 8558 | #3机高压疏水阀组均已关闭 |  | digital
N2DCS.TURBDRNHPOP | 8559 | #3机高压疏水门组均已全开 |  | digital
N2DCS.TURBDRNIP_CL | 8560 | #3机中压疏水阀组关闭指令 |  | digital
N2DCS.TURBDRNIP_OP | 8561 | #3机中压疏水阀组打开指令 |  | digital
N2DCS.TURBDRNIPCP | 8562 | #3机中压疏水阀组均已关闭 |  | digital
N2DCS.TURBDRNIPOP | 8563 | #3机中压疏水门组均已全开 |  | digital
N2DCS.TURBDRNLP_CL | 8564 | #3机低压疏水阀组关闭指令 |  | digital
N2DCS.TURBDRNLP_OP | 8565 | #3机低压疏水阀组打开指令 |  | digital
N2DCS.TURBDRNLPCP | 8566 | #3机低压疏水阀组均已关闭 |  | digital
N2DCS.TURBDRNLPOP | 8567 | #3机低压疏水门组均已全开 |  | digital
N2DCS.XOCAE01EY301 | 8568 | BOILER PROTECTION CH. A |  | digital
N2DCS.XOCAE01EY302 | 8569 | BOILER PROTECTION CH. B |  | digital
N2DCS.XOCAE01EY303 | 8570 | BOILER PROTECTION CH. C |  | digital
N2DCS.XOLBC10CL002H | 8571 | 冷段逆止阀前疏水罐液位2高 |  | digital
N2DCS.XOLBC10CL004H | 8572 | 冷段逆止阀后疏水罐液位2高 |  | digital
N2DCS.XOLBC10CL006H | 8573 | 高旁后再热冷段疏水罐液位2 高 |  | digital
N2DCS.XOMBY10DE010 | 8574 | EXT LOAD SET POINT REL. TO DCS |  | digital
N2DCS.XOMYB01EC001 | 8575 | GT NOT FIRING CH A |  | digital
N2DCS.XOMYB01EC002 | 8576 | GT NOT FIRING CH B |  | digital
N2DCS.XOMYB01EC003 | 8577 | GT NOT FIRING CH C |  | digital
N2DCS.XOMYB01EC051 | 8578 | GT IN SHUTDOWN |  | digital
N2DCS.XOMYB01EC061 | 8579 | GT ON TURNING GEAR TO ESD CH 1 |  | digital
N2DCS.XOMYB01EC062 | 8580 | GT ON TURNING GEAR TO ESD CH 2 |  | digital
N2DCS.XOMYB01EC063 | 8581 | GT ON TURNING GEAR TO ESD CH 3 |  | digital
N2DCS.XOMYB01EC304 | 8582 | GT IN LOAD REJECTION TO ESD CH |  | digital
N2DCS.XOMYB01EC305 | 8583 | GT IN LOAD REJECTION TO ESD CH |  | digital
N2DCS.XOMYB01EC306 | 8584 | GT IN LOAD REJECTION TO ESD CH |  | digital
N2DCS.XOMYB01EZ001 | 8585 | GT TRIP TO SER |  | digital
N2DCS.Y0AEA14GS101RP | 8586 |  |  | digital
N2DCS.Y0AEA14GS101TP | 8587 |  |  | digital
N2DCS.ZERO1 | 8588 | 开关量0 |  | digital
N2DCS.21AEA01EA100_XB05 | 8589 | #4主变220KV断路器允许同期 |  | digital
N2DCS.21BBE00EG001_XB27 | 8590 | #1 SFC 6KV母线低电压信号 |  | digital
N2DCS.21MKY01EZ120_XB01 | 8591 | #4发电机保护A装置失电/装置闭锁 |  | digital
N2DCS.21MKY01EZ122_XB01 | 8592 | #4发电机保护A告警总信号 |  | digital
N2DCS.21MKY01EZ220_XB01 | 8593 | #4发电机保护B装置失电/装置闭锁 |  | digital
N2DCS.21MKY01EZ222_XB01 | 8594 | #4发电机保护B告警总信号 |  | digital
N2DCS.AGCOK | 8595 | AGC总指令与负荷反馈偏差<10 |  | digital
N2DCS.AGCOKORNOTCCS1 | 8596 | AGC已投入/CCS已退出 |  | digital
N2DCS.AGCPMT1 | 8597 | AGC投入允许 |  | digital
N2DCS.AGCREADY | 8598 | AGC已就绪 |  | digital
N2DCS.ANYGTRB1 | 8599 | Ovation Control Builder |  | digital
N2DCS.CCSMODE1 | 8600 | CCS已投入 |  | digital
N2DCS.CCSNOTAGC1 | 8601 | CCS已投入且AGC已退出 |  | digital
N2DCS.CCSPMT | 8602 | CCS投入允许 |  | digital
N2DCS.DCS_AUXOK1 | 8603 | #3机润滑油、控制油系统运行正常 |  | digital
N2DCS.DCS_DRNWTR1 | 8604 | #3机疏水系统运行正常 |  | digital
N2DCS.DCS_GLANDSTEAMON1 | 8605 | #3机轴封系统运行正常 |  | digital
N2DCS.DCSSTOPTURB | 8606 | DCS停止#3机 |  | digital
N2DCS.DCSTRIPTURB | 8607 | 汽机跳闸 |  | digital
N2DCS.DEHTRIPPED | 8608 | #3机跳闸 |  | digital
N2DCS.EXT_LOADSET_SEL | 8609 | #4机负荷设定在DCS控制 |  | digital
N2DCS.FC_MODE | 8610 | 纯凝模式 |  | digital
N2DCS.GT_REMOTE_PER | 8611 | #4机允许CCS控制 |  | digital
N2DCS.GTCBOFF1 | 8612 | #4发电机已解列 |  | digital
N2DCS.GTCBON1 | 8613 | #4发电机已并网 |  | digital
N2DCS.GTCCS | 8614 | Ovation Control Builder |  | digital
N2DCS.GTCCSONDMD1 | 8615 | CCS投入请求 |  | digital
N2DCS.GTCCSONDMDPMT1 | 8616 | CCS投入请求允许 |  | digital
N2DCS.GTCCSPMT1 | 8617 | #4机负荷>120且负荷在DCS控制 |  | digital
N2DCS.GTFIRE | 8618 | Ovation Control Builder |  | digital
N2DCS.GTHINTERLOCK | 8619 | #4机跳闸信号（联跳#3炉） |  | digital
N2DCS.GTLOAD_AUTO1 | 8620 | Ovation Control Builder |  | digital
N2DCS.GTNOFIRE1 | 8621 | #4机无火焰通道1 |  | digital
N2DCS.GTNOFIRE2 | 8622 | #4机无火焰通道2 |  | digital
N2DCS.GTNOFIRE3 | 8623 | #4机无火焰通道3 |  | digital
N2DCS.GTPCTR1 | 8624 | #4机盘车已投入通道1(ESD) |  | digital
N2DCS.GTPCTR2 | 8625 | #4机盘车已投入通道2(ESD) |  | digital
N2DCS.GTPCTR3 | 8626 | #4机盘车已投入通道3(ESD) |  | digital
N2DCS.GTRB | 8627 | #4机发生RB |  | digital
N2DCS.GTRB1 | 8628 | #4机发生RB通道1 |  | digital
N2DCS.GTRB2 | 8629 | #4机发生RB通道2 |  | digital
N2DCS.GTREJ1 | 8630 | #4机甩负荷通道1(ESD) |  | digital
N2DCS.GTREJ2 | 8631 | #4机甩负荷通道2(ESD) |  | digital
N2DCS.GTREJ3 | 8632 | #4机甩负荷通道3(ESD) |  | digital
N2DCS.GTRUN1 | 8633 | #4机在运行 |  | digital
N2DCS.GTSTOP1 | 8634 | #4机已停止 |  | digital
N2DCS.GTTRIP | 8635 | #4机已跳闸 |  | digital
N2DCS.HINTERLOCK | 8636 | Ovation Control Builder |  | digital
N2DCS.HREXHOT | 8637 | #3炉极热态模式启动 |  | digital
N2DCS.HRSGRUN | 8638 | #3炉在运行 |  | digital
N2DCS.HRSGSTOP | 8639 | #3炉已停止 |  | digital
N2DCS.HSELFC_MODE | 8640 | #2机组纯凝模式 |  | digital
N2DCS.HSELPC_MODE | 8641 | #2机组抽凝模式 |  | digital
N2DCS.HSTRUPMODESEL | 8642 | #3炉在任一启动方式（冷、温、热 |  | digital
N2DCS.HTRIPDMD | 8643 | #3炉跳闸信号（联跳燃机） |  | digital
N2DCS.IGVFOP | 8644 | IGV全开(慢速速率) |  | digital
N2DCS.IGVOP | 8645 | IGV全开 |  | digital
N2DCS.J0LBG10AA003CP_DI1 | 8646 | Ovation Control Builder |  | digital
N2DCS.J0LBG22AA001CP_DI1 | 8647 | 启动锅炉至辅汽母管关断阀全关 |  | digital
N2DCS.J0LBG22AA001OP_DI1 | 8648 | Ovation Control Builder |  | digital
N2DCS.J0QFB50CP101DI1 | 8649 | 空压机顺控启动完成 |  | digital
N2DCS.LIFTPUMPS_1OF2ON | 8650 | 至少一台顶轴油泵在运行 |  | digital
N2DCS.LIFTPUMPS_ALLOFF1 | 8651 | 顶轴油泵均已停止 |  | digital
N2DCS.LOADATMAX1 | 8652 | #2机组总负荷设定>高限值 |  | digital
N2DCS.LOADATMIN1 | 8653 | #2机组总负荷设定<低限值 |  | digital
N2DCS.LOADGO1 | 8654 | 负荷开始增减 |  | digital
N2DCS.LOADHOLD1 | 8655 | 负荷停止增减/保持原值 |  | digital
N2DCS.LOADSP_AUTO1 | 8656 | #2机组负荷设定在自动模式 |  | digital
N2DCS.MONTH_CHG | 8657 | 月份变化 |  | digital
N2DCS.NOTCCSMODE1 | 8658 | CCS已退出 |  | digital
N2DCS.OPCACT | 8659 | OPC动作（DEH至DCS） |  | digital
N2DCS.OPLBYPS | 8660 | 停#3机时打开低旁阀 |  | digital
N2DCS.PC_MODE | 8661 | #2机组抽凝模式 |  | digital
N2DCS.RB1PUTIN | 8662 | #3炉跳闸联锁#4机RB保护投入 |  | digital
N2DCS.RBOCCUR1 | 8663 | #4机RB回路1 |  | digital
N2DCS.RBOCCUR2 | 8664 | #4机RB回路2 |  | digital
N2DCS.RBORNOTCCS1 | 8665 | #4机发生RB或CCS已退出 |  | digital
N2DCS.RBPUTIN | 8666 | 凝结水泵跳闸联锁#4机RB保护投入 |  | digital
N2DCS.SPTINTRHRSG | 8667 | 停#3机联锁停余热锅炉 |  | digital
N2DCS.STCBOFF1 | 8668 | #3发电机已解列 |  | digital
N2DCS.STCBON | 8669 | Ovation Control Builder |  | digital
N2DCS.STCBON1 | 8670 | #3发电机已并网 |  | digital
N2DCS.STOPTURBCMD | 8671 | DCS停止#3机指令 |  | digital
N2DCS.STRUN | 8672 | #3机负荷>20MW |  | digital
N2DCS.TEST_AUTO | 8673 | Ovation Control Builder |  | digital
N2DCS.THINTERLOCK | 8674 | #4机跳闸信号（联跳#3炉） |  | digital
N2DCS.TURBLATCHED1 | 8675 | #3机无遮断信号 |  | digital
N2DCS.TURBRUN | 8676 | #3机无遮断信号 |  | digital
N2DCS.TURBTRIP1 | 8677 | #3机已遮断 |  | digital
N2DCS.TURBTRIPACKOK1 | 8678 | #3机打闸已确认（APS停机） |  | digital
N2DCS.Y0AEA11GS101RP | 8679 | Ovation Control Builder |  | digital
N2DCS.Y0AEA11GS101TP | 8680 | Ovation Control Builder |  | digital
N2DCS.YEAR_CHG | 8681 | 年份变化 |  | digital
N2DCS.20LBD20AA001CD | 8682 | #3机冷再供热电动门关闭指令 |  | digital
N2DCS.20LBD20AA001CP | 8683 | #3机冷再供热电动门全关位置 |  | digital
N2DCS.20LBD20AA001F | 8684 | #3机冷再供热电动门综合故障 |  | digital
N2DCS.20LBD20AA001OD | 8685 | #3机冷再供热电动门打开指令 |  | digital
N2DCS.20LBD20AA001OP | 8686 | #3机冷再供热电动门全开位置 |  | digital
N2DCS.20LBD20AA001RC | 8687 | #3机冷再供热电动门在远控 |  | digital
N2DCS.20LBD20AA002CD | 8688 | 冷再供热逆止门后电动门关指令 |  | digital
N2DCS.20LBD20AA002CP | 8689 | 冷再供热逆止门后电动门全关位 |  | digital
N2DCS.20LBD20AA002F | 8690 | 冷再供热逆止门后电动门综合故障 |  | digital
N2DCS.20LBD20AA002OD | 8691 | 冷再供热逆止门后电动门开指令 |  | digital
N2DCS.20LBD20AA002OP | 8692 | 冷再供热逆止门后电动门全开位 |  | digital
N2DCS.20LBD20AA002RC | 8693 | 冷再供热逆止门后电动门在远控 |  | digital
N2DCS.20LBD20AA402CP | 8694 | 冷再供热母管气动疏水门全关位 |  | digital
N2DCS.20LBD20AA402F | 8695 | 冷再供热母管气动疏水门无电源 |  | digital
N2DCS.20LBD20AA402OD/CD | 8696 | 冷再供热母管气动疏水门开指令 |  | digital
N2DCS.20LBD20AA402OP | 8697 | 冷再供热母管气动疏水门全开位 |  | digital
N2DCS.20LBD20AC001AUTO | 8698 | 冷再供热减温减压器在自动模式 |  | digital
N2DCS.20LBD20AC001DVHI | 8699 | 冷再供热减压器指令、反馈偏差大 |  | digital
N2DCS.20LBD20AC001F | 8700 | 冷再供热减温减压器综合故障 |  | digital
N2DCS.20LBD20AC001RC | 8701 | 冷再供热减温减压器在远控 |  | digital
N2DCS.20LBD20AC001SPDH | 8702 | 冷再供热减压器设定、反馈偏差大 |  | digital
N2DCS.20LBD40AA001CD | 8703 | #3机热再供热电动门关指令 |  | digital
N2DCS.20LBD40AA001CP | 8704 | #3机热再供热电动门全关位 |  | digital
N2DCS.20LBD40AA001F | 8705 | #3机热再供热电动门综合故障 |  | digital
N2DCS.20LBD40AA001OD | 8706 | #3机热再供热电动门开指令 |  | digital
N2DCS.20LBD40AA001OP | 8707 | #3机热再供热电动门全开位 |  | digital
N2DCS.20LBD40AA001RC | 8708 | #3机热再供热电动门在远控 |  | digital
N2DCS.20LBD40AA002CD | 8709 | 热再供热逆止门后电动门关指令 |  | digital
N2DCS.20LBD40AA002CP | 8710 | 热再供热逆止门后电动门全关位 |  | digital
N2DCS.20LBD40AA002F | 8711 | 热再供热逆止门后电动门综合故障 |  | digital
N2DCS.20LBD40AA002OD | 8712 | 热再供热逆止门后电动门开指令 |  | digital
N2DCS.20LBD40AA002OP | 8713 | 热再供热逆止门后电动门全开位 |  | digital
N2DCS.20LBD40AA002RC | 8714 | 热再供热逆止门后电动门在远控 |  | digital
N2DCS.20LBD40AA402CP | 8715 | 热再供热母管气动疏水门全关位 |  | digital
N2DCS.20LBD40AA402F | 8716 | 热再供热母管气动疏水门无电源 |  | digital
N2DCS.20LBD40AA402OD/CD | 8717 | 热再供热母管气动疏水门开指令 |  | digital
N2DCS.20LBD40AA402OP | 8718 | 热再供热母管气动疏水门全开位 |  | digital
N2DCS.20LBD40AC001AUTO | 8719 | 热再供热减温减压器在自动模式 |  | digital
N2DCS.20LBD40AC001DVHI | 8720 | 热再供热减压器指令、反馈偏差大 |  | digital
N2DCS.20LBD40AC001F | 8721 | 热再供热减温减压器综合故障 |  | digital
N2DCS.20LBD40AC001RC | 8722 | 热再供热减温减压器在远控 |  | digital
N2DCS.20LBD40AC001SPDH | 8723 | 热再供热减压器设定、反馈偏差大 |  | digital
N2DCS.20LBD60AA001CD | 8724 | #3机供热母管电动门关闭指令 |  | digital
N2DCS.20LBD60AA001CP | 8725 | #3机供热母管电动门全关位置 |  | digital
N2DCS.20LBD60AA001F | 8726 | #3机供热母管电动门综合故障 |  | digital
N2DCS.20LBD60AA001OD | 8727 | #3机供热母管电动门打开指令 |  | digital
N2DCS.20LBD60AA001OP | 8728 | #3机供热母管电动门全开位置 |  | digital
N2DCS.20LBD60AA001RC | 8729 | #3机供热母管电动门在远控 |  | digital
N2DCS.20LBD80AA001CD | 8730 | 冷再抽汽至预留中压电动门关指令 |  | digital
N2DCS.20LBD80AA001CP | 8731 | 冷再抽汽至预留中压电动门全关位 |  | digital
N2DCS.20LBD80AA001F | 8732 | 冷再抽汽至预留中压电动门故障 |  | digital
N2DCS.20LBD80AA001OD | 8733 | 冷再抽汽至预留中压电动门开指令 |  | digital
N2DCS.20LBD80AA001OP | 8734 | 冷再抽汽至预留中压电动门全开位 |  | digital
N2DCS.20LBD80AA001RC | 8735 | 冷再抽汽至预留中压电动门在远控 |  | digital
N2DCS.20LBD80AA402CP | 8736 | 冷再抽汽至预留管道疏水门全关位 |  | digital
N2DCS.20LBD80AA402F | 8737 | 冷再抽汽至预留管道疏水门无电源 |  | digital
N2DCS.20LBD80AA402OD/CD | 8738 | 冷再抽汽至预留管疏水门关/开令 |  | digital
N2DCS.20LBD80AA402OP | 8739 | 冷再抽汽至预留管道疏水门全开位 |  | digital
N2DCS.20LBG11AA007CD | 8740 | 高排至辅汽母管供汽电动门关指令 |  | digital
N2DCS.20LBG11AA007CP | 8741 | 高排至辅汽母管供汽电动门全关位 |  | digital
N2DCS.20LBG11AA007F | 8742 | 高排至辅汽母管供汽电动门故障 |  | digital
N2DCS.20LBG11AA007OD | 8743 | 高排至辅汽母管供汽电动门开指令 |  | digital
N2DCS.20LBG11AA007OP | 8744 | 高排至辅汽母管供汽电动门全开位 |  | digital
N2DCS.20LBG11AA007RC | 8745 | 高排至辅汽母管供汽电动门在远控 |  | digital
N2DCS.20LBG11AC001AUTO | 8746 | 高排至辅汽母管供汽减压器在自动 |  | digital
N2DCS.20LBG11AC001DVHI | 8747 | 高排至辅汽减压器指令反馈偏差大 |  | digital
N2DCS.20LBG11AC001F | 8748 | 高排至辅汽母管供汽减压器故障 |  | digital
N2DCS.20LBG11AC001RC | 8749 | 高排至辅汽母管供汽减压器在远控 |  | digital
N2DCS.20LBG11AC001SPDH | 8750 | 高排至辅汽减压器设定反馈偏差大 |  | digital
N2DCS.20LBG21AA001CD | 8751 | 辅汽至#3机轴封供汽电动门关指令 |  | digital
N2DCS.20LBG21AA001CP | 8752 | 辅汽至#3机轴封供汽电动门全关位 |  | digital
N2DCS.20LBG21AA001F | 8753 | 辅汽至#3机轴封供汽电动门故障 |  | digital
N2DCS.20LBG21AA001OD | 8754 | 辅汽至#3机轴封供汽电动门开指令 |  | digital
N2DCS.20LBG21AA001OP | 8755 | 辅汽至#3机轴封供汽电动门全开位 |  | digital
N2DCS.20LBG21AA001RC | 8756 | 辅汽至#3机轴封供汽电动门在远控 |  | digital
N2DCS.20LBG22AA001CD | 8757 | 辅汽至#3机喷射器电动门关指令 |  | digital
N2DCS.20LBG22AA001CP | 8758 | 辅汽至#3机喷射器电动门全关位 |  | digital
N2DCS.20LBG22AA001F | 8759 | 辅汽至#3机喷射器电动门综合故障 |  | digital
N2DCS.20LBG22AA001OD | 8760 | 辅汽至#3机喷射器电动门打开指令 |  | digital
N2DCS.20LBG22AA001OP | 8761 | 辅汽至#3机喷射器电动门全开位 |  | digital
N2DCS.20LBG22AA001RC | 8762 | 辅汽至#3机喷射器电动门在远控 |  | digital
N2DCS.20LCE11AA001CD | 8763 | 凝结水至辅汽减温水电动门关指令 |  | digital
N2DCS.20LCE11AA001CP | 8764 | 凝结水至辅汽减温水电动门全关位 |  | digital
N2DCS.20LCE11AA001F | 8765 | 凝结水至辅汽减温水电动门故障 |  | digital
N2DCS.20LCE11AA001OD | 8766 | 凝结水至辅汽减温水电动门开指令 |  | digital
N2DCS.20LCE11AA001OP | 8767 | 凝结水至辅汽减温水电动门全开位 |  | digital
N2DCS.20LCE11AA001RC | 8768 | 凝结水至辅汽减温水电动门在远控 |  | digital
N2DCS.20LCE11AA101AUTO | 8769 | 凝结水至辅汽减温水调阀在自动 |  | digital
N2DCS.20LCE11AA101DVHI | 8770 | 辅汽减温水调阀指令反馈偏差大 |  | digital
N2DCS.20LCE11AA101F | 8771 | 凝结水至辅汽减温水调阀故障 |  | digital
N2DCS.20LCE11AA101RC | 8772 | 凝结水至辅汽减温水调阀在远控 |  | digital
N2DCS.20LCE11AA101SPDH | 8773 | 辅汽减温水调阀设定反馈偏差大 |  | digital
N2DCS.20LCE12AA001CD | 8774 | 凝结水至低旁减温水气动门关指令 |  | digital
N2DCS.20LCE12AA001F | 8775 | 凝结水至低旁减温水气动门无电源 |  | digital
N2DCS.20LCE12AA001OD | 8776 | 凝结水至低旁减温水气动门开指令 |  | digital
N2DCS.20LCE12AA001OP | 8777 | 凝结水至低旁减温水气动门全开位 |  | digital
N2DCS.20LCE12AA101_CUT | 8778 | Ovation Control Builder |  | digital
N2DCS.20LCE12AA101_OP | 8779 | Ovation Control Builder |  | digital
N2DCS.20LCE12AA101AUTO | 8780 | 凝结水至低旁减温水调节阀在自动 |  | digital
N2DCS.20LCE12AA101CD | 8781 | 凝结水至低旁减温水调阀快关指令 |  | digital
N2DCS.20LCE12AA101DVHI | 8782 | Ovation Control Builder |  | digital
N2DCS.20LCE12AA101F | 8783 | 凝结水至低旁减温水调节阀故障 |  | digital
N2DCS.20LCE12AA101OD | 8784 | 凝结水至低旁减温水调阀快开指令 |  | digital
N2DCS.20LCE12AA101SPDH | 8785 | Ovation Control Builder |  | digital
N2DCS.20LCE13AA001CD | 8786 | 凝结水至热再减温水电动门关指令 |  | digital
N2DCS.20LCE13AA001CP | 8787 | 凝结水至热再减温水电动门全关位 |  | digital
N2DCS.20LCE13AA001F | 8788 | 凝结水至热再减温水电动门故障 |  | digital
N2DCS.20LCE13AA001OD | 8789 | 凝结水至热再减温水电动门开指令 |  | digital
N2DCS.20LCE13AA001OP | 8790 | 凝结水至热再减温水电动门全开位 |  | digital
N2DCS.20LCE13AA001RC | 8791 | 凝结水至热再减温水电动门在远控 |  | digital
N2DCS.20LCE13AA101AUTO | 8792 | 凝结水至热再减温水调阀在自动 |  | digital
N2DCS.20LCE13AA101DVHI | 8793 | 热再减温水调阀指令反馈偏差大 |  | digital
N2DCS.20LCE13AA101F | 8794 | 凝结水至热再减温水调阀故障 |  | digital
N2DCS.20LCE13AA101RC | 8795 | 凝结水至热再减温水调阀在远控 |  | digital
N2DCS.20LCE13AA101SPDH | 8796 | 热再减温水调阀设定反馈偏差大 |  | digital
N2DCS.20LCE15AA001CD | 8797 | 凝结水至中旁减温水气动门关指令 |  | digital
N2DCS.20LCE15AA001F | 8798 | 凝结水至中旁减温水气动门无电源 |  | digital
N2DCS.20LCE15AA001OD | 8799 | 凝结水至中旁减温水气动门开指令 |  | digital
N2DCS.20LCE15AA001OP | 8800 | 凝结水至中旁减温水气动门全开位 |  | digital
N2DCS.20LCE15AA101_CUT | 8801 | 中压旁路喷水减温阀CUT |  | digital
N2DCS.20LCE15AA101_OP | 8802 | 中压旁路喷水减温阀OP |  | digital
N2DCS.20LCE15AA101AUTO | 8803 | 凝结水至中旁减温水调节阀在自动 |  | digital
N2DCS.20LCE15AA101CD | 8804 | 凝结水至中旁减温水调阀快关指令 |  | digital
N2DCS.20LCE15AA101DVHI | 8805 | Ovation Control Builder |  | digital
N2DCS.20LCE15AA101F | 8806 | 凝结水至中旁减温水调节阀故障 |  | digital
N2DCS.20LCE15AA101OD | 8807 | 凝结水至中旁减温水调阀快开指令 |  | digital
N2DCS.20LCE15AA101SPDH | 8808 | Ovation Control Builder |  | digital
N2DCS.20LCE17AA001CD | 8809 | 凝结水至冷再减温水电动门关指令 |  | digital
N2DCS.20LCE17AA001CP | 8810 | 凝结水至冷再减温水电动门全关位 |  | digital
N2DCS.20LCE17AA001F | 8811 | 凝结水至冷再减温水电动门故障 |  | digital
N2DCS.20LCE17AA001OD | 8812 | 凝结水至冷再减温水电动门开指令 |  | digital
N2DCS.20LCE17AA001OP | 8813 | 凝结水至冷再减温水电动门全开位 |  | digital
N2DCS.20LCE17AA001RC | 8814 | 凝结水至冷再减温水电动门在远控 |  | digital
N2DCS.20LCE17AA101AUTO | 8815 | 凝结水至冷再减温水调阀在自动 |  | digital
N2DCS.20LCE17AA101DVHI | 8816 | 冷再减温水调阀指令反馈偏差大 |  | digital
N2DCS.20LCE17AA101F | 8817 | 凝结水至冷再减温水调阀故障 |  | digital
N2DCS.20LCE17AA101RC | 8818 | 凝结水至冷再减温水调阀在远控 |  | digital
N2DCS.20LCE17AA101SPDH | 8819 | 冷再减温水调阀设定反馈偏差大 |  | digital
N2DCS.20LCE18AA052CD | 8820 | 凝结水至轴封减温水电动门关指令 |  | digital
N2DCS.20LCE18AA052CP | 8821 | 凝结水至轴封减温水电动门全关位 |  | digital
N2DCS.20LCE18AA052F | 8822 | 凝结水至轴封减温水电动门无电源 |  | digital
N2DCS.20LCE18AA052OD | 8823 | 凝结水至轴封减温水电动门开指令 |  | digital
N2DCS.20LCE18AA052OP | 8824 | 凝结水至轴封减温水电动门全开位 |  | digital
N2DCS.20LCE18AA152AUTO | 8825 | 凝结水至轴封减温水调阀在自动 |  | digital
N2DCS.20LCE18AA152DVHI | 8826 | 轴封减温水调阀指令、反馈偏差大 |  | digital
N2DCS.20LCE18AA152SPDH | 8827 | 轴封减温水调阀设定、反馈偏差大 |  | digital
N2DCS.20LCE19AA101AUTO | 8828 | 凝汽器水幕喷水气动阀在自动 |  | digital
N2DCS.20LCE19AA101CP | 8829 | 凝汽器水幕喷水气动阀全关位 |  | digital
N2DCS.20LCE19AA101DVHI | 8830 | 凝汽器水幕喷水阀指令反馈偏差大 |  | digital
N2DCS.20LCE19AA101OD | 8831 | 凝汽器水幕喷水气动阀关/开指令 |  | digital
N2DCS.20LCE19AA101OP | 8832 | 凝汽器水幕喷水气动阀全开位 |  | digital
N2DCS.20LCE19AA101PF | 8833 | 凝汽器水幕喷水气动阀无电源 |  | digital
N2DCS.20LCE19AA101SPDH | 8834 | 凝汽器水幕喷水阀设定反馈偏差大 |  | digital
N2DCS.20LCE20AA101AUTO | 8835 | 疏水扩容器减温水调阀在自动 |  | digital
N2DCS.20LCE20AA101DVHI | 8836 | 疏扩减温水调阀指令反馈偏差大 |  | digital
N2DCS.20LCE20AA101SPDH | 8837 | 疏扩减温水调阀设定反馈偏差大 |  | digital
N2DCS.20LCM40AA403CD | 8838 | #1疏水泵出口真空电动门关闭指令 |  | digital
N2DCS.20LCM40AA403CP | 8839 | #1疏水泵出口真空电动门全关位置 |  | digital
N2DCS.20LCM40AA403F | 8840 | #1疏水泵出口真空电动门故障 |  | digital
N2DCS.20LCM40AA403OD | 8841 | #1疏水泵出口真空电动门打开指令 |  | digital
N2DCS.20LCM40AA403OP | 8842 | #1疏水泵出口真空电动门全开位置 |  | digital
N2DCS.20LCM40AA403RC | 8843 | #1疏水泵出口真空电动门在远控 |  | digital
N2DCS.20LCM40AA406CD | 8844 | #2疏水泵出口真空电动门关闭指令 |  | digital
N2DCS.20LCM40AA406CP | 8845 | #2疏水泵出口真空电动门全关位置 |  | digital
N2DCS.20LCM40AA406F | 8846 | #2疏水泵出口真空电动门故障 |  | digital
N2DCS.20LCM40AA406OD | 8847 | #2疏水泵出口真空电动门打开指令 |  | digital
N2DCS.20LCM40AA406OP | 8848 | #2疏水泵出口真空电动门全开位置 |  | digital
N2DCS.20LCM40AA406RC | 8849 | #2疏水泵出口真空电动门在远控 |  | digital
N2DCS.20LCM40AA407CD | 8850 | 疏扩放水至凝泵坑电动门关指令 |  | digital
N2DCS.20LCM40AA407CP | 8851 | 疏扩放水至凝泵坑电动门全关位 |  | digital
N2DCS.20LCM40AA407F | 8852 | 疏扩放水至凝泵坑电动门故障 |  | digital
N2DCS.20LCM40AA407OD | 8853 | 疏扩放水至凝泵坑电动门开指令 |  | digital
N2DCS.20LCM40AA407OP | 8854 | 疏扩放水至凝泵坑电动门全开位 |  | digital
N2DCS.20LCM40AA407RC | 8855 | 疏扩放水至凝泵坑电动门在远控 |  | digital
N2DCS.20LCM40AP001PF | 8856 | #1疏水泵综合故障 |  | digital
N2DCS.20LCM40AP001RC | 8857 | #1疏水泵已预选且远方控制 |  | digital
N2DCS.20LCM40AP001RD | 8858 | #1/#2疏水泵远方启动指令 |  | digital
N2DCS.20LCM40AP001RP | 8859 | #1疏水泵已停止 |  | digital
N2DCS.20LCM40AP001TD | 8860 | #1/#2疏水泵远方停止指令 |  | digital
N2DCS.20LCM40AP001TP | 8861 | #1疏水泵已停止 |  | digital
N2DCS.20LCM40AP002PF | 8862 | #2疏水泵综合故障 |  | digital
N2DCS.20LCM40AP002RC | 8863 | #2疏水泵已预选且远方控制 |  | digital
N2DCS.20LCM40AP002RD | 8864 | #2疏水泵启动指令 |  | digital
N2DCS.20LCM40AP002RP | 8865 | #2疏水泵已停止 |  | digital
N2DCS.20LCM40AP002TD | 8866 | #2疏水泵停止指令 |  | digital
N2DCS.20LCM40AP002TP | 8867 | #2疏水泵已停止 |  | digital
N2DCS.20MAL22AA051CP | 8868 | 高压缸气动疏水门1全关位置 |  | digital
N2DCS.20MAL22AA051F | 8869 | 高压缸气动疏水门1电源消失 |  | digital
N2DCS.20MAL22AA051OD/CD | 8870 | 高压缸气动疏水门1关闭/打开指令 |  | digital
N2DCS.20MAL22AA051OP | 8871 | 高压缸气动疏水门1全开位置 |  | digital
N2DCS.20MAL22AA053CP | 8872 | 高压缸气动疏水门2全关位置 |  | digital
N2DCS.20MAL22AA053F | 8873 | 高压缸气动疏水门2电源消失 |  | digital
N2DCS.20MAL22AA053OD/CD | 8874 | 高压缸气动疏水门2打开/关闭指令 |  | digital
N2DCS.20MAL22AA053OP | 8875 | 高压缸气动疏水门2全开位置 |  | digital
N2DCS.20MAL22AA054CP | 8876 | 高压缸气动疏水门3全关位置 |  | digital
N2DCS.20MAL22AA054F | 8877 | 高压缸气动疏水门3电源消失 |  | digital
N2DCS.20MAL22AA054OD/CD | 8878 | 高压缸气动疏水门3打开/关闭指令 |  | digital
N2DCS.20MAL22AA054OP | 8879 | 高压缸气动疏水门3全开位置 |  | digital
N2DCS.20MAL35AA051CP | 8880 | 中压缸气动疏水门1全关位置 |  | digital
N2DCS.20MAL35AA051F | 8881 | 中压缸气动疏水门1电源消失 |  | digital
N2DCS.20MAL35AA051OD/CD | 8882 | 中压缸气动疏水门1关闭/打开指令 |  | digital
N2DCS.20MAL35AA051OP | 8883 | 中压缸气动疏水门1全开位置 |  | digital
N2DCS.20MAL36AA051CP | 8884 | 中压缸气动疏水门2全关位置 |  | digital
N2DCS.20MAL36AA051F | 8885 | 中压缸气动疏水门2电源消失 |  | digital
N2DCS.20MAL36AA051OD/CD | 8886 | 中压缸气动疏水门2关闭/打开指令 |  | digital
N2DCS.20MAL36AA051OP | 8887 | 中压缸气动疏水门2全开位置 |  | digital
N2DCS.20MAL50AA051CP | 8888 | 低压缸气动疏水门全关位置 |  | digital
N2DCS.20MAL50AA051F | 8889 | 低压缸气动疏水门电源消失 |  | digital
N2DCS.20MAL50AA051OD/CD | 8890 | 低压缸气动疏水门关闭/打开指令 |  | digital
N2DCS.20MAL50AA051OP | 8891 | 低压缸气动疏水门全开位置 |  | digital
N2DCS.20MAW10AA151AUTO | 8892 | 辅汽至高、中压轴封调阀在自动 |  | digital
N2DCS.20MAW10AA151DVHI | 8893 | 高、中压轴封调阀指令反馈偏差大 |  | digital
N2DCS.20MAW10AA151SPDH | 8894 | 高、中压轴封调阀设定反馈偏差大 |  | digital
N2DCS.20MAW13AA151AUTO | 8895 | 辅汽至低压轴封调阀在自动 |  | digital
N2DCS.20MAW13AA151DVHI | 8896 | 低压轴封调阀指令、反馈偏差大 |  | digital
N2DCS.20MAW13AA151SPDH | 8897 | 低压轴封调阀设定、反馈偏差大 |  | digital
N2DCS.20MAW50AA151AUTO | 8898 | 轴封供汽溢流阀在自动 |  | digital
N2DCS.20MAW50AA151DVHI | 8899 | 轴封供汽溢流阀指令、反馈偏差大 |  | digital
N2DCS.20MAW50AA151SPDH | 8900 | 轴封供汽溢流阀设定、反馈偏差大 |  | digital
N2DCS.20MAW65AA051CP | 8901 | 高压缸轴封漏汽至中压缸门全关位 |  | digital
N2DCS.20MAW65AA051F | 8902 | 高压缸轴封漏汽至中压缸门无电源 |  | digital
N2DCS.20MAW65AA051OD/CD | 8903 | 高压缸轴封至中压缸门开/关指令 |  | digital
N2DCS.20MAW65AA051OP | 8904 | 高压缸轴封漏汽至中压缸门全开位 |  | digital
N2DCS.20MAW65AA052CP | 8905 | 高压缸轴封漏汽至凝汽器门全关位 |  | digital
N2DCS.20MAW65AA052F | 8906 | 高压缸轴封漏汽至凝汽器门无电源 |  | digital
N2DCS.20MAW65AA052OD/CD | 8907 | 高压缸轴封至凝汽器门开/关指令 |  | digital
N2DCS.20MAW65AA052OP | 8908 | 高压缸轴封漏汽至凝汽器门全开位 |  | digital
N2DCS.20MAW80AN001PF | 8909 | #1轴封风机综合故障 |  | digital
N2DCS.20MAW80AN001PS | 8910 | #1轴封风机保护动作 |  | digital
N2DCS.20MAW80AN001RC | 8911 | #1轴封风机远方控制 |  | digital
N2DCS.20MAW80AN001RD | 8912 | #1轴封风机启动指令 |  | digital
N2DCS.20MAW80AN001RP | 8913 | #1轴封风机在运行 |  | digital
N2DCS.20MAW80AN001TD | 8914 | #1轴封风机停止指令 |  | digital
N2DCS.20MAW80AN001TP | 8915 | #1轴封风机已停止 |  | digital
N2DCS.20MAW80AN002PF | 8916 | #2轴封风机综合故障 |  | digital
N2DCS.20MAW80AN002PS | 8917 | #2轴封风机保护动作 |  | digital
N2DCS.20MAW80AN002RC | 8918 | #2轴封风机远方控制 |  | digital
N2DCS.20MAW80AN002RD | 8919 | #2轴封风机启动指令 |  | digital
N2DCS.20MAW80AN002RP | 8920 | #2轴封风机在运行 |  | digital
N2DCS.20MAW80AN002TD | 8921 | #2轴封风机停止指令 |  | digital
N2DCS.20MAW80AN002TP | 8922 | #2轴封风机已停止 |  | digital
N2DCS.20MAW80CL011H | 8923 | 轴封冷却器蒸汽入口液位高 |  | digital
N2DCS.AUXSTM_SEQSTFINISH | 8924 | Ovation Control Builder |  | digital
N2DCS.AUXSTMSYS_SEQSTFINISH | 8925 | 辅汽系统启顺控已成功完成 |  | digital
N2DCS.AUXSTMSYS_SEQSTOK | 8926 | Ovation Control Builder |  | digital
N2DCS.GLDSTMSYS_SEQSPOK | 8927 | 轴封系统停顺控已成功完成 |  | digital
N2DCS.GLDSTMSYS_SEQSTFINISH | 8928 | 轴封系统启顺控已成功完成 |  | digital
N2DCS.GLDSTMSYS_SEQSTOK | 8929 | Ovation Control Builder |  | digital
N2DCS.HGLDHDRPRS_MRE | 8930 | #3机高中压轴封供汽母管压力坏点 |  | digital
N2DCS.HGLDHDRTEM_MRE | 8931 | #3机高中压轴封供汽母管温度坏点 |  | digital
N2DCS.IPBYSPYCVCLS | 8932 | 中旁减温水调阀快关指令 |  | digital
N2DCS.IPBYSPYCVOP | 8933 | 中旁减温水调阀快开指令 |  | digital
N2DCS.J0LBG10CPX2_MRE | 8934 | 辅汽母管压力坏点 |  | digital
N2DCS.J0LBG10CTX2_MRE | 8935 | 辅汽母管温度坏点 |  | digital
N2DCS.LOWGLDSPLPRS_MRE | 8936 | #3机低压轴封供汽母管压力坏点 |  | digital
N2DCS.LOWGLDSPLTEM_MRE | 8937 | #3机低压轴封供汽母管温度坏点 |  | digital
N2DCS.LPBYSPYCVCLS | 8938 | 低旁减温水调阀快关指令 |  | digital
N2DCS.LPBYSPYCVOP | 8939 | 低旁减温水调阀快开指令 |  | digital
N2DCS.ONE2 | 8940 | 开关量1 |  | digital
N2DCS.QDGL00069 | 8941 |  |  | digital
N2DCS.X0LCM40AA403CD | 8942 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AA403CP | 8943 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AA403F | 8944 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AA403OD | 8945 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AA403OP | 8946 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AA403RC | 8947 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AA406CD | 8948 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AA406CP | 8949 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AA406F | 8950 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AA406OD | 8951 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AA406OP | 8952 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AA406RC | 8953 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AA407CD | 8954 | 疏水扩容器疏水至凝结水排污坑电 |  | digital
N2DCS.X0LCM40AA407CP | 8955 | 疏水扩容器疏水至凝结水排污坑电 |  | digital
N2DCS.X0LCM40AA407F | 8956 | 疏水扩容器疏水至凝结水排污坑电 |  | digital
N2DCS.X0LCM40AA407OD | 8957 | 疏水扩容器疏水至凝结水排污坑电 |  | digital
N2DCS.X0LCM40AA407OP | 8958 | 疏水扩容器疏水至凝结水排污坑电 |  | digital
N2DCS.X0LCM40AA407RC | 8959 | 疏水扩容器疏水至凝结水排污坑电 |  | digital
N2DCS.X0LCM40AP001PF | 8960 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AP001RC | 8961 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AP001RD | 8962 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AP001RP | 8963 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AP001TD | 8964 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AP001TP | 8965 | 疏水扩容器疏水至凝汽器疏水泵A? |  | digital
N2DCS.X0LCM40AP002PF | 8966 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AP002RC | 8967 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AP002RD | 8968 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AP002RP | 8969 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AP002TD | 8970 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.X0LCM40AP002TP | 8971 | 疏水扩容器疏水至凝汽器疏水泵B? |  | digital
N2DCS.ZERO2 | 8972 | 开关量0 |  | digital
N2DCS.DCSCOLDMODE1 | 8973 | 汽机冷态启动 |  | digital
N2DCS.DCSEXHOTMODE1 | 8974 | 汽机极热态态启动 |  | digital
N2DCS.DCSHOTMODE1 | 8975 | 汽机热态启动 |  | digital
N2DCS.DCSWARMMODE1 | 8976 | 汽机温态启动 |  | digital
N2DCS.QDGLZFQACKOK | 8977 | 手动确认启动锅炉供辅汽门已全开 |  | digital
N2DCS.QUERENNOCON | 8978 | 手动确认轴封系统不需要暖管 |  | digital
N2DCS.QUERENYESCON | 8979 | 手动确认轴封系统需要暖管 |  | digital
N2DCS.20CNSRPRCTACT1 | 8980 | 凝汽器保护动作通道1 |  | digital
N2DCS.20CNSRPRCTACT2 | 8981 | 凝汽器保护动作通道2 |  | digital
N2DCS.20CNSRPRCTACT3 | 8982 | 凝汽器保护动作通道3 |  | digital
N2DCS.20LCA11AA001CD | 8983 | #1凝结水泵进口电动门关闭指令 |  | digital
N2DCS.20LCA11AA001CP | 8984 | #1凝结水泵进口电动门全关位置 |  | digital
N2DCS.20LCA11AA001F | 8985 | #1凝结水泵进口电动门综合故障 |  | digital
N2DCS.20LCA11AA001OD | 8986 | #1凝结水泵进口电动门打开指令 |  | digital
N2DCS.20LCA11AA001OP | 8987 | #1凝结水泵进口电动门全开位置 |  | digital
N2DCS.20LCA11AA001RC | 8988 | #1凝结水泵进口电动门在远控 |  | digital
N2DCS.20LCA11AA003CD | 8989 | #1凝结水泵出口电动门关闭指令 |  | digital
N2DCS.20LCA11AA003CP | 8990 | #1凝结水泵出口电动门全关位置 |  | digital
N2DCS.20LCA11AA003F | 8991 | #1凝结水泵出口电动门综合故障 |  | digital
N2DCS.20LCA11AA003OD | 8992 | #1凝结水泵出口电动门打开指令 |  | digital
N2DCS.20LCA11AA003OP | 8993 | #1凝结水泵出口电动门全开位置 |  | digital
N2DCS.20LCA11AA003RC | 8994 | #1凝结水泵出口电动门在远控 |  | digital
N2DCS.20LCA30AA101AUTO | 8995 | 凝结水再循环气动调节阀在自动 |  | digital
N2DCS.20LCA30AA101DVHI | 8996 | 凝结水再循环调阀指令反馈偏差大 |  | digital
N2DCS.20LCA30AA101SPDH | 8997 | 凝结水再循环调阀设定反馈偏差大 |  | digital
N2DCS.20LCA40AA002CD | 8998 | 凝结水无压放水电动门关闭指令 |  | digital
N2DCS.20LCA40AA002CP | 8999 | 凝结水无压放水电动门全关位置 |  | digital
N2DCS.20LCA40AA002F | 9000 | 凝结水无压放水电动门综合故障 |  | digital
N2DCS.20LCA40AA002OD | 9001 | 凝结水无压放水电动门打开指令 |  | digital
N2DCS.20LCA40AA002OP | 9002 | 凝结水无压放水电动门全开位置 |  | digital
N2DCS.20LCA40AA002RC | 9003 | 凝结水无压放水电动门在远控 |  | digital
N2DCS.20LCB11AP001PF | 9004 | #1凝结水泵综合故障 |  | digital
N2DCS.20LCB11AP001PS | 9005 | #1凝结水泵电气保护动作 |  | digital
N2DCS.20LCB11AP001RC | 9006 | #1凝结水泵远方控制 |  | digital
N2DCS.20LCB11AP001RD | 9007 | #1凝结水泵启动指令 |  | digital
N2DCS.20LCB11AP001RP | 9008 | #1凝结水泵在运行 |  | digital
N2DCS.20LCB11AP001SW | 9009 | #1凝结水泵试验位置 |  | digital
N2DCS.20LCB11AP001TD | 9010 | #1凝结水泵停止指令 |  | digital
N2DCS.20LCB11AP001TP | 9011 | #1凝结水泵已停止 |  | digital
N2DCS.20LCB11AP001YW | 9012 | #1凝结水泵工作位置 |  | digital
N2DCS.20LCB11GH001AUTO | 9013 | #1凝结水泵永磁控制在自动模式 |  | digital
N2DCS.20LCB11GH001RD1 | 9014 | #1凝泵#1永磁调速水泵启动指令 |  | digital
N2DCS.20LCB11GH001RD2 | 9015 | #1凝泵#2永磁调速水泵启动指令 |  | digital
N2DCS.20LCB11GH001SDVHI | 9016 | #1凝泵永磁控制指令反馈偏差大 |  | digital
N2DCS.20LCB11GH001SPDH | 9017 | #1凝泵永磁控制设定反馈偏差大 |  | digital
N2DCS.20LCB11GH001TD1 | 9018 | #1凝泵#1永磁调速水泵停止指令 |  | digital
N2DCS.20LCB11GH001TD2 | 9019 | #1凝泵#2永磁调速水泵停止指令 |  | digital
N2DCS.20LCE01AA001CD | 9020 | 凝结水杂用水母管电动门关闭指令 |  | digital
N2DCS.20LCE01AA001CP | 9021 | 凝结水杂用水母管电动门全关位 |  | digital
N2DCS.20LCE01AA001F | 9022 | 凝结水杂用水母管电门综合故障 |  | digital
N2DCS.20LCE01AA001OD | 9023 | 凝结水杂用水母管电动门开指令 |  | digital
N2DCS.20LCE01AA001OP | 9024 | 凝结水杂用水母管电动门全开位 |  | digital
N2DCS.20LCE01AA001RC | 9025 | 凝结水杂用水母管电动门在远控 |  | digital
N2DCS.20LCE16AA101AUTO | 9026 | 闭式水箱补水电动调节阀在自动 |  | digital
N2DCS.20LCE16AA101F | 9027 | 闭式水箱补水电动调节阀故障 |  | digital
N2DCS.20LCE16AA101RC | 9028 | 闭式水箱补水电动调节阀在远控 |  | digital
N2DCS.20LCR10AA001CD | 9029 | #2机组除盐水补水电动门关指令 |  | digital
N2DCS.20LCR10AA001CP | 9030 | #2机组除盐水补水电动门全关位 |  | digital
N2DCS.20LCR10AA001F | 9031 | #2机组除盐水补水电门综合故障 |  | digital
N2DCS.20LCR10AA001OD | 9032 | #2机组除盐水补水电动门开指令 |  | digital
N2DCS.20LCR10AA001OP | 9033 | #2机组除盐水补水电动门全开位 |  | digital
N2DCS.20LCR10AA001RC | 9034 | #2机组除盐水补水电动门在远控 |  | digital
N2DCS.20LCR10AA101AUTO | 9035 | 凝汽器正常补水电动调节阀在自动 |  | digital
N2DCS.20LCR10AA101DVHI | 9036 | 凝器正常补水调阀指令反馈偏差大 |  | digital
N2DCS.20LCR10AA101SPDH | 9037 | 凝器正常补水调阀设定反馈偏差大 |  | digital
N2DCS.20LCR10AA102AUTO | 9038 | 凝汽器启动补水电动调节阀在自动 |  | digital
N2DCS.20LCR10AA102DVHI | 9039 | 凝器启动补水调阀指令反馈偏差大 |  | digital
N2DCS.20LCR10AA102SPDH | 9040 | 凝器启动补水调阀设定反馈偏差大 |  | digital
N2DCS.20LCR14AA001CD | 9041 | 闭式水箱启动注水电动门关指令 |  | digital
N2DCS.20LCR14AA001CP | 9042 | 闭式水箱启动注水电动门全关位 |  | digital
N2DCS.20LCR14AA001F | 9043 | 闭式水箱启动注水电动门综合故障 |  | digital
N2DCS.20LCR14AA001OD | 9044 | 闭式水箱启动注水电动门开指令 |  | digital
N2DCS.20LCR14AA001OP | 9045 | 闭式水箱启动注水电动门全开位 |  | digital
N2DCS.20LCR14AA001RC | 9046 | 闭式水箱启动注水电动门在远控 |  | digital
N2DCS.20LDK10AA003CD | 9047 | 除铁过滤器升压气动门关指令 |  | digital
N2DCS.20LDK10AA003CP | 9048 | 除铁过滤器升压气动门全关位 |  | digital
N2DCS.20LDK10AA003OD | 9049 | 除铁过滤器升压气动门开指令 |  | digital
N2DCS.20LDK10AA003OP | 9050 | 除铁过滤器升压气动门全开位 |  | digital
N2DCS.20LDK10AA004CD | 9051 | 除铁过滤器出水电动门关指令 |  | digital
N2DCS.20LDK10AA004CP | 9052 | 除铁过滤器出水电动门全关位 |  | digital
N2DCS.20LDK10AA004F | 9053 | 除铁过滤器出水电动门综合故障 |  | digital
N2DCS.20LDK10AA004OD | 9054 | 除铁过滤器出水电动门开指令 |  | digital
N2DCS.20LDK10AA004OP | 9055 | 除铁过滤器出水电动门全开位 |  | digital
N2DCS.20LDK10AA004RC | 9056 | 除铁过滤器出水电动门在远控 |  | digital
N2DCS.20MAG10CL001H | 9057 | 凝汽器热井液位高高 |  | digital
N2DCS.20MAG10CL002L | 9058 | 凝汽器热井液位低低 |  | digital
N2DCS.20PAB11AA001CD | 9059 | 凝汽器循环水进水#1电动门关指令 |  | digital
N2DCS.20PAB11AA001CP | 9060 | 凝汽器循环水进水#1电动门全关位 |  | digital
N2DCS.20PAB11AA001F | 9061 | 凝汽器循环水进水#1电动门故障 |  | digital
N2DCS.20PAB11AA001OD | 9062 | 凝汽器循环水进水#1电动门开指令 |  | digital
N2DCS.20PAB11AA001OP | 9063 | 凝汽器循环水进水#1电动门全开位 |  | digital
N2DCS.20PAB11AA001RC | 9064 | 凝汽器循环水进水#1电动门在远控 |  | digital
N2DCS.20PAB11AA011CD | 9065 | 凝汽器A侧循环水进水阀关闭指令 |  | digital
N2DCS.20PAB11AA011CP | 9066 | A侧循环水进水电动阀全关位置 |  | digital
N2DCS.20PAB11AA011F | 9067 | A侧循环水进水电动阀综合故障 |  | digital
N2DCS.20PAB11AA011OD | 9068 | 凝汽器A侧循环水进水阀打开指令 |  | digital
N2DCS.20PAB11AA011OP | 9069 | A侧循环水进水电动阀全开位置 |  | digital
N2DCS.20PAB11AA011RC | 9070 | A侧循环水进水电动阀在远控 |  | digital
N2DCS.20PAB21AA001CD | 9071 | 凝汽器循环水#1出水电动门关指令 |  | digital
N2DCS.20PAB21AA001CP | 9072 | 凝汽器循环水#1出水电动门全关位 |  | digital
N2DCS.20PAB21AA001F | 9073 | 凝汽器循环水#1出水电动门故障 |  | digital
N2DCS.20PAB21AA001OD | 9074 | 凝汽器循环水#1出水电动门开指令 |  | digital
N2DCS.20PAB21AA001OP | 9075 | 凝汽器循环水#1出水电动门全开位 |  | digital
N2DCS.20PAB21AA001RC | 9076 | 凝汽器循环水#1出水电动门在远控 |  | digital
N2DCS.20PAH10GH001RC | 9077 | 胶球清洗装置在远控 |  | digital
N2DCS.20PAH11AA002CD | 9078 | #1胶球泵出口电动门关闭指令 |  | digital
N2DCS.20PAH11AA002CP | 9079 | #1胶球泵出口电动门全关位置 |  | digital
N2DCS.20PAH11AA002F | 9080 | #1胶球泵出口电动门综合故障 |  | digital
N2DCS.20PAH11AA002OD | 9081 | #1胶球泵出口电动门打开指令 |  | digital
N2DCS.20PAH11AA002OP | 9082 | #1胶球泵出口电动门全开位置 |  | digital
N2DCS.20PAH11AP001PF | 9083 | #1胶球泵综合故障 |  | digital
N2DCS.20PAH11AP001RD | 9084 | #1胶球泵启动指令 |  | digital
N2DCS.20PAH11AP001RP | 9085 | #1胶球泵在运行 |  | digital
N2DCS.20PAH11AP001TD | 9086 | #1胶球泵停止指令 |  | digital
N2DCS.20PAH11AP001TP | 9087 | #1胶球泵已停止 |  | digital
N2DCS.20PAH11AT001F | 9088 | #1收球网综合故障 |  | digital
N2DCS.20PAH11AT001FX | 9089 | #1收球网反洗指令 |  | digital
N2DCS.20PAH11AT001FXP | 9090 | #1收球网在反洗位置 |  | digital
N2DCS.20PAH11AT001SQ | 9091 | #1收球网收球指令 |  | digital
N2DCS.20PAH11AT001SQP | 9092 | #1收球网在收球位置 |  | digital
N2DCS.20PAH11BB001CD | 9093 | #1装球室关闭指令 |  | digital
N2DCS.20PAH11BB001CP | 9094 | #1装球室全关位置 |  | digital
N2DCS.20PAH11BB001F | 9095 | #1装球室综合故障 |  | digital
N2DCS.20PAH11BB001OD | 9096 | #1装球室打开指令 |  | digital
N2DCS.20PAH11BB001OP | 9097 | #1装球室全开位置 |  | digital
N2DCS.20PCB10AA001CD | 9098 | 开式水电动过滤器进水门关指令 |  | digital
N2DCS.20PCB10AA001CP | 9099 | 开式水电动过滤器进水门全关位置 |  | digital
N2DCS.20PCB10AA001F | 9100 | 开式水电动过滤器进水门综合故障 |  | digital
N2DCS.20PCB10AA001OD | 9101 | 开式水电动过滤器进水门打开指令 |  | digital
N2DCS.20PCB10AA001OP | 9102 | 开式水电动过滤器进水门全开位置 |  | digital
N2DCS.20PCB10AA001RC | 9103 | 开式水电动过滤器进水门在远控 |  | digital
N2DCS.20PCB10AA002CD | 9104 | 开式水电动过滤器出水门关闭指令 |  | digital
N2DCS.20PCB10AA002CP | 9105 | 开式水电动过滤器出水门全关位置 |  | digital
N2DCS.20PCB10AA002F | 9106 | 开式水电动过滤器出水门综合故障 |  | digital
N2DCS.20PCB10AA002OD | 9107 | 开式水电动过滤器出水门打开指令 |  | digital
N2DCS.20PCB10AA002OP | 9108 | 开式水电动过滤器出水门全开位置 |  | digital
N2DCS.20PCB10AA002RC | 9109 | 开式水电动过滤器出水门在远控 |  | digital
N2DCS.20PCB10AA003CD | 9110 | 开式水电动过滤器旁路门关闭指令 |  | digital
N2DCS.20PCB10AA003CP | 9111 | 开式水电动过滤器旁路门全关位置 |  | digital
N2DCS.20PCB10AA003F | 9112 | 开式水电动过滤器旁路门综合故障 |  | digital
N2DCS.20PCB10AA003OD | 9113 | 开式水电动过滤器旁路门打开指令 |  | digital
N2DCS.20PCB10AA003OP | 9114 | 开式水电动过滤器旁路门全开位置 |  | digital
N2DCS.20PCB10AA003RC | 9115 | 开式水电动过滤器旁路门在远控 |  | digital
N2DCS.20PCB10GH501CD | 9116 | 开式水电动过滤器停止反冲洗指令 |  | digital
N2DCS.20PCB10GH501CP | 9117 | 开式水电动过滤器排污门门全关位 |  | digital
N2DCS.20PCB10GH501F | 9118 | 开式水电动过滤器滤水器电机故障 |  | digital
N2DCS.20PCB10GH501OD | 9119 | 开式水电动过滤器启动反冲洗指令 |  | digital
N2DCS.20PCB10GH501OP | 9120 | 开式水电动过滤器排污门门全开位 |  | digital
N2DCS.20PCB10GH501PF | 9121 | 开式水电动过滤器电源消失 |  | digital
N2DCS.20PCB10GH501RC | 9122 | 开式水电动过滤器在远控 |  | digital
N2DCS.20PCB10GH501W | 9123 | 开式水电动过滤器反冲洗进行中 |  | digital
N2DCS.20PCB11AA001CD | 9124 | #1开式水泵进口电动门关闭指令 |  | digital
N2DCS.20PCB11AA001CP | 9125 | #1开式水泵进口电动门全关位 |  | digital
N2DCS.20PCB11AA001F | 9126 | #1开式水泵进口电动门综合故障 |  | digital
N2DCS.20PCB11AA001OD | 9127 | #1开式水泵进口电动门打开指令 |  | digital
N2DCS.20PCB11AA001OP | 9128 | #1开式水泵进口电动门全开位 |  | digital
N2DCS.20PCB11AA001RC | 9129 | #1开式水泵进口电动门在远控 |  | digital
N2DCS.20PCB11AA002CD | 9130 | #1开式水泵出口电动门关闭指令 |  | digital
N2DCS.20PCB11AA002CP | 9131 | #1开式水泵出口电动门全关位 |  | digital
N2DCS.20PCB11AA002F | 9132 | #1开式水泵出口电动门综合故障 |  | digital
N2DCS.20PCB11AA002OD | 9133 | #1开式水泵出口电动门打开指令 |  | digital
N2DCS.20PCB11AA002OP | 9134 | #1开式水泵出口电动门全开位 |  | digital
N2DCS.20PCB11AA002RC | 9135 | #1开式水泵出口电动门在远控 |  | digital
N2DCS.20PCB11AP001PF | 9136 | #1开式水泵综合故障 |  | digital
N2DCS.20PCB11AP001RC | 9137 | #1开式水泵远方控制 |  | digital
N2DCS.20PCB11AP001RD | 9138 | #1开式水泵启动指令 |  | digital
N2DCS.20PCB11AP001RP | 9139 | #1开式水泵在运行 |  | digital
N2DCS.20PCB11AP001TD | 9140 | #1开式水泵停止指令 |  | digital
N2DCS.20PCB11AP001TP | 9141 | #1开式水泵已停止 |  | digital
N2DCS.20PCB13AA011CD | 9142 | #1真空泵冷却器开式进水门关指令 |  | digital
N2DCS.20PCB13AA011CP | 9143 | #1真空泵冷却器开式进水门全关位 |  | digital
N2DCS.20PCB13AA011F | 9144 | #1真空泵冷却器开式进水水门故障 |  | digital
N2DCS.20PCB13AA011OD | 9145 | #1真空泵冷却器开式进水门开指令 |  | digital
N2DCS.20PCB13AA011OP | 9146 | #1真空泵冷却器开式进水门全开位 |  | digital
N2DCS.20PCB13AA011RC | 9147 | #1真空泵冷却器开式进水门在远控 |  | digital
N2DCS.20PCB21AA001CD | 9148 | #1热交换器开式进水电动门关指令 |  | digital
N2DCS.20PCB21AA001CP | 9149 | #1热交换器开式进水电动门全关位 |  | digital
N2DCS.20PCB21AA001F | 9150 | #1热交换器开式进水电动门故障 |  | digital
N2DCS.20PCB21AA001OD | 9151 | #1热交换器开式进水电动门开指令 |  | digital
N2DCS.20PCB21AA001OP | 9152 | #1热交换器开式进水电动门全开位 |  | digital
N2DCS.20PCB21AA001RC | 9153 | #1热交换器开式进水电动门在远控 |  | digital
N2DCS.20PCB23AA011CD | 9154 | #1真空泵冷却器开式出水门关指令 |  | digital
N2DCS.20PCB23AA011CP | 9155 | #1真空泵冷却器开式出水门全关位 |  | digital
N2DCS.20PCB23AA011F | 9156 | #1真空泵冷却器开式出水门故障 |  | digital
N2DCS.20PCB23AA011OD | 9157 | #1真空泵冷却器开式出水门开指令 |  | digital
N2DCS.20PCB23AA011OP | 9158 | #1真空泵冷却器开式出水门全开位 |  | digital
N2DCS.20PCB23AA011RC | 9159 | #1真空泵冷却器开式出水门在远控 |  | digital
N2DCS.20PCB31AA001CD | 9160 | #1热交换器开式出水电动门关指令 |  | digital
N2DCS.20PCB31AA001CP | 9161 | #1热交换器开式出水电动门全关位 |  | digital
N2DCS.20PCB31AA001F | 9162 | #1热交换器开式出水电动门故障 |  | digital
N2DCS.20PCB31AA001OD | 9163 | #1热交换器开式出水电动门开指令 |  | digital
N2DCS.20PCB31AA001OP | 9164 | #1热交换器开式出水电动门全开位 |  | digital
N2DCS.20PCB31AA001RC | 9165 | #1热交换器开式出水电动门在远控 |  | digital
N2DCS.20PGA10CL101SPDH | 9166 | 闭式水箱补水调阀设定反馈偏差大 |  | digital
N2DCS.20PGA11AA001CD | 9167 | #1闭式水泵进口电动门关闭指令 |  | digital
N2DCS.20PGA11AA001CP | 9168 | #1闭式水泵进口电动门全关位置 |  | digital
N2DCS.20PGA11AA001F | 9169 | #1闭式水泵进口电动门综合故障 |  | digital
N2DCS.20PGA11AA001OD | 9170 | #1闭式水泵进口电动门打开指令 |  | digital
N2DCS.20PGA11AA001OP | 9171 | #1闭式水泵进口电动门全开位置 |  | digital
N2DCS.20PGA11AA001RC | 9172 | #1闭式水泵进口电动门在远控 |  | digital
N2DCS.20PGA11AA003CD | 9173 | #1闭式水泵出口电动门关闭指令 |  | digital
N2DCS.20PGA11AA003CP | 9174 | #1闭式水泵出口电动门全关位置 |  | digital
N2DCS.20PGA11AA003F | 9175 | #1闭式水泵出口电动门综合故障 |  | digital
N2DCS.20PGA11AA003OD | 9176 | #1闭式水泵出口电动门打开指令 |  | digital
N2DCS.20PGA11AA003OP | 9177 | #1闭式水泵出口电动门全开位置 |  | digital
N2DCS.20PGA11AA003RC | 9178 | #1闭式水泵出口电动门在远控 |  | digital
N2DCS.20PGA11AP001PF | 9179 | #1闭式水泵综合故障 |  | digital
N2DCS.20PGA11AP001PS | 9180 | #1闭式水泵电气保护动作 |  | digital
N2DCS.20PGA11AP001RC | 9181 | #1闭式水泵远方控制 |  | digital
N2DCS.20PGA11AP001RD | 9182 | #1闭式水泵启动指令 |  | digital
N2DCS.20PGA11AP001RP | 9183 | #1闭式水泵在运行 |  | digital
N2DCS.20PGA11AP001SW | 9184 | #1闭式水泵试验位置 |  | digital
N2DCS.20PGA11AP001TD | 9185 | #1闭式水泵停止指令 |  | digital
N2DCS.20PGA11AP001TP | 9186 | #1闭式水泵已停止 |  | digital
N2DCS.20PGA11AP001YW | 9187 | #1闭式水泵工作位置 |  | digital
N2DCS.20PGA21AA001CD | 9188 | #1热交换器闭式进水电动门关指令 |  | digital
N2DCS.20PGA21AA001CP | 9189 | #1热交换器闭式进水电动门全关位 |  | digital
N2DCS.20PGA21AA001F | 9190 | #1热交换器闭式进水电动门故障 |  | digital
N2DCS.20PGA21AA001OD | 9191 | #1热交换器闭式进水电动门开指令 |  | digital
N2DCS.20PGA21AA001OP | 9192 | #1热交换器闭式进水电动门全开位 |  | digital
N2DCS.20PGA21AA001RC | 9193 | #1热交换器闭式进水电动门在远控 |  | digital
N2DCS.20PGA21AA002CD | 9194 | #1热交换器闭式出水电动门关指令 |  | digital
N2DCS.20PGA21AA002CP | 9195 | #1热交换器闭式出水电动门全关位 |  | digital
N2DCS.20PGA21AA002F | 9196 | #1热交换器闭式出水电动门故障 |  | digital
N2DCS.20PGA21AA002OD | 9197 | #1热交换器闭式出水电动门开指令 |  | digital
N2DCS.20PGA21AA002OP | 9198 | #1热交换器闭式出水电动门全开位 |  | digital
N2DCS.20PGA21AA002RC | 9199 | #1热交换器闭式出水电动门在远控 |  | digital
N2DCS.CLCLGPMPA_PMT | 9200 | 闭冷水泵A启动允许 |  | digital
N2DCS.CLCLGPMPA_PMT1 | 9201 | #1闭式水泵启动允许 |  | digital
N2DCS.CLCLGPMPA_SEQSTOK | 9202 | #1闭式水泵启顺控已成功完成 |  | digital
N2DCS.CLCLGPMPA_STPMT | 9203 | #1闭式水泵启动允许 |  | digital
N2DCS.CLCLGPMPA_TEMALM | 9204 | #1闭式水泵超温保护报警 |  | digital
N2DCS.CLCLGPMPA_TEMALMCUT | 9205 | #1闭式水泵超温保护功能解除 |  | digital
N2DCS.CLCLGPMPA_TP | 9206 | #1闭式水泵跳闸信号 |  | digital
N2DCS.CLCLGPMPAMANSTOP | 9207 | #1闭式水泵手动停止指令 |  | digital
N2DCS.CLCLGPMPARUN | 9208 | 闭冷泵A运行 |  | digital
N2DCS.CLCLGPMPASTOP | 9209 | #1闭式水泵已停止 |  | digital
N2DCS.CLCLGPMPATEMPMT | 9210 | #1闭式水泵温度允许 |  | digital
N2DCS.CLCLGPMPBRUN | 9211 | 闭冷泵B运行 |  | digital
N2DCS.CLCLGPMPBSTOP | 9212 | #2闭式水泵已停止 |  | digital
N2DCS.CLCLGWTR_FILLACK | 9213 | 闭式冷却水系统注水确认 |  | digital
N2DCS.CLCLGWTR_SEQSTFINISH | 9214 | 闭式冷却水系统启顺控已成功完成 |  | digital
N2DCS.CLCLGWTRTENCY | 9215 | 热交换器闭式水管路畅通 |  | digital
N2DCS.CLGCHANLGOOD | 9216 | 热交换器开式水管路畅通 |  | digital
N2DCS.CNDHWLVL_MRE | 9217 | 凝汽器热井液位坏点 |  | digital
N2DCS.CNDPA_SEQSTOK | 9218 | #1凝结水泵启顺控已成功完成 |  | digital
N2DCS.CNDPARUN | 9219 | 凝结水泵A运行 |  | digital
N2DCS.CNDPMPA_PMT1 | 9220 | #1凝结水泵启动允许 |  | digital
N2DCS.CNDPMPA_STPMT | 9221 | #1凝结水泵启动允许 |  | digital
N2DCS.CNDPMPA_TEMALM | 9222 | #1凝结水泵超温保护报警 |  | digital
N2DCS.CNDPMPA_TEMALMCUT | 9223 | #1凝结水泵超温保护报警功能解除 |  | digital
N2DCS.CNDPMPA_TEMTRIP | 9224 | 凝结水泵A温度保护 |  | digital
N2DCS.CNDPMPA_TP | 9225 | #1凝结水泵跳闸信号 |  | digital
N2DCS.CNDPMPAMANSTOP | 9226 | #1凝结水泵手动停止指令 |  | digital
N2DCS.CNDPMPARUN | 9227 | #1凝结水泵在运行 |  | digital
N2DCS.CNDPMPARUN1 | 9228 | #1凝结水泵工频运行 |  | digital
N2DCS.CNDPMPARUN2 | 9229 | #1凝结水泵变频运行 |  | digital
N2DCS.CNDPMPASTOP | 9230 | #1凝结水泵已停止 |  | digital
N2DCS.CNDPMPATEMPMT | 9231 | #1凝结水泵温度允许 |  | digital
N2DCS.CNDWTRSYS_SEQSTFINISH | 9232 | 凝结水系统启顺控已成功完成 |  | digital
N2DCS.CNSRHOTWLVL_MRE | 9233 | 凝汽器热井液位坏质量 |  | digital
N2DCS.CNSRLVL_MRE | 9234 | 凝汽器热井液位坏点 |  | digital
N2DCS.J0PGA41AA011OP | 9235 |  |  | digital
N2DCS.J0PGA41AA012OP | 9236 |  |  | digital
N2DCS.J0PGA41AA021OP | 9237 |  |  | digital
N2DCS.J0PGA41AA022OP | 9238 |  |  | digital
N2DCS.L0LCE50AA101DVHI | 9239 | 闭式水箱补水调阀指令反馈偏差大 |  | digital
N2DCS.ONE3 | 9240 | 开关量1 |  | digital
N2DCS.OPNCIRPMPA_PMT | 9241 | #1开式水泵启动允许 |  | digital
N2DCS.OPNCIRPMPA_PMT1 | 9242 | #1开式水泵启动允许 |  | digital
N2DCS.OPNCIRPMPA_SEQSTOK | 9243 | #1开式水泵启顺控已成功完成 |  | digital
N2DCS.OPNCIRPMPA_TEMALM | 9244 | #1开式水泵温度保护 |  | digital
N2DCS.OPNCIRPMPA_TEMALMCUT | 9245 | #1开式水泵温度保护功能解除 |  | digital
N2DCS.OPNCIRPMPA_TP | 9246 | #1开式水泵跳闸信号 |  | digital
N2DCS.OPNCIRPMPAMANSTOP | 9247 | #1开式水泵手动停止指令 |  | digital
N2DCS.OPNCIRPMPATEMPMT | 9248 | #1开式水泵温度允许 |  | digital
N2DCS.OPNCIRWTR_SEQSTFINISH | 9249 | 开式水系统启顺控已成功完成 |  | digital
N2DCS.OPNWTRTENCY | 9250 | 热交换器开式水管路畅通 |  | digital
N2DCS.SELCLWTRCLRA | 9251 | 预选闭式水系统#1热交换器 |  | digital
N2DCS.SELCLWTRCLRB | 9252 | 预选闭式水系统#2热交换器 |  | digital
N2DCS.SELCNSRCIRWTRCHANL_A | 9253 | 凝汽器循环水通道选择A侧 |  | digital
N2DCS.SELCNSRCIRWTRCHANL_B | 9254 | 凝汽器循环水通道选择B侧 |  | digital
N2DCS.SELOPNCIRWTRCHANL_A | 9255 | 预选开式水电动过滤器通道 |  | digital
N2DCS.SELOPNCIRWTRCHANL_B | 9256 | 预选开式水电动过滤器旁路通道 |  | digital
N2DCS.SELOPNWTRCLRA | 9257 | 预选开式水系统#1热交换器 |  | digital
N2DCS.SELOPNWTRCLRB | 9258 | 预选开式水系统#2热交换器 |  | digital
N2DCS.SELVACMCLGSYSA | 9259 | 预选#1真空泵冷却器 |  | digital
N2DCS.SELVACMCLGSYSB | 9260 | 预选#2真空泵冷却器 |  | digital
N2DCS.STARTPULLWATERCOF | 9261 | Ovation Control Builder |  | digital
N2DCS.ZERO3 | 9262 | 开关量0 |  | digital
N2DCS.20LCB11AP001SWNOT | 9263 | Ovation Control Builder |  | digital
N2DCS.20LCB11AP001YWAND | 9264 | Ovation Control Builder |  | digital
N2DCS.CESHI2 | 9265 | Ovation Control Builder |  | digital
N2DCS.CLCLGWTRSTRESET | 9266 | 闭式水系统启顺控复位指令 |  | digital
N2DCS.CNSRPRTCT | 9267 | 凝汽器保护动作 |  | digital
N2DCS.CPRESSAIRCWOK | 9268 | Ovation Control Builder |  | digital
N2DCS.TALM001 | 9269 | 高压缸排汽口温度高(大于384℃） |  | digital
N2DCS.TALM002 | 9270 | 凝汽器真空低(大于-81KPa） |  | digital
N2DCS.TALM003 | 9271 | 凝汽器热井液位低(小于600mm） |  | digital
N2DCS.TALM004 | 9272 | #3机真空泵异常跳闸 |  | digital
N2DCS.TALM005 | 9273 | #3机真空泵超温报警 |  | digital
N2DCS.TALM006 | 9274 | 辅汽母管温度低(小于260℃） |  | digital
N2DCS.TALM006A | 9275 | 辅汽母管温度低(小于260℃） |  | digital
N2DCS.TALM007 | 9276 | #3机闭式水箱液位低(小于500℃） |  | digital
N2DCS.TALM008 | 9277 | #3机闭式冷却水泵异常跳闸 |  | digital
N2DCS.TALM009 | 9278 | #3机闭式冷却水泵超温报警 |  | digital
N2DCS.TALM010 | 9279 | #3机开式冷却水泵异常跳闸 |  | digital
N2DCS.TALM011 | 9280 | #3机开式冷却水泵超温报警 |  | digital
N2DCS.TALM012 | 9281 | #3机凝结水泵异常跳闸 |  | digital
N2DCS.TALM013 | 9282 | #3机凝结水泵超温报警 |  | digital
N2DCS.TALM014 | 9283 | #3机轴封风机异常跳闸 |  | digital
N2DCS.TALM015 | 9284 | #3机循环水泵异常跳闸 |  | digital
N2DCS.TALM016 | 9285 | #3机循环水泵超温报警 |  | digital
N2DCS.TALM017 | 9286 | 循环水前池液位低 |  | digital
N2DCS.TALM018 | 9287 | #3循环水泵冷却水加压泵跳闸 |  | digital
N2DCS.TALM019 | 9288 | #4循环水泵冷却水加压泵跳闸 |  | digital
N2DCS.TALM020 | 9289 | #3机润滑油箱液位高(大于1050mm |  | digital
N2DCS.TALM021 | 9290 | #3机润滑油箱液位低(小于850mm） |  | digital
N2DCS.TALM022 | 9291 | #3机润滑油泵异常跳闸 |  | digital
N2DCS.TALM023 | 9292 | #3机润滑油滤网压差高 |  | digital
N2DCS.TALM024 | 9293 | #3机润滑油供油母管压力低 |  | digital
N2DCS.TALM025 | 9294 | #3机应急润滑油泵异常跳闸 |  | digital
N2DCS.TALM026 | 9295 | #3机顶轴油泵异常跳闸 |  | digital
N2DCS.TALM027 | 9296 | #3机EH油泵异常跳闸 |  | digital
N2DCS.TALM028 | 9297 | #3机轴承振动大(大于83um） |  | digital
N2DCS.TALM029 | 9298 | #3机轴承座振动大(大于9.3mm/s） |  | digital
N2DCS.TALM030 | 9299 | #3机轴向位移大(大于0.5mm） |  | digital
N2DCS.TALM031 | 9300 | #3机高压缸压比低(小于1.5） |  | digital
N2DCS.TALM032 | 9301 | #3机转速高(大于3090rpm） |  | digital
N2DCS.TALMALL | 9302 | #3机机炉光字牌报警总信号 |  | digital
N2DCS.TALMUNACK | 9303 | #3机机炉光字牌报警手动确认指令 |  | digital
N2DCS.THREEPICKTWO | 9304 | #3机轴承超温 |  | digital
N2DCS.20LCA12AA001CD | 9305 | #2凝结水泵进口电动门关闭指令 |  | digital
N2DCS.20LCA12AA001CP | 9306 | #2凝结水泵进口电动门全关位置 |  | digital
N2DCS.20LCA12AA001F | 9307 | #2凝结水泵进口电动门综合故障 |  | digital
N2DCS.20LCA12AA001OD | 9308 | #2凝结水泵进口电动门打开指令 |  | digital
N2DCS.20LCA12AA001OP | 9309 | #2凝结水泵进口电动门全开位置 |  | digital
N2DCS.20LCA12AA001RC | 9310 | #2凝结水泵进口电动门在远控 |  | digital
N2DCS.20LCA12AA003CD | 9311 | #2凝结水泵出口电动门关闭指令 |  | digital
N2DCS.20LCA12AA003CP | 9312 | #2凝结水泵出口电动门全关位置 |  | digital
N2DCS.20LCA12AA003F | 9313 | #2凝结水泵出口电动门综合故障 |  | digital
N2DCS.20LCA12AA003OD | 9314 | #2凝结水泵出口电动门打开指令 |  | digital
N2DCS.20LCA12AA003OP | 9315 | #2凝结水泵出口电动门全开位置 |  | digital
N2DCS.20LCA12AA003RC | 9316 | #2凝结水泵出口电动门在远控 |  | digital
N2DCS.20LCB12AP001SW | 9317 | #2凝结水泵试验位置 |  | digital
N2DCS.20LCB12AP001YW | 9318 | #2凝结水泵工作位置 |  | digital
N2DCS.20LCB12AP002PF | 9319 | #2凝结水泵综合故障 |  | digital
N2DCS.20LCB12AP002PS | 9320 | #2凝结水泵电气保护动作 |  | digital
N2DCS.20LCB12AP002RC | 9321 | #2凝结水泵远方控制 |  | digital
N2DCS.20LCB12AP002RD | 9322 | #2凝结水泵启动指令 |  | digital
N2DCS.20LCB12AP002RP | 9323 | #2凝结水泵在运行 |  | digital
N2DCS.20LCB12AP002TD | 9324 | #2凝结水泵停止指令 |  | digital
N2DCS.20LCB12AP002TP | 9325 | #2凝结水泵已停止 |  | digital
N2DCS.20LCB12GH001F1 | 9326 | #2凝泵#1永磁调速水泵故障 |  | digital
N2DCS.20LCB12GH001F2 | 9327 | #2凝泵#2永磁调速水泵故障 |  | digital
N2DCS.20LCB12GH001RD1 | 9328 | #2凝泵#1永磁调速水泵启动指令 |  | digital
N2DCS.20LCB12GH001RD2 | 9329 | #2凝泵#2永磁调速水泵启动指令 |  | digital
N2DCS.20LCB12GH001RP1 | 9330 | #2凝泵#1永磁调速水泵在运行 |  | digital
N2DCS.20LCB12GH001RP2 | 9331 | #2凝泵#2永磁调速水泵在运行 |  | digital
N2DCS.20LCB12GH001TD1 | 9332 | #2凝泵#1永磁调速水泵停止指令 |  | digital
N2DCS.20LCB12GH001TD2 | 9333 | #2凝泵#2永磁调速水泵停止指令 |  | digital
N2DCS.20LCB12GH001TP1 | 9334 | #2凝结水泵#1永磁调速水泵已停止 |  | digital
N2DCS.20LCB12GH001TP2 | 9335 | #2凝结水泵#2永磁调速水泵已停止 |  | digital
N2DCS.20LDB10AA501CD | 9336 | 除铁过滤器#1排气气动门关指令 |  | digital
N2DCS.20LDB10AA501CP | 9337 | 除铁过滤器#1排气气动门全关位 |  | digital
N2DCS.20LDB10AA501OD | 9338 | 除铁过滤器#1排气气动门开指令 |  | digital
N2DCS.20LDB10AA501OP | 9339 | 除铁过滤器#1排气气动门全开位 |  | digital
N2DCS.20LDB10AA502CD | 9340 | 除铁过滤器#2排气气动门关指令 |  | digital
N2DCS.20LDB10AA502CP | 9341 | 除铁过滤器#2排气气动门全关位 |  | digital
N2DCS.20LDB10AA502OD | 9342 | 除铁过滤器#2排气气动门开指令 |  | digital
N2DCS.20LDB10AA502OP | 9343 | 除铁过滤器#2排气气动门全开位 |  | digital
N2DCS.20LDB10GA001RC | 9344 | 1号机组除铁过滤器电磁阀箱在远? |  | digital
N2DCS.20LDK10AA002CD | 9345 | 除铁过滤器进口电动门关指令 |  | digital
N2DCS.20LDK10AA002CP | 9346 | 除铁过滤器进口电动门全关位 |  | digital
N2DCS.20LDK10AA002F | 9347 | 除铁过滤器进口电动门故障 |  | digital
N2DCS.20LDK10AA002OD | 9348 | 除铁过滤器进口电动门开指令 |  | digital
N2DCS.20LDK10AA002OP | 9349 | 除铁过滤器进口电动门全开位 |  | digital
N2DCS.20LDK10AA002RC | 9350 | 除铁过滤器进口电动门在远控 |  | digital
N2DCS.20LDK20AA002CD | 9351 | 除铁过滤器旁路电动门关指令 |  | digital
N2DCS.20LDK20AA002CP | 9352 | 除铁过滤器旁路电动门全关位 |  | digital
N2DCS.20LDK20AA002F | 9353 | 除铁过滤器旁路电动门故障 |  | digital
N2DCS.20LDK20AA002OD | 9354 | 除铁过滤器旁路电动门开指令 |  | digital
N2DCS.20LDK20AA002OP | 9355 | 除铁过滤器旁路电动门全开位 |  | digital
N2DCS.20LDK20AA002RC | 9356 | 除铁过滤器旁路电动门在远控 |  | digital
N2DCS.20PAB12AA001CD | 9357 | 凝汽器循环水进水#2电动门关指令 |  | digital
N2DCS.20PAB12AA001CP | 9358 | 凝汽器循环水进水#2电动门全关位 |  | digital
N2DCS.20PAB12AA001F | 9359 | 凝汽器循环水进水#2电动门故障 |  | digital
N2DCS.20PAB12AA001OD | 9360 | 凝汽器循环水进水#2电动门开指令 |  | digital
N2DCS.20PAB12AA001OP | 9361 | 凝汽器循环水进水#2电动门全开位 |  | digital
N2DCS.20PAB12AA001RC | 9362 | 凝汽器循环水进水#2电动门在远控 |  | digital
N2DCS.20PAB12AA011CD | 9363 | 凝汽器B侧循环水进水阀关闭指令 |  | digital
N2DCS.20PAB12AA011CP | 9364 | 凝汽器B侧循环水进水阀全关位置 |  | digital
N2DCS.20PAB12AA011F | 9365 | 凝汽器B侧循环水进水阀综合故障 |  | digital
N2DCS.20PAB12AA011OD | 9366 | 凝汽器B侧循环水进水阀打开指令 |  | digital
N2DCS.20PAB12AA011OP | 9367 | 凝汽器B侧循环水进水阀全开位置 |  | digital
N2DCS.20PAB12AA011RC | 9368 | 凝汽器B侧循环水进水阀在远控 |  | digital
N2DCS.20PAB22AA001CD | 9369 | 凝汽器循环水#2出水电动门关指令 |  | digital
N2DCS.20PAB22AA001CP | 9370 | 凝汽器循环水#2出水电动门全关位 |  | digital
N2DCS.20PAB22AA001F | 9371 | 凝汽器循环水#2出水电动门故障 |  | digital
N2DCS.20PAB22AA001OD | 9372 | 凝汽器循环水#2出水电动门开指令 |  | digital
N2DCS.20PAB22AA001OP | 9373 | 凝汽器循环水#2出水电动门全开位 |  | digital
N2DCS.20PAB22AA001RC | 9374 | 凝汽器循环水#2出水电动门在远控 |  | digital
N2DCS.20PAH12AA002CD | 9375 | #2胶球泵出口电动门关闭指令 |  | digital
N2DCS.20PAH12AA002CP | 9376 | #2胶球泵出口电动门全关位置 |  | digital
N2DCS.20PAH12AA002F | 9377 | #2胶球泵出口电动门综合故障 |  | digital
N2DCS.20PAH12AA002OD | 9378 | #2胶球泵出口电动门打开指令 |  | digital
N2DCS.20PAH12AA002OP | 9379 | #2胶球泵出口电动门全开位置 |  | digital
N2DCS.20PAH12AP001PF | 9380 | #2胶球泵综合故障 |  | digital
N2DCS.20PAH12AP001RD | 9381 | #2胶球泵启动指令 |  | digital
N2DCS.20PAH12AP001RP | 9382 | #2胶球泵在运行 |  | digital
N2DCS.20PAH12AP001TD | 9383 | #2胶球泵停止指令 |  | digital
N2DCS.20PAH12AP001TP | 9384 | #2胶球泵已停止 |  | digital
N2DCS.20PAH12AT001F | 9385 | #2收球网综合故障 |  | digital
N2DCS.20PAH12AT001FX | 9386 | #2收球网反洗指令 |  | digital
N2DCS.20PAH12AT001FXP | 9387 | #2收球网在反洗位置 |  | digital
N2DCS.20PAH12AT001SQ | 9388 | #2收球网收球指令 |  | digital
N2DCS.20PAH12AT001SQP | 9389 | #2收球网在收球位置 |  | digital
N2DCS.20PAH12BB001CD | 9390 | #2装球室关闭指令 |  | digital
N2DCS.20PAH12BB001CP | 9391 | #2装球室全关位置 |  | digital
N2DCS.20PAH12BB001F | 9392 | #2装球室综合故障 |  | digital
N2DCS.20PAH12BB001OD | 9393 | #2装球室打开指令 |  | digital
N2DCS.20PAH12BB001OP | 9394 | #2装球室全开位置 |  | digital
N2DCS.20PCB11AA003CD | 9395 | #2开式水泵进口电动门关闭指令 |  | digital
N2DCS.20PCB11AA003CP | 9396 | #2开式水泵进口电动门全关位 |  | digital
N2DCS.20PCB11AA003F | 9397 | #2开式水泵进口电动门综合故障 |  | digital
N2DCS.20PCB11AA003OD | 9398 | #2开式水泵进口电动门打开指令 |  | digital
N2DCS.20PCB11AA003OP | 9399 | #2开式水泵进口电动门全开位 |  | digital
N2DCS.20PCB11AA003RC | 9400 | #2开式水泵进口电动门在远控 |  | digital
N2DCS.20PCB11AA004CD | 9401 | #2开式水泵出口电动门关闭指令 |  | digital
N2DCS.20PCB11AA004CP | 9402 | #2开式水泵出口电动门全关位 |  | digital
N2DCS.20PCB11AA004F | 9403 | #2开式水泵出口电动门综合故障 |  | digital
N2DCS.20PCB11AA004OD | 9404 | #2开式水泵出口电动门打开指令 |  | digital
N2DCS.20PCB11AA004OP | 9405 | #2开式水泵出口电动门全开位 |  | digital
N2DCS.20PCB11AA004RC | 9406 | #2开式水泵出口电动门在远控 |  | digital
N2DCS.20PCB11AP002PF | 9407 | #2开式水泵综合故障 |  | digital
N2DCS.20PCB11AP002RC | 9408 | #2开式水泵远方控制 |  | digital
N2DCS.20PCB11AP002RD | 9409 | #2开式水泵启动指令 |  | digital
N2DCS.20PCB11AP002RP | 9410 | #2开式水泵在运行 |  | digital
N2DCS.20PCB11AP002TD | 9411 | #2开式水泵停止指令 |  | digital
N2DCS.20PCB11AP002TP | 9412 | #2开式水泵已停止 |  | digital
N2DCS.20PCB13AA012CD | 9413 | #2真空泵冷却器开式进水门关指令 |  | digital
N2DCS.20PCB13AA012CP | 9414 | #2真空泵冷却器开式进水门全关位 |  | digital
N2DCS.20PCB13AA012F | 9415 | #2真空泵冷却器开式进水水门故障 |  | digital
N2DCS.20PCB13AA012OD | 9416 | #2真空泵冷却器开式进水门开指令 |  | digital
N2DCS.20PCB13AA012OP | 9417 | #2真空泵冷却器开式进水门全开位 |  | digital
N2DCS.20PCB13AA012RC | 9418 | #2真空泵冷却器开式进水门在远控 |  | digital
N2DCS.20PCB22AA001CD | 9419 | #2热交换器开式进水电动门关指令 |  | digital
N2DCS.20PCB22AA001CP | 9420 | #2热交换器开式进水电动门全关位 |  | digital
N2DCS.20PCB22AA001F | 9421 | #2热交换器开式进水电动门故障 |  | digital
N2DCS.20PCB22AA001OD | 9422 | #2热交换器开式进水电动门开指令 |  | digital
N2DCS.20PCB22AA001OP | 9423 | #2热交换器开式进水电动门全开位 |  | digital
N2DCS.20PCB22AA001RC | 9424 | #2热交换器开式进水电动门在远控 |  | digital
N2DCS.20PCB23AA012CD | 9425 | #2真空泵冷却器开式出水门关指令 |  | digital
N2DCS.20PCB23AA012CP | 9426 | #2真空泵冷却器开式出水门全关位 |  | digital
N2DCS.20PCB23AA012F | 9427 | #2真空泵冷却器开式出水门故障 |  | digital
N2DCS.20PCB23AA012OD | 9428 | #2真空泵冷却器开式出水门开指令 |  | digital
N2DCS.20PCB23AA012OP | 9429 | #2真空泵冷却器开式出水门全开位 |  | digital
N2DCS.20PCB23AA012RC | 9430 | #2真空泵冷却器开式出水门在远控 |  | digital
N2DCS.20PCB32AA001CD | 9431 | #2热交换器开式出水电动门关指令 |  | digital
N2DCS.20PCB32AA001CP | 9432 | #2热交换器开式出水电动门全关位 |  | digital
N2DCS.20PCB32AA001F | 9433 | #2热交换器开式出水电动门故障 |  | digital
N2DCS.20PCB32AA001OD | 9434 | #2热交换器开式出水电动门开指令 |  | digital
N2DCS.20PCB32AA001OP | 9435 | #2热交换器开式出水电动门全开位 |  | digital
N2DCS.20PCB32AA001RC | 9436 | #2热交换器开式出水电动门在远控 |  | digital
N2DCS.20PGA12AA001CD | 9437 | #2闭式水泵进口电动门关闭指令 |  | digital
N2DCS.20PGA12AA001CP | 9438 | #2闭式水泵进口电动门全关位置 |  | digital
N2DCS.20PGA12AA001F | 9439 | #2闭式水泵进口电动门综合故障 |  | digital
N2DCS.20PGA12AA001OD | 9440 | #2闭式水泵进口电动门打开指令 |  | digital
N2DCS.20PGA12AA001OP | 9441 | #2闭式水泵进口电动门全开位置 |  | digital
N2DCS.20PGA12AA001RC | 9442 | #2闭式水泵进口电动门在远控 |  | digital
N2DCS.20PGA12AA003CD | 9443 | #2闭式水泵出口电动门关闭指令 |  | digital
N2DCS.20PGA12AA003CP | 9444 | #2闭式水泵出口电动门全关位置 |  | digital
N2DCS.20PGA12AA003F | 9445 | #2闭式水泵出口电动门综合故障 |  | digital
N2DCS.20PGA12AA003OD | 9446 | #2闭式水泵出口电动门打开指令 |  | digital
N2DCS.20PGA12AA003OP | 9447 | #2闭式水泵出口电动门全开位置 |  | digital
N2DCS.20PGA12AA003RC | 9448 | #2闭式水泵出口电动门在远控 |  | digital
N2DCS.20PGA12AP001PF | 9449 | #2闭式水泵综合故障 |  | digital
N2DCS.20PGA12AP001PS | 9450 | #2闭式水泵电气保护动作 |  | digital
N2DCS.20PGA12AP001RC | 9451 | #2闭式水泵远方控制 |  | digital
N2DCS.20PGA12AP001RD | 9452 | #2闭式水泵启动指令 |  | digital
N2DCS.20PGA12AP001RP | 9453 | #2闭式水泵在运行 |  | digital
N2DCS.20PGA12AP001SW | 9454 | #2闭式水泵试验位置 |  | digital
N2DCS.20PGA12AP001TD | 9455 | #2闭式水泵停止指令 |  | digital
N2DCS.20PGA12AP001TP | 9456 | #2闭式水泵已停止 |  | digital
N2DCS.20PGA12AP001YW | 9457 | #2闭式水泵工作位置 |  | digital
N2DCS.20PGA22AA001CD | 9458 | #2热交换器闭式进水电动门关指令 |  | digital
N2DCS.20PGA22AA001CP | 9459 | #2热交换器闭式进水电动门全关位 |  | digital
N2DCS.20PGA22AA001F | 9460 | #2热交换器闭式进水电动门故障 |  | digital
N2DCS.20PGA22AA001OD | 9461 | #2热交换器闭式进水电动门开指令 |  | digital
N2DCS.20PGA22AA001OP | 9462 | #2热交换器闭式进水电动门全开位 |  | digital
N2DCS.20PGA22AA001RC | 9463 | #2热交换器闭式进水电动门在远控 |  | digital
N2DCS.20PGA22AA002CD | 9464 | #2热交换器闭式出水电动门关指令 |  | digital
N2DCS.20PGA22AA002CP | 9465 | #2热交换器闭式出水电动门全关位 |  | digital
N2DCS.20PGA22AA002F | 9466 | #2热交换器闭式出水电动门故障 |  | digital
N2DCS.20PGA22AA002OD | 9467 | #2热交换器闭式出水电动门开指令 |  | digital
N2DCS.20PGA22AA002OP | 9468 | #2热交换器闭式出水电动门全开位 |  | digital
N2DCS.20PGA22AA002RC | 9469 | #2热交换器闭式出水电动门在远控 |  | digital
N2DCS.20PGA26AA101AUTO | 9470 | #4发电机定冷水进水调节阀在自动 |  | digital
N2DCS.20PGA26AA101DVHI | 9471 | #4发电机定冷调阀指令反馈偏差大 |  | digital
N2DCS.20PGA26AA101F | 9472 | #4发电机定冷水进水调节阀故障 |  | digital
N2DCS.20PGA26AA101RC | 9473 | #4发电机定冷水进水调节阀在远控 |  | digital
N2DCS.20PGA26AA101SPDH | 9474 | #4发电机定冷调阀设定反馈偏差大 |  | digital
N2DCS.20PGA26AA102AUTO | 9475 | #4发电机氢冷器进水调节阀在自动 |  | digital
N2DCS.20PGA26AA102DVHI | 9476 | #4发电机氢冷调阀指令反馈偏差大 |  | digital
N2DCS.20PGA26AA102F | 9477 | #4发电机氢冷器进水调节阀故障 |  | digital
N2DCS.20PGA26AA102RC | 9478 | #4发电机氢冷器进水调节阀在远控 |  | digital
N2DCS.20PGA26AA102SPDH | 9479 | #4发电机氢冷调阀设定反馈偏差大 |  | digital
N2DCS.20PGA26AA103AUTO | 9480 | #4机润滑油冷却器进水调阀在自动 |  | digital
N2DCS.20PGA26AA103DVHI | 9481 | #4机滑油冷却调阀指令反馈偏差大 |  | digital
N2DCS.20PGA26AA103F | 9482 | #4机润滑油冷却器进水调节阀故障 |  | digital
N2DCS.20PGA26AA103RC | 9483 | #4机润滑油冷却器进水调阀在远控 |  | digital
N2DCS.20PGA26AA103SPDH | 9484 | #4机滑油冷却调阀设定反馈偏差大 |  | digital
N2DCS.20PGA32AA101AUTO | 9485 | #3机EH油冷却器进水调阀在自动 |  | digital
N2DCS.20PGA32AA101DVHI | 9486 | #3机EH油冷却调阀指令反馈偏差大 |  | digital
N2DCS.20PGA32AA101F | 9487 | #3机EH油冷却器进水调节阀故障 |  | digital
N2DCS.20PGA32AA101RC | 9488 | #3机EH油冷却器进水调阀在远控 |  | digital
N2DCS.20PGA32AA101SPDH | 9489 | #3机EH油冷却调阀设定反馈偏差大 |  | digital
N2DCS.20PGA33AA101AUTO | 9490 | #3机润滑油冷却器进水调阀在自动 |  | digital
N2DCS.20PGA33AA101DVHI | 9491 | #3机滑油冷却调阀指令反馈偏差大 |  | digital
N2DCS.20PGA33AA101F | 9492 | #3机润滑油冷却器进水调节阀故障 |  | digital
N2DCS.20PGA33AA101RC | 9493 | #3机润滑油冷却器进水调阀在远控 |  | digital
N2DCS.20PGA33AA101SPDH | 9494 | #3机滑油冷却调阀设定反馈偏差大 |  | digital
N2DCS.20PGA34AA101AUTO | 9495 | #3发电机空冷器进水调节阀在自动 |  | digital
N2DCS.20PGA34AA101DVHI | 9496 | #3发电机空冷调阀指令反馈偏差大 |  | digital
N2DCS.20PGA34AA101F | 9497 | #3发电机空冷器进水调节阀故障 |  | digital
N2DCS.20PGA34AA101RC | 9498 | #3发电机空冷器进水调节阀在远控 |  | digital
N2DCS.20PGA34AA101SPDH | 9499 | #3发电机空冷调阀设定反馈偏差大 |  | digital
N2DCS.CLCLGPMPB_PMT1 | 9500 | #2闭式水泵启动允许 |  | digital
N2DCS.CLCLGPMPB_SEQSTOK | 9501 | #2闭式水泵启顺控已成功完成 |  | digital
N2DCS.CLCLGPMPB_STPMT | 9502 | #2闭式水泵启动允许 |  | digital
N2DCS.CLCLGPMPB_TEMALM | 9503 | #2闭式水泵超温保护报警 |  | digital
N2DCS.CLCLGPMPB_TEMALMCUT | 9504 | #2闭式水泵超温保护功能解除 |  | digital
N2DCS.CLCLGPMPB_TP | 9505 | #2闭式水泵跳闸信号 |  | digital
N2DCS.CLCLGPMPBMANSTOP | 9506 | #2闭式水泵手动停止指令 |  | digital
N2DCS.CLCLGPMPBTEMPMT | 9507 | #2闭式水泵已停止 |  | digital
N2DCS.CNDPB_SEQSTOK | 9508 | #2凝结水泵启顺控已成功完成 |  | digital
N2DCS.CNDPBRUN | 9509 | 凝结水泵B运行 |  | digital
N2DCS.CNDPMPB_PMT1 | 9510 | #2凝结水泵启动允许 |  | digital
N2DCS.CNDPMPB_STPMT | 9511 | #2凝结水泵启动允许 |  | digital
N2DCS.CNDPMPB_TEMALM | 9512 | #2凝结水泵超温报警 |  | digital
N2DCS.CNDPMPB_TEMALMCUT | 9513 | #2凝结水泵温度保护功能解除 |  | digital
N2DCS.CNDPMPB_TP | 9514 | #2凝结水泵跳闸信号 |  | digital
N2DCS.CNDPMPBPLC | 9515 | 保护停 |  | digital
N2DCS.CNDPMPBTEMPMT | 9516 | #2凝结水泵温度允许 |  | digital
N2DCS.ONE4 | 9517 | 开关量1 |  | digital
N2DCS.OPNCIRPMPB_PMT | 9518 | #2开式水泵启动允许 |  | digital
N2DCS.OPNCIRPMPB_PMT1 | 9519 | #2开式水泵启动允许 |  | digital
N2DCS.OPNCIRPMPB_SEQSTOK | 9520 | #2开式水泵启顺控已成功完成 |  | digital
N2DCS.OPNCIRPMPB_TEMALM | 9521 | #2开式水泵温度报警 |  | digital
N2DCS.OPNCIRPMPB_TEMALMCUT | 9522 | #2开式水泵超温保护报警功能解除 |  | digital
N2DCS.OPNCIRPMPB_TP | 9523 | #2开式水泵跳闸信号 |  | digital
N2DCS.OPNCIRPMPBMANSTOP | 9524 | #2开式水泵手动停止指令 |  | digital
N2DCS.OPNCIRPMPBTEMPMT | 9525 | #2开式水泵温度允许 |  | digital
N2DCS.ZERO4 | 9526 | 开关量0 |  | digital
N2DCS.20LCB12GH001AUTO | 9527 | #2凝结水泵永磁调速控制器在自动 |  | digital
N2DCS.20LCB12GH001DVHI | 9528 | #2凝泵永磁调速指令反馈偏差大 |  | digital
N2DCS.20LCB12GH001SPDH | 9529 | #2凝泵永磁调速设定反馈偏差大 |  | digital
N2DCS.CNDPMPBMANSTOP | 9530 | #2凝结水泵逻辑发出停止指令 |  | digital
N2DCS.CNDPMPBPRT | 9531 | #2凝结水泵保护停指令 |  | digital
N2DCS.CNDPMPBRUN | 9532 | #2凝结水泵在运行 |  | digital
N2DCS.CNDPMPBRUN1 | 9533 | #2凝结水泵在运行 |  | digital
N2DCS.CNDPMPBRUN2 | 9534 | #2凝结水泵在运行 |  | digital
N2DCS.CNDPMPBSTOP | 9535 | #2凝结水泵已停止 |  | digital
N2DCS.HXCTQ_SEQSPOK | 9536 | 除铁过滤器停顺控已完成 |  | digital
N2DCS.HXCTQ_SEQSTOK | 9537 | 除铁过滤器启顺控已完成 |  | digital
N2DCS.20CSF01LP | 9538 | #3循环水泵房热力配电柜电源故障 |  | digital
N2DCS.20MAG01GH001F1 | 9539 | 热井检漏装置泵过热故障 |  | digital
N2DCS.20MAG01GH001LLL | 9540 | 热井检漏装置样水液位过低 |  | digital
N2DCS.20MAG01GH001RP1 | 9541 | 热井检漏装置泵运行状态 |  | digital
N2DCS.20MAG21CL001H | 9542 | #1真空泵汽水分离器液位高 |  | digital
N2DCS.20MAG21CL002L | 9543 | #1真空泵汽水分离器液位低 |  | digital
N2DCS.20MAJ21AA001CD | 9544 | #1真空泵进口气动门2关闭指令 |  | digital
N2DCS.20MAJ21AA001CP | 9545 | #1真空泵进口气动门2全关位置 |  | digital
N2DCS.20MAJ21AA001F | 9546 | #1真空泵进口气动门2电源消失 |  | digital
N2DCS.20MAJ21AA001OD | 9547 | #1真空泵进口气动门2打开指令 |  | digital
N2DCS.20MAJ21AA001OP | 9548 | #1真空泵进口气动门2全开位置 |  | digital
N2DCS.20MAJ21AA007F | 9549 | #1真空泵汽水分离器补水阀无电源 |  | digital
N2DCS.20MAJ21AA007OD/CD | 9550 | #1真空泵分离器补水阀开/关指令 |  | digital
N2DCS.20MAJ21AA011CD | 9551 | #1真空泵进口气动门1关闭指令 |  | digital
N2DCS.20MAJ21AA011CP | 9552 | #1真空泵进口气动门1全关位置 |  | digital
N2DCS.20MAJ21AA011F | 9553 | #1真空泵进口气动门1电源消失 |  | digital
N2DCS.20MAJ21AA011OD | 9554 | #1真空泵进口气动门1打开指令 |  | digital
N2DCS.20MAJ21AA011OP | 9555 | #1真空泵进口气动门1全开位置 |  | digital
N2DCS.20MAJ21AP001PF | 9556 | #1真空泵综合故障 |  | digital
N2DCS.20MAJ21AP001PS | 9557 | 真空泵A电气保护动作 |  | digital
N2DCS.20MAJ21AP001RC | 9558 | #1真空泵远方控制 |  | digital
N2DCS.20MAJ21AP001RD | 9559 | #1真空泵启动指令 |  | digital
N2DCS.20MAJ21AP001RP | 9560 | #1真空泵在运行 |  | digital
N2DCS.20MAJ21AP001TD | 9561 | #1真空泵停止指令 |  | digital
N2DCS.20MAJ21AP001TP | 9562 | #1真空泵已停止 |  | digital
N2DCS.20MAJ23AA009CD | 9563 | 蒸汽喷射装置进口气动门关闭指令 |  | digital
N2DCS.20MAJ23AA009CP | 9564 | 蒸汽喷射装置进口气动门全关位置 |  | digital
N2DCS.20MAJ23AA009F | 9565 | 蒸汽喷射装置进口气动门电源消失 |  | digital
N2DCS.20MAJ23AA009OD | 9566 | 蒸汽喷射装置进口气动门打开指令 |  | digital
N2DCS.20MAJ23AA009OP | 9567 | 蒸汽喷射装置进口气动门全开位置 |  | digital
N2DCS.20MAJ23AA014CD | 9568 | 蒸汽喷射装置换热器放水门关指令 |  | digital
N2DCS.20MAJ23AA014CP | 9569 | 蒸汽喷射装置换热器放水门全关位 |  | digital
N2DCS.20MAJ23AA014F | 9570 | 蒸汽喷射装置换热器放水门无电源 |  | digital
N2DCS.20MAJ23AA014OD | 9571 | 蒸汽喷射装置换热器放水门开指令 |  | digital
N2DCS.20MAJ23AA014OP | 9572 | 蒸汽喷射装置换热器放水门全开位 |  | digital
N2DCS.20MAJ23AA016CD | 9573 | 喷射装置换热器汽侧出口门关指令 |  | digital
N2DCS.20MAJ23AA016CP | 9574 | 喷射装置换热器汽侧出口门全关位 |  | digital
N2DCS.20MAJ23AA016F | 9575 | 喷射装置换热器汽侧出口门无电源 |  | digital
N2DCS.20MAJ23AA016OD | 9576 | 喷射装置换热器汽侧出口门开指令 |  | digital
N2DCS.20MAJ23AA016OP | 9577 | 喷射装置换热器汽侧出口门全开位 |  | digital
N2DCS.20MAJ23AA101AUTO | 9578 | 蒸汽喷射装置压力调节阀在自动 |  | digital
N2DCS.20MAJ23AA101CP | 9579 | 蒸汽喷射装置压力调节阀全关位 |  | digital
N2DCS.20MAJ23AA101DVHI | 9580 | 喷射装置压力调阀指令反馈偏差大 |  | digital
N2DCS.20MAJ23AA101OP | 9581 | 蒸汽喷射装置压力调节阀全开位 |  | digital
N2DCS.20MAJ23AA101SPDH | 9582 | 喷射装置压力调阀设定反馈偏差大 |  | digital
N2DCS.20MAJ30AA002CD | 9583 | 凝汽器真空破坏气动门关闭指令 |  | digital
N2DCS.20MAJ30AA002CP | 9584 | 凝汽器真空破坏气动门门全关位置 |  | digital
N2DCS.20MAJ30AA002F | 9585 | 凝汽器真空破坏气动门电源消失 |  | digital
N2DCS.20MAJ30AA002OD | 9586 | 凝汽器真空破坏气动门打开指令 |  | digital
N2DCS.20MAV10AH001PF | 9587 | #3机润滑油箱#1电加热器综合故障 |  | digital
N2DCS.20MAV10AH001PS | 9588 | #3机润滑油箱#1电加热器保护动作 |  | digital
N2DCS.20MAV10AH001RC | 9589 | #3机润滑油箱#1电加热器远方控制 |  | digital
N2DCS.20MAV10AH001RD | 9590 | #3机润滑油箱#1电加热器启动指令 |  | digital
N2DCS.20MAV10AH001RP | 9591 | #3机润滑油箱#1电加热器在运行 |  | digital
N2DCS.20MAV10AH001TD | 9592 | #3机润滑油箱#1电加热器停止指令 |  | digital
N2DCS.20MAV10AH001TP | 9593 | #3机润滑油箱#1电加热器已停止 |  | digital
N2DCS.20MAV10AH002PF | 9594 | #3机润滑油箱#2电加热器综合故障 |  | digital
N2DCS.20MAV10AH002PS | 9595 | #3机润滑油箱#2电加热器保护动作 |  | digital
N2DCS.20MAV10AH002RC | 9596 | #3机润滑油箱#2电加热器远方控制 |  | digital
N2DCS.20MAV10AH002RD | 9597 | #3机润滑油箱#2电加热器启动指令 |  | digital
N2DCS.20MAV10AH002RP | 9598 | #3机润滑油箱#2电加热器在运行 |  | digital
N2DCS.20MAV10AH002TD | 9599 | #3机润滑油箱#2电加热器停止指令 |  | digital
N2DCS.20MAV10AH002TP | 9600 | #3机润滑油箱#2电加热器已停止 |  | digital
N2DCS.20MAV21AP021PF | 9601 | #3机#1润滑油泵综合故障 |  | digital
N2DCS.20MAV21AP021PS | 9602 | #1交流润滑油泵保护动作 |  | digital
N2DCS.20MAV21AP021RC | 9603 | #3机#1润滑油泵远方控制 |  | digital
N2DCS.20MAV21AP021RD | 9604 | #3机#1润滑油泵启动指令 |  | digital
N2DCS.20MAV21AP021RP | 9605 | #3机#1润滑油泵在运行 |  | digital
N2DCS.20MAV21AP021TD | 9606 | #3机#1润滑油泵停止指令 |  | digital
N2DCS.20MAV21AP021TP | 9607 | #3机#1润滑油泵已停止 |  | digital
N2DCS.20MAV21CP005L | 9608 | #3机#1润滑油泵出口压力低 |  | digital
N2DCS.20MAV31AP001PF | 9609 | #3机#1顶轴油泵综合故障 |  | digital
N2DCS.20MAV31AP001PS | 9610 | 顶轴油泵A保护动作 |  | digital
N2DCS.20MAV31AP001RC | 9611 | #3机#1顶轴油泵远方控制 |  | digital
N2DCS.20MAV31AP001RD | 9612 | #3机#1顶轴油泵启动指令 |  | digital
N2DCS.20MAV31AP001RP | 9613 | #3机#1顶轴油泵在运行 |  | digital
N2DCS.20MAV31AP001TD | 9614 | #3机#1顶轴油泵停止指令 |  | digital
N2DCS.20MAV31AP001TP | 9615 | #3机#1顶轴油泵已停止 |  | digital
N2DCS.20MAV82AN001PF | 9616 | #3机#1润滑油风机综合故障 |  | digital
N2DCS.20MAV82AN001PS | 9617 | 润滑油排烟风机A保护动作 |  | digital
N2DCS.20MAV82AN001RC | 9618 | #3机#1润滑油风机远方控制 |  | digital
N2DCS.20MAV82AN001RD | 9619 | #3机#1润滑油风机启动指令 |  | digital
N2DCS.20MAV82AN001RP | 9620 | #3机#1润滑油风机在运行 |  | digital
N2DCS.20MAV82AN001TD | 9621 | #3机#1润滑油风机停止指令 |  | digital
N2DCS.20MAV82AN001TP | 9622 | #3机#1润滑油风机已停止 |  | digital
N2DCS.20MAX01AP001PF | 9623 | #3机#1EH油泵综合故障 |  | digital
N2DCS.20MAX01AP001PS | 9624 | #3机#1EH油泵保护动作 |  | digital
N2DCS.20MAX01AP001RC | 9625 | #3机#1EH油泵远方控制 |  | digital
N2DCS.20MAX01AP001RD | 9626 | #3机#1EH油泵启动指令 |  | digital
N2DCS.20MAX01AP001RP | 9627 | #3机#1EH油泵在运行 |  | digital
N2DCS.20MAX01AP001TD | 9628 | #3机#1EH油泵停止指令 |  | digital
N2DCS.20MAX01AP001TP | 9629 | #3机#1EH油泵已停止 |  | digital
N2DCS.20MAX01AP011PF | 9630 | #3机#1EH油循环泵综合故障 |  | digital
N2DCS.20MAX01AP011PS | 9631 | #1EH油循环泵保护动作 |  | digital
N2DCS.20MAX01AP011RC | 9632 | #3机#1EH油循环泵远方控制 |  | digital
N2DCS.20MAX01AP011RD | 9633 | #3机#1EH油循环泵启动指令 |  | digital
N2DCS.20MAX01AP011RP | 9634 | #3机#1EH油循环泵在运行 |  | digital
N2DCS.20MAX01AP011TD | 9635 | #3机#1EH油循环泵停止指令 |  | digital
N2DCS.20MAX01AP011TP | 9636 | #3机#1EH油循环泵已停止 |  | digital
N2DCS.20MAX01CP004L | 9637 | #3机#1EH油循环泵出口压力低 |  | digital
N2DCS.20MAX01CP011H | 9638 | #3机#1EH油泵出口滤网差压高 |  | digital
N2DCS.20MAX01CP013H | 9639 | #3机#1EH油循环滤网差压高 |  | digital
N2DCS.20PAA11AA001CD | 9640 | #1旋转滤网冲洗水电动门关指令 |  | digital
N2DCS.20PAA11AA001CP | 9641 | #1旋转滤网冲洗水电动门全关位 |  | digital
N2DCS.20PAA11AA001F | 9642 | #1旋转滤网冲洗水电动门综合故障 |  | digital
N2DCS.20PAA11AA001OD | 9643 | #1旋转滤网冲洗水电动门开指令 |  | digital
N2DCS.20PAA11AA001OP | 9644 | #1旋转滤网冲洗水电动门全开位 |  | digital
N2DCS.20PAB11AA002CD | 9645 | #3循环水泵出口液控蝶阀全关指令 |  | digital
N2DCS.20PAB11AA002CDH | 9646 | #3循环水泵出口液控蝶阀半关指令 |  | digital
N2DCS.20PAB11AA002CER | 9647 | #3循环水泵出口液控蝶阀不能全关 |  | digital
N2DCS.20PAB11AA002CGLJ | 9648 | #3循环水泵出口液控蝶阀关过力矩 |  | digital
N2DCS.20PAB11AA002CL | 9649 | #3循环水泵出口碟阀事故关阀指令 |  | digital
N2DCS.20PAB11AA002CP | 9650 | #3循环水泵出口液控蝶阀正在关 |  | digital
N2DCS.20PAB11AA002CP1 | 9651 | #3循环水泵出口液控蝶阀全关位置 |  | digital
N2DCS.20PAB11AA002L1 | 9652 | #3循环水泵出口液控蝶阀阀位1 |  | digital
N2DCS.20PAB11AA002L2 | 9653 | #3循环水泵出口液控蝶阀阀位2 |  | digital
N2DCS.20PAB11AA002LP | 9654 | #3循环水泵出口液控蝶阀在就地 |  | digital
N2DCS.20PAB11AA002OD | 9655 | #3循环水泵出口液控蝶阀全开指令 |  | digital
N2DCS.20PAB11AA002ODH | 9656 | #3循环水泵出口液控蝶阀半开指令 |  | digital
N2DCS.20PAB11AA002OER | 9657 | #3循环水泵出口液控蝶阀不能全开 |  | digital
N2DCS.20PAB11AA002OGLJ | 9658 | #3循环水泵出口液控蝶阀开过力矩 |  | digital
N2DCS.20PAB11AA002OLF | 9659 | #3循环水泵出口液控蝶阀滤油堵塞 |  | digital
N2DCS.20PAB11AA002OLL | 9660 | #3循环水泵出口液控蝶阀油位低 |  | digital
N2DCS.20PAB11AA002OP | 9661 | #3循环水泵出口液控蝶阀正在开 |  | digital
N2DCS.20PAB11AA002OP1 | 9662 | #3循环水泵出口液控蝶阀全开位置 |  | digital
N2DCS.20PAB11AA002POF | 9663 | #3循环水泵出口液控蝶阀电源故障 |  | digital
N2DCS.20PAB11AA002ST | 9664 | #3循环水泵出口液控蝶阀停止指令 |  | digital
N2DCS.20PAB11AA002YK | 9665 | #3循环水泵出口液控蝶阀在远控 |  | digital
N2DCS.20PAB11AA002YYF | 9666 | #3循环水泵出口液控蝶阀液压故障 |  | digital
N2DCS.20PAB11AT001CD | 9667 | #1旋转滤网急停指令 |  | digital
N2DCS.20PAB11AT001DSQD | 9668 | #1旋转滤网低速定时启动 |  | digital
N2DCS.20PAB11AT001F | 9669 | #1旋转滤网故障 |  | digital
N2DCS.20PAB11AT001JT | 9670 | #1旋转滤网已急停 |  | digital
N2DCS.20PAB11AT001LC | 9671 | #1旋转滤网本地模式 |  | digital
N2DCS.20PAB11AT001QZ | 9672 | #1旋转滤网轻载 |  | digital
N2DCS.20PAB11AT001RC | 9673 | #1旋转滤网在远控 |  | digital
N2DCS.20PAB11AT001RD1 | 9674 | #1旋转滤网低速启动指令 |  | digital
N2DCS.20PAB11AT001RD2 | 9675 | #1旋转滤网高速启动指令 |  | digital
N2DCS.20PAB11AT001RP | 9676 | #1旋转滤网运行 |  | digital
N2DCS.20PAB11AT001RP1 | 9677 | #1旋转滤网低速运行 |  | digital
N2DCS.20PAB11AT001RP2 | 9678 | #1旋转滤网高速运行 |  | digital
N2DCS.20PAB11AT001SL1 | 9679 | #1旋转滤网松链1 |  | digital
N2DCS.20PAB11AT001SL2 | 9680 | #1旋转滤网松链2 |  | digital
N2DCS.20PAB11AT001ZZ | 9681 | #1旋转滤网重载 |  | digital
N2DCS.20PAB41AP001PF | 9682 | #3循环水泵#1增压泵综合故障 |  | digital
N2DCS.20PAB41AP001PS | 9683 | #3循环水泵#1增压泵保护动作 |  | digital
N2DCS.20PAB41AP001RC | 9684 | #3循环水泵冷却水#1增压泵在远控 |  | digital
N2DCS.20PAB41AP001RD | 9685 | #3循环水泵#1增压泵启动指令 |  | digital
N2DCS.20PAB41AP001RP | 9686 | #3循环水泵冷却水#1增压泵在运行 |  | digital
N2DCS.20PAB41AP001TD | 9687 | #3循环水泵#1增压泵停止指令 |  | digital
N2DCS.20PAB41AP001TP | 9688 | #3循环水泵冷却水#1增压泵已停止 |  | digital
N2DCS.20PAB42AP001PF | 9689 | #3循环水泵#1加压泵综合故障 |  | digital
N2DCS.20PAB42AP001PS | 9690 | #3循环水泵#1加压泵保护动作 |  | digital
N2DCS.20PAB42AP001RC | 9691 | #3循环水泵#1加压泵在远控 |  | digital
N2DCS.20PAB42AP001RD | 9692 | #3循环水泵#1加压泵启动指令 |  | digital
N2DCS.20PAB42AP001RP | 9693 | #3循环水泵#1加压泵在运行 |  | digital
N2DCS.20PAB42AP001TD | 9694 | #3循环水泵#1加压泵停止指令 |  | digital
N2DCS.20PAB42AP001TP | 9695 | #3循环水泵#1加压泵已停止 |  | digital
N2DCS.20PAB43CF001L | 9696 | #3循环水泵冷却水进口流量低 |  | digital
N2DCS.20PAB61AA001OD/CD | 9697 | 生活水至#1循泵电磁阀开/关指令 |  | digital
N2DCS.20PAB61AA001PF | 9698 | 生活水至#1循泵电磁阀无电源 |  | digital
N2DCS.20PAC11AP001CO | 9699 | #1、#4循环水泵均在运行且同速 |  | digital
N2DCS.20PAC11AP001LP | 9700 | #3循环水泵电气保护动作 |  | digital
N2DCS.20PAC11AP001OD0 | 9701 | #3循环水泵备用联启指令 |  | digital
N2DCS.20PAC11AP001PF | 9702 | #1循泵控制电源消失及装置故障 |  | digital
N2DCS.20PAC11AP001PFH | 9703 | #3循环水泵高速控制电源消失 |  | digital
N2DCS.20PAC11AP001PFL | 9704 | 1A循环水泵低速控制电源消失 |  | digital
N2DCS.20PAC11AP001PS | 9705 | #3循环水泵电气保护动作 |  | digital
N2DCS.20PAC11AP001RC | 9706 | #3循环水泵远方控制状态 |  | digital
N2DCS.20PAC11AP001RCH | 9707 | #3循环水泵高速在远控 |  | digital
N2DCS.20PAC11AP001RCL | 9708 | 1A循环水泵低速在远控 |  | digital
N2DCS.20PAC11AP001RD | 9709 | #3循环水泵合闸指令 |  | digital
N2DCS.20PAC11AP001RDH | 9710 | #3循环水泵高速合闸指令 |  | digital
N2DCS.20PAC11AP001RDL | 9711 | #3循环水泵低速合闸指令 |  | digital
N2DCS.20PAC11AP001RP | 9712 | #3循环水泵在运行 |  | digital
N2DCS.20PAC11AP001RPH | 9713 | #3循环水泵高速运行 |  | digital
N2DCS.20PAC11AP001RPL | 9714 | #3循环水泵低速运行 |  | digital
N2DCS.20PAC11AP001SW | 9715 | #3循环水泵试验位置 |  | digital
N2DCS.20PAC11AP001TD | 9716 | #3循环水泵跳闸指令 |  | digital
N2DCS.20PAC11AP001TDH | 9717 | #3循环水泵高速跳闸指令 |  | digital
N2DCS.20PAC11AP001TDL | 9718 | #3循环水泵低速跳闸指令 |  | digital
N2DCS.20PAC11AP001TP | 9719 | #3循环水泵已停止 |  | digital
N2DCS.20PAC11AP001TP1 | 9720 | #3循环水泵已停止 |  | digital
N2DCS.20PAC11AP001TPH | 9721 | #3循环水泵高速停止 |  | digital
N2DCS.20PAC11AP001TPH1 | 9722 | #3循环水泵高速停止 |  | digital
N2DCS.20PAC11AP001TPL | 9723 | #3循环水泵低速停止 |  | digital
N2DCS.20PAC11AP001TPL1 | 9724 | #3循环水泵低速停止 |  | digital
N2DCS.20PAC11AP001YW | 9725 | #3循环水泵工作位置 |  | digital
N2DCS.20PAC12AP001CO | 9726 | #3、#4循环水泵均在运行且同速 |  | digital
N2DCS.20PSA01AP001PF | 9727 | #2冷却塔排水池#1排污泵综合故障 |  | digital
N2DCS.20PSA01AP001RC | 9728 | #2冷却塔排水池#1排污泵在远控 |  | digital
N2DCS.20PSA01AP001RD | 9729 | #2冷却塔排水池#1排污泵启动指令 |  | digital
N2DCS.20PSA01AP001RP | 9730 | #2冷却塔排水池#1排污泵在运行 |  | digital
N2DCS.20PSA01AP001TD | 9731 | #2冷却塔排水池#1排污泵停止指令 |  | digital
N2DCS.20PSA01AP001TP | 9732 | #2冷却塔排水池#1排污泵已停止 |  | digital
N2DCS.CIRPMPA_STPMT | 9733 | #3循环水泵启动允许 |  | digital
N2DCS.CIRPMPA_TEMALM | 9734 | #3循环水泵温度报警 |  | digital
N2DCS.CIRPMPA_TEMPMT | 9735 | #3循环水泵温度允许 |  | digital
N2DCS.CIRPMPA_TEMTRIP | 9736 | #3循环水泵温度保护跳闸信号 |  | digital
N2DCS.CIRPMPA_TP | 9737 | #3循环水泵跳闸信号 |  | digital
N2DCS.CIRPMPAMANSTOP | 9738 | #3循环水泵手动停止指令 |  | digital
N2DCS.CIRWTRPMPA_SEQSPOK | 9739 | #3循环水泵停顺控已成功完成 |  | digital
N2DCS.CIRWTRPMPA_SEQSTOK | 9740 | #3循环水泵启顺控已成功完成 |  | digital
N2DCS.CIRWTRPMPAFRMODE | 9741 | #3循环水泵注水模式 |  | digital
N2DCS.CIRWTRSYS_SEQSTFINISH | 9742 | Ovation Control Builder |  | digital
N2DCS.CNSRVACM_MRE | 9743 | 凝汽器真空坏点 |  | digital
N2DCS.EHOILSYS_SEQOK | 9744 | EH油系统EH油泵启动完成 |  | digital
N2DCS.EHOILSYS_SEQSPOK | 9745 | EN油系统停顺控已成功完成 |  | digital
N2DCS.EHOILSYS_SEQSTFINISH | 9746 | Ovation Control Builder |  | digital
N2DCS.EHOILSYS_SEQSTOK | 9747 | EH油系统启顺控已成功完成 |  | digital
N2DCS.J0PAB60AA004CD_DO | 9748 | 二号机关闭生活水至循环水冷却电 |  | digital
N2DCS.J0PAB60AA004CP_DI | 9749 | 生活水至循环水冷却电动门全关 |  | digital
N2DCS.J0PAB60AA004OD_DO | 9750 | 二号机打开生活水至循环水冷却电 |  | digital
N2DCS.J0PAB60AA004OP_DI | 9751 | 生活水至循环水冷却电动门全开送 |  | digital
N2DCS.JACKOILPRSL | 9752 | 顶轴油压力低 |  | digital
N2DCS.LUBOILBOXTEM_MRE | 9753 | #3机润滑油箱温度坏点 |  | digital
N2DCS.LUBOILHTR_STPMT | 9754 | #3机润滑油电加热器启允许 |  | digital
N2DCS.ONE5 | 9755 | 开关量1 |  | digital
N2DCS.ROTFLTRAHSPDMODE | 9756 | #1旋转滤网预选高速 |  | digital
N2DCS.ROTFLTRAINTRFLSH | 9757 | #1旋转滤网联锁冲洗中 |  | digital
N2DCS.ROTFLTRAINTRON | 9758 | #1旋转滤网冲洗联锁投入 |  | digital
N2DCS.TCSEHOILOK | 9759 | TCSEH油系统运行 |  | digital
N2DCS.TEST1 | 9760 | 测试 |  | digital
N2DCS.TURBDRNALLCP | 9761 | #3机本体疏水门均已全关 |  | digital
N2DCS.TURBDRNALLOP | 9762 | #3机本体疏水门均已全开 |  | digital
N2DCS.TURBOILSYS_SEQSTFINISH | 9763 | #3机润滑油系统启顺控已完成 |  | digital
N2DCS.TURBOILSYS_SEQSTOK | 9764 | #3机润滑油系统启顺控已完成 |  | digital
N2DCS.VACMPMPA_PMT | 9765 | #1真空泵启动允许 |  | digital
N2DCS.VACMPMPA_SEQSTOK | 9766 | #1真空泵启顺控已成功完成 |  | digital
N2DCS.VACMPMPA_TEMALM | 9767 | #1真空泵温度报警 |  | digital
N2DCS.VACMPMPA_TEMPMT | 9768 | #1真空泵温度允许 |  | digital
N2DCS.VACMPMPA_TEMTRIP | 9769 | #1真空泵温度保护跳闸信号 |  | digital
N2DCS.VACMPMPA_TP | 9770 | #1真空泵跳闸信号 |  | digital
N2DCS.VACMPMPAMANSTOP | 9771 | #1真空泵逻辑联锁停止指令 |  | digital
N2DCS.VACMPMPATEMPMT | 9772 | 真空泵A温度允许 |  | digital
N2DCS.VACMSYS_SEQSTFINISH | 9773 | 抽真空系统启顺控已成功完成 |  | digital
N2DCS.ZERO5 | 9774 | 开关量0 |  | digital
N2DCS.20MAJ21AA007CL | 9775 | #1真空泵汽水分离器补水阀自动关 |  | digital
N2DCS.20MAJ21AA007OP | 9776 | #1真空泵汽水分离器补水阀自动开 |  | digital
N2DCS.CIRWTRSYS_SEQFINISH | 9777 | 循环水系统启顺控已完成 |  | digital
N2DCS.J0PAB60AA004OP | 9778 | Ovation Control Builder |  | digital
N2DCS.J0PAB60AA004OP_DI1 | 9779 | 生活水至循环水冷却电动门全开 |  | digital
N2DCS.XZLWDISU | 9780 | #1旋转滤网预选低速 |  | digital
N2DCS.XZLWGAOSU | 9781 | #1旋转滤网预选高速 |  | digital
N2DCS.1STCWPMODE | 9782 | 循环水泵注水模式 |  | digital
N2DCS.20LBD20CP001H1 | 9783 | 冷再快关调阀进油滤网差压高 |  | digital
N2DCS.20LBD20CP111L | 9784 | 冷再快关调阀进油压力低 |  | digital
N2DCS.20LBD20GH101ESDA | 9785 | 热再快关调阀ESD动作 |  | digital
N2DCS.20LBD20GH101FL | 9786 | 热再快关调阀反馈消失 |  | digital
N2DCS.20LBD20GH101LC | 9787 | 热再快关调阀就地控制 |  | digital
N2DCS.20LBD20GH101OL | 9788 | 热再快关调阀指令消失 |  | digital
N2DCS.20LBD20GH101PF1 | 9789 | 热再快关调阀正常电源消失 |  | digital
N2DCS.20LBD20GH101PF2 | 9790 | 热再快关调阀备用电源消失 |  | digital
N2DCS.20LBD20GH101PL | 9791 | 热再快关调阀供油压力低 |  | digital
N2DCS.20LBD20GH101TL | 9792 | 热再快关调阀跟踪丢失 |  | digital
N2DCS.20LBD40CP001H1 | 9793 | 热再快关调阀进油滤网差压高 |  | digital
N2DCS.20LBD40CP111L | 9794 | 热再快关调阀进油压力低 |  | digital
N2DCS.20LBD40GH101ESDA | 9795 | 冷再快关调阀ESD动作 |  | digital
N2DCS.20LBD40GH101FL | 9796 | 冷再快关调阀反馈消失 |  | digital
N2DCS.20LBD40GH101LC | 9797 | 冷再快关调阀就地控制 |  | digital
N2DCS.20LBD40GH101OL | 9798 | 冷再快关调阀指令消失 |  | digital
N2DCS.20LBD40GH101PF1 | 9799 | 冷再快关调阀正常电源消失 |  | digital
N2DCS.20LBD40GH101PF2 | 9800 | 冷再快关调阀备用电源消失 |  | digital
N2DCS.20LBD40GH101PL | 9801 | 冷再快关调阀供油压力低 |  | digital
N2DCS.20LBD40GH101TL | 9802 | 冷再快关调阀跟踪丢失 |  | digital
N2DCS.20MAC45CP001H1 | 9803 | 低压补汽主汽门进油滤网差压高 |  | digital
N2DCS.20MAC45CP002L1 | 9804 | 低压补汽主汽门进油压力低 |  | digital
N2DCS.20MAC45GH101ESDA | 9805 | 低压补汽主汽门ESD动作 |  | digital
N2DCS.20MAC45GH101LC | 9806 | 低压补汽主汽门就地控制 |  | digital
N2DCS.20MAC45GH101PF1 | 9807 | 低压补汽主汽门正常电源消失 |  | digital
N2DCS.20MAC45GH101PF2 | 9808 | 低压补汽主汽门备用电源消失 |  | digital
N2DCS.20MAC45GH101PSTF | 9809 | 低压补汽主汽门PST故障 |  | digital
N2DCS.20MAC46CP001H1 | 9810 | 低压补汽调门进油滤网差压高 |  | digital
N2DCS.20MAC46CP101L | 9811 | 低压补汽调门进油压力低 |  | digital
N2DCS.20MAC46GH101ESDA | 9812 | 低压补汽调门ESD动作 |  | digital
N2DCS.20MAC46GH101FL | 9813 | 低压补汽调门反馈消失 |  | digital
N2DCS.20MAC46GH101LC | 9814 | 低压补汽调门就地控制 |  | digital
N2DCS.20MAC46GH101OL | 9815 | 低压补汽调门指令消失 |  | digital
N2DCS.20MAC46GH101PF1 | 9816 | 低压补汽调门正常电源消失 |  | digital
N2DCS.20MAC46GH101PF2 | 9817 | 低压补汽调门备用电源消失 |  | digital
N2DCS.20MAC46GH101PL | 9818 | 低压补汽调门供油压力低 |  | digital
N2DCS.20MAC46GH101TL | 9819 | 低压补汽调门跟踪丢失 |  | digital
N2DCS.20MAG22CL001H | 9820 | #2真空泵汽水分离器液位高 |  | digital
N2DCS.20MAG22CL002L | 9821 | #2真空泵汽水分离器液位低 |  | digital
N2DCS.20MAJ22AA001CD | 9822 | #2真空泵进口气动门2关闭指令 |  | digital
N2DCS.20MAJ22AA001CP | 9823 | #2真空泵进口气动门2全关位置 |  | digital
N2DCS.20MAJ22AA001F | 9824 | #2真空泵进口气动门2电源消失 |  | digital
N2DCS.20MAJ22AA001OD | 9825 | #2真空泵进口气动门2打开指令 |  | digital
N2DCS.20MAJ22AA001OP | 9826 | #2真空泵进口气动门2全开位置 |  | digital
N2DCS.20MAJ22AA007CL | 9827 | #2真空泵汽水分离器补水阀自动关 |  | digital
N2DCS.20MAJ22AA007F | 9828 | #2真空泵汽水分离器补水阀无电源 |  | digital
N2DCS.20MAJ22AA007OD/CD | 9829 | #2真空泵分离器补水阀开/关指令 |  | digital
N2DCS.20MAJ22AA007OP | 9830 | #2真空泵汽水分离器补水阀自动开 |  | digital
N2DCS.20MAJ22AA011CD | 9831 | #2真空泵进口气动门1关闭指令 |  | digital
N2DCS.20MAJ22AA011CP | 9832 | #2真空泵进口气动门1全关位置 |  | digital
N2DCS.20MAJ22AA011F | 9833 | #2真空泵进口气动门1电源消失 |  | digital
N2DCS.20MAJ22AA011OD | 9834 | #2真空泵进口气动门1打开指令 |  | digital
N2DCS.20MAJ22AA011OP | 9835 | #2真空泵进口气动门1全开位置 |  | digital
N2DCS.20MAJ22AP001PF | 9836 | #2真空泵综合故障 |  | digital
N2DCS.20MAJ22AP001PS | 9837 | #2真空泵电气保护动作 |  | digital
N2DCS.20MAJ22AP001RC | 9838 | #2真空泵远方控制 |  | digital
N2DCS.20MAJ22AP001RD | 9839 | #2真空泵启动指令 |  | digital
N2DCS.20MAJ22AP001RP | 9840 | #2真空泵在运行 |  | digital
N2DCS.20MAJ22AP001TD | 9841 | #2真空泵停止指令 |  | digital
N2DCS.20MAJ22AP001TP | 9842 | #2真空泵已停止 |  | digital
N2DCS.20MAV10AH003PF | 9843 | #3机润滑油箱#3电加热器综合故障 |  | digital
N2DCS.20MAV10AH003PS | 9844 | #3机润滑油箱#3电加热器保护动作 |  | digital
N2DCS.20MAV10AH003RC | 9845 | #3机润滑油箱#3电加热器远方控制 |  | digital
N2DCS.20MAV10AH003RD | 9846 | #3机润滑油箱#3电加热器启动指令 |  | digital
N2DCS.20MAV10AH003RP | 9847 | #3机润滑油箱#3电加热器在运行 |  | digital
N2DCS.20MAV10AH003TD | 9848 | #3机润滑油箱#3电加热器停止指令 |  | digital
N2DCS.20MAV10AH003TP | 9849 | #3机润滑油箱#3电加热器已停止 |  | digital
N2DCS.20MAV10AH004PF | 9850 | #3机润滑油箱#4电加热器综合故障 |  | digital
N2DCS.20MAV10AH004PS | 9851 | #3机润滑油箱#4电加热器保护动作 |  | digital
N2DCS.20MAV10AH004RC | 9852 | #3机润滑油箱#4电加热器远方控制 |  | digital
N2DCS.20MAV10AH004RD | 9853 | #3机润滑油箱#4电加热器启动指令 |  | digital
N2DCS.20MAV10AH004RP | 9854 | #3机润滑油箱#4电加热器在运行 |  | digital
N2DCS.20MAV10AH004TD | 9855 | #3机润滑油箱#4电加热器停止指令 |  | digital
N2DCS.20MAV10AH004TP | 9856 | #3机润滑油箱#4电加热器已停止 |  | digital
N2DCS.20MAV10CT011 | 9857 | #3机润滑油箱温度高 |  | digital
N2DCS.20MAV10CT012 | 9858 | #3机润滑油箱温度低 |  | digital
N2DCS.20MAV21AA321OD/CD | 9859 | #3机滑油泵出口电磁阀开/关指令 |  | digital
N2DCS.20MAV21AA321PF | 9860 | #3机滑油泵出口电磁阀无电源 |  | digital
N2DCS.20MAV21AP022PF | 9861 | #3机#2润滑油泵综合故障 |  | digital
N2DCS.20MAV21AP022PS | 9862 | #2交流润滑油泵保护动作 |  | digital
N2DCS.20MAV21AP022RC | 9863 | #3机#2润滑油泵远方控制 |  | digital
N2DCS.20MAV21AP022RD | 9864 | #3机#2润滑油泵启动指令 |  | digital
N2DCS.20MAV21AP022RP | 9865 | #3机#2润滑油泵在运行 |  | digital
N2DCS.20MAV21AP022TD | 9866 | #3机#2润滑油泵停止指令 |  | digital
N2DCS.20MAV21AP022TP | 9867 | #3机#2润滑油泵已停止 |  | digital
N2DCS.20MAV21CP001L | 9868 | #3机润滑油泵出口母管压力低 |  | digital
N2DCS.20MAV21CP006L | 9869 | #3机#2润滑油泵出口压力低 |  | digital
N2DCS.20MAV24AP001PF | 9870 | #3机润滑油应急油泵综合故障 |  | digital
N2DCS.20MAV24AP001PS | 9871 | #3机润滑油应急油泵保护动作 |  | digital
N2DCS.20MAV24AP001RC | 9872 | #3机润滑油应急油泵远方控制 |  | digital
N2DCS.20MAV24AP001RD | 9873 | #3机润滑油应急油泵启动指令 |  | digital
N2DCS.20MAV24AP001RP | 9874 | #3机润滑油应急油泵在运行 |  | digital
N2DCS.20MAV24AP001TD | 9875 | #3机润滑油应急油泵停止指令 |  | digital
N2DCS.20MAV24AP001TP | 9876 | #3机润滑油应急油泵已停止 |  | digital
N2DCS.20MAV24CP001L | 9877 | #3机润滑油应急油泵出口压力低 |  | digital
N2DCS.20MAV32AP001PF | 9878 | #3机#2顶轴油泵综合故障 |  | digital
N2DCS.20MAV32AP001PS | 9879 | 顶轴油泵B保护动作 |  | digital
N2DCS.20MAV32AP001RC | 9880 | #3机#2顶轴油泵远方控制 |  | digital
N2DCS.20MAV32AP001RD | 9881 | #3机#2顶轴油泵启动指令 |  | digital
N2DCS.20MAV32AP001RP | 9882 | #3机#2顶轴油泵在运行 |  | digital
N2DCS.20MAV32AP001TD | 9883 | #3机#2顶轴油泵停止指令 |  | digital
N2DCS.20MAV32AP001TP | 9884 | #3机#2顶轴油泵已停止 |  | digital
N2DCS.20MAV35CP016H | 9885 | #3机顶轴油泵出口母管滤网差压高 |  | digital
N2DCS.20MAV42AA322OD/CD | 9886 | 润滑油母管试验电磁阀1开/关指令 |  | digital
N2DCS.20MAV42AA322PF | 9887 | 润滑油母管试验电磁阀1无电源 |  | digital
N2DCS.20MAV42AA329OD/CD | 9888 | 润滑油母管试验电磁阀2开/关指令 |  | digital
N2DCS.20MAV42AA329PF | 9889 | 润滑油母管试验电磁阀2无电源 |  | digital
N2DCS.20MAV42CP013H | 9890 | #3机润滑油泵出口母管滤网差压高 |  | digital
N2DCS.20MAV42CP019L | 9891 | #3机润滑油母管压力低 |  | digital
N2DCS.20MAV51AA012OD/CD | 9892 | #3机盘车电磁门打开/关闭指令 |  | digital
N2DCS.20MAV51AA012PF | 9893 | #3机盘车电磁门电源消失 |  | digital
N2DCS.20MAV82AN002PF | 9894 | #3机#2润滑油风机综合故障 |  | digital
N2DCS.20MAV82AN002PS | 9895 | 润滑油排烟风机B保护动作 |  | digital
N2DCS.20MAV82AN002RC | 9896 | #3机#2润滑油风机远方控制 |  | digital
N2DCS.20MAV82AN002RD | 9897 | #3机#2润滑油风机启动指令 |  | digital
N2DCS.20MAV82AN002RP | 9898 | #3机#2润滑油风机在运行 |  | digital
N2DCS.20MAV82AN002TD | 9899 | #3机#2润滑油风机停止指令 |  | digital
N2DCS.20MAV82AN002TP | 9900 | #3机#2润滑油风机已停止 |  | digital
N2DCS.20MAX01AP002PF | 9901 | #3机#2EH油泵综合故障 |  | digital
N2DCS.20MAX01AP002PS | 9902 | #3机#2EH油泵保护动作 |  | digital
N2DCS.20MAX01AP002RC | 9903 | #3机#2EH油泵远方控制 |  | digital
N2DCS.20MAX01AP002RD | 9904 | #3机#2EH油泵启动指令 |  | digital
N2DCS.20MAX01AP002RP | 9905 | #3机#2EH油泵在运行 |  | digital
N2DCS.20MAX01AP002TD | 9906 | #3机#2EH油泵停止指令 |  | digital
N2DCS.20MAX01AP002TP | 9907 | #3机#2EH油泵已停止 |  | digital
N2DCS.20MAX01AP012PF | 9908 | #3机#2EH油循环泵综合故障 |  | digital
N2DCS.20MAX01AP012PS | 9909 | #2EH油循环泵保护动作 |  | digital
N2DCS.20MAX01AP012RC | 9910 | #3机#2EH油循环泵远方控制 |  | digital
N2DCS.20MAX01AP012RD | 9911 | #3机#2EH油循环泵启动指令 |  | digital
N2DCS.20MAX01AP012RP | 9912 | #3机#2EH油循环泵在运行 |  | digital
N2DCS.20MAX01AP012TD | 9913 | #3机#2EH油循环泵停止指令 |  | digital
N2DCS.20MAX01AP012TP | 9914 | #3机#2EH油循环泵已停止 |  | digital
N2DCS.20MAX01CL001X0 | 9915 | #3机EH油箱液位 |  | digital
N2DCS.20MAX01CL001X0H | 9916 | #3机EH油箱液位高 |  | digital
N2DCS.20MAX01CL001X0LL | 9917 | #3机EH油箱液位低低 |  | digital
N2DCS.20MAX01CL002L | 9918 | #3机EH油箱液位低 |  | digital
N2DCS.20MAX01CL002LLL | 9919 | #3机EH油箱液位低低低 |  | digital
N2DCS.20MAX01CP005L | 9920 | #3机#2EH油循环泵出口压力低 |  | digital
N2DCS.20MAX01CP012H | 9921 | #3机#2EH油泵出口滤网差压高 |  | digital
N2DCS.20MAX01CP014H | 9922 | #3机#2EH油循环滤网差压高 |  | digital
N2DCS.20PAA12AA001CD | 9923 | #1旋转滤网冲洗水电动门关指令 |  | digital
N2DCS.20PAA12AA001CP | 9924 | #1旋转滤网冲洗水电动门全关位 |  | digital
N2DCS.20PAA12AA001F | 9925 | #1旋转滤网冲洗水电动门综合故障 |  | digital
N2DCS.20PAA12AA001OD | 9926 | #1旋转滤网冲洗水电动门开指令 |  | digital
N2DCS.20PAA12AA001OP | 9927 | #1旋转滤网冲洗水电动门全开位 |  | digital
N2DCS.20PAAINTERLOCK1DO | 9928 | 冲洗水泵连锁条件1 |  | digital
N2DCS.20PAAINTERLOCK2DO | 9929 | 冲洗水泵连锁条件2 |  | digital
N2DCS.20PAB10AA001CD | 9930 | 循环水母管电动联络门关闭指令 |  | digital
N2DCS.20PAB10AA001CP | 9931 | 循环水母管电动联络门全关位置 |  | digital
N2DCS.20PAB10AA001F | 9932 | 循环水母管电动联络门综合故障 |  | digital
N2DCS.20PAB10AA001OD | 9933 | 循环水母管电动联络门打开指令 |  | digital
N2DCS.20PAB10AA001OP | 9934 | 循环水母管电动联络门全开位置 |  | digital
N2DCS.20PAB10AA001RC | 9935 | 循环水母管电动联络门在远控 |  | digital
N2DCS.20PAB12AA002CD | 9936 | #4循环水泵出口液控蝶阀全关指令 |  | digital
N2DCS.20PAB12AA002CDH | 9937 | #4循环水泵出口液控蝶阀半关指令 |  | digital
N2DCS.20PAB12AA002CER | 9938 | #4循环水泵出口液控蝶阀不能全关 |  | digital
N2DCS.20PAB12AA002CGLJ | 9939 | #4循环水泵出口液控蝶阀关过力矩 |  | digital
N2DCS.20PAB12AA002CL | 9940 | #4循环水泵出口碟阀事故关阀指令 |  | digital
N2DCS.20PAB12AA002CP | 9941 | #4循环水泵出口液控蝶阀正在关 |  | digital
N2DCS.20PAB12AA002CP1 | 9942 | #4循环水泵出口液控蝶阀全关位置 |  | digital
N2DCS.20PAB12AA002L1 | 9943 | #4循环水泵出口液控蝶阀阀位1 |  | digital
N2DCS.20PAB12AA002L2 | 9944 | #4循环水泵出口液控蝶阀阀位2 |  | digital
N2DCS.20PAB12AA002LP | 9945 | #4循环水泵出口液控蝶阀在就地 |  | digital
N2DCS.20PAB12AA002OD | 9946 | #4循环水泵出口液控蝶阀全开指令 |  | digital
N2DCS.20PAB12AA002ODH | 9947 | #4循环水泵出口液控蝶阀半开指令 |  | digital
N2DCS.20PAB12AA002OER | 9948 | #4循环水泵出口液控蝶阀不能全开 |  | digital
N2DCS.20PAB12AA002OGLJ | 9949 | #4循环水泵出口液控蝶阀开过力矩 |  | digital
N2DCS.20PAB12AA002OLF | 9950 | #4循环水泵出口液控蝶阀滤油堵塞 |  | digital
N2DCS.20PAB12AA002OLL | 9951 | #4循环水泵出口液控蝶阀油位低 |  | digital
N2DCS.20PAB12AA002OP | 9952 | #4循环水泵出口液控蝶阀正在开 |  | digital
N2DCS.20PAB12AA002OP1 | 9953 | #4循环水泵出口液控蝶阀全开位置 |  | digital
N2DCS.20PAB12AA002POF | 9954 | #4循环水泵出口液控蝶阀电源故障 |  | digital
N2DCS.20PAB12AA002ST | 9955 | #4循环水泵出口液控蝶阀停止指令 |  | digital
N2DCS.20PAB12AA002YK | 9956 | #4循环水泵出口液控蝶阀在远控 |  | digital
N2DCS.20PAB12AA002YYF | 9957 | #4循环水泵出口液控蝶阀液压故障 |  | digital
N2DCS.20PAB12AT001CD | 9958 | #2旋转滤网急停指令 |  | digital
N2DCS.20PAB12AT001DSQD | 9959 | #2旋转滤网低速定时启动 |  | digital
N2DCS.20PAB12AT001F | 9960 | #2旋转滤网故障 |  | digital
N2DCS.20PAB12AT001JT | 9961 | #2旋转滤网已急停 |  | digital
N2DCS.20PAB12AT001LC | 9962 | #2旋转滤网本地模式 |  | digital
N2DCS.20PAB12AT001QZ | 9963 | #2旋转滤网轻载 |  | digital
N2DCS.20PAB12AT001RC | 9964 | #2旋转滤网在远控 |  | digital
N2DCS.20PAB12AT001RD1 | 9965 | #2旋转滤网低速启动指令 |  | digital
N2DCS.20PAB12AT001RD2 | 9966 | #2旋转滤网高速启动指令 |  | digital
N2DCS.20PAB12AT001RP | 9967 | #2旋转滤网运行 |  | digital
N2DCS.20PAB12AT001RP1 | 9968 | #2旋转滤网低速运行 |  | digital
N2DCS.20PAB12AT001RP2 | 9969 | #2旋转滤网高速运行 |  | digital
N2DCS.20PAB12AT001SL1 | 9970 | #2旋转滤网松链1 |  | digital
N2DCS.20PAB12AT001SL2 | 9971 | #2旋转滤网松链2 |  | digital
N2DCS.20PAB12AT001ZZ | 9972 | #2旋转滤网重载 |  | digital
N2DCS.20PAB31AA002CD | 9973 | 循环水母管至循泵冷却水门关指令 |  | digital
N2DCS.20PAB31AA002CP | 9974 | 循环水母管至循泵冷却水门全关位 |  | digital
N2DCS.20PAB31AA002OD | 9975 | 循环水母管至循泵冷却水门开指令 |  | digital
N2DCS.20PAB31AA002OP | 9976 | 循环水母管至循泵冷却水门全开位 |  | digital
N2DCS.20PAB51AP001PF | 9977 | #4循环水泵#1加压泵综合故障 |  | digital
N2DCS.20PAB51AP001PS | 9978 | #4循环水泵#1加压泵保护动作 |  | digital
N2DCS.20PAB51AP001RC | 9979 | #4循环水泵#1加压泵在远控 |  | digital
N2DCS.20PAB51AP001RD | 9980 | #4循环水泵#1加压泵启动指令 |  | digital
N2DCS.20PAB51AP001RP | 9981 | #4循环水泵#1加压泵在运行 |  | digital
N2DCS.20PAB51AP001TD | 9982 | #4循环水泵#1加压泵停止指令 |  | digital
N2DCS.20PAB51AP001TP | 9983 | #4循环水泵#1加压泵已停止 |  | digital
N2DCS.20PAB52AP001PF | 9984 | #4循环水泵#2加压泵综合故障 |  | digital
N2DCS.20PAB52AP001PS | 9985 | #4循环水泵#2加压泵保护动作 |  | digital
N2DCS.20PAB52AP001RC | 9986 | #4循环水泵#2加压泵在远控 |  | digital
N2DCS.20PAB52AP001RD | 9987 | #4循环水泵#2加压泵启动指令 |  | digital
N2DCS.20PAB52AP001RP | 9988 | #4循环水泵#2加压泵在运行 |  | digital
N2DCS.20PAB52AP001TD | 9989 | #4循环水泵#2加压泵停止指令 |  | digital
N2DCS.20PAB52AP001TP | 9990 | #4循环水泵#2加压泵已停止 |  | digital
N2DCS.20PAB53CF001L | 9991 | #4循环水泵冷却水进口流量低 |  | digital
N2DCS.20PAB62AA001OD/CD | 9992 | 生活水至#2循泵电磁阀开/关指令 |  | digital
N2DCS.20PAB62AA001PF | 9993 | 生活水至#2循泵电磁阀无电源 |  | digital
N2DCS.20PAC12AP001LP | 9994 | #1、#4循环水泵均在运行且同速 |  | digital
N2DCS.20PAC12AP001PF | 9995 | #2循泵控制电源消失及装置故障 |  | digital
N2DCS.20PAC12AP001PFH | 9996 | #4循环水泵高速控制电源消失 |  | digital
N2DCS.20PAC12AP001PFL | 9997 | #4循环水泵低速控制电源消失 |  | digital
N2DCS.20PAC12AP001PS | 9998 | 1B循环水泵电气保护动作 |  | digital
N2DCS.20PAC12AP001RC | 9999 | #4循环水泵在远控 |  | digital
N2DCS.20PAC12AP001RCH | 10000 | #4循环水泵高速在远控 |  | digital
N2DCS.20PAC12AP001RCL | 10001 | #4循环水泵低速在远控 |  | digital
N2DCS.20PAC12AP001RD | 10002 | #4循环水泵合闸指令 |  | digital
N2DCS.20PAC12AP001RDH | 10003 | #4循环水泵高速合闸指令 |  | digital
N2DCS.20PAC12AP001RDL | 10004 | #4循环水泵低速合闸指令 |  | digital
N2DCS.20PAC12AP001RP | 10005 | #4循环水泵在运行 |  | digital
N2DCS.20PAC12AP001RPH | 10006 | #4循环水泵高速运行 |  | digital
N2DCS.20PAC12AP001RPL | 10007 | #4循环水泵低速运行 |  | digital
N2DCS.20PAC12AP001SW | 10008 | #4循环水泵试验位置 |  | digital
N2DCS.20PAC12AP001TD | 10009 | #4循环水泵跳闸指令 |  | digital
N2DCS.20PAC12AP001TD0 | 10010 | #4循环水泵跳闸指令 |  | digital
N2DCS.20PAC12AP001TDH | 10011 | #4循环水泵高速跳闸指令 |  | digital
N2DCS.20PAC12AP001TDL | 10012 | #4循环水泵低速跳闸指令 |  | digital
N2DCS.20PAC12AP001TP | 10013 | #4循环水泵已停止 |  | digital
N2DCS.20PAC12AP001TP1 | 10014 | #4循环水泵已停止 |  | digital
N2DCS.20PAC12AP001TPH | 10015 | #4循环水泵高速停止 |  | digital
N2DCS.20PAC12AP001TPH1 | 10016 | #4循环水泵高速停止 |  | digital
N2DCS.20PAC12AP001TPL | 10017 | #4循环水泵低速停止 |  | digital
N2DCS.20PAC12AP001TPL1 | 10018 | #4循环水泵低速停止 |  | digital
N2DCS.20PAC12AP001YW | 10019 | #4循环水泵工作位置 |  | digital
N2DCS.20PAR01AA001CD | 10020 | #2冷却塔进口电动蝶门关闭指令 |  | digital
N2DCS.20PAR01AA001CP | 10021 | #2冷却塔进口电动蝶门全关位置 |  | digital
N2DCS.20PAR01AA001F | 10022 | #2冷却塔进口电动蝶门综合故障 |  | digital
N2DCS.20PAR01AA001OD | 10023 | #2冷却塔进口电动蝶门打开指令 |  | digital
N2DCS.20PAR01AA001OP | 10024 | #2冷却塔进口电动蝶门全开位置 |  | digital
N2DCS.20PAR01AA001RC | 10025 | #2冷却塔进口电动蝶门在远控 |  | digital
N2DCS.20PAR01AA002AUTO | 10026 | #2冷却塔进口流量调节门在自动 |  | digital
N2DCS.20PAR01AA002DVHI | 10027 | #2冷却塔进口调门指令反馈偏差大 |  | digital
N2DCS.20PAR01AA002F | 10028 | #2冷却塔进口流量调节门故障 |  | digital
N2DCS.20PAR01AA002RC | 10029 | #2冷却塔进口流量调节门在远控 |  | digital
N2DCS.20PAR01AA002SPDH | 10030 | #2冷却塔进口调门速度反馈偏差大 |  | digital
N2DCS.20PSA02AP001PF | 10031 | #2冷却塔排水池#2排污泵综合故障 |  | digital
N2DCS.20PSA02AP001RC | 10032 | #2冷却塔排水池#2排污泵在远控 |  | digital
N2DCS.20PSA02AP001RD | 10033 | #2冷却塔排水池#2排污泵启动指令 |  | digital
N2DCS.20PSA02AP001RP | 10034 | #2冷却塔排水池#2排污泵在运行 |  | digital
N2DCS.20PSA02AP001TD | 10035 | #2冷却塔排水池#2排污泵停止指令 |  | digital
N2DCS.20PSA02AP001TP | 10036 | #2冷却塔排水池#2排污泵已停止 |  | digital
N2DCS.2STCWPMODE | 10037 | 循环水泵注水模式 |  | digital
N2DCS.CIRPMPB_STPMT | 10038 | #4循环水泵启动允许 |  | digital
N2DCS.CIRPMPB_TEMALM | 10039 | #4循环水泵温度报警 |  | digital
N2DCS.CIRPMPB_TEMPMT | 10040 | #4循环水泵温度允许 |  | digital
N2DCS.CIRPMPB_TEMTRIP | 10041 | #4循环水泵温度保护跳闸信号 |  | digital
N2DCS.CIRPMPB_TP | 10042 | #4循环水泵跳闸信号 |  | digital
N2DCS.CIRPMPBMANSTOP | 10043 | #4循环水泵手动停止指令 |  | digital
N2DCS.CIRWTRPMPB_SEQSPOK | 10044 | #4循环水泵停顺控已成功完成 |  | digital
N2DCS.CIRWTRPMPB_SEQSTOK | 10045 | #4循环水泵启顺控已成功完成 |  | digital
N2DCS.CIRWTRPMPBFRMODE | 10046 | #4循环水泵注水模式 |  | digital
N2DCS.CLEANOILBOXLVL_MRE | 10047 | 净油箱液位坏点 |  | digital
N2DCS.DCEMGOILP_BK | 10048 | #3机应急油泵联锁备用投入 |  | digital
N2DCS.EHOILSPLPRS_MRE | 10049 | #3机EH供油压力坏点 |  | digital
N2DCS.ONE6 | 10050 | 开关量1 |  | digital
N2DCS.ROTFLTRBHSPDMODE | 10051 | #2旋转滤网预选高速 |  | digital
N2DCS.ROTFLTRBINTRFLSH | 10052 | #2旋转滤网联锁冲洗中 |  | digital
N2DCS.ROTFLTRBINTRON | 10053 | #2旋转滤网冲洗联锁投入 |  | digital
N2DCS.VACMPMPB_PMT | 10054 | #2真空泵启动允许 |  | digital
N2DCS.VACMPMPB_SEQSTOK | 10055 | #2真空泵启顺控已成功完成 |  | digital
N2DCS.VACMPMPB_TEMALM | 10056 | #2真空泵温度报警 |  | digital
N2DCS.VACMPMPB_TEMPMT | 10057 | #2真空泵温度允许 |  | digital
N2DCS.VACMPMPB_TEMTRIP | 10058 | #2真空泵超温保护跳闸 |  | digital
N2DCS.VACMPMPB_TP | 10059 | #2真空泵跳闸信号 |  | digital
N2DCS.VACMPMPBMANSTOP | 10060 | #2真空泵逻辑联锁停止指令 |  | digital
N2DCS.VACMPMPBTEMPMT | 10061 | Ovation Control Builder |  | digital
N2DCS.ZERO6 | 10062 | 开关量0 |  | digital
N2DCS.2XZLWDISU | 10063 | #2旋转滤网预选低速 |  | digital
N2DCS.2XZLWGAOSU | 10064 | #2旋转滤网预选高速 |  | digital
N2DCS.ANYWASHPMPRUN | 10065 | Ovation Control Builder |  | digital
N2DCS.20CDB76XB01 | 10066 | 低压汽包水位摄像综合故障 |  | digital
N2DCS.20CDB76YB01 | 10067 | 低压汽包水位A侧画面显示 |  | digital
N2DCS.20CDB76YB02 | 10068 | 低压汽包水位B侧画面显示 |  | digital
N2DCS.20CDB76YB03 | 10069 | 低压汽包水位AB侧合成画面显示 |  | digital
N2DCS.20CDB76YB31 | 10070 | 高中低压汽包水位合成画面显示 |  | digital
N2DCS.20CDB77XB03 | 10071 | 低压汽包水位A侧超温报警 |  | digital
N2DCS.20CDB77YB01 | 10072 | 低压汽包水位A侧光圈+ |  | digital
N2DCS.20CDB77YB02 | 10073 | 低压汽包水位A侧光圈- |  | digital
N2DCS.20CDB77YB11 | 10074 | 低压汽包水位A侧变倍+ |  | digital
N2DCS.20CDB77YB12 | 10075 | 低压汽包水位A侧变倍- |  | digital
N2DCS.20CDB77YB21 | 10076 | 低压汽包水位A侧焦距+ |  | digital
N2DCS.20CDB77YB22 | 10077 | 低压汽包水位A侧焦距- |  | digital
N2DCS.20CDB78XB03 | 10078 | 低压汽包水位B侧超温报警 |  | digital
N2DCS.20CDB78YB01 | 10079 | 低压汽包水位B侧光圈+ |  | digital
N2DCS.20CDB78YB02 | 10080 | 低压汽包水位B侧光圈- |  | digital
N2DCS.20CDB78YB11 | 10081 | 低压汽包水位B侧变倍+ |  | digital
N2DCS.20CDB78YB12 | 10082 | 低压汽包水位B侧变倍- |  | digital
N2DCS.20CDB78YB21 | 10083 | 低压汽包水位B侧焦距+ |  | digital
N2DCS.20CDB78YB22 | 10084 | 低压汽包水位B侧焦距- |  | digital
N2DCS.20HAD70CL001F | 10085 | 低压汽包左电接点水位计故障 |  | digital
N2DCS.20HAD70CL001H | 10086 | 低压汽包左电接点水位计高I |  | digital
N2DCS.20HAD70CL001HH | 10087 | 低压汽包左电接点水位计高II |  | digital
N2DCS.20HAD70CL001HHH | 10088 | 低压汽包左电接点水位计高III |  | digital
N2DCS.20HAD70CL001L | 10089 | 低压汽包左电接点水位计低I |  | digital
N2DCS.20HAD70CL001LL | 10090 | 低压汽包左电接点水位计低II |  | digital
N2DCS.20HAD70CL001LLL | 10091 | 低压汽包左电接点水位计低III |  | digital
N2DCS.20HAD70CL002F | 10092 | 低压汽包右电接点水位计故障 |  | digital
N2DCS.20HAD70CL002H | 10093 | 低压汽包右电接点水位计高I |  | digital
N2DCS.20HAD70CL002HH | 10094 | 低压汽包右电接点水位计高II |  | digital
N2DCS.20HAD70CL002HHH | 10095 | 低压汽包右电接点水位计高III |  | digital
N2DCS.20HAD70CL002L | 10096 | 低压汽包右电接点水位计低I |  | digital
N2DCS.20HAD70CL002LL | 10097 | 低压汽包右电接点水位计低II |  | digital
N2DCS.20HAD70CL002LLL | 10098 | 低压汽包右电接点水位计低III |  | digital
N2DCS.20HAD70CLHH1 | 10099 | 低压汽包液位1高高高 |  | digital
N2DCS.20HAD70CLHH2 | 10100 | 低压汽包液位2高高高 |  | digital
N2DCS.20HAD70CLHH3 | 10101 | 低压汽包液位3高高高 |  | digital
N2DCS.20HAD70CLLL1 | 10102 | 低压汽包液位1低低低 |  | digital
N2DCS.20HAD70CLLL2 | 10103 | 低压汽包液位2低低低 |  | digital
N2DCS.20HAD70CLLL3 | 10104 | 低压汽包液位3低低低 |  | digital
N2DCS.20HAD74AA401CD | 10105 | 低压蒸发器定排电动门关指令 |  | digital
N2DCS.20HAD74AA401CP | 10106 | 低压蒸发器定排电动门关到位 |  | digital
N2DCS.20HAD74AA401F | 10107 | 低压蒸发器定排电动门故障 |  | digital
N2DCS.20HAD74AA401OD | 10108 | 低压蒸发器定排电动门开指令 |  | digital
N2DCS.20HAD74AA401OP | 10109 | 低压蒸发器定排电动门开到位 |  | digital
N2DCS.20HAD74AA401RC | 10110 | 低压蒸发器定排电动门在远控 |  | digital
N2DCS.20HAD75AA001CD | 10111 | 低压汽包连排电动门关指令 |  | digital
N2DCS.20HAD75AA001CP | 10112 | 低压汽包连排电动门关到位 |  | digital
N2DCS.20HAD75AA001F | 10113 | 低压汽包连排电动门故障 |  | digital
N2DCS.20HAD75AA001OD | 10114 | 低压汽包连排电动门开指令 |  | digital
N2DCS.20HAD75AA001OP | 10115 | 低压汽包连排电动门开到位 |  | digital
N2DCS.20HAD75AA001RC | 10116 | 低压汽包连排电动门在远控 |  | digital
N2DCS.20HAD76AA001CD | 10117 | 低压汽包启动放水电动门关指令 |  | digital
N2DCS.20HAD76AA001CP | 10118 | 低压汽包启动放水电动门关到位 |  | digital
N2DCS.20HAD76AA001F | 10119 | 低压汽包启动放水电动门故障 |  | digital
N2DCS.20HAD76AA001OD | 10120 | 低压汽包启动放水电动门开指令 |  | digital
N2DCS.20HAD76AA001OP | 10121 | 低压汽包启动放水电动门开到位 |  | digital
N2DCS.20HAD76AA001RC | 10122 | 低压汽包启动放水电动门在远控 |  | digital
N2DCS.20HAD76AA002CD | 10123 | 低压汽包启动放水调节门关指令 |  | digital
N2DCS.20HAD76AA002CP | 10124 | 低压汽包启动放水调节门关到位 |  | digital
N2DCS.20HAD76AA002F | 10125 | 低压汽包启动放水调节门故障 |  | digital
N2DCS.20HAD76AA002OD | 10126 | 低压汽包启动放水调节门开指令 |  | digital
N2DCS.20HAD76AA002OP | 10127 | 低压汽包启动放水调节门开到位 |  | digital
N2DCS.20HAD76AA002RC | 10128 | 低压汽包启动放水调节门在远控 |  | digital
N2DCS.20HAH70AA502CD | 10129 | 低压饱和蒸汽放空电动门关指令 |  | digital
N2DCS.20HAH70AA502CP | 10130 | 低压饱和蒸汽放空电动门关到位 |  | digital
N2DCS.20HAH70AA502F | 10131 | 低压饱和蒸汽放空电动门故障 |  | digital
N2DCS.20HAH70AA502OD | 10132 | 低压饱和蒸汽放空电动门开指令 |  | digital
N2DCS.20HAH70AA502OP | 10133 | 低压饱和蒸汽放空电动门开到位 |  | digital
N2DCS.20HAH70AA502RC | 10134 | 低压饱和蒸汽放空电动门在远控 |  | digital
N2DCS.20HAJ80AA502CD | 10135 | 一级再热器进口集箱放空门关指令 |  | digital
N2DCS.20HAJ80AA502CP | 10136 | 一级再热器进口集箱放空门关到位 |  | digital
N2DCS.20HAJ80AA502F | 10137 | 一级再热器进口集箱放空门故障 |  | digital
N2DCS.20HAJ80AA502OD | 10138 | 一级再热器进口集箱放空门开指令 |  | digital
N2DCS.20HAJ80AA502OP | 10139 | 一级再热器进口集箱放空门开到位 |  | digital
N2DCS.20HAJ80AA502RC | 10140 | 一级再热器进口集箱放空门在远控 |  | digital
N2DCS.20HAJ80AA504CD | 10141 | 一级再热器出口集箱放空门关指令 |  | digital
N2DCS.20HAJ80AA504CP | 10142 | 一级再热器出口集箱放空门关到位 |  | digital
N2DCS.20HAJ80AA504F | 10143 | 一级再热器出口集箱放空门故障 |  | digital
N2DCS.20HAJ80AA504OD | 10144 | 一级再热器出口集箱放空门开指令 |  | digital
N2DCS.20HAJ80AA504OP | 10145 | 一级再热器出口集箱放空门开到位 |  | digital
N2DCS.20HAJ80AA504RC | 10146 | 一级再热器出口集箱放空门在远控 |  | digital
N2DCS.20HAJ81AA402CD | 10147 | 一级再热器连接管疏水门关指令 |  | digital
N2DCS.20HAJ81AA402CP | 10148 | 一级再热器连接管疏水门关到位 |  | digital
N2DCS.20HAJ81AA402F | 10149 | 一级再热器连接管疏水门故障 |  | digital
N2DCS.20HAJ81AA402OD | 10150 | 一级再热器连接管疏水门开指令 |  | digital
N2DCS.20HAJ81AA402OP | 10151 | 一级再热器连接管疏水门开到位 |  | digital
N2DCS.20HAJ81AA402RC | 10152 | 一级再热器连接管疏水门在远控 |  | digital
N2DCS.20HAJ81AA404CD | 10153 | 二级再热器进口疏水电动门关指令 |  | digital
N2DCS.20HAJ81AA404CP | 10154 | 二级再热器进口疏水电动门关到位 |  | digital
N2DCS.20HAJ81AA404F | 10155 | 二级再热器进口疏水电动门故障 |  | digital
N2DCS.20HAJ81AA404OD | 10156 | 二级再热器进口疏水电动门开指令 |  | digital
N2DCS.20HAJ81AA404OP | 10157 | 二级再热器进口疏水电动门开到位 |  | digital
N2DCS.20HAJ81AA404RC | 10158 | 二级再热器进口疏水电动门在远控 |  | digital
N2DCS.20LAA70AA501CD | 10159 | #3炉除氧头放空电动门关指令 |  | digital
N2DCS.20LAA70AA501CP | 10160 | #3炉除氧头放空电动门关到位 |  | digital
N2DCS.20LAA70AA501F | 10161 | #3炉除氧头放空电动门故障 |  | digital
N2DCS.20LAA70AA501OD | 10162 | #3炉除氧头放空电动门开指令 |  | digital
N2DCS.20LAA70AA501OP | 10163 | #3炉除氧头放空电动门开到位 |  | digital
N2DCS.20LAA70AA501RC | 10164 | #3炉除氧头放空电动门在远控 |  | digital
N2DCS.20LAB70AA101_MRE | 10165 | #3炉低压汽包液位坏点 |  | digital
N2DCS.20LAF80AA002CD | 10166 | 一级再热器减温水电动门关指令 |  | digital
N2DCS.20LAF80AA002CP | 10167 | 一级再热器减温水电动门关到位 |  | digital
N2DCS.20LAF80AA002F | 10168 | 一级再热器减温水电动门故障 |  | digital
N2DCS.20LAF80AA002OD | 10169 | 一级再热器减温水电动门开指令 |  | digital
N2DCS.20LAF80AA002OP | 10170 | 一级再热器减温水电动门开到位 |  | digital
N2DCS.20LAF80AA002RC | 10171 | 一级再热器减温水电动门在远控 |  | digital
N2DCS.20LAF80AA004CD | 10172 | 二级再热器减温水电动门关指令 |  | digital
N2DCS.20LAF80AA004CP | 10173 | 二级再热器减温水电动门关到位 |  | digital
N2DCS.20LAF80AA004F | 10174 | 二级再热器减温水电动门故障 |  | digital
N2DCS.20LAF80AA004OD | 10175 | 二级再热器减温水电动门开指令 |  | digital
N2DCS.20LAF80AA004OP | 10176 | 二级再热器减温水电动门开到位 |  | digital
N2DCS.20LAF80AA004RC | 10177 | 二级再热器减温水电动门在远控 |  | digital
N2DCS.20LAF80AA101_MRE | 10178 | 一级再热器减温器后温度坏点 |  | digital
N2DCS.20LAF80AA102_MRE | 10179 | 热再主蒸汽温度坏点 |  | digital
N2DCS.20LBA70AA402CD | 10180 | 低压过热器出口疏水电动门关指令 |  | digital
N2DCS.20LBA70AA402CP | 10181 | 低压过热器出口疏水电动门关到位 |  | digital
N2DCS.20LBA70AA402F | 10182 | 低压过热器出口疏水电动门故障 |  | digital
N2DCS.20LBA70AA402OD | 10183 | 低压过热器出口疏水电动门开指令 |  | digital
N2DCS.20LBA70AA402OP | 10184 | 低压过热器出口疏水电动门开到位 |  | digital
N2DCS.20LBA70AA402RC | 10185 | 低压过热器出口疏水电动门在远控 |  | digital
N2DCS.20LBA70AA502CD | 10186 | 低压过热器启动排汽电动门关指令 |  | digital
N2DCS.20LBA70AA502CP | 10187 | 低压过热器启动排汽电动门关到位 |  | digital
N2DCS.20LBA70AA502F | 10188 | 低压过热器启动排汽电动门故障 |  | digital
N2DCS.20LBA70AA502OD | 10189 | 低压过热器启动排汽电动门开指令 |  | digital
N2DCS.20LBA70AA502OP | 10190 | 低压过热器启动排汽电动门开到位 |  | digital
N2DCS.20LBA70AA502RC | 10191 | 低压过热器启动排汽电动门在远控 |  | digital
N2DCS.20LBB80AA502CD | 10192 | 热再主蒸汽启动排气电动门关指令 |  | digital
N2DCS.20LBB80AA502CP | 10193 | 热再主蒸汽启动排气电动门关到位 |  | digital
N2DCS.20LBB80AA502F | 10194 | 热再主蒸汽启动排气电动门故障 |  | digital
N2DCS.20LBB80AA502OD | 10195 | 热再主蒸汽启动排气电动门开指令 |  | digital
N2DCS.20LBB80AA502OP | 10196 | 热再主蒸汽启动排气电动门开到位 |  | digital
N2DCS.20LBB80AA502RC | 10197 | 热再主蒸汽启动排气电动门在远控 |  | digital
N2DCS.20LBC80AA402CD | 10198 | 冷再进口疏水罐疏水电动门关指令 |  | digital
N2DCS.20LBC80AA402CP | 10199 | 冷再进口疏水罐疏水电动门关到位 |  | digital
N2DCS.20LBC80AA402F | 10200 | 冷再进口疏水罐疏水电动门故障 |  | digital
N2DCS.20LBC80AA402OD | 10201 | 冷再进口疏水罐疏水电动门开指令 |  | digital
N2DCS.20LBC80AA402OP | 10202 | 冷再进口疏水罐疏水电动门开到位 |  | digital
N2DCS.20LBC80AA402RC | 10203 | 冷再进口疏水罐疏水电动门在远控 |  | digital
N2DCS.20LBC80CL001 | 10204 | 一级再热器进口疏水罐液位高 |  | digital
N2DCS.20LBG70AA002CD | 10205 | 辅汽至#3炉除氧头电动门关指令 |  | digital
N2DCS.20LBG70AA002CP | 10206 | 辅汽至#3炉除氧头电动门关到位 |  | digital
N2DCS.20LBG70AA002F | 10207 | 辅汽至#3炉除氧头电动门故障 |  | digital
N2DCS.20LBG70AA002OD | 10208 | 辅汽至#3炉除氧头电动门开指令 |  | digital
N2DCS.20LBG70AA002OP | 10209 | 辅汽至#3炉除氧头电动门开到位 |  | digital
N2DCS.20LBG70AA002RC | 10210 | 辅汽至#3炉除氧头电动门在远控 |  | digital
N2DCS.20LBG70AA101_MRE | 10211 | 辅汽至#3炉除氧头调节阀偏差大 |  | digital
N2DCS.20LCC70AA502CD | 10212 | #3炉低压省煤器放空电动门关指令 |  | digital
N2DCS.20LCC70AA502CP | 10213 | #3炉低压省煤器放空电动门关到位 |  | digital
N2DCS.20LCC70AA502F | 10214 | #3炉低压省煤器放空电动门故障 |  | digital
N2DCS.20LCC70AA502OD | 10215 | #3炉低压省煤器放空电动门开指令 |  | digital
N2DCS.20LCC70AA502OP | 10216 | #3炉低压省煤器放空电动门开到位 |  | digital
N2DCS.20LCC70AA502RC | 10217 | #3炉低压省煤器放空电动门在远控 |  | digital
N2DCS.20LCC71AA101_MRE | 10218 | 低省再循环泵出口调阀偏差大 |  | digital
N2DCS.20LCC71AA101OP | 10219 | 低省再循环泵出口调阀开到位 |  | digital
N2DCS.20LCC72AA003CD | 10220 | #1再循环泵出口电动门关指令 |  | digital
N2DCS.20LCC72AA003CP | 10221 | #1再循环泵出口电动门关到位 |  | digital
N2DCS.20LCC72AA003F | 10222 | #1再循环泵出口电动门故障 |  | digital
N2DCS.20LCC72AA003OD | 10223 | #1再循环泵出口电动门开指令 |  | digital
N2DCS.20LCC72AA003OP | 10224 | #1再循环泵出口电动门开到位 |  | digital
N2DCS.20LCC72AA003RC | 10225 | #1再循环泵出口电动门在远控 |  | digital
N2DCS.20LCC72AP001DY | 10226 | #1再循环泵电机加热器投/退指令 |  | digital
N2DCS.20LCC72AP001PF | 10227 | 低压省煤器#1再循环泵综合故障 |  | digital
N2DCS.20LCC72AP001RC | 10228 | 低压省煤器#1再循环泵在远控 |  | digital
N2DCS.20LCC72AP001RD | 10229 | 低压省煤器#1再循环泵启动指令 |  | digital
N2DCS.20LCC72AP001RP | 10230 | 低压省煤器#1再循环泵在运行 |  | digital
N2DCS.20LCC72AP001RP1 | 10231 | #1再循环泵电机电加热器在运行 |  | digital
N2DCS.20LCC72AP001TD | 10232 | 低压省煤器#1再循环泵停止指令 |  | digital
N2DCS.20LCC72AP001TP | 10233 | 低压省煤器#1再循环泵已停止 |  | digital
N2DCS.20LCC72CP101_OK | 10234 | #1再循环泵出口压力正常 |  | digital
N2DCS.20LCC73AA003CD | 10235 | #2再循环泵出口电动门关指令 |  | digital
N2DCS.20LCC73AA003CP | 10236 | #2再循环泵出口电动门关到位 |  | digital
N2DCS.20LCC73AA003F | 10237 | #2再循环泵出口电动门故障 |  | digital
N2DCS.20LCC73AA003OD | 10238 | #2再循环泵出口电动门开指令 |  | digital
N2DCS.20LCC73AA003OP | 10239 | #2再循环泵出口电动门开到位 |  | digital
N2DCS.20LCC73AA003RC | 10240 | #2再循环泵出口电动门在远控 |  | digital
N2DCS.20LCC73AP001DY | 10241 | #2再循环泵电机加热器投/退指令 |  | digital
N2DCS.20LCC73AP001PF | 10242 | 低压省煤器#2再循环泵综合故障 |  | digital
N2DCS.20LCC73AP001RC | 10243 | 低压省煤器#2再循环泵在远控 |  | digital
N2DCS.20LCC73AP001RD | 10244 | 低压省煤器#2再循环泵启动指令 |  | digital
N2DCS.20LCC73AP001RP | 10245 | 低压省煤器#2再循环泵在运行 |  | digital
N2DCS.20LCC73AP001RP1 | 10246 | #2再循环泵电机电加热器在运行 |  | digital
N2DCS.20LCC73AP001TD | 10247 | 低压省煤器#2再循环泵停止指令 |  | digital
N2DCS.20LCC73AP001TP | 10248 | 低压省煤器#2再循环泵已停止 |  | digital
N2DCS.20LCC73CP101_OK | 10249 | #2再循环泵出口压力正常 |  | digital
N2DCS.20LCQ74AA101_MRE | 10250 | #3炉连排至定排气动调节阀偏差大 |  | digital
N2DCS.HRSGPRCT | 10251 | #1余热锅炉保护动作 |  | digital
N2DCS.LP_DRN_ACD | 10252 | 低压系统疏水门自动关 |  | digital
N2DCS.LPDRUMCP_MRE | 10253 | 低压汽包压力坏点 |  | digital
N2DCS.LPDRUMCTD_MRE | 10254 | 低压汽包下外壁温坏点 |  | digital
N2DCS.LPDRUMCTU_MRE | 10255 | 低压汽包上外壁温坏点 |  | digital
N2DCS.LPDRUMLVL_AL | 10256 | 低压汽包液位（计算后）报警 |  | digital
N2DCS.LPDRUMLVL_HI | 10257 | 低压汽包液位（计算后）高 |  | digital
N2DCS.LPDRUMLVL_HII | 10258 | 低压汽包液位（计算后）高高 |  | digital
N2DCS.LPDRUMLVL_HIII | 10259 | 低压汽包液位（计算后）高高高 |  | digital
N2DCS.LPDRUMLVL_HIII1 | 10260 | 低压汽包液位1（计算后）高高高 |  | digital
N2DCS.LPDRUMLVL_HIII2 | 10261 | 低压汽包液位2（计算后）高高高 |  | digital
N2DCS.LPDRUMLVL_HIII3 | 10262 | 低压汽包液位3（计算后）高高高 |  | digital
N2DCS.LPDRUMLVL_LII | 10263 | 低压汽包液位（计算后）低低 |  | digital
N2DCS.LPDRUMLVL_LIII | 10264 | 低压汽包液位（计算后）低低低 |  | digital
N2DCS.LPDRUMLVL_LIII1 | 10265 | 低压汽包液位1（计算后）低低低 |  | digital
N2DCS.LPDRUMLVL_LIII2 | 10266 | 低压汽包液位2（计算后）低低低 |  | digital
N2DCS.LPDRUMLVL_LIII3 | 10267 | 低压汽包液位3（计算后）低低低 |  | digital
N2DCS.LPDRUMLVL_MRE | 10268 | 低压汽包液位（计算后）坏点 |  | digital
N2DCS.LPDSTCF_MRE | 10269 | 低压主蒸汽流量（计算后）坏点 |  | digital
N2DCS.LPDSTCP_MRE | 10270 | 低压主蒸汽压力坏点 |  | digital
N2DCS.LPDSTCP_OK | 10271 | 低压主蒸汽压力正常（高于0.1MPa |  | digital
N2DCS.LPDSTCT_MRE | 10272 | 低压主蒸汽温度坏点 |  | digital
N2DCS.LPDWTCF_MRE | 10273 | 低压汽包给水流量(计算后)坏点 |  | digital
N2DCS.LPDWTCF_NORM | 10274 | 低压汽包给水流量(计算后)正常 |  | digital
N2DCS.LPDWTCT_MRE | 10275 | 低压省煤器出口温度坏点 |  | digital
N2DCS.LPECON_SEQFINSH | 10276 | 低省再循环系统启顺控已完成 |  | digital
N2DCS.LPECON_SEQST_OK | 10277 | 低省再循环系统已投运 |  | digital
N2DCS.LPECON_SEQST_TEST | 10278 | 凝结水循环水系统程控仿真 |  | digital
N2DCS.LPECONPA_OK | 10279 | #1低省再循环泵运行正常 |  | digital
N2DCS.LPECONPA_STRPEM | 10280 | #1低省再循环泵启动允许 |  | digital
N2DCS.LPECONPA_TEMALM | 10281 | #1低省再循环泵超温保护报警 |  | digital
N2DCS.LPECONPA_TEMALMCUT | 10282 | #1低省再循环泵温度报警功能解除 |  | digital
N2DCS.LPECONPA_TEMPMT | 10283 | #1低省再循环泵温度允许 |  | digital
N2DCS.LPECONPA_TP | 10284 | #1低省再循环泵保护跳闸信号 |  | digital
N2DCS.LPECONPAMANSTOP | 10285 | #1低省再循环泵手动跳闸 |  | digital
N2DCS.LPECONPB_OK | 10286 | #2低省再循环泵运行正常 |  | digital
N2DCS.LPECONPB_STRPEM | 10287 | #2低省再循环泵启动允许 |  | digital
N2DCS.LPECONPB_TEMALM | 10288 | #2低省再循环泵超温保护报警 |  | digital
N2DCS.LPECONPB_TEMALMCUT | 10289 | #2低省再循环泵温度报警功能解除 |  | digital
N2DCS.LPECONPB_TEMPMT | 10290 | #2低省再循环泵温度允许 |  | digital
N2DCS.LPECONPB_TP | 10291 | #2低省再循环泵保护跳闸信号 |  | digital
N2DCS.LPECONPBMANSTOP | 10292 | #2低省再循环泵手动跳闸 |  | digital
N2DCS.LPFW_SEQST_KB1G | 10293 | 手动确认低压给水管道系统已排空 |  | digital
N2DCS.LPFW_SEQSTFINSH | 10294 | 低压汽包上水顺控已完成 |  | digital
N2DCS.LPFW3ELE | 10295 | 低压给水在三冲量调节 |  | digital
N2DCS.LPMS_SEQSTFINISH | 10296 | 低压主汽升温升压顺控已完成 |  | digital
N2DCS.ONE7 | 10297 | 开关量1 |  | digital
N2DCS.RH2_DRN_ACD | 10298 | 一级再热器进口疏水电动门自动关 |  | digital
N2DCS.RH2INSTCT_MRE | 10299 | 一级再热器减温器后温度坏点 |  | digital
N2DCS.RH2OUTSTCP_MRE | 10300 | 二级再热器出口蒸汽压力坏点 |  | digital
N2DCS.RH2OUTSTCT_MRE | 10301 | 二级再热器出口蒸汽温度坏点 |  | digital
N2DCS.ZERO7 | 10302 | 开关量0 |  | digital
N2DCS.20LAF80AA101_AUTO | 10303 | 一级再热器减温水调节阀在自动 |  | digital
N2DCS.20LAF80AA102_AUTO | 10304 | 二级再热器减温水调节阀在自动 |  | digital
N2DCS.BALM001 | 10305 | #3炉高压给水泵异常跳闸 |  | digital
N2DCS.BALM002 | 10306 | #3炉高压给水泵超温报警 |  | digital
N2DCS.BALM003 | 10307 | #3炉高压汽包液位（计算后）高高 |  | digital
N2DCS.BALM004 | 10308 | #3炉高压汽包液位（计算后）低低 |  | digital
N2DCS.BALM005 | 10309 | #3炉高压省煤器出口水温高 |  | digital
N2DCS.BALM006 | 10310 | 高压汽包上、下外壁温差大于60 |  | digital
N2DCS.BALM007 | 10311 | #3炉高压主蒸汽压力高（13.5） |  | digital
N2DCS.BALM008 | 10312 | #3炉中压给水泵异常跳闸 |  | digital
N2DCS.BALM009 | 10313 | #3炉中压给水泵超温报警 |  | digital
N2DCS.BALM010 | 10314 | #3炉中压汽包液位（计算后）高高 |  | digital
N2DCS.BALM011 | 10315 | #3炉中压汽包液位（计算后）低低 |  | digital
N2DCS.BALM012 | 10316 | 中压汽包上、下外壁温差大于60 |  | digital
N2DCS.BALM013 | 10317 | #3炉热再主蒸汽压力高（3.3） |  | digital
N2DCS.BALM014 | 10318 | #3炉低压汽包液位（计算后）高高 |  | digital
N2DCS.BALM015 | 10319 | #3炉低压汽包液位（计算后）低低 |  | digital
N2DCS.BALM016 | 10320 | 低压汽包上、下外壁温差大于60 |  | digital
N2DCS.BALM017 | 10321 | #3炉低省再循环泵异常跳闸 |  | digital
N2DCS.BALM018 | 10322 | #3炉低省再循环泵超温报警 |  | digital
N2DCS.BALM019 | 10323 | #3炉入口烟气压力高（大于6KPa） |  | digital
N2DCS.BALM020 | 10324 | #3炉烟囱出口挡板未在全开位置 |  | digital
N2DCS.BALM021 | 10325 | 高压给水泵稀油站润滑油泵跳闸 |  | digital
N2DCS.BALM022 | 10326 | 调压站火警阀未全开或故障 |  | digital
N2DCS.BALM023 | 10327 | #3炉保护跳闸信号 |  | digital
N2DCS.BALM024 | 10328 | #4机跳闸 |  | digital
N2DCS.BALM025 | 10329 | #3机跳闸 |  | digital
N2DCS.BALM026 | 10330 | #4机跳闸 |  | digital
N2DCS.BALM027 | 10331 | #3机跳闸 |  | digital
N2DCS.BALMALL | 10332 | #3炉光字牌报警汇总 |  | digital
N2DCS.BALMUNACK | 10333 | #3炉光字牌报警手动确认指令 |  | digital
N2DCS.LPDRUMCTC | 10334 | 低压汽包上、下外壁温差小于50 |  | digital
N2DCS.LPFW3ELE1 | 10335 | 低压给水在单冲量调节 |  | digital
N2DCS.TBALMALL | 10336 | 机炉光字牌报警汇总 |  | digital
N2DCS.TBALMUNACK | 10337 | 机炉光字牌报警手动确认指令 |  | digital
N2DCS.20CDB76XB11 | 10338 | 中压汽包水位摄像综合故障 |  | digital
N2DCS.20CDB76YB11 | 10339 | 中压汽包液位A侧画面显示 |  | digital
N2DCS.20CDB76YB12 | 10340 | 中压汽包液位B侧画面显示 |  | digital
N2DCS.20CDB76YB13 | 10341 | 中压汽包液位AB侧合成画面显示 |  | digital
N2DCS.20CDB76YB23 | 10342 | 高汽包液位AB侧合成画面显示 |  | digital
N2DCS.20CDB79XB03 | 10343 | 中压汽包液位A侧超温报警 |  | digital
N2DCS.20CDB79YB01 | 10344 | 中压汽包液位A侧光圈+ |  | digital
N2DCS.20CDB79YB02 | 10345 | 中压汽包液位A侧光圈- |  | digital
N2DCS.20CDB79YB11 | 10346 | 中压汽包液位A侧变倍+ |  | digital
N2DCS.20CDB79YB12 | 10347 | 中压汽包液位A侧变倍- |  | digital
N2DCS.20CDB79YB21 | 10348 | 中压汽包液位A侧焦距+ |  | digital
N2DCS.20CDB79YB22 | 10349 | 中压汽包液位A侧焦距- |  | digital
N2DCS.20CDB80XB03 | 10350 | 中压汽包液位B侧超温报警 |  | digital
N2DCS.20CDB80YB01 | 10351 | 中压汽包液位B侧光圈+ |  | digital
N2DCS.20CDB80YB02 | 10352 | 中压汽包液位B侧光圈- |  | digital
N2DCS.20CDB80YB11 | 10353 | 中压汽包液位B侧变倍+ |  | digital
N2DCS.20CDB80YB12 | 10354 | 中压汽包液位B侧变倍- |  | digital
N2DCS.20CDB80YB21 | 10355 | 中压汽包液位B侧焦距+ |  | digital
N2DCS.20CDB80YB22 | 10356 | 中压汽包液位B侧焦距- |  | digital
N2DCS.20CNSRPRCTACT1DI | 10357 | 凝汽器保护动作通道1 |  | digital
N2DCS.20CNSRPRCTACT2DI | 10358 | 凝汽器保护动作通道2 |  | digital
N2DCS.20CNSRPRCTACT3DI | 10359 | 凝汽器保护动作通道3 |  | digital
N2DCS.20CSB51PF | 10360 | 锅炉热力配电柜电源消失 |  | digital
N2DCS.20HAD70CLHH1DI | 10361 | 低压汽包液位1（计算后）高高高 |  | digital
N2DCS.20HAD70CLHH2DI | 10362 | 低压汽包液位2（计算后）高高高 |  | digital
N2DCS.20HAD70CLHH3DI | 10363 | 低压汽包液位3（计算后）高高高 |  | digital
N2DCS.20HAD70CLLL1DI | 10364 | 低压汽包液位1（计算后）低低低 |  | digital
N2DCS.20HAD70CLLL2DI | 10365 | 低压汽包液位2（计算后）低低低 |  | digital
N2DCS.20HAD70CLLL3DI | 10366 | 低压汽包液位3（计算后）低低低 |  | digital
N2DCS.20HAD80CL001F | 10367 | 中压汽包左电接点液位计故障 |  | digital
N2DCS.20HAD80CL001H | 10368 | 中压汽包左电接点液位计高I |  | digital
N2DCS.20HAD80CL001HH | 10369 | 中压汽包左电接点液位计高II |  | digital
N2DCS.20HAD80CL001HHH | 10370 | 中压汽包左电接点液位计高III |  | digital
N2DCS.20HAD80CL001L | 10371 | 中压汽包左电接点液位计低I |  | digital
N2DCS.20HAD80CL001LL | 10372 | 中压汽包左电接点液位计低II |  | digital
N2DCS.20HAD80CL001LLL | 10373 | 中压汽包左电接点液位计低III |  | digital
N2DCS.20HAD80CL002F | 10374 | 中压汽包右电接点液位计故障 |  | digital
N2DCS.20HAD80CL002H | 10375 | 中压汽包右电接点液位计高I |  | digital
N2DCS.20HAD80CL002HH | 10376 | 中压汽包右电接点液位计高II |  | digital
N2DCS.20HAD80CL002HHH | 10377 | 中压汽包右电接点液位计高III |  | digital
N2DCS.20HAD80CL002L | 10378 | 中压汽包右电接点液位计低I |  | digital
N2DCS.20HAD80CL002LL | 10379 | 中压汽包右电接点液位计低II |  | digital
N2DCS.20HAD80CL002LLL | 10380 | 中压汽包右电接点液位计低III |  | digital
N2DCS.20HAD84AA401CD | 10381 | 中压蒸发器定排电动门关指令 |  | digital
N2DCS.20HAD84AA401CP | 10382 | 中压蒸发器定排电动门关到位 |  | digital
N2DCS.20HAD84AA401F | 10383 | 中压蒸发器定排电动门故障 |  | digital
N2DCS.20HAD84AA401OD | 10384 | 中压蒸发器定排电动门开指令 |  | digital
N2DCS.20HAD84AA401OP | 10385 | 中压蒸发器定排电动门开到位 |  | digital
N2DCS.20HAD84AA401RC | 10386 | 中压蒸发器定排电动门在远控 |  | digital
N2DCS.20HAD85AA001CD | 10387 | 中压汽包连排电动门关指令 |  | digital
N2DCS.20HAD85AA001CP | 10388 | 中压汽包连排电动门关到位 |  | digital
N2DCS.20HAD85AA001F | 10389 | 中压汽包连排电动门故障 |  | digital
N2DCS.20HAD85AA001OD | 10390 | 中压汽包连排电动门开指令 |  | digital
N2DCS.20HAD85AA001OP | 10391 | 中压汽包连排电动门开到位 |  | digital
N2DCS.20HAD85AA001RC | 10392 | 中压汽包连排电动门在远控 |  | digital
N2DCS.20HAD86AA001CD | 10393 | 中压汽包启动放水电动门关指令 |  | digital
N2DCS.20HAD86AA001CP | 10394 | 中压汽包启动放水电动门关到位 |  | digital
N2DCS.20HAD86AA001F | 10395 | 中压汽包启动放水电动门故障 |  | digital
N2DCS.20HAD86AA001OD | 10396 | 中压汽包启动放水电动门开指令 |  | digital
N2DCS.20HAD86AA001OP | 10397 | 中压汽包启动放水电动门开到位 |  | digital
N2DCS.20HAD86AA001RC | 10398 | 中压汽包启动放水电动门在远控 |  | digital
N2DCS.20HAD86AA002CD | 10399 | 中压汽包启动放水调节门关指令 |  | digital
N2DCS.20HAD86AA002CP | 10400 | 中压汽包启动放水调节门关到位 |  | digital
N2DCS.20HAD86AA002F | 10401 | 中压汽包启动放水调节门故障 |  | digital
N2DCS.20HAD86AA002OD | 10402 | 中压汽包启动放水调节门开指令 |  | digital
N2DCS.20HAD86AA002OP | 10403 | 中压汽包启动放水调节门开到位 |  | digital
N2DCS.20HAD86AA002RC | 10404 | 中压汽包启动放水调节门在远控 |  | digital
N2DCS.20HAD90CLHH1DI | 10405 | 高压汽包液位1（计算后）高高高 |  | digital
N2DCS.20HAD90CLHH2DI | 10406 | 高压汽包液位2（计算后）高高高 |  | digital
N2DCS.20HAD90CLHH3DI | 10407 | 高压汽包液位3（计算后）高高高 |  | digital
N2DCS.20HAD90CLLL1DI | 10408 | 高压汽包液位1（计算后）低低低 |  | digital
N2DCS.20HAD90CLLL2DI | 10409 | 高压汽包液位2（计算后）低低低 |  | digital
N2DCS.20HAD90CLLL3DI | 10410 | 高压汽包液位3（计算后）低低低 |  | digital
N2DCS.20HAH80AA502CD | 10411 | 中压饱和蒸汽放空电动门关到位 |  | digital
N2DCS.20HAH80AA502CP | 10412 | 中压饱和蒸汽放空电动门关到位 |  | digital
N2DCS.20HAH80AA502F | 10413 | 中压饱和蒸汽放空电动门故障 |  | digital
N2DCS.20HAH80AA502OD | 10414 | 中压饱和蒸汽放空电动门开指令 |  | digital
N2DCS.20HAH80AA502OP | 10415 | 中压饱和蒸汽放空电动门开到位 |  | digital
N2DCS.20HAH80AA502RC | 10416 | 中压饱和蒸汽放空电动门在远控 |  | digital
N2DCS.20HNE70AA001CD | 10417 | 烟囱出口挡板关指令 |  | digital
N2DCS.20HNE70AA001CP | 10418 | 烟囱出口挡板关到位 |  | digital
N2DCS.20HNE70AA001F | 10419 | 烟囱出口挡板故障 |  | digital
N2DCS.20HNE70AA001OD | 10420 | 烟囱出口挡板开指令 |  | digital
N2DCS.20HNE70AA001OP | 10421 | 烟囱出口挡板开到位 |  | digital
N2DCS.20HNE70AA001RC | 10422 | 烟囱出口挡板远控 |  | digital
N2DCS.20LAB81AA001CD | 10423 | #1中压给水泵出口电动门关指令 |  | digital
N2DCS.20LAB81AA001CP | 10424 | #1中压给水泵出口电动门关到位 |  | digital
N2DCS.20LAB81AA001F | 10425 | #1中压给水泵出口电动门故障 |  | digital
N2DCS.20LAB81AA001OD | 10426 | #1中压给水泵出口电动门开指令 |  | digital
N2DCS.20LAB81AA001OP | 10427 | #1中压给水泵出口电动门开到位 |  | digital
N2DCS.20LAB81AA001RC | 10428 | #1中压给水泵出口电动门在远控 |  | digital
N2DCS.20LAB81AP001FW | 10429 | #1中压给水泵工作位置 |  | digital
N2DCS.20LAB81AP001PF | 10430 | #1中压给水泵综合故障 |  | digital
N2DCS.20LAB81AP001PS | 10431 | #1中压给水泵保护动作 |  | digital
N2DCS.20LAB81AP001RC | 10432 | #1中压给水泵在远控 |  | digital
N2DCS.20LAB81AP001RD | 10433 | #1中压给水泵启动指令 |  | digital
N2DCS.20LAB81AP001RP | 10434 | #1中压给水泵在运行 |  | digital
N2DCS.20LAB81AP001SW | 10435 | #1中压给水泵试验位置 |  | digital
N2DCS.20LAB81AP001TD | 10436 | #1中压给水泵停止指令 |  | digital
N2DCS.20LAB81AP001TP | 10437 | #1中压给水泵已停止 |  | digital
N2DCS.20LAB81AP001TP1 | 10438 | #1中压给水泵已停止 |  | digital
N2DCS.20LAB82AP001TP1 | 10439 | #2中压给水泵已停止 |  | digital
N2DCS.20LAB82AP001TP2DI | 10440 | #2中压给水泵已停止 |  | digital
N2DCS.20LAB83AA101_AUTO | 10441 | 中压给水调节阀在自动 |  | digital
N2DCS.20LAB83AA101_MRE | 10442 | 中压给水调节阀报警 |  | digital
N2DCS.20LAB91AA001CD | 10443 | #1高压给水泵出口电动门关指令 |  | digital
N2DCS.20LAB91AA001CP | 10444 | #1高压给水泵出口电动门关到位 |  | digital
N2DCS.20LAB91AA001F | 10445 | #1高压给水泵出口电动门故障 |  | digital
N2DCS.20LAB91AA001OD | 10446 | #1高压给水泵出口电动门开指令 |  | digital
N2DCS.20LAB91AA001OP | 10447 | #1高压给水泵出口电动门开到位 |  | digital
N2DCS.20LAB91AA001RC | 10448 | #1高压给水泵出口电动门在远控 |  | digital
N2DCS.20LAB91AP001FW | 10449 | #1高压给水泵工作位置 |  | digital
N2DCS.20LAB91AP001PF | 10450 | #1高压给水泵综合故障 |  | digital
N2DCS.20LAB91AP001PS | 10451 | #1高压给水泵电气保护动作 |  | digital
N2DCS.20LAB91AP001RC | 10452 | #1高压给水泵在远控 |  | digital
N2DCS.20LAB91AP001RP | 10453 | #1高压给水泵在运行 |  | digital
N2DCS.20LAB91AP001SW | 10454 | #1高压给水泵试验位置 |  | digital
N2DCS.20LAB91AP001TP | 10455 | #1高压给水泵已停止 |  | digital
N2DCS.20LAB91AP001TP1 | 10456 | #1高压给水泵已停止 |  | digital
N2DCS.20LAB91CS001 | 10457 | #1高压给水泵反转 |  | digital
N2DCS.20LAB92AP001TP1 | 10458 | #2高压给水泵已停止 |  | digital
N2DCS.20LAB92AP001TP2DI | 10459 | #2高压给水泵已停止 |  | digital
N2DCS.20LAC91AP001EH004 | 10460 | #1高压给水泵高压柜QS1合闸位置 |  | digital
N2DCS.20LAC91AP001EH005 | 10461 | #1高压给水泵高压柜QS3合闸位置 |  | digital
N2DCS.20LAC91AP001RD | 10462 | #1高压给水泵6KV开关合闸指令 |  | digital
N2DCS.20LAC91AP001TD | 10463 | #1高压给水泵6KV开关分闸指令 |  | digital
N2DCS.20LAC91G10001RP1 | 10464 | #1高压给水泵变频运行指示 |  | digital
N2DCS.20LAC91GX0001RP1 | 10465 | #1高压给水泵变频器在运行 |  | digital
N2DCS.20LBA80AA001CD | 10466 | 中压主蒸汽电动门关指令 |  | digital
N2DCS.20LBA80AA001CP | 10467 | 中压主蒸汽电动门关到位 |  | digital
N2DCS.20LBA80AA001F | 10468 | 中压主蒸汽电动门故障 |  | digital
N2DCS.20LBA80AA001OD | 10469 | 中压主蒸汽电动门开指令 |  | digital
N2DCS.20LBA80AA001OP | 10470 | 中压主蒸汽电动门开到位 |  | digital
N2DCS.20LBA80AA001RC | 10471 | 中压主蒸汽电动门在远控 |  | digital
N2DCS.20LBA80AA402CD | 10472 | 中压主蒸汽疏水至定排门关指令 |  | digital
N2DCS.20LBA80AA402CP | 10473 | 中压主蒸汽疏水至定排门关到位 |  | digital
N2DCS.20LBA80AA402F | 10474 | 中压主蒸汽疏水至定排门故障 |  | digital
N2DCS.20LBA80AA402OD | 10475 | 中压主蒸汽疏水至定排门开指令 |  | digital
N2DCS.20LBA80AA402OP | 10476 | 中压主蒸汽疏水至定排门开到位 |  | digital
N2DCS.20LBA80AA402RC | 10477 | 中压主蒸汽疏水至定排门在远控 |  | digital
N2DCS.20LBA80AA502CD | 10478 | 中压主蒸汽启动排汽电动门关指令 |  | digital
N2DCS.20LBA80AA502CP | 10479 | 中压主蒸汽启动排汽电动门关到位 |  | digital
N2DCS.20LBA80AA502F | 10480 | 中压主蒸汽启动排汽电动门故障 |  | digital
N2DCS.20LBA80AA502OD | 10481 | 中压主蒸汽启动排汽电动门开指令 |  | digital
N2DCS.20LBA80AA502OP | 10482 | 中压主蒸汽启动排汽电动门开到位 |  | digital
N2DCS.20LBA80AA502RC | 10483 | 中压主蒸汽启动排汽电动门在远控 |  | digital
N2DCS.20MAY01EZ011_XK463 | 10484 | #3机遮断系统已遮断3 |  | digital
N2DCS.20MAY01EZ011_XK464 | 10485 | #3机遮断系统已遮断4 |  | digital
N2DCS.20MAY01EZ011_XK465 | 10486 | #3机遮断系统已遮断5 |  | digital
N2DCS.20QFB80CD | 10487 | #3炉压缩空气净化分配装置停指令 |  | digital
N2DCS.20QFB80OD | 10488 | #3炉压缩空气净化分配装置启指令 |  | digital
N2DCS.20QFB80P | 10489 | #3炉压缩空气净化分配装置在运行 |  | digital
N2DCS.20QFB80RC | 10490 | #3炉压缩空气净化分配装置在远控 |  | digital
N2DCS.20XAV91CL001 | 10491 | #1高压给水泵稀油站油箱液位低 |  | digital
N2DCS.20XAV91CP001 | 10492 | #1高压给水泵稀油站滤网差压高低 |  | digital
N2DCS.20XAV91GH001AP1RD | 10493 | #1高压给水泵稀油站#1油泵启指令 |  | digital
N2DCS.20XAV91GH001AP1TD | 10494 | #1高压给水泵稀油站#1油泵停指令 |  | digital
N2DCS.20XAV91GH001AP2RD | 10495 | #1高压给水泵稀油站#2油泵启指令 |  | digital
N2DCS.20XAV91GH001AP2TD | 10496 | #1高压给水泵稀油站#2油泵停指令 |  | digital
N2DCS.20XAV91GH001HTRD | 10497 | #1高压给水泵稀油站加热器启指令 |  | digital
N2DCS.20XAV91GH001HTTD | 10498 | #1高压给水泵稀油站加热器停指令 |  | digital
N2DCS.20XAV91GH001PF | 10499 | #1高给泵稀油站重大故障停主机 |  | digital
N2DCS.20XAV91GH001RC1 | 10500 | #1高压给水泵稀油站远程备妥 |  | digital
N2DCS.20XAV91GH001RC2 | 10501 | #1高压给水泵稀油站允许主机启动 |  | digital
N2DCS.20XAV91GH001RD1 | 10502 | #1高压给水泵稀油站远程驱动 |  | digital
N2DCS.20XAV91GH001RD2 | 10503 | #1高压给水泵在运行（送至稀油站 |  | digital
N2DCS.20XAV91GH001RP1 | 10504 | #1高给泵稀油站#1油泵在运行 |  | digital
N2DCS.20XAV91GH001RP2 | 10505 | #1高给泵稀油站#2油泵在运行 |  | digital
N2DCS.20XAV91GH001RP3 | 10506 | #1高给泵稀油站电加热器已投入 |  | digital
N2DCS.20XAV91GH002PF1 | 10507 | #1高压给水泵稀油站轻故障 |  | digital
N2DCS.HPFWPA_OILP_RUN | 10508 | 高压给水泵A润滑油泵运行 |  | digital
N2DCS.HPFWPA_RUN | 10509 | #1高压给水泵在运行(工频或变频) |  | digital
N2DCS.HPFWPA_STOP | 10510 | #1高压给水泵已停止(工频和变频) |  | digital
N2DCS.HPFWPA_STRPEM | 10511 | #1高压给水泵启动允许 |  | digital
N2DCS.HPFWPA_TEMPEM | 10512 | #1高压给水泵温度允许 |  | digital
N2DCS.HPFWPA_TEMPRT | 10513 | #1高压给水泵温度保护信号 |  | digital
N2DCS.HPFWPA_TP | 10514 | #1高压给水泵跳闸信号 |  | digital
N2DCS.HPFWPAMANSTOP | 10515 | #1高压给水泵手动停止指令 |  | digital
N2DCS.HPFWPARUN | 10516 | #1高压给水泵在运行 |  | digital
N2DCS.IPDRUMCP_MRE | 10517 | 中压汽包压力坏点 |  | digital
N2DCS.IPDRUMCTD_MRE | 10518 | 中压汽包下外壁温坏点 |  | digital
N2DCS.IPDRUMCTU_MRE | 10519 | 中压汽包上外壁温坏点 |  | digital
N2DCS.IPDRUMLVL_AL | 10520 | 中压汽包液位（计算后）报警 |  | digital
N2DCS.IPDRUMLVL_HI | 10521 | 中压汽包液位（计算后）高 |  | digital
N2DCS.IPDRUMLVL_HII | 10522 | 中压汽包液位（计算后）高高 |  | digital
N2DCS.IPDRUMLVL_HIII | 10523 | 中压汽包液位（计算后）高高高 |  | digital
N2DCS.IPDRUMLVL_HIII1 | 10524 | 中压汽包液位1（计算后）高高高 |  | digital
N2DCS.IPDRUMLVL_HIII2 | 10525 | 中压汽包液位2（计算后）高高高 |  | digital
N2DCS.IPDRUMLVL_HIII3 | 10526 | 中压汽包液位3（计算后）高高高 |  | digital
N2DCS.IPDRUMLVL_LII | 10527 | 中压汽包液位（计算后）低低 |  | digital
N2DCS.IPDRUMLVL_LIII | 10528 | 中压汽包液位（计算后）低低低 |  | digital
N2DCS.IPDRUMLVL_LIII1 | 10529 | 中压汽包液位1（计算后）低低低 |  | digital
N2DCS.IPDRUMLVL_LIII2 | 10530 | 中压汽包液位2（计算后）低低低 |  | digital
N2DCS.IPDRUMLVL_LIII3 | 10531 | 中压汽包液位3（计算后）低低低 |  | digital
N2DCS.IPDRUMLVL_MRE | 10532 | 中压汽包液位（计算后）坏点 |  | digital
N2DCS.IPDRUMLVLDEVHI | 10533 | 中压给水调节阀设定、反馈偏差大 |  | digital
N2DCS.IPDSTCF_MRE | 10534 | 中压主蒸汽流量（计算后）坏点 |  | digital
N2DCS.IPDSTCP_MRE | 10535 | 中压主蒸汽压力坏点 |  | digital
N2DCS.IPDSTCT_MRE | 10536 | 中压主蒸汽温度坏点 |  | digital
N2DCS.IPDWTCF_MRE | 10537 | 中压给水流量（计算后）坏点 |  | digital
N2DCS.IPDWTCF_NORM | 10538 | 中压给水流量正常（大于80t/h） |  | digital
N2DCS.IPDWTCT_MRE | 10539 | 中压给水温度坏点 |  | digital
N2DCS.IPFW_SEQSTFINSH | 10540 | 中压汽包上水顺控已完成 |  | digital
N2DCS.IPFW3ELE | 10541 | 中压给水在三冲量调节 |  | digital
N2DCS.IPFWACK | 10542 | 中压汽包上水排空确认 |  | digital
N2DCS.IPFWACK_PMT | 10543 | Ovation Control Builder |  | digital
N2DCS.IPFWPA_PRCT | 10544 | 中压给水泵A保护跳闸 |  | digital
N2DCS.IPFWPA_STRPEM | 10545 | #1中压给水泵启动允许 |  | digital
N2DCS.IPFWPA_TEMPEM | 10546 | #1中压给水泵温度允许 |  | digital
N2DCS.IPFWPA_TEMPRT | 10547 | #1中压给水泵温度保护信号 |  | digital
N2DCS.IPFWPA_TP | 10548 | #1中压给水泵保护跳闸指令 |  | digital
N2DCS.IPFWPAMANSTOP | 10549 | #1中压给水泵手动停止指令 |  | digital
N2DCS.IPMS_SEQSTFINISH | 10550 | 中压主汽升温升压顺控已完成 |  | digital
N2DCS.ONE8 | 10551 | 开关量1 |  | digital
N2DCS.ZERO8 | 10552 | 开关量0 |  | digital
N2DCS.CLOSEZHONGYAPAIOK | 10553 | Ovation Control Builder |  | digital
N2DCS.CZYLMZI | 10554 | Ovation Control Builder |  | digital
N2DCS.GYGSPMPABP | 10555 | #1高压给水泵在变频位置 |  | digital
N2DCS.GYGSPMPAGP | 10556 | #1高压给水泵在工频位置 |  | digital
N2DCS.HPFWPA_SEQBPSTFINISH | 10557 | #1高压给水泵变频启顺控已完成 |  | digital
N2DCS.HPFWPA_SEQSTFINISH | 10558 | #1高压给水泵工频启顺控已完成 |  | digital
N2DCS.IPFW3ELE1 | 10559 | 中压给水在单冲量调节 |  | digital
N2DCS.20CDB76XB21 | 10560 | 高压汽包液位摄像综合故障 |  | digital
N2DCS.20CDB76YB21 | 10561 | 高压汽包液位A侧画面显示 |  | digital
N2DCS.20CDB76YB22 | 10562 | 高压汽包液位B侧画面显示 |  | digital
N2DCS.20CDB81XB03 | 10563 | 高压汽包液位A侧超温报警 |  | digital
N2DCS.20CDB81YB01 | 10564 | 高压汽包液位A侧光圈+ |  | digital
N2DCS.20CDB81YB02 | 10565 | 高压汽包液位A侧光圈- |  | digital
N2DCS.20CDB81YB11 | 10566 | 高压汽包液位A侧变倍+ |  | digital
N2DCS.20CDB81YB12 | 10567 | 高压汽包液位A侧变倍- |  | digital
N2DCS.20CDB81YB21 | 10568 | 高压汽包液位A侧焦距+ |  | digital
N2DCS.20CDB81YB22 | 10569 | 高压汽包液位A侧焦距- |  | digital
N2DCS.20CDB82XB03 | 10570 | 高压汽包液位B侧超温报警 |  | digital
N2DCS.20CDB82YB01 | 10571 | 高压汽包液位B侧光圈+ |  | digital
N2DCS.20CDB82YB02 | 10572 | 高压汽包液位B侧光圈- |  | digital
N2DCS.20CDB82YB11 | 10573 | 高压汽包液位B侧变倍+ |  | digital
N2DCS.20CDB82YB12 | 10574 | 高压汽包液位B侧变倍- |  | digital
N2DCS.20CDB82YB21 | 10575 | 高压汽包液位B侧焦距+ |  | digital
N2DCS.20CDB82YB22 | 10576 | 高压汽包液位B侧焦距- |  | digital
N2DCS.20GUC01GH001PF | 10577 | #3炉电梯井集水坑液位高报警 |  | digital
N2DCS.20HAC90AA502CD | 10578 | 高压省煤器放空气电动门关指令 |  | digital
N2DCS.20HAC90AA502CP | 10579 | 高压省煤器放空气电动门关到位 |  | digital
N2DCS.20HAC90AA502F | 10580 | 高压省煤器放空气电动门故障 |  | digital
N2DCS.20HAC90AA502OD | 10581 | 高压省煤器放空气电动门开指令 |  | digital
N2DCS.20HAC90AA502OP | 10582 | 高压省煤器放空气电动门开到位 |  | digital
N2DCS.20HAC90AA502RC | 10583 | 高压省煤器放空气电动门在远控 |  | digital
N2DCS.20HAD90CL001F | 10584 | 高压汽包左电接点液位计故障 |  | digital
N2DCS.20HAD90CL001H | 10585 | 高压汽包左电接点液位计高I |  | digital
N2DCS.20HAD90CL001HH | 10586 | 高压汽包左电接点液位计高II |  | digital
N2DCS.20HAD90CL001HHH | 10587 | 高压汽包左电接点液位计高III |  | digital
N2DCS.20HAD90CL001L | 10588 | 高压汽包左电接点液位计低I |  | digital
N2DCS.20HAD90CL001LL | 10589 | 高压汽包左电接点液位计低II |  | digital
N2DCS.20HAD90CL001LLL | 10590 | 高压汽包左电接点液位计低III |  | digital
N2DCS.20HAD90CL002F | 10591 | 高压汽包右电接点液位计故障 |  | digital
N2DCS.20HAD90CL002H | 10592 | 高压汽包右电接点液位计高I |  | digital
N2DCS.20HAD90CL002HH | 10593 | 高压汽包右电接点液位计高II |  | digital
N2DCS.20HAD90CL002HHH | 10594 | 高压汽包右电接点液位计高III |  | digital
N2DCS.20HAD90CL002L | 10595 | 高压汽包右电接点液位计低I |  | digital
N2DCS.20HAD90CL002LL | 10596 | 高压汽包右电接点液位计低II |  | digital
N2DCS.20HAD90CL002LLL | 10597 | 高压汽包右电接点液位计低III |  | digital
N2DCS.20HAD90CLHH1 | 10598 | 高压汽包液位1（计算后）高高高 |  | digital
N2DCS.20HAD90CLHH2 | 10599 | 高压汽包液位2（计算后）高高高 |  | digital
N2DCS.20HAD90CLHH3 | 10600 | 高压汽包液位3（计算后）高高高 |  | digital
N2DCS.20HAD90CLLL1 | 10601 | 高压汽包液位1（计算后）低低低 |  | digital
N2DCS.20HAD90CLLL2 | 10602 | 高压汽包液位2（计算后）低低低 |  | digital
N2DCS.20HAD90CLLL3 | 10603 | 高压汽包液位3（计算后）低低低 |  | digital
N2DCS.20HAD91AA405CD | 10604 | 高压蒸发器定排电动门关指令 |  | digital
N2DCS.20HAD91AA405CP | 10605 | 高压蒸发器定排电动门关到位 |  | digital
N2DCS.20HAD91AA405F | 10606 | 高压蒸发器定排电动门故障 |  | digital
N2DCS.20HAD91AA405OD | 10607 | 高压蒸发器定排电动门开指令 |  | digital
N2DCS.20HAD91AA405OP | 10608 | 高压蒸发器定排电动门开到位 |  | digital
N2DCS.20HAD91AA405RC | 10609 | 高压蒸发器定排电动门在远控 |  | digital
N2DCS.20HAD95AA001CD | 10610 | 高压汽包连排电动门关指令 |  | digital
N2DCS.20HAD95AA001CP | 10611 | 高压汽包连排电动门关到位 |  | digital
N2DCS.20HAD95AA001F | 10612 | 高压汽包连排电动门故障 |  | digital
N2DCS.20HAD95AA001OD | 10613 | 高压汽包连排电动门开指令 |  | digital
N2DCS.20HAD95AA001OP | 10614 | 高压汽包连排电动门开到位 |  | digital
N2DCS.20HAD95AA001RC | 10615 | 高压汽包连排电动门在远控 |  | digital
N2DCS.20HAD96AA001CD | 10616 | 高压汽包启动放水电动门关指令 |  | digital
N2DCS.20HAD96AA001CP | 10617 | 高压汽包启动放水电动门关到位 |  | digital
N2DCS.20HAD96AA001F | 10618 | 高压汽包启动放水电动门故障 |  | digital
N2DCS.20HAD96AA001OD | 10619 | 高压汽包启动放水电动门开指令 |  | digital
N2DCS.20HAD96AA001OP | 10620 | 高压汽包启动放水电动门开到位 |  | digital
N2DCS.20HAD96AA001RC | 10621 | 高压汽包启动放水电动门在远控 |  | digital
N2DCS.20HAD96AA002CD | 10622 | 高压汽包启动放水调节门关指令 |  | digital
N2DCS.20HAD96AA002CP | 10623 | 高压汽包启动放水调节门关到位 |  | digital
N2DCS.20HAD96AA002F | 10624 | 高压汽包启动放水调节门故障 |  | digital
N2DCS.20HAD96AA002OD | 10625 | 高压汽包启动放水调节门开指令 |  | digital
N2DCS.20HAD96AA002OP | 10626 | 高压汽包启动放水调节门开到位 |  | digital
N2DCS.20HAD96AA002RC | 10627 | 高压汽包启动放水调节门在远控 |  | digital
N2DCS.20HAH90AA402CD | 10628 | 高压一级过热器疏水电动门关指令 |  | digital
N2DCS.20HAH90AA402CP | 10629 | 高压一级过热器疏水电动门关到位 |  | digital
N2DCS.20HAH90AA402F | 10630 | 高压一级过热器疏水电动门故障 |  | digital
N2DCS.20HAH90AA402OD | 10631 | 高压一级过热器疏水电动门开指令 |  | digital
N2DCS.20HAH90AA402OP | 10632 | 高压一级过热器疏水电动门开到位 |  | digital
N2DCS.20HAH90AA402RC | 10633 | 高压一级过热器疏水电动门在远控 |  | digital
N2DCS.20HAH90AA412CD | 10634 | 高压二级过热器疏水电动门关指令 |  | digital
N2DCS.20HAH90AA412CP | 10635 | 高压二级过热器疏水电动门关到位 |  | digital
N2DCS.20HAH90AA412F | 10636 | 高压二级过热器疏水电动门故障 |  | digital
N2DCS.20HAH90AA412OD | 10637 | 高压二级过热器疏水电动门开指令 |  | digital
N2DCS.20HAH90AA412OP | 10638 | 高压二级过热器疏水电动门开到位 |  | digital
N2DCS.20HAH90AA412RC | 10639 | 高压二级过热器疏水电动门在远控 |  | digital
N2DCS.20HAH90AA502CD | 10640 | 高压饱和蒸汽放空电动门关指令 |  | digital
N2DCS.20HAH90AA502CP | 10641 | 高压饱和蒸汽放空电动门关到位 |  | digital
N2DCS.20HAH90AA502F | 10642 | 高压饱和蒸汽放空电动门故障 |  | digital
N2DCS.20HAH90AA502OD | 10643 | 高压饱和蒸汽放空电动门开指令 |  | digital
N2DCS.20HAH90AA502OP | 10644 | 高压饱和蒸汽放空电动门开到位 |  | digital
N2DCS.20HAH90AA502RC | 10645 | 高压饱和蒸汽放空电动门在远控 |  | digital
N2DCS.20HAH90AA504CD | 10646 | 高压二级过热器出口放空门关指令 |  | digital
N2DCS.20HAH90AA504CP | 10647 | 高压二级过热器出口放空门关到位 |  | digital
N2DCS.20HAH90AA504F | 10648 | 高压二级过热器出口放空门故障 |  | digital
N2DCS.20HAH90AA504OD | 10649 | 高压二级过热器出口放空门开指令 |  | digital
N2DCS.20HAH90AA504OP | 10650 | 高压二级过热器出口放空门到位 |  | digital
N2DCS.20HAH90AA504RC | 10651 | 高压二级过热器出口放空门在远控 |  | digital
N2DCS.20LAB82AA001CD | 10652 | #2中压给水泵出口电动门关指令 |  | digital
N2DCS.20LAB82AA001CP | 10653 | #2中压给水泵出口电动门关到位 |  | digital
N2DCS.20LAB82AA001F | 10654 | #2中压给水泵出口电动门故障 |  | digital
N2DCS.20LAB82AA001OD | 10655 | #2中压给水泵出口电动门开指令 |  | digital
N2DCS.20LAB82AA001OP | 10656 | #2中压给水泵出口电动门开到位 |  | digital
N2DCS.20LAB82AA001RC | 10657 | #2中压给水泵出口电动门在远控 |  | digital
N2DCS.20LAB82AP001FW | 10658 | #2中压给水泵工作位置 |  | digital
N2DCS.20LAB82AP001PF | 10659 | #2中压给水泵综合故障 |  | digital
N2DCS.20LAB82AP001PS | 10660 | #2中压给水泵保护动作 |  | digital
N2DCS.20LAB82AP001RC | 10661 | #2中压给水泵在远控 |  | digital
N2DCS.20LAB82AP001RD | 10662 | #2中压给水泵启动指令 |  | digital
N2DCS.20LAB82AP001RP | 10663 | #2中压给水泵在运行 |  | digital
N2DCS.20LAB82AP001SW | 10664 | #2中压给水泵试验位置 |  | digital
N2DCS.20LAB82AP001TD | 10665 | #2中压给水泵停止指令 |  | digital
N2DCS.20LAB82AP001TP | 10666 | #2中压给水泵已停止 |  | digital
N2DCS.20LAB82AP001TP2 | 10667 | #2中压给水泵已停止 |  | digital
N2DCS.20LAB90AA101_AUTO | 10668 | 高压给水调节阀在自动 |  | digital
N2DCS.20LAB90AA101_MRE | 10669 | 高压给水气动调节阀报警 |  | digital
N2DCS.20LAB90AA101DVHI | 10670 | 高压给水调节阀指令反馈偏差大 |  | digital
N2DCS.20LAB92AA001CD | 10671 | #2高压给水泵出口电动门关指令 |  | digital
N2DCS.20LAB92AA001CP | 10672 | #2高压给水泵出口电动门关到位 |  | digital
N2DCS.20LAB92AA001F | 10673 | #2高压给水泵出口电动门故障 |  | digital
N2DCS.20LAB92AA001OD | 10674 | #2高压给水泵出口电动门开指令 |  | digital
N2DCS.20LAB92AA001OP | 10675 | #2高压给水泵出口电动门开到位 |  | digital
N2DCS.20LAB92AA001RC | 10676 | #2高压给水泵出口电动门远控 |  | digital
N2DCS.20LAB92AP001FW | 10677 | #2高压给水泵工作位置 |  | digital
N2DCS.20LAB92AP001PF | 10678 | #2高压给水泵综合故障 |  | digital
N2DCS.20LAB92AP001PS | 10679 | #2高压给水泵电气保护动作 |  | digital
N2DCS.20LAB92AP001RC | 10680 | #2高压给水泵在远控 |  | digital
N2DCS.20LAB92AP001RP | 10681 | #2高压给水泵在运行 |  | digital
N2DCS.20LAB92AP001SW | 10682 | #2高压给水泵试验位置 |  | digital
N2DCS.20LAB92AP001TP | 10683 | #2高压给水泵已停止 |  | digital
N2DCS.20LAB92AP001TP2 | 10684 | #2高压给水泵已停止 |  | digital
N2DCS.20LAB92CS001 | 10685 | #2高压给水泵反转 |  | digital
N2DCS.20LAC91_A | 10686 | #1高压给水泵在变频模式 |  | digital
N2DCS.20LAC91_B | 10687 | #2高压给水泵在变频模式 |  | digital
N2DCS.20LAC91G10001CR | 10688 | 高压给水泵变频器充电中指示 |  | digital
N2DCS.20LAC91G10001DC | 10689 | 高压给水泵DCS控制指示 |  | digital
N2DCS.20LAC91G10001ED | 10690 | 高压给水泵变频器紧急停机指令 |  | digital
N2DCS.20LAC91G10001LF | 10691 | 高压给水泵轻故障指示 |  | digital
N2DCS.20LAC91G10001PW | 10692 | 高压给水泵允许启动指示 |  | digital
N2DCS.20LAC91G10001RD1 | 10693 | 高压给水泵变频启动指令 |  | digital
N2DCS.20LAC91G10001RP2 | 10694 | #2高压给水泵变频运行指示 |  | digital
N2DCS.20LAC91G10001RS | 10695 | 高压给水泵变频器复位指令 |  | digital
N2DCS.20LAC91G10001SF | 10696 | 高压给水泵重故障指示 |  | digital
N2DCS.20LAC91G10001TD1 | 10697 | 高压给水泵变频停止指令 |  | digital
N2DCS.20LAC91GX0001_AUTO | 10698 | 高压给水泵变频器在自动 |  | digital
N2DCS.20LAC91GX0001_DVHI | 10699 | 高压给水泵变频器指令反馈偏差大 |  | digital
N2DCS.20LAC91GX0001_SPDH | 10700 | 高压给水泵变频器设定反馈偏差大 |  | digital
N2DCS.20LAC91GX0001CR | 10701 | 高压给水泵变频器充电中指示 |  | digital
N2DCS.20LAC91GX0001DC | 10702 | 高压给水泵变频器在DCS控制 |  | digital
N2DCS.20LAC91GX0001ED | 10703 | 高压给水泵变频器紧急停机指令 |  | digital
N2DCS.20LAC91GX0001LF | 10704 | 高压给水泵变频器轻故障指示 |  | digital
N2DCS.20LAC91GX0001LVLAUTO | 10705 | 高压给水泵变频器在三冲量调节 |  | digital
N2DCS.20LAC91GX0001PW | 10706 | 高压给水泵变频器启允许 |  | digital
N2DCS.20LAC91GX0001RD1 | 10707 | 高压给水泵变频器启动指令 |  | digital
N2DCS.20LAC91GX0001RP2 | 10708 | #2高压给水泵在变频运行 |  | digital
N2DCS.20LAC91GX0001RS | 10709 | 高压给水泵变频器复位指令 |  | digital
N2DCS.20LAC91GX0001SF | 10710 | 高压给水泵重故障指示 |  | digital
N2DCS.20LAC91GX0001TD1 | 10711 | 高压给水泵变频器停止指令 |  | digital
N2DCS.20LAC92AP001EH004 | 10712 | #2高压给水泵高压柜QS2合闸位置 |  | digital
N2DCS.20LAC92AP001EH005 | 10713 | #2高压给水泵高压柜QS4合闸位置 |  | digital
N2DCS.20LAC92AP001RD | 10714 | #2高压给水泵6KV开关合闸指令 |  | digital
N2DCS.20LAC92AP001TD | 10715 | #2高压给水泵6KV开关跳闸指令 |  | digital
N2DCS.20LAE90AA002CD | 10716 | 高压二级过热器减温水门关指令 |  | digital
N2DCS.20LAE90AA002CP | 10717 | 高压二级过热器减温水门关到位 |  | digital
N2DCS.20LAE90AA002F | 10718 | 高压二级过热器减温水门故障 |  | digital
N2DCS.20LAE90AA002OD | 10719 | 高压二级过热器减温水门开指令 |  | digital
N2DCS.20LAE90AA002OP | 10720 | 高压二级过热器减温水门开到位 |  | digital
N2DCS.20LAE90AA002RC | 10721 | 高压二级过热器减温水门在远控 |  | digital
N2DCS.20LAE90AA004CD | 10722 | 高压主蒸汽减温水电动门关指令 |  | digital
N2DCS.20LAE90AA004CP | 10723 | 高压主蒸汽减温水电动门关到位 |  | digital
N2DCS.20LAE90AA004F | 10724 | 高压主蒸汽减温水电动门故障 |  | digital
N2DCS.20LAE90AA004OD | 10725 | 高压主蒸汽减温水电动门开指令 |  | digital
N2DCS.20LAE90AA004OP | 10726 | 高压主蒸汽减温水电动门开到位 |  | digital
N2DCS.20LAE90AA004RC | 10727 | 高压主蒸汽减温水电动门在远控 |  | digital
N2DCS.20LAE90AA101_MRE | 10728 | 高压二级过热器减温水调阀报警 |  | digital
N2DCS.20LAE90AA102_MRE | 10729 | 高压主蒸汽减温水调阀报警 |  | digital
N2DCS.20LAE91AA101_AUTO | 10730 | 高压省煤器旁路调节阀在自动 |  | digital
N2DCS.20LAE91AA101_DVHI | 10731 | 高省旁路调阀指令反馈偏差大 |  | digital
N2DCS.20LAE91AA101_RSDVH | 10732 | Ovation Control Builder |  | digital
N2DCS.20LAE91AA101_SPDH | 10733 | 高省旁路调阀设定反馈偏差大 |  | digital
N2DCS.20LBA90AA192CD | 10734 | 高压主蒸汽出口PCV阀关指令 |  | digital
N2DCS.20LBA90AA192CP | 10735 | 高压主蒸汽出口PCV阀关到位 |  | digital
N2DCS.20LBA90AA192OD | 10736 | 高压主蒸汽出口PCV阀开指令 |  | digital
N2DCS.20LBA90AA192OP | 10737 | 高压主蒸汽出口PCV阀开到位 |  | digital
N2DCS.20LBA90AA502CD | 10738 | 高压主蒸汽启动排汽电动门关指令 |  | digital
N2DCS.20LBA90AA502CP | 10739 | 高压主蒸汽启动排汽电动门关到位 |  | digital
N2DCS.20LBA90AA502F | 10740 | 高压主蒸汽启动排汽电动门故障 |  | digital
N2DCS.20LBA90AA502OD | 10741 | 高压主蒸汽启动排汽电动门开指令 |  | digital
N2DCS.20LBA90AA502OP | 10742 | 高压主蒸汽启动排汽电动门开到位 |  | digital
N2DCS.20LBA90AA502RC | 10743 | 高压主蒸汽启排汽电动门在远控 |  | digital
N2DCS.20LBG90AA001CD | 10744 | 辅汽至高压蒸发器电动门关指令 |  | digital
N2DCS.20LBG90AA001CP | 10745 | 辅汽至高压蒸发器电动门关到位 |  | digital
N2DCS.20LBG90AA001F | 10746 | 辅汽至高压蒸发器电动门故障 |  | digital
N2DCS.20LBG90AA001OD | 10747 | 辅汽至高压蒸发器电动门开指令 |  | digital
N2DCS.20LBG90AA001OP | 10748 | 辅汽至高压蒸发器电动门开到位 |  | digital
N2DCS.20LBG90AA001RC | 10749 | 辅汽至高压蒸发器电动门在远控 |  | digital
N2DCS.20XAV92CL001 | 10750 | #2高压给水泵稀油站油箱液位低 |  | digital
N2DCS.20XAV92CP001 | 10751 | #2高压给水泵稀油站滤网差压高 |  | digital
N2DCS.20XAV92GH001AP1RD | 10752 | #2高压给水泵稀油站#1油泵启指令 |  | digital
N2DCS.20XAV92GH001AP1TD | 10753 | #2高压给水泵稀油站#1油泵停指令 |  | digital
N2DCS.20XAV92GH001AP2RD | 10754 | #2高压给水泵稀油站#2油泵启指令 |  | digital
N2DCS.20XAV92GH001AP2TD | 10755 | #2高压给水泵稀油站#2油泵停指令 |  | digital
N2DCS.20XAV92GH001HTRD | 10756 | #2高压给水泵稀油站加热器启指令 |  | digital
N2DCS.20XAV92GH001HTTD | 10757 | #2高压给水泵稀油站加热器停指令 |  | digital
N2DCS.20XAV92GH001PF | 10758 | #2高给泵稀油站重大故障停主机 |  | digital
N2DCS.20XAV92GH001RC1 | 10759 | #2高压给水泵稀油站远程备妥 |  | digital
N2DCS.20XAV92GH001RC2 | 10760 | #2高压给水泵稀油站允许主机启动 |  | digital
N2DCS.20XAV92GH001RD1 | 10761 | #2高压给水泵稀油站远程驱动 |  | digital
N2DCS.20XAV92GH001RD2 | 10762 | #2高压给水泵在运行（送至稀油站 |  | digital
N2DCS.20XAV92GH001RP1 | 10763 | #2高给泵稀油站#1油泵在运行 |  | digital
N2DCS.20XAV92GH001RP2 | 10764 | #2高给泵稀油站#2油泵在运行 |  | digital
N2DCS.20XAV92GH001RP3 | 10765 | #2高给泵稀油站电加热器已投入 |  | digital
N2DCS.20XAV92GH002PF1 | 10766 | #2高压给水泵稀油站轻故障 |  | digital
N2DCS.GYSJGRQJKWD_MRE | 10767 | 高压三级过热器进口温度坏点 |  | digital
N2DCS.H1HPDRUMLVLDEVHI | 10768 | Ovation Control Builder |  | digital
N2DCS.H1HPFW3ELE | 10769 | Ovation Control Builder |  | digital
N2DCS.HP_DRN_ACD | 10770 | 高压蒸汽疏水门自动关 |  | digital
N2DCS.HPDRUMCP_MRE | 10771 | 高压汽包压力坏点 |  | digital
N2DCS.HPDRUMCTD_MRE | 10772 | 高压汽包下外壁温坏点 |  | digital
N2DCS.HPDRUMCTU_MRE | 10773 | 高压汽包上外壁温坏点 |  | digital
N2DCS.HPDRUMCTU2_MRE | 10774 | 高压汽包上内壁温坏点 |  | digital
N2DCS.HPDRUMLVL_AL | 10775 | 高压汽包液位（计算后）报警 |  | digital
N2DCS.HPDRUMLVL_HI | 10776 | 高压汽包液位（计算后）高 |  | digital
N2DCS.HPDRUMLVL_HII | 10777 | 高压汽包液位（计算后）高高 |  | digital
N2DCS.HPDRUMLVL_HIII | 10778 | 高压汽包液位（计算后）高高高 |  | digital
N2DCS.HPDRUMLVL_HIII1 | 10779 | 高压汽包液位1（计算后）高高高 |  | digital
N2DCS.HPDRUMLVL_HIII2 | 10780 | 高压汽包液位2（计算后）高高高 |  | digital
N2DCS.HPDRUMLVL_HIII3 | 10781 | 高压汽包液位3（计算后）高高高 |  | digital
N2DCS.HPDRUMLVL_LII | 10782 | 高压汽包液位（计算后）低低 |  | digital
N2DCS.HPDRUMLVL_LIII | 10783 | 高压汽包液位（计算后）低低低 |  | digital
N2DCS.HPDRUMLVL_LIII1 | 10784 | 高压汽包液位1（计算后）低低低 |  | digital
N2DCS.HPDRUMLVL_LIII2 | 10785 | 高压汽包液位2（计算后）低低低 |  | digital
N2DCS.HPDRUMLVL_LIII3 | 10786 | 高压汽包液位3（计算后）低低低 |  | digital
N2DCS.HPDRUMLVL_MRE | 10787 | 高压汽包液位（计算后）报警 |  | digital
N2DCS.HPDRUMLVLDEVHI | 10788 | 高压给水调阀设定反馈偏差大 |  | digital
N2DCS.HPDSTCF_MRE | 10789 | 高压主蒸汽流量（计算后）坏点 |  | digital
N2DCS.HPDSTCP_MRE | 10790 | 高压主蒸汽压力坏点 |  | digital
N2DCS.HPDSTCT_MRE | 10791 | 高压主蒸汽温度坏点 |  | digital
N2DCS.HPDWTCF_MRE | 10792 | 高压汽包给水流量(计算后)坏点 |  | digital
N2DCS.HPDWTCF_NORM | 10793 | 高压汽包给水流量(计算后)正常 |  | digital
N2DCS.HPDWTCT_MRE | 10794 | 高压汽包给水温度坏点 |  | digital
N2DCS.HPFW_ACK | 10795 | Ovation Control Builder |  | digital
N2DCS.HPFW_SEQSTFINSH | 10796 | 高压汽包上水顺控已完成 |  | digital
N2DCS.HPFW3ELE | 10797 | 高压给水在三冲量调节 |  | digital
N2DCS.HPFWACK | 10798 | 高压汽包上水排空确认 |  | digital
N2DCS.HPFWACK_PMT | 10799 | 高压汽包上水排空确认允许 |  | digital
N2DCS.HPFWP_FRQ_RUN | 10800 | 任一高压给水泵在变频运行 |  | digital
N2DCS.HPFWP_FRQ_STOP | 10801 | 2台高压给水泵变频已停止 |  | digital
N2DCS.HPFWPB_OILP_RUN | 10802 | Ovation Control Builder |  | digital
N2DCS.HPFWPB_RUN | 10803 | #2高压给水泵在运行(工频或变频) |  | digital
N2DCS.HPFWPB_STOP | 10804 | #2高压给水泵已停止(工频和变频) |  | digital
N2DCS.HPFWPB_STRPEM | 10805 | #2高压给水泵启动允许 |  | digital
N2DCS.HPFWPB_TEMPEM | 10806 | #2高压给水泵温度允许 |  | digital
N2DCS.HPFWPB_TEMPRT | 10807 | #2高压给水泵温度保护信号 |  | digital
N2DCS.HPFWPB_TP | 10808 | #2高压给水泵跳闸信号 |  | digital
N2DCS.HPFWPBMANSTOP | 10809 | #2高压给水泵手动停止指令 |  | digital
N2DCS.HPFWPBRUN | 10810 | #2高压给水泵在运行 |  | digital
N2DCS.HPMS_SEQSTFINISH | 10811 | 高压主汽升温升压顺控已完成 |  | digital
N2DCS.IPFWPB_STRPEM | 10812 | #2中压给水泵启动允许 |  | digital
N2DCS.IPFWPB_TEMPEM | 10813 | #2中压给水泵温度允许 |  | digital
N2DCS.IPFWPB_TEMPRT | 10814 | #2中压给水泵温度保护信号 |  | digital
N2DCS.IPFWPB_TP | 10815 | #2中压给水泵跳闸信号 |  | digital
N2DCS.IPFWPBMANSTOP | 10816 | #2中压给水泵手动停止指令 |  | digital
N2DCS.ONE9 | 10817 | 开关量1 |  | digital
N2DCS.ZERO9 | 10818 | 开关量0 |  | digital
N2DCS.20LAC91GX0001LVLAUTO1 | 10819 | 高压变频器在单冲量调节 |  | digital
N2DCS.20LAE90AA002RC_N | 10820 | Ovation Control Builder |  | digital
N2DCS.20LAE90AA101_AUTO | 10821 | 高压二级过热器减温水调阀在自动 |  | digital
N2DCS.20LAE90AA102_AUTO | 10822 | 高压主蒸汽减温水调节阀在自动 |  | digital
N2DCS.20LAE91AA101CP | 10823 | 高压二级过热器减温水调阀全关位 |  | digital
N2DCS.CLOSEGAOYAPAIOK | 10824 | Ovation Control Builder |  | digital
N2DCS.CNSRVACMLOW | 10825 | Ovation Control Builder |  | digital
N2DCS.GYGSPMPBBP | 10826 | #2高压给水泵在变频位置 |  | digital
N2DCS.GYGSPMPBGP | 10827 | #2高压给水泵在工频位置 |  | digital
N2DCS.HPDRUMCT_MRE | 10828 | 高压汽包壁温坏点 |  | digital
N2DCS.HPDRUMCTC | 10829 | 高压汽包上下壁温差<60度 |  | digital
N2DCS.HPFW3ELE1 | 10830 | 高压给水在单冲量调节 |  | digital
N2DCS.HPFWPB_SEQBPSTFINISH | 10831 | #2高压给水泵变频启顺控已完成 |  | digital
N2DCS.HPFWPB_SEQSTFINISH | 10832 | #2高压给水泵工频启顺控已完成 |  | digital
N2DCS.HRSGTP1 | 10833 | 高压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTP10 | 10834 | 烟囱挡板全关 |  | digital
N2DCS.HRSGTP11 | 10835 | OPC或汽机跳闸30S后任一旁路未开 |  | digital
N2DCS.HRSGTP12 | 10836 | 凝汽器真空低跳闸联跳锅炉 |  | digital
N2DCS.HRSGTP13 | 10837 | 手动保护跳锅炉 |  | digital
N2DCS.HRSGTP14 | 10838 | 燃机保护跳闸联跳锅炉 |  | digital
N2DCS.HRSGTP1A | 10839 | 高压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTP2 | 10840 | 高压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTP2A | 10841 | 高压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTP3 | 10842 | 中压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTP3A | 10843 | 中压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTP4 | 10844 | 中压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTP4A | 10845 | 中压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTP5 | 10846 | 低压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTP5A | 10847 | 低压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTP6 | 10848 | 低压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTP6A | 10849 | 低压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTP7 | 10850 | 高压给水泵全停 |  | digital
N2DCS.HRSGTP8 | 10851 | 中压给水泵全停 |  | digital
N2DCS.HRSGTP9 | 10852 | 凝结水泵全停 |  | digital
N2DCS.HRSGTRIP | 10853 | 余热锅炉保护跳闸 |  | digital
N2DCS.HRSGTRIPRSPB | 10854 | 余热锅炉保护跳闸复位 |  | digital
N2DCS.20AVC0025 | 10855 | AVC下位机遥信电源消失 |  | digital
N2DCS.20AVC0026 | 10856 | AVC投入/退出信号 |  | digital
N2DCS.20BBA00EH001 | 10857 | 6KV 2A段母线PT保护装置故障 |  | digital
N2DCS.20BBA00EH002 | 10858 | 6kV 2A段母线过压报警 |  | digital
N2DCS.20BBA00EH003 | 10859 | 6kV 2A段母线低压报警 |  | digital
N2DCS.20BBA00EH004 | 10860 | 6kV 2A段母线失压报警 |  | digital
N2DCS.20BBA00EH005 | 10861 | 6kV 2A段母线接地报警 |  | digital
N2DCS.20BBA00EH006 | 10862 | 6kV 2A段母线谐振报警 |  | digital
N2DCS.20BBA00EH101 | 10863 | 6KV 2A段工作进线PT异常 |  | digital
N2DCS.20BBA00EH102 | 10864 | 6KV 2A段工作进线PT保护小车位置 |  | digital
N2DCS.20BBA00GS001PF | 10865 | 6KV 2A段工作开关保护异常总信号 |  | digital
N2DCS.20BBA00GS001PF1 | 10866 | 6KV 2A段工作开关弧光保护故障 |  | digital
N2DCS.20BBA00GS001PS | 10867 | 6KV 2A段工作开关弧光保护动作 |  | digital
N2DCS.20BBA00GS001RC | 10868 | 6kV 2A段工作电源开关远方控制 |  | digital
N2DCS.20BBA00GS001RD | 10869 | 6kV 2A段工作电源进线开关合指令 |  | digital
N2DCS.20BBA00GS001RP | 10870 | 6KV 2A段工作进线开关合闸位置 |  | digital
N2DCS.20BBA00GS001SW | 10871 | 6KV 2A段工作进线开关试验位置 |  | digital
N2DCS.20BBA00GS001TD | 10872 | 6kV 2A段工作电源进线开关分指令 |  | digital
N2DCS.20BBA00GS001TP | 10873 | 6KV 2A段工作进线开关分闸位置 |  | digital
N2DCS.20BBA00GS001TP1 | 10874 | 6KV 2A段工作进线开关分闸位置 |  | digital
N2DCS.20BBA00GS001YW | 10875 | 6kV 2A段工作进线开关工作位置 |  | digital
N2DCS.20BBB00EH201 | 10876 | 6kV 2B段备用进线PT异常 |  | digital
N2DCS.20BBB00EH202 | 10877 | 6kV 2B段备用进线PT保护小车位置 |  | digital
N2DCS.20BBB00GS001TP1 | 10878 | 6KV 2B段工作进线开关分闸位置 |  | digital
N2DCS.20BBB00GS002PF | 10879 | 6kV 2B段备用电源保护异常总信号 |  | digital
N2DCS.20BBB00GS002RC | 10880 | 6kV 2B段备用电源开关远方控制 |  | digital
N2DCS.20BBB00GS002RD | 10881 | 6kV 2B段备用电源进线开关合指令 |  | digital
N2DCS.20BBB00GS002RP | 10882 | 6kV 2B段备用电源开关合闸位置 |  | digital
N2DCS.20BBB00GS002SW | 10883 | 6kV 2B段备用电源开关试验位置 |  | digital
N2DCS.20BBB00GS002TD | 10884 | 6kV 2B段备用电源进线开关分指令 |  | digital
N2DCS.20BBB00GS002TP | 10885 | 6kV 2B段备用电源开关分闸位置 |  | digital
N2DCS.20BBB00GS002YW | 10886 | 6kV 2B段备用电源开关工作位置 |  | digital
N2DCS.20BBB13GS001PF | 10887 | SFC隔离变馈线开关综合故障 |  | digital
N2DCS.20BBB13GS001PS | 10888 | SFC隔离变馈线开关电气保护动作 |  | digital
N2DCS.20BBB13GS001RP | 10889 | SFC隔离变馈线开关合闸位置 |  | digital
N2DCS.20BBB13GS001TP | 10890 | SFC隔离变馈线开关分闸位置 |  | digital
N2DCS.20BFA00EH201 | 10891 | 380V工作PC 2A段母线电压低 |  | digital
N2DCS.20BFA00EH202 | 10892 | 380V工作PC 2A段PT保护装置故障 |  | digital
N2DCS.20BFA00EH203 | 10893 | 380V工作PC 2A段PT刀熔开关分位 |  | digital
N2DCS.20BFA00GS103PF | 10894 | 工作PC IIA至保安段开关综合故障 |  | digital
N2DCS.20BFA00GS103RC | 10895 | 工作PC IIA至保安段开关远方控制 |  | digital
N2DCS.20BFA00GS103RD | 10896 | 工作PC IIA至保安段馈线开关合闸 |  | digital
N2DCS.20BFA00GS103RP | 10897 | 工作PC IIA至保安段开关合闸位置 |  | digital
N2DCS.20BFA00GS103TD | 10898 | 工作PC IIA至保安段馈线开关分闸 |  | digital
N2DCS.20BFA00GS103TP | 10899 | 工作PC IIA至保安段开关分闸位置 |  | digital
N2DCS.20BFA00GS201PF | 10900 | 工作PC 2A至保安段开关综合故障 |  | digital
N2DCS.20BFA00GS201RC | 10901 | 工作PC 2A至保安段开关在远方 |  | digital
N2DCS.20BFA00GS201RD | 10902 | 工作PC 2A至保安段开关合闸指令 |  | digital
N2DCS.20BFA00GS201RP | 10903 | 工作PC 2A至保安段开关合闸位置 |  | digital
N2DCS.20BFA00GS201TD | 10904 | 工作PC 2A至保安段开关分闸指令 |  | digital
N2DCS.20BFA00GS201TP | 10905 | 工作PC 2A至保安段开关分闸位置 |  | digital
N2DCS.20BFB00GS001_PUT | 10906 | 机组工作PC段分段开关联锁投入 |  | digital
N2DCS.20BFB00GS001L_PUT | 10907 | 工作PC段分段开关允许并联运行 |  | digital
N2DCS.20BFB00GS001PF | 10908 | 机组工作PC段分段开关综合故障 |  | digital
N2DCS.20BFB00GS001RC | 10909 | 机组工作PC段分段开关远方控制 |  | digital
N2DCS.20BFB00GS001RD | 10910 | 机组工作PC段分段开关合闸指令 |  | digital
N2DCS.20BFB00GS001RP | 10911 | 机组工作PC段分段开关合闸位置 |  | digital
N2DCS.20BFB00GS001TD | 10912 | 机组工作PC段分段开关分闸指令 |  | digital
N2DCS.20BFB00GS001TP | 10913 | 机组工作PC段分段开关分闸位置 |  | digital
N2DCS.20BFT10GS101PF | 10914 | 工作2A变6kV侧开关综合故障 |  | digital
N2DCS.20BFT10GS101PS | 10915 | 工作2A变6kV侧开关保护动作 |  | digital
N2DCS.20BFT10GS101RC | 10916 | 工作2A变6kV侧开关远方控制 |  | digital
N2DCS.20BFT10GS101RD | 10917 | 工作2A变6kV侧开关合闸指令 |  | digital
N2DCS.20BFT10GS101RP | 10918 | 工作2A变6kV侧开关合闸位置 |  | digital
N2DCS.20BFT10GS101SW | 10919 | 工作2A变6kV侧开关试验位置 |  | digital
N2DCS.20BFT10GS101TD | 10920 | 工作2A变6kV侧开关分闸指令 |  | digital
N2DCS.20BFT10GS101TP | 10921 | 工作2A变6kV侧开关分闸位置 |  | digital
N2DCS.20BFT10GS101YW | 10922 | 工作2A变6kV侧开关工作位置 |  | digital
N2DCS.20BFT10GS102PF | 10923 | 工作2A变380V侧开关综合故障 |  | digital
N2DCS.20BFT10GS102RC | 10924 | 工作2A变380V侧开关远方控制 |  | digital
N2DCS.20BFT10GS102RD | 10925 | 工作2A变380V侧开关合闸指令 |  | digital
N2DCS.20BFT10GS102RP | 10926 | 工作2A变380V侧开关合闸位置 |  | digital
N2DCS.20BFT10GS102TD | 10927 | 工作2A变380V侧开关分闸指令 |  | digital
N2DCS.20BFT10GS102TP | 10928 | 工作2A变380V侧开关分闸位置 |  | digital
N2DCS.20BJA00GS201RP | 10929 | 工作PC2A至#3机MCCA开关合闸位置 |  | digital
N2DCS.20BJA00GS201TP | 10930 | 工作PC2A至#3机MCCA开关分闸位置 |  | digital
N2DCS.20BJB00GS201RP | 10931 | 工作PC2A至#3机MCCB开关合闸位置 |  | digital
N2DCS.20BJB00GS201TP | 10932 | 工作PC2A至#3机MCCB开关分闸位置 |  | digital
N2DCS.20BJC00GS201RP | 10933 | 工作PC 2A至余炉MCC开关合闸位置 |  | digital
N2DCS.20BJC00GS201TP | 10934 | 工作PC 2A至余炉MCC开关分闸位置 |  | digital
N2DCS.20BJD00GS201PF | 10935 | 工作PC2A至#4机MCCA开关综合故障 |  | digital
N2DCS.20BJD00GS201RC | 10936 | 工作PC2A至#4机MCCA开关远方控制 |  | digital
N2DCS.20BJD00GS201RD | 10937 | 工作PC 2A至#4机MCC A开关合闸令 |  | digital
N2DCS.20BJD00GS201RP | 10938 | 工作PC2A至#4机MCCA开关合闸位置 |  | digital
N2DCS.20BJD00GS201TD | 10939 | 工作PC 2A至#4机MCC A开关分闸令 |  | digital
N2DCS.20BJD00GS201TP | 10940 | 工作PC2A至#4机MCCA开关分闸位置 |  | digital
N2DCS.20BJE00GS201PF | 10941 | 工作PC2A至#4机MCCB开关综合故障 |  | digital
N2DCS.20BJE00GS201RC | 10942 | 工作PC2A至#4机MCCB开关远方控制 |  | digital
N2DCS.20BJE00GS201RD | 10943 | 工作PC 2A至#4机MCC B开关合闸令 |  | digital
N2DCS.20BJE00GS201RP | 10944 | 工作PC2A至#4机MCCB开关合闸位置 |  | digital
N2DCS.20BJE00GS201TD | 10945 | 工作PC 2A至#4机MCC B开关分闸令 |  | digital
N2DCS.20BJE00GS201TP | 10946 | 工作PC2A至#4机MCCB开关分闸位置 |  | digital
N2DCS.20BNA00GS201PF | 10947 | 保安段至#4机EMCC段开关综合故障 |  | digital
N2DCS.20BNA00GS201RC | 10948 | 保安段至#4机EMCC段开关远方控制 |  | digital
N2DCS.20BNA00GS201RD | 10949 | 保安段至#4机EMCC段馈线开关合闸 |  | digital
N2DCS.20BNA00GS201RP | 10950 | 保安段至#4机EMCC段开关合闸位置 |  | digital
N2DCS.20BNA00GS201TD | 10951 | 保安段至#4机EMCC段馈线开关分闸 |  | digital
N2DCS.20BNA00GS201TP | 10952 | 保安段至#4机EMCC段开关分闸位置 |  | digital
N2DCS.20CBQ01EH_FL | 10953 | #3机6kV A段快切装置故障 |  | digital
N2DCS.20CBQ01EH_PMT | 10954 | #3机6kV A段快切装置启动允许 |  | digital
N2DCS.20CBQ01EH1_FL | 10955 | #2机组6kV A段快切装置故障 |  | digital
N2DCS.20CBQ01EH1_PMT | 10956 | #3机6kV A段快切装置启动允许 |  | digital
N2DCS.20CBQ01EH101 | 10957 | 6kV 2A段快切装置启动正常切换 |  | digital
N2DCS.20CBQ01EH102 | 10958 | 6kV 2A段快切装置手动闭锁 |  | digital
N2DCS.20CBQ01EH103 | 10959 | 6kV 2A段快切装置远方复归 |  | digital
N2DCS.20CBQ01EH104 | 10960 | 6kV 2A段快切装置合工作 |  | digital
N2DCS.20CBQ01EH105 | 10961 | 6kV 2A段快切装置合备用 |  | digital
N2DCS.20CBQ01EH106 | 10962 | 6kV 2A段快切装置总告警 |  | digital
N2DCS.20CBQ01EH107 | 10963 | 6kV 2A段快切装置切换完毕 |  | digital
N2DCS.20CBQ01EH108 | 10964 | 6kV 2A段快切装置电源失压 |  | digital
N2DCS.20CBQ01EH109 | 10965 | 6kV 2A快切装置切换失败 |  | digital
N2DCS.20CBQ01EH110 | 10966 | 6kV 2A段快切装置切换闭锁 |  | digital
N2DCS.20CBQ01EH111 | 10967 | 6kV 2A段快切装置自动允许 |  | digital
N2DCS.20CBQ01EH112 | 10968 | 6kV 2A段快切装置手动允许 |  | digital
N2DCS.20CBQ01EH113 | 10969 | 6kV 2A段快切装置单操允许 |  | digital
N2DCS.21BAC01GS101TP2 | 10970 | #4发电机出口GCB开关分闸位(SOE) |  | digital
N2DCS.21CHA05EH116 | 10971 | #4主变油面温度高信号 |  | digital
N2DCS.21CHA05EH117 | 10972 | #2高厂变重瓦斯跳闸 |  | digital
N2DCS.21CHA05EH118 | 10973 | #2高厂变绕组温度过高跳闸 |  | digital
N2DCS.21CHA05EH119 | 10974 | #2高厂变本体突发压力跳闸 |  | digital
N2DCS.21CHA05EH120 | 10975 | #2高厂变油温高跳闸 |  | digital
N2DCS.21CHA05EH121 | 10976 | #4机励磁系统故障 |  | digital
N2DCS.21CHA05EH122 | 10977 | #4机励磁变温度保护跳闸 |  | digital
N2DCS.21CHA05EH123 | 10978 | #2高厂变轻瓦斯信号 |  | digital
N2DCS.21CHA05EH124 | 10979 | #2高厂变绕组温度高信号 |  | digital
N2DCS.21CHA05EH125 | 10980 | #2高厂变压力释放信号 |  | digital
N2DCS.21CHA05EH126 | 10981 | #2高厂变油位异常信号 |  | digital
N2DCS.21CHA05EH127 | 10982 | #2高厂变油温高信号 |  | digital
N2DCS.21CWA001PB006 | 10983 | 集控室操作台紧急跳闸指令 |  | digital
N2DCS.22AVC0021 | 10984 | DCS允许#3机AVC自动调节 |  | digital
N2DCS.22AVC0027 | 10985 | 增加#3机励磁信号 |  | digital
N2DCS.22AVC0028 | 10986 | 减少#3机励磁信号 |  | digital
N2DCS.22BAT01EH001 | 10987 | #3主变冷却器Ⅰ段电源运行 |  | digital
N2DCS.22BAT01EH002 | 10988 | #3主变冷却器Ⅱ段电源运行 |  | digital
N2DCS.22BAT01EH003 | 10989 | #3主变冷却器Ⅰ段电源故障 |  | digital
N2DCS.22BAT01EH004 | 10990 | #3主变冷却器Ⅱ段电源故障 |  | digital
N2DCS.22BAT01EH005 | 10991 | #3主变冷却器控制电源故障 |  | digital
N2DCS.22BAT01EH006 | 10992 | #3主变工作冷却器故障 |  | digital
N2DCS.22BAT01EH007 | 10993 | #3主变备用冷却器故障 |  | digital
N2DCS.22BAT01EH008 | 10994 | #3主变风冷全停 |  | digital
N2DCS.22BAT01EH009 | 10995 | #3主变辅助投入 |  | digital
N2DCS.22BAW20EH101 | 10996 | #3发电机PT端子箱空开分闸信号 |  | digital
N2DCS.22CBP01_PMT | 10997 | #3主变开关2203同期装置启允许 |  | digital
N2DCS.22CBP01EH201 | 10998 | #3主变开关2203同期允许(DEH来) |  | digital
N2DCS.22CBP01EH202 | 10999 | #3主变开关2203同期功角越限 |  | digital
N2DCS.22CBP01EH203 | 11000 | #3主变开关2203同期装置闭锁 |  | digital
N2DCS.22CBP01EH204 | 11001 | #3主变开关2203自动准同期启动 |  | digital
N2DCS.22CBP01EH205 | 11002 | #3主变开关2203自动准同期就绪 |  | digital
N2DCS.22CBP01EH206 | 11003 | #3主变开关2203同期失电告警 |  | digital
N2DCS.22CBP01EH207 | 11004 | #3主变开关2203同期总告警 |  | digital
N2DCS.22CBP01EJ511 | 11005 | #3主变2203自动准同期DTK投入 |  | digital
N2DCS.22CBP01EJ512 | 11006 | #3主变2203自动准同期DTK退出 |  | digital
N2DCS.22CBP01EJ513 | 11007 | #3主变2203自动准同期装置启动 |  | digital
N2DCS.22CBP01EJ514 | 11008 | #3主变2203自动准同期装置复位 |  | digital
N2DCS.22CBP01EJ515 | 11009 | 2203自动准同期装置紧急中断同期 |  | digital
N2DCS.22CBP01EJ518 | 11010 | #3主变开关2203同期请求(至DEH） |  | digital
N2DCS.22CBP01EJ519 | 11011 | #3主变开关2201手动同期装置复位 |  | digital
N2DCS.22CEQ01EH001 | 11012 | #3发变组故障录波装置故障 |  | digital
N2DCS.22CEQ01EH002 | 11013 | #3发变组故障录波装置启动 |  | digital
N2DCS.22CEQ01EH003 | 11014 | #3发变组故障录波器失电报警 |  | digital
N2DCS.22CHA01EH101 | 11015 | #3发电机A套发电机差动跳闸 |  | digital
N2DCS.22CHA01EH102 | 11016 | #3发电机A套定子接地跳闸 |  | digital
N2DCS.22CHA01EH103 | 11017 | #3发电机A套匝间跳闸 |  | digital
N2DCS.22CHA01EH104 | 11018 | #3发电机A套过负荷跳闸 |  | digital
N2DCS.22CHA01EH105 | 11019 | #3发电机A套过电压保护跳闸 |  | digital
N2DCS.22CHA01EH106 | 11020 | #3发电机A套失磁保护跳闸 |  | digital
N2DCS.22CHA01EH107 | 11021 | #3发电机A套失步保护跳闸 |  | digital
N2DCS.22CHA01EH108 | 11022 | #3发电机A套负序过负荷跳闸 |  | digital
N2DCS.22CHA01EH109 | 11023 | #3发电机A套过励磁跳闸 |  | digital
N2DCS.22CHA01EH110 | 11024 | #3发电机A套频率保护跳闸 |  | digital
N2DCS.22CHA01EH111 | 11025 | #3发电机A套相间后备跳闸 |  | digital
N2DCS.22CHA01EH112 | 11026 | #3发电机A套误上电跳闸 |  | digital
N2DCS.22CHA01EH113 | 11027 | #3发电机A套逆功率跳闸 |  | digital
N2DCS.22CHA01EH114 | 11028 | #3发电机A套程序逆功率跳闸 |  | digital
N2DCS.22CHA01EH115 | 11029 | #3发电机A套启停机跳闸 |  | digital
N2DCS.22CHA01EH116 | 11030 | #3发电机A套低频保护跳闸 |  | digital
N2DCS.22CHA01EH117 | 11031 | #3发电机A套励磁后备跳闸 |  | digital
N2DCS.22CHA01EH118 | 11032 | #3主变A套非全相保护跳闸 |  | digital
N2DCS.22CHA01EH119 | 11033 | #3主变A套断路器闪络跳闸 |  | digital
N2DCS.22CHA01EH120 | 11034 | #3主变A套差动跳闸 |  | digital
N2DCS.22CHA01EH121 | 11035 | #3主变A套相间后备跳闸 |  | digital
N2DCS.22CHA01EH122 | 11036 | #3主变A套接地零序跳闸 |  | digital
N2DCS.22CHA01EH123 | 11037 | #3主变A套间隙零序跳闸 |  | digital
N2DCS.22CHA01EH124 | 11038 | #3发变组A套保护装置闭锁 |  | digital
N2DCS.22CHA01EH125 | 11039 | #3发变组A套保护装置报警 |  | digital
N2DCS.22CHA01EH126 | 11040 | #3发变组A套保护TA断线 |  | digital
N2DCS.22CHA01EH127 | 11041 | #3发变组A套保护TV断线 |  | digital
N2DCS.22CHA01EH128 | 11042 | #3发电机A套逆功率报警 |  | digital
N2DCS.22CHA01EH129 | 11043 | #3发电机A套过励磁报警 |  | digital
N2DCS.22CHA01EH130 | 11044 | #3发电机A套定子过负荷报警 |  | digital
N2DCS.22CHA01EH131 | 11045 | #3发电机A套负序过负荷报警 |  | digital
N2DCS.22CHA01EH132 | 11046 | #3发电机A套定子接地报警 |  | digital
N2DCS.22CHA01EH133 | 11047 | #3发电机A套频率报警 |  | digital
N2DCS.22CHA01EH134 | 11048 | #3主变A套保护切换继电器动作 |  | digital
N2DCS.22CHA01EH135 | 11049 | #3主变A套保护切换继电器失电 |  | digital
N2DCS.22CHA02EH101 | 11050 | #3主变B套差动保护动作 |  | digital
N2DCS.22CHA02EH102 | 11051 | #3发电机B套励磁主保护动作 |  | digital
N2DCS.22CHA02EH103 | 11052 | #3发电机B套差动保护动作 |  | digital
N2DCS.22CHA02EH104 | 11053 | #3发电机B套失灵启动保护动作 |  | digital
N2DCS.22CHA02EH105 | 11054 | #3主变B套非全相保护动作 |  | digital
N2DCS.22CHA02EH106 | 11055 | #3主变B套断口闪络保护动作 |  | digital
N2DCS.22CHA02EH107 | 11056 | #3发电机B套匝间保护动作 |  | digital
N2DCS.22CHA02EH108 | 11057 | #3发电机B套零序定子接地保护动 |  | digital
N2DCS.22CHA02EH109 | 11058 | #3发电机B套对称过负荷跳闸 |  | digital
N2DCS.22CHA02EH110 | 11059 | #3发电机B套负序过负荷跳闸 |  | digital
N2DCS.22CHA02EH111 | 11060 | #3发电机B套失磁保护动作 |  | digital
N2DCS.22CHA02EH112 | 11061 | #3发电机B套失步保护动作 |  | digital
N2DCS.22CHA02EH113 | 11062 | #3发电机B套过电压保护动作 |  | digital
N2DCS.22CHA02EH114 | 11063 | #3发电机B套过励磁保护动作 |  | digital
N2DCS.22CHA02EH115 | 11064 | #3发电机B套逆功率保护动作 |  | digital
N2DCS.22CHA02EH116 | 11065 | #3发电机B套频率异常跳闸 |  | digital
N2DCS.22CHA02EH117 | 11066 | #3发电机B套相间后备保护动作 |  | digital
N2DCS.22CHA02EH118 | 11067 | #3发电机B套起停机保护动作 |  | digital
N2DCS.22CHA02EH119 | 11068 | #3发电机B套误上电保护动作 |  | digital
N2DCS.22CHA02EH120 | 11069 | #3主变B套相间后备保护动作 |  | digital
N2DCS.22CHA02EH121 | 11070 | #3主变B套接地后备保护动作 |  | digital
N2DCS.22CHA02EH122 | 11071 | #3主变B套间隙后备保护动作 |  | digital
N2DCS.22CHA02EH123 | 11072 | #3机B套励磁后备与异常保护动 |  | digital
N2DCS.22CHA02EH124 | 11073 | #3机B套发变组保护TA异常 |  | digital
N2DCS.22CHA02EH125 | 11074 | #3机B套发变组保护TV异常 |  | digital
N2DCS.22CHA02EH126 | 11075 | #3机B套发变组保护差流越限 |  | digital
N2DCS.22CHA02EH127 | 11076 | #3主变B套启动通风告警 |  | digital
N2DCS.22CHA02EH128 | 11077 | #3发电机B套三次谐波定子接地 |  | digital
N2DCS.22CHA02EH129 | 11078 | #3机B套发变组保护装置告警 |  | digital
N2DCS.22CHA02EH130 | 11079 | #3机B套发变组保护失电告警 |  | digital
N2DCS.22CHA02EH131 | 11080 | #3机B套发变组保护失压告警 |  | digital
N2DCS.22CHA02EH132 | 11081 | #3机B套主变保护切换继电器动作 |  | digital
N2DCS.22CHA02EH133 | 11082 | #3机B套主变保护切换继电器失电 |  | digital
N2DCS.22CHA03EH101 | 11083 | #3机非电量保护装置闭锁 |  | digital
N2DCS.22CHA03EH102 | 11084 | #3机非电量保护装置报警 |  | digital
N2DCS.22CHA03EH103 | 11085 | #3主变非电量电源监视 |  | digital
N2DCS.22CHA03EH104 | 11086 | #3主变冷控失电延时跳闸 |  | digital
N2DCS.22CHA03EH105 | 11087 | #3机安稳装置切机 |  | digital
N2DCS.22CHA03EH106 | 11088 | #3主变本体重瓦斯跳闸 |  | digital
N2DCS.22CHA03EH107 | 11089 | #3主变油面温度高跳闸 |  | digital
N2DCS.22CHA03EH108 | 11090 | #3主变绕组温度高跳闸 |  | digital
N2DCS.22CHA03EH109 | 11091 | #3主变压力突变跳闸 |  | digital
N2DCS.22CHA03EH110 | 11092 | #3机母差及失灵联跳 |  | digital
N2DCS.22CHA03EH111 | 11093 | #3主变本体轻瓦斯信号 |  | digital
N2DCS.22CHA03EH112 | 11094 | #3主变绕组温度高信号 |  | digital
N2DCS.22CHA03EH113 | 11095 | #3主变油面温度高信号 |  | digital
N2DCS.22CHA03EH114 | 11096 | #3主变压力释放信号 |  | digital
N2DCS.22CHA03EH115 | 11097 | #3主变本体油位异常信号 |  | digital
N2DCS.22CHA03EH116 | 11098 | #3机励磁系统故障 |  | digital
N2DCS.22CHA03EH117 | 11099 | #3发电机转子一点接地保护跳闸 |  | digital
N2DCS.22CHA03EH118 | 11100 | #3机励磁变压器温度保护跳闸 |  | digital
N2DCS.22CHA03EH119 | 11101 | #3发变组操作箱第一控制回路断线 |  | digital
N2DCS.22CHA03EH120 | 11102 | #3发变组操作箱第二控制回路断线 |  | digital
N2DCS.22CHA03EH121 | 11103 | #3发变组操作箱第一出口跳闸 |  | digital
N2DCS.22CHA03EH122 | 11104 | #3发变组操作箱第二出口跳闸 |  | digital
N2DCS.22CHA03EH123 | 11105 | #3主变高压侧开关位置不一致 |  | digital
N2DCS.22CHA03EH124 | 11106 | #3机失步解列跳闸 |  | digital
N2DCS.22MKC01_ACK | 11107 | 励磁系统确认按钮 |  | digital
N2DCS.22MKC01_DPMT | 11108 | #3发电机减少励磁允许 |  | digital
N2DCS.22MKC01_UPMT | 11109 | #3发电机增加励磁允许 |  | digital
N2DCS.22MKC01EH001 | 11110 | #3机励磁系统励磁已投入 |  | digital
N2DCS.22MKC01EH002 | 11111 | #3机励磁系统励磁已退出 |  | digital
N2DCS.22MKC01EH003 | 11112 | #3机励磁系统自动控制已投入 |  | digital
N2DCS.22MKC01EH004 | 11113 | #3机励磁系统手动控制已投入 |  | digital
N2DCS.22MKC01EH005 | 11114 | #3机励磁系统就地控制已投入 |  | digital
N2DCS.22MKC01EH006 | 11115 | #3机励磁系统启动就绪 |  | digital
N2DCS.22MKC01EH007 | 11116 | #3机励磁系统故障 |  | digital
N2DCS.22MKC01EH008 | 11117 | #3机励磁系统过励限制 |  | digital
N2DCS.22MKC01EH009 | 11118 | #3机励磁系统欠励限制动作 |  | digital
N2DCS.22MKC01EH010 | 11119 | #3机励磁系统U/f限制动作 |  | digital
N2DCS.22MKC01EH011 | 11120 | #3机励磁系统起励失败 |  | digital
N2DCS.22MKC01EH012 | 11121 | #3机励磁系统设定值越限 |  | digital
N2DCS.22MKC01EH013 | 11122 | #3发电机定子电压检测故障 |  | digital
N2DCS.22MKC01EH014 | 11123 | #3机励磁系统无功调节已投入 |  | digital
N2DCS.22MKC01EH015 | 11124 | #3机励磁系统功率因数调节投入 |  | digital
N2DCS.22MKC01EH016 | 11125 | #3机励磁系统总报警 |  | digital
N2DCS.22MKC01EH017 | 11126 | #3机励磁系统控制通道1运行 |  | digital
N2DCS.22MKC01EH018 | 11127 | #3机励磁系统控制通道2运行 |  | digital
N2DCS.22MKC01EH019 | 11128 | #3机励磁系统有功率柜退出 |  | digital
N2DCS.22MKC01EH020 | 11129 | #3发电机灭磁开关合位 |  | digital
N2DCS.22MKC01EH021 | 11130 | #3发电机灭磁开关分位 |  | digital
N2DCS.22MKC01EH022 | 11131 | #3机灭磁开关分位 |  | digital
N2DCS.22MKC01EJ001 | 11132 | #3机励磁系统DCS增磁命令 |  | digital
N2DCS.22MKC01EJ002 | 11133 | #3机励磁系统DCS减磁命令 |  | digital
N2DCS.22MKC01EJ003 | 11134 | #3机励磁系统DCS起励 |  | digital
N2DCS.22MKC01EJ004 | 11135 | #3机励磁系统DCS灭磁 |  | digital
N2DCS.22MKC01EJ005 | 11136 | #3机励磁系统切换至自动模式 |  | digital
N2DCS.22MKC01EJ006 | 11137 | #3机励磁系统切换至手动模式 |  | digital
N2DCS.22MKC01EJ007 | 11138 | #3机励磁系统切至恒无功功率调节 |  | digital
N2DCS.22MKC01EJ008 | 11139 | #3机励磁系统切至恒功率因数调节 |  | digital
N2DCS.ECSALMA1 | 11140 |  |  | digital
N2DCS.ECSALMA2 | 11141 |  |  | digital
N2DCS.20CBQ01EH113A | 11142 | 6KV 2A段快切装置切换允许 |  | digital
N2DCS.AVCEXCNDOWN | 11143 | AVC减磁 |  | digital
N2DCS.AVCEXCNUP | 11144 | AVC增磁 |  | digital
N2DCS.EALM001 | 11145 | 6KV 2A段母线PT保护装置故障 |  | digital
N2DCS.EALM002 | 11146 | 6kV 2A段母线过压报警 |  | digital
N2DCS.EALM003 | 11147 | 6kV 2A段母线低压报警 |  | digital
N2DCS.EALM004 | 11148 | 6kV 2A段母线失压报警 |  | digital
N2DCS.EALM005 | 11149 | 6kV 2A段母线接地报警 |  | digital
N2DCS.EALM006 | 11150 | 6kV 2A段母线谐振报警 |  | digital
N2DCS.EALM007 | 11151 | 6kV 2A段快切装置启动正常切换 |  | digital
N2DCS.EALM008 | 11152 | 6kV 2A段快切装置总告警 |  | digital
N2DCS.EALM009 | 11153 | 6KV 2B段母线PT保护装置故障 |  | digital
N2DCS.EALM010 | 11154 | 6KV 2B段母线过压报警 |  | digital
N2DCS.EALM011 | 11155 | 6KV 2B段母线低压报警 |  | digital
N2DCS.EALM012 | 11156 | 6KV 2B段母线失压报警 |  | digital
N2DCS.EALM013 | 11157 | 6KV 2B段母线接地报警 |  | digital
N2DCS.EALM014 | 11158 | 6KV 2B段母线谐振报警 |  | digital
N2DCS.EALM015 | 11159 | 6kV 2B段快切装置启动正常切换 |  | digital
N2DCS.EALM016 | 11160 | 6kV 2B段快切装置总告警 |  | digital
N2DCS.EALM017 | 11161 | 6KV 2A段工作分支PT异常 |  | digital
N2DCS.EALM018 | 11162 | 6KV 2B段工作分支PT异常 |  | digital
N2DCS.EALM019 | 11163 | 生产办公楼A变6kV侧开关异常跳闸 |  | digital
N2DCS.EALM020 | 11164 | 机组公用A变6kV侧开关异常跳闸 |  | digital
N2DCS.EALM021 | 11165 | 厂区公用A变6kV侧开关异常跳闸 |  | digital
N2DCS.EALM022 | 11166 | 补给水A变6kV侧开关异常跳闸 |  | digital
N2DCS.EALM023 | 11167 | 进气冷却A变6kV侧开关异常跳闸 |  | digital
N2DCS.EALM024 | 11168 | #2机组保安段备自投装置故障 |  | digital
N2DCS.EALM025 | 11169 | #2机组保安段母线异常 |  | digital
N2DCS.EALM026 | 11170 | 柴油发电机异常 |  | digital
N2DCS.EALM027 | 11171 | 110V直流母线电压低 |  | digital
N2DCS.EALM028 | 11172 | 110V直流蓄电池故障 |  | digital
N2DCS.EALM029 | 11173 | 220V直流母线电压低 |  | digital
N2DCS.EALM030 | 11174 | 220V直流蓄电池故障 |  | digital
N2DCS.EALM031 | 11175 | UPS主控柜故障 |  | digital
N2DCS.EALM032 | 11176 | 发电机漏水 |  | digital
N2DCS.EALMALL | 11177 | #3机电气光字牌报警汇总1 |  | digital
N2DCS.EALMUNACK | 11178 | #3机电气光字牌报警手动确认指令 |  | digital
N2DCS.LCALARM | 11179 | #3机励磁故障总信号 |  | digital
N2DCS.ONE10 | 11180 | Ovation Control Builder |  | digital
N2DCS.QJBW_SEQSTACKOK | 11181 | #3机并网前各刀闸在正确位置 |  | digital
N2DCS.QJBW_SEQSTFINISH | 11182 | #3机并网顺控控已完成 |  | digital
N2DCS.QJTQYX1 | 11183 | #3机并网允许条件 |  | digital
N2DCS.ZERO10 | 11184 | 开关量0 |  | digital
N2DCS.20BBA00EH201 | 11185 | 6KV 2A段备用分支PT异常 |  | digital
N2DCS.20BBA00EH202 | 11186 | 6KV 2A段备用分支PT保护小车位置 |  | digital
N2DCS.20BBA00GS002PF | 11187 | 6KV开关62A02保护装置异常总信号 |  | digital
N2DCS.20BBA00GS002RC | 11188 | 6KV 2A段备用进线开关远方控制 |  | digital
N2DCS.20BBA00GS002RD | 11189 | 6KV 2A段备用电源进线开关合闸 |  | digital
N2DCS.20BBA00GS002RP | 11190 | 6KV 2A段备用进线开关合闸位置 |  | digital
N2DCS.20BBA00GS002SW | 11191 | 6KV 2A段备用进线开关试验位置 |  | digital
N2DCS.20BBA00GS002TD | 11192 | 6KV 2A段备用电源进线开关分闸 |  | digital
N2DCS.20BBA00GS002TP | 11193 | 6KV 2A段备用进线开关分闸位置 |  | digital
N2DCS.20BBA00GS002YW | 11194 | 6KV 2A段备用进线开关工作位置 |  | digital
N2DCS.20BBB00EH001 | 11195 | 6KV 2B段母线PT保护装置故障 |  | digital
N2DCS.20BBB00EH002 | 11196 | 6KV 2B段母线过压报警 |  | digital
N2DCS.20BBB00EH003 | 11197 | 6KV 2B段母线低压报警 |  | digital
N2DCS.20BBB00EH004 | 11198 | 6KV 2B段母线失压报警 |  | digital
N2DCS.20BBB00EH005 | 11199 | 6KV 2B段母线接地报警 |  | digital
N2DCS.20BBB00EH006 | 11200 | 6KV 2B段母线谐振报警 |  | digital
N2DCS.20BBB00EH101 | 11201 | 6kV 2B段工作分支PT异常 |  | digital
N2DCS.20BBB00EH102 | 11202 | 6kV 2B段工作分支PT保护小车位置 |  | digital
N2DCS.20BBB00GS001PF | 11203 | 6KV开关62B01保护装置异常总信号 |  | digital
N2DCS.20BBB00GS001PF1 | 11204 | 6KV开关62B01弧光保护装置故障 |  | digital
N2DCS.20BBB00GS001PS1 | 11205 | 6KV开关62B01弧光保护动作 |  | digital
N2DCS.20BBB00GS001RC | 11206 | 6KV 2B段工作进线开关远方控制 |  | digital
N2DCS.20BBB00GS001RD | 11207 | 6KV 2B段工作电源进线开关合闸 |  | digital
N2DCS.20BBB00GS001RP | 11208 | 6KV 2B段工作进线开关合闸位置 |  | digital
N2DCS.20BBB00GS001SW | 11209 | 6KV 2B段工作进线开关试验位置 |  | digital
N2DCS.20BBB00GS001TD | 11210 | 6KV 2B段工作电源进线开关分闸 |  | digital
N2DCS.20BBB00GS001TP | 11211 | 6KV 2B段工作进线开关分闸位置 |  | digital
N2DCS.20BBB00GS001YW | 11212 | 6KV 2B段工作进线开关工作位置 |  | digital
N2DCS.20BBT01_DPMT | 11213 | #2高厂变有载调压升压允许 |  | digital
N2DCS.20BBT01_UPMT | 11214 | #2高厂变有载调压降压允许 |  | digital
N2DCS.20BBT01EH901 | 11215 | 高厂变有载调压开关分接头位置1 |  | digital
N2DCS.20BBT01EH902 | 11216 | 高厂变有载调压开关分接头位置2 |  | digital
N2DCS.20BBT01EH903 | 11217 | 高厂变有载调压开关分接头位置3 |  | digital
N2DCS.20BBT01EH904 | 11218 | 高厂变有载调压开关分接头位置4 |  | digital
N2DCS.20BBT01EH905 | 11219 | 高厂变有载调压开关分接头位置5 |  | digital
N2DCS.20BBT01EH906 | 11220 | 高厂变有载调压开关分接头位置6 |  | digital
N2DCS.20BBT01EH907 | 11221 | 高厂变有载调压开关分接头位置7 |  | digital
N2DCS.20BBT01EH908 | 11222 | 高厂变有载调压开关分接头位置8 |  | digital
N2DCS.20BBT01EH909A | 11223 | 高厂变有载调压开关分接头位置9A |  | digital
N2DCS.20BBT01EH909B | 11224 | 高厂变有载调压开关分接头位置9B |  | digital
N2DCS.20BBT01EH909C | 11225 | 高厂变有载调压开关分接头位置9C |  | digital
N2DCS.20BBT01EH910 | 11226 | 高厂变有载调压开关分接头位置10 |  | digital
N2DCS.20BBT01EH911 | 11227 | 高厂变有载调压开关分接头位置11 |  | digital
N2DCS.20BBT01EH912 | 11228 | 高厂变有载调压开关分接头位置12 |  | digital
N2DCS.20BBT01EH913 | 11229 | 高厂变有载调压开关分接头位置13 |  | digital
N2DCS.20BBT01EH914 | 11230 | 高厂变有载调压开关分接头位置14 |  | digital
N2DCS.20BBT01EH915 | 11231 | 高厂变有载调压开关分接头位置15 |  | digital
N2DCS.20BBT01EH916 | 11232 | 高厂变有载调压开关分接头位置16 |  | digital
N2DCS.20BBT01EH917 | 11233 | 高厂变有载调压开关分接头位置17 |  | digital
N2DCS.20BBT01GS001_DPMT | 11234 | 高厂变有载调压允许降压 |  | digital
N2DCS.20BBT01GS001_UPMT | 11235 | 高厂变有载调压允许升压 |  | digital
N2DCS.20BBT01GS001PF | 11236 | #2高厂变有载调压故障 |  | digital
N2DCS.20BBT01GS001PS | 11237 | #2高厂变有载调压切换操作未完成 |  | digital
N2DCS.20BBT01GS001RC | 11238 | #2高厂变有载调压远方控制 |  | digital
N2DCS.20BBT01GS001RD1 | 11239 | #2高厂变有载调压开关降压指令 |  | digital
N2DCS.20BBT01GS001RD2 | 11240 | #2高厂变有载调压开关升压指令 |  | digital
N2DCS.20BBT01GS001RP | 11241 | #2高厂变有载调压开关正在调压 |  | digital
N2DCS.20BBT01GS001TD | 11242 | #2高厂变有载调压开关停止调压 |  | digital
N2DCS.20BFB00EH201 | 11243 | 380V机组工作PC 2B段母线电压低 |  | digital
N2DCS.20BFB00EH202 | 11244 | 380V工作PC 2B段PT保护装置故障 |  | digital
N2DCS.20BFB00EH203 | 11245 | 380V工作PC 2B段PT刀熔开关分位 |  | digital
N2DCS.20BFB00GS103PF | 11246 | 工作PC IIB至保安段开关综合故障 |  | digital
N2DCS.20BFB00GS103RC | 11247 | 工作PC IIB至保安段开关远方控制 |  | digital
N2DCS.20BFB00GS103RD | 11248 | 380V工作PC IIB至保安段开关合闸 |  | digital
N2DCS.20BFB00GS103RP | 11249 | 工作PC IIB至保安段开关合闸位置 |  | digital
N2DCS.20BFB00GS103TD | 11250 | 380V工作PC IIB至保安段开关分闸 |  | digital
N2DCS.20BFB00GS103TP | 11251 | 工作PC IIB至保安段开关分闸位置 |  | digital
N2DCS.20BFB00GS201PF | 11252 | 工作PC 2B至保安段开关综合故障 |  | digital
N2DCS.20BFB00GS201RC | 11253 | 工作PC 2B至保安段开关在远控 |  | digital
N2DCS.20BFB00GS201RD | 11254 | 工作PC 2B至保安段开关合闸指令 |  | digital
N2DCS.20BFB00GS201RP | 11255 | 工作PC 2B至保安段开关合闸位置 |  | digital
N2DCS.20BFB00GS201TD | 11256 | 工作PC 2B至保安段开关分闸指令 |  | digital
N2DCS.20BFB00GS201TP | 11257 | 工作PC 2B至保安段开关分闸位置 |  | digital
N2DCS.20BFT20GS101PF | 11258 | 6KV开关62B10保护装置异常总信号 |  | digital
N2DCS.20BFT20GS101PS | 11259 | 工作2B变6kV侧开关保护动作 |  | digital
N2DCS.20BFT20GS101RC | 11260 | 工作2B变6kV侧开关远方控制 |  | digital
N2DCS.20BFT20GS101RD | 11261 | 工作2B变6kV侧开关合闸指令 |  | digital
N2DCS.20BFT20GS101RP | 11262 | 工作2B变6kV侧开关合闸位置 |  | digital
N2DCS.20BFT20GS101SW | 11263 | 工作2B变6kV侧开关试验位置 |  | digital
N2DCS.20BFT20GS101TD | 11264 | 工作2B变6kV侧开关分闸指令 |  | digital
N2DCS.20BFT20GS101TP | 11265 | 工作2B变6kV侧开关分闸位置 |  | digital
N2DCS.20BFT20GS101YW | 11266 | 工作2B变6kV侧开关工作位置 |  | digital
N2DCS.20BFT20GS102PF | 11267 | 工作2B变380V侧开关综合故障 |  | digital
N2DCS.20BFT20GS102RC | 11268 | 工作2B变380V侧开关远方控制 |  | digital
N2DCS.20BFT20GS102RD | 11269 | 工作2B变380V侧开关合闸指令 |  | digital
N2DCS.20BFT20GS102RP | 11270 | 工作2B变380V侧开关合闸位置 |  | digital
N2DCS.20BFT20GS102TD | 11271 | 工作2B变380V侧开关分闸指令 |  | digital
N2DCS.20BFT20GS102TP | 11272 | 工作2B变380V侧开关分闸位置 |  | digital
N2DCS.20BJA00GS202RP | 11273 | 工作PC2B至#3机MCCA开关合闸位置 |  | digital
N2DCS.20BJA00GS202TP | 11274 | 工作PC2B至#3机MCCA开关分闸位置 |  | digital
N2DCS.20BJB00GS202RP | 11275 | 工作PC2B至#3机MCCB开关合闸位置 |  | digital
N2DCS.20BJB00GS202TP | 11276 | 工作PC2B至#3机MCCB开关分闸位置 |  | digital
N2DCS.20BJC00GS202RP | 11277 | 工作PC 2B至余炉MCC开关合闸位置 |  | digital
N2DCS.20BJC00GS202TP | 11278 | 工作PC 2B至余炉MCC开关分闸位置 |  | digital
N2DCS.20BJD00GS202PF | 11279 | 工作PC2B至#4机MCCA开关综合故障 |  | digital
N2DCS.20BJD00GS202RC | 11280 | 工作PC2B至#4机MCCA开关远方控制 |  | digital
N2DCS.20BJD00GS202RD | 11281 | 工作PC 2B至#4机MCC A开关合指令 |  | digital
N2DCS.20BJD00GS202RP | 11282 | 工作PC2B至#4机MCCA开关合闸位置 |  | digital
N2DCS.20BJD00GS202TD | 11283 | 工作PC 2B至#4机MCC A开关分指令 |  | digital
N2DCS.20BJD00GS202TP | 11284 | 工作PC2B至#4机MCCA开关分闸位置 |  | digital
N2DCS.20BJE00GS202PF | 11285 | 工作PC2B至#4机MCCB开关综合故障 |  | digital
N2DCS.20BJE00GS202RC | 11286 | 工作PC2B至#4机MCCB开关远方控制 |  | digital
N2DCS.20BJE00GS202RD | 11287 | 工作PC2B至#4机MCC B开关合指令 |  | digital
N2DCS.20BJE00GS202RP | 11288 | 工作PC2B至#4机MCCB开关合闸位置 |  | digital
N2DCS.20BJE00GS202TD | 11289 | 工作PC2B至#4机MCC B开关分指令 |  | digital
N2DCS.20BJE00GS202TP | 11290 | 工作PC2B至#4机MCCB开关分闸位置 |  | digital
N2DCS.20BMA00EH201 | 11291 | 380V保安段母线电压低 |  | digital
N2DCS.20BMA00EH202 | 11292 | 380V保安段PT保护装置故障 |  | digital
N2DCS.20BMA00GS001_PUT | 11293 | 保安段备自投装置已投入 |  | digital
N2DCS.20BMA00GS001PF | 11294 | 保安段柴油机进线K11开关故障 |  | digital
N2DCS.20BMA00GS001RC | 11295 | 保安段柴油机进线K11开关在远控 |  | digital
N2DCS.20BMA00GS001RD | 11296 | 保安段柴油机进线K11开关合闸令 |  | digital
N2DCS.20BMA00GS001RP | 11297 | 保安段柴油机进线K11开关合闸位 |  | digital
N2DCS.20BMA00GS001TD | 11298 | 保安段柴油机进线K11开关分闸令 |  | digital
N2DCS.20BMA00GS001TP | 11299 | 保安段柴油机进线K11开关分闸位 |  | digital
N2DCS.20BMA00GS002_PUT | 11300 | 保安段备自投装置已投入 |  | digital
N2DCS.20BMA00GS002PF | 11301 | 保安段工作进线K12开关综合故障 |  | digital
N2DCS.20BMA00GS002RC | 11302 | 保安段工作进线K12开关远方控制 |  | digital
N2DCS.20BMA00GS002RD | 11303 | 保安段工作进线K12开关合闸指令 |  | digital
N2DCS.20BMA00GS002RP | 11304 | 保安段工作进线K12开关合闸位置 |  | digital
N2DCS.20BMA00GS002TD | 11305 | 保安段工作进线K12开关分闸指令 |  | digital
N2DCS.20BMA00GS002TP | 11306 | 保安段工作进线K12开关分闸位置 |  | digital
N2DCS.20BMA00GS003_PUT | 11307 | 保安段备自投装置已投入 |  | digital
N2DCS.20BMA00GS003PF | 11308 | 保安段工作进线K13开关综合故障 |  | digital
N2DCS.20BMA00GS003RC | 11309 | 保安段工作进线K13开关远方控制 |  | digital
N2DCS.20BMA00GS003RD | 11310 | 保安段工作进线K13开关合闸指令 |  | digital
N2DCS.20BMA00GS003RP | 11311 | 保安段工作进线K13开关合闸位置 |  | digital
N2DCS.20BMA00GS003TD | 11312 | 保安段工作进线K13开关分闸指令 |  | digital
N2DCS.20BMA00GS003TP | 11313 | 保安段工作进线K13开关分闸位置 |  | digital
N2DCS.20BNA00GS202PF | 11314 | 工作PC2B至#4机EMCC开关综合故障 |  | digital
N2DCS.20BNA00GS202RC | 11315 | 工作PC2B至#4机EMCC开关远方控制 |  | digital
N2DCS.20BNA00GS202RD | 11316 | 工作PC2B至#4机EMCC开关合闸指令 |  | digital
N2DCS.20BNA00GS202RP | 11317 | 工作PC2B至#4机EMCC开关合闸位置 |  | digital
N2DCS.20BNA00GS202TD | 11318 | 工作PC2B至#4机EMCC开关分闸指令 |  | digital
N2DCS.20BNA00GS202TP | 11319 | 工作PC2B至#4机EMCC开关分闸位置 |  | digital
N2DCS.20BRU01EH001 | 11320 | #2机组UPS系统主机柜1综合报警 |  | digital
N2DCS.20BRU01EH003 | 11321 | #2机组UPS系统主机柜2综合报警 |  | digital
N2DCS.20BRU02EH002 | 11322 | #2机组UPS系统配电开关报警 |  | digital
N2DCS.20BTL01EH001 | 11323 | #3机220V直流系统交流电源告警 |  | digital
N2DCS.20BTL01EH002 | 11324 | #3机220V直流系统整流模块告警 |  | digital
N2DCS.20BTL01EH003 | 11325 | #3机220V直流系统蓄电池组告警 |  | digital
N2DCS.20BTL01EH004 | 11326 | #3机220V直流系统直流母线告警 |  | digital
N2DCS.20BTL01EH005 | 11327 | #3机220V直流系统直流配电告警 |  | digital
N2DCS.20BTL01EH006 | 11328 | #3机220V直流系统通信中断告警 |  | digital
N2DCS.20BTL01EH007 | 11329 | #3机220V直流系统微机监控故障 |  | digital
N2DCS.20BTL01EH008 | 11330 | #3机220V直流联络开关合闸报警 |  | digital
N2DCS.20BTM01EH001 | 11331 | #3机110V直流A段交流电源告警 |  | digital
N2DCS.20BTM01EH002 | 11332 | #3机110V直流A段整流模块告警 |  | digital
N2DCS.20BTM01EH003 | 11333 | #3机110V直流#1蓄电池组告警 |  | digital
N2DCS.20BTM01EH004 | 11334 | #3机110V直流A段直流母线告警 |  | digital
N2DCS.20BTM01EH005 | 11335 | #3机110V直流A段直流配电告警 |  | digital
N2DCS.20BTM01EH006 | 11336 | #3机110V直流A段通信中断告警 |  | digital
N2DCS.20BTM01EH007 | 11337 | #3机110V直流A段微机监控故障 |  | digital
N2DCS.20BTM02EH001 | 11338 | #3机110V直流B段交流电源告警 |  | digital
N2DCS.20BTM02EH002 | 11339 | #3机110V直流B段整流模块告警 |  | digital
N2DCS.20BTM02EH003 | 11340 | #3机110V直流#2蓄电池组告警 |  | digital
N2DCS.20BTM02EH004 | 11341 | #3机110V直流B段直流母线告警 |  | digital
N2DCS.20BTM02EH005 | 11342 | #3机110V直流B段直流配电告警 |  | digital
N2DCS.20BTM02EH006 | 11343 | #3机110V直流B段通信中断告警 |  | digital
N2DCS.20BTM02EH007 | 11344 | #3机110V直流B段微机监控故障 |  | digital
N2DCS.20CBQ01EH2_FL | 11345 | 6kV 2B段快切装置故障 |  | digital
N2DCS.20CBQ01EH2_PMT | 11346 | 6kV IIB段快切装置启动允许 |  | digital
N2DCS.20CBQ01EH201 | 11347 | 6kV 2B段快切装置启动正常切换 |  | digital
N2DCS.20CBQ01EH202 | 11348 | 6kV 2B段快切装置手动闭锁 |  | digital
N2DCS.20CBQ01EH203 | 11349 | 6kV 2B段快切装置远方复归 |  | digital
N2DCS.20CBQ01EH204 | 11350 | 6kV 2B段快切装置合工作 |  | digital
N2DCS.20CBQ01EH205 | 11351 | 6kV 2B段快切装置合备用 |  | digital
N2DCS.20CBQ01EH206 | 11352 | 6kV 2B段快切装置总告警 |  | digital
N2DCS.20CBQ01EH207 | 11353 | 6kV 2B段快切装置切换完毕 |  | digital
N2DCS.20CBQ01EH208 | 11354 | 6kV 2B段快切装置电源失压 |  | digital
N2DCS.20CBQ01EH209 | 11355 | 6kV 2B段快切装置切换失败 |  | digital
N2DCS.20CBQ01EH210 | 11356 | 6kV 2B段快切装置切换闭锁 |  | digital
N2DCS.20CBQ01EH211 | 11357 | 6kV 2B段快切装置自动允许 |  | digital
N2DCS.20CBQ01EH212 | 11358 | 6kV 2B段快切装置手动允许 |  | digital
N2DCS.20CBQ01EH213 | 11359 | 6kV 2B段快切装置单操 |  | digital
N2DCS.20CBQ02EH101 | 11360 | #3机保安段备自投远方手动切换 |  | digital
N2DCS.20CBQ02EH102 | 11361 | #3机保安段备自投信号复归 |  | digital
N2DCS.20CBQ02EH103 | 11362 | #3机保安段备自投远方闭锁 |  | digital
N2DCS.20CBQ02EH104 | 11363 | #3机保安段备自投动作 |  | digital
N2DCS.20CBQ02EH105 | 11364 | #3机保安段备自投装置故障报警 |  | digital
N2DCS.20CBQ02EH106 | 11365 | #3机保安段备自投装置已闭锁 |  | digital
N2DCS.20CBQ02EH107 | 11366 | #3机保安段备自投装置失电告警 |  | digital
N2DCS.20MJA01EH001 | 11367 | #3机柴油发电机水温故障 |  | digital
N2DCS.20MJA01EH002 | 11368 | #3机柴油发电机低油压故障 |  | digital
N2DCS.20MJA01EH003 | 11369 | #3机柴油发电机超速故障 |  | digital
N2DCS.20MJA01EH004 | 11370 | #3机柴油发电机三次启动失败 |  | digital
N2DCS.20MJA01EH005 | 11371 | #3机柴油发电机运行正常 |  | digital
N2DCS.20MJA01EH006 | 11372 | #3机柴油发电机系统处于自动 |  | digital
N2DCS.20MJA01EH007 | 11373 | #3机柴油发电机蓄电池电压低报警 |  | digital
N2DCS.20MJA01EH008 | 11374 | #3机柴油发电机公共预报警 |  | digital
N2DCS.20MJA01EH009 | 11375 | #3机柴油发电机公共报警 |  | digital
N2DCS.20MJA01EH010 | 11376 | #3机柴油发电机差动保护 |  | digital
N2DCS.20MJA01EH011 | 11377 | #3机柴油发电机DC 24V电源丢失 |  | digital
N2DCS.20MJA01EH012 | 11378 | #3机柴油发电机DC 110V电源丢失 |  | digital
N2DCS.20MJA01GS001RP | 11379 | #3机柴油发电机K0开关合闸状态 |  | digital
N2DCS.20MJA01GS001TP | 11380 | #3机柴油发电机K0开关分闸状态 |  | digital
N2DCS.21BAC01GS101RP | 11381 | #4发电机出口GCB开关合闸位置 |  | digital
N2DCS.21BAC01GS101TP | 11382 | #4发电机出口GCB开关分闸位置 |  | digital
N2DCS.21BAC01GS201RP | 11383 | #4发电机出口隔离开关8020合位置 |  | digital
N2DCS.21BAC01GS201TP | 11384 | #4发电机出口隔离开关8020分位置 |  | digital
N2DCS.21BAC01GS202RP | 11385 | #4发电机SFC启动开关8021合位置 |  | digital
N2DCS.21BAC01GS202TP | 11386 | #4发电机SFC启动开关8021分位置 |  | digital
N2DCS.21BAC01GS301RP | 11387 | #4发电机出口接地开关GS301合位 |  | digital
N2DCS.21BAC01GS301TP | 11388 | #4发电机出口接地开关82000分位 |  | digital
N2DCS.21BAC01GS302RP | 11389 | #4发电机出口接地开关GS303合位 |  | digital
N2DCS.21BAC01GS302TP | 11390 | #4发电机出口接地开关GS303分位 |  | digital
N2DCS.21BAT01EH001 | 11391 | #4主变冷却器Ⅰ段电源运行 |  | digital
N2DCS.21BAT01EH002 | 11392 | #4主变冷却器II段电源运行 |  | digital
N2DCS.21BAT01EH003 | 11393 | #4主变冷却器Ⅰ段电源故障 |  | digital
N2DCS.21BAT01EH004 | 11394 | #4主变冷却器II段电源故障 |  | digital
N2DCS.21BAT01EH005 | 11395 | #4主变冷却器控制电源故障 |  | digital
N2DCS.21BAT01EH006 | 11396 | #4主变工作冷却器故障 |  | digital
N2DCS.21BAT01EH007 | 11397 | #4主变备用冷却器故障 |  | digital
N2DCS.21BAT01EH008 | 11398 | #4主变风冷全停 |  | digital
N2DCS.21BAT01EH009 | 11399 | #4主变辅助投入 |  | digital
N2DCS.21BAW10GS201RP | 11400 | #4发电机中性点地刀82000合闸位 |  | digital
N2DCS.21BAW10GS201TP | 11401 | #4发电机中性点地刀82000分闸位 |  | digital
N2DCS.21BAW20EH101 | 11402 | #3发电机PT端子箱开关分闸信号 |  | digital
N2DCS.21CEQ01EH001 | 11403 | #4发变组故障录波装置故障 |  | digital
N2DCS.21CEQ01EH002 | 11404 | #4发变组故障录波装置启动 |  | digital
N2DCS.21CEQ01EH003 | 11405 | #4发变组故障录波装置失电报警 |  | digital
N2DCS.21CHA01EH101 | 11406 | #4发电机A套差动跳闸 |  | digital
N2DCS.21CHA01EH102 | 11407 | #4发电机A套定子接地跳闸 |  | digital
N2DCS.21CHA01EH103 | 11408 | #4发电机A套匝间跳闸 |  | digital
N2DCS.21CHA01EH104 | 11409 | #4发电机A套过负荷跳闸 |  | digital
N2DCS.21CHA01EH105 | 11410 | #4发电机A套电压异常保护跳闸 |  | digital
N2DCS.21CHA01EH106 | 11411 | #4发电机A套失磁保护跳闸 |  | digital
N2DCS.21CHA01EH107 | 11412 | #4发电机A套失步保护跳闸 |  | digital
N2DCS.21CHA01EH108 | 11413 | #4发电机A套负序过负荷跳闸 |  | digital
N2DCS.21CHA01EH109 | 11414 | #4发电机A套过励磁跳闸 |  | digital
N2DCS.21CHA01EH110 | 11415 | #4发电机A套过频保护跳闸 |  | digital
N2DCS.21CHA01EH111 | 11416 | #4发电机A套相间后备跳闸 |  | digital
N2DCS.21CHA01EH112 | 11417 | #4发电机A套误上电跳闸 |  | digital
N2DCS.21CHA01EH113 | 11418 | #4发电机A套逆功率跳闸 |  | digital
N2DCS.21CHA01EH114 | 11419 | #4发电机A套低功率跳闸 |  | digital
N2DCS.21CHA01EH115 | 11420 | #4发电机A套启停机跳闸 |  | digital
N2DCS.21CHA01EH116 | 11421 | #4发电机A套GCB失灵保护跳闸 |  | digital
N2DCS.21CHA01EH117 | 11422 | #4发电机A套低频保护跳闸 |  | digital
N2DCS.21CHA01EH118 | 11423 | #4发电机A套励磁后备保护跳闸 |  | digital
N2DCS.21CHA01EH119 | 11424 | #4发电机A套逆功率报警 |  | digital
N2DCS.21CHA01EH120 | 11425 | #4发电机A套过励磁报警 |  | digital
N2DCS.21CHA01EH121 | 11426 | #4发电机A套定子过负荷报警 |  | digital
N2DCS.21CHA01EH122 | 11427 | #4发电机A套负序过负荷报警 |  | digital
N2DCS.21CHA01EH123 | 11428 | #4发电机A套励磁过负荷报警 |  | digital
N2DCS.21CHA01EH124 | 11429 | #4发电机A套定子接地报警 |  | digital
N2DCS.21CHA01EH125 | 11430 | #4发电机A套失磁报警 |  | digital
N2DCS.21CHA01EH126 | 11431 | #4发电机A套失步报警 |  | digital
N2DCS.21CHA01EH127 | 11432 | #4发电机A套频率保护报警 |  | digital
N2DCS.21CHA01EH128 | 11433 | #4发电机A套保护TA回路断线 |  | digital
N2DCS.21CHA01EH129 | 11434 | #4发电机A套保护TV回路断线 |  | digital
N2DCS.21CHA01EH130 | 11435 | #4发电机A套保护装置闭锁 |  | digital
N2DCS.21CHA01EH131 | 11436 | #4发电机A套保护装置报警 |  | digital
N2DCS.21CHA01EH132 | 11437 | #4发电机A套SFC系统故障联跳 |  | digital
N2DCS.21CHA02EH101 | 11438 | #4发电机B套差动跳闸 |  | digital
N2DCS.21CHA02EH102 | 11439 | #4发电机B套匝间保护跳闸 |  | digital
N2DCS.21CHA02EH103 | 11440 | #4发电机B套起停机接地保护跳闸 |  | digital
N2DCS.21CHA02EH104 | 11441 | #4发电机B套对称过负荷保护跳闸 |  | digital
N2DCS.21CHA02EH105 | 11442 | #4发电机B套负荷过负荷保护跳闸 |  | digital
N2DCS.21CHA02EH106 | 11443 | #4发电机B套失磁保护跳闸 |  | digital
N2DCS.21CHA02EH107 | 11444 | #4发电机B套失步保护跳闸 |  | digital
N2DCS.21CHA02EH108 | 11445 | #4发电机B套电压异常跳闸 |  | digital
N2DCS.21CHA02EH109 | 11446 | #4发电机B套过励磁保护跳闸 |  | digital
N2DCS.21CHA02EH110 | 11447 | #4发电机B套逆功率保护跳闸 |  | digital
N2DCS.21CHA02EH111 | 11448 | #4机B套机端开关失灵启动动作 |  | digital
N2DCS.21CHA02EH112 | 11449 | #4机B套发电机相间后备保护跳 |  | digital
N2DCS.21CHA02EH113 | 11450 | #4机B套发电机频率异常保护跳 |  | digital
N2DCS.21CHA02EH114 | 11451 | #4发电机B套误上电保护跳闸 |  | digital
N2DCS.21CHA02EH115 | 11452 | #4发电机B套励磁变保护跳闸 |  | digital
N2DCS.21CHA02EH116 | 11453 | #4机B套燃机控制系统保护联跳 |  | digital
N2DCS.21CHA02EH117 | 11454 | #4发电机B套差流越限告警 |  | digital
N2DCS.21CHA02EH118 | 11455 | #4发电机B套定时限过负荷告警 |  | digital
N2DCS.21CHA02EH119 | 11456 | #4机B套三次谐波定子接地告警 |  | digital
N2DCS.21CHA02EH120 | 11457 | #4发电机B套TA异常告警 |  | digital
N2DCS.21CHA02EH121 | 11458 | #4发电机B套TV异常告警 |  | digital
N2DCS.21CHA02EH122 | 11459 | #4发电机B套装置故障告警 |  | digital
N2DCS.21CHA02EH123 | 11460 | #4发电机B套失电告警 |  | digital
N2DCS.21CHA02EH124 | 11461 | #4发电机B套SFC系统故障联跳 |  | digital
N2DCS.21CHA03EH101 | 11462 | #4主变A套差动跳闸 |  | digital
N2DCS.21CHA03EH102 | 11463 | #4主变A套相间后备跳闸 |  | digital
N2DCS.21CHA03EH103 | 11464 | #4主变A套接地零序跳闸 |  | digital
N2DCS.21CHA03EH104 | 11465 | #4主变A套间隙零序跳闸 |  | digital
N2DCS.21CHA03EH105 | 11466 | #4主变A套过励磁保护跳闸 |  | digital
N2DCS.21CHA03EH106 | 11467 | #4主变A套开关断口闪络保护跳 |  | digital
N2DCS.21CHA03EH107 | 11468 | #4主变A套非全相跳闸 |  | digital
N2DCS.21CHA03EH108 | 11469 | #2高厂变A套差动跳闸 |  | digital
N2DCS.21CHA03EH109 | 11470 | #2高厂变A套高压侧后备跳闸 |  | digital
N2DCS.21CHA03EH110 | 11471 | #2高厂变A套A分支后备跳闸 |  | digital
N2DCS.21CHA03EH111 | 11472 | #2高厂变A套A分支接地后备跳闸 |  | digital
N2DCS.21CHA03EH112 | 11473 | #2高厂变A套B分支后备跳闸 |  | digital
N2DCS.21CHA03EH113 | 11474 | #2高厂变A套B分支接地后备跳闸 |  | digital
N2DCS.21CHA03EH114 | 11475 | #4主变A套保护装置闭锁 |  | digital
N2DCS.21CHA03EH115 | 11476 | #4主变A套保护装置报警 |  | digital
N2DCS.21CHA03EH116 | 11477 | #4主变A套保护TA断线 |  | digital
N2DCS.21CHA03EH117 | 11478 | #4主变A套保护TV断线 |  | digital
N2DCS.21CHA03EH118 | 11479 | #4主变A套保护失灵启动报警 |  | digital
N2DCS.21CHA03EH119 | 11480 | #4主变A套过激磁报警 |  | digital
N2DCS.21CHA03EH120 | 11481 | #4主变A套过负荷报警 |  | digital
N2DCS.21CHA03EH121 | 11482 | #2高厂变A套过负荷报警 |  | digital
N2DCS.21CHA03EH122 | 11483 | #4主变A套低压侧零序电压报警 |  | digital
N2DCS.21CHA03EH123 | 11484 | #4主变A套保护切换继电器动作 |  | digital
N2DCS.21CHA03EH124 | 11485 | #4主变A套保护切换继电器失电 |  | digital
N2DCS.21CHA04EH101 | 11486 | #4主变B套差动跳闸 |  | digital
N2DCS.21CHA04EH102 | 11487 | #4主变B套相间后备跳闸 |  | digital
N2DCS.21CHA04EH103 | 11488 | #4主变B套接地后备跳闸 |  | digital
N2DCS.21CHA04EH104 | 11489 | #4主变B套间隙后备跳闸 |  | digital
N2DCS.21CHA04EH105 | 11490 | #4主变B套高压侧失灵启动动 |  | digital
N2DCS.21CHA04EH106 | 11491 | #4主变B套高压侧非全相动作 |  | digital
N2DCS.21CHA04EH107 | 11492 | #4主变B套高压侧断口闪络动 |  | digital
N2DCS.21CHA04EH108 | 11493 | #4主变B套过励磁动作 |  | digital
N2DCS.21CHA04EH109 | 11494 | #2高厂变B套主保护动作 |  | digital
N2DCS.21CHA04EH110 | 11495 | #2高厂变B套后备保护动作 |  | digital
N2DCS.21CHA04EH111 | 11496 | #2高厂变B套A分支后备动作 |  | digital
N2DCS.21CHA04EH112 | 11497 | #2高厂变B套B分支后备动作 |  | digital
N2DCS.21CHA04EH113 | 11498 | #2高厂变B套低压侧接地动作 |  | digital
N2DCS.21CHA04EH114 | 11499 | #4机B套差流越限告警 |  | digital
N2DCS.21CHA04EH115 | 11500 | #4机B套定时限过负荷报警 |  | digital
N2DCS.21CHA04EH116 | 11501 | #4机B套启动主变通风告警 |  | digital
N2DCS.21CHA04EH117 | 11502 | #4机B套启动厂变通风告警 |  | digital
N2DCS.21CHA04EH118 | 11503 | #4机B套TA异常告警 |  | digital
N2DCS.21CHA04EH119 | 11504 | #4机B套TV异常告警 |  | digital
N2DCS.21CHA04EH120 | 11505 | #4主变B套低压侧接地告警 |  | digital
N2DCS.21CHA04EH121 | 11506 | #4机B套装置故障告警 |  | digital
N2DCS.21CHA04EH122 | 11507 | #4机B套失电告警 |  | digital
N2DCS.21CHA04EH123 | 11508 | #4主变B套保护切换继电器动作 |  | digital
N2DCS.21CHA04EH124 | 11509 | #4主变B套保护切换继电器失电 |  | digital
N2DCS.21CHA05EH101 | 11510 | #4主变保护装置闭锁 |  | digital
N2DCS.21CHA05EH102 | 11511 | #4主变保护装置报警 |  | digital
N2DCS.21CHA05EH103 | 11512 | #4主变非电量电源监视 |  | digital
N2DCS.21CHA05EH104 | 11513 | #4主变冷控失电延时跳闸 |  | digital
N2DCS.21CHA05EH105 | 11514 | #4主变本体重瓦斯跳闸 |  | digital
N2DCS.21CHA05EH106 | 11515 | #4主变绕组温度高跳闸 |  | digital
N2DCS.21CHA05EH107 | 11516 | #4主变压力突变跳闸 |  | digital
N2DCS.21CHA05EH108 | 11517 | #4主变油温高跳闸 |  | digital
N2DCS.21CHA05EH109 | 11518 | #4机母差及失灵联跳 |  | digital
N2DCS.21CHA05EH110 | 11519 | #4机安稳切机跳闸 |  | digital
N2DCS.21CHA05EH111 | 11520 | #4机转子一点接地保护跳闸 |  | digital
N2DCS.21CHA05EH112 | 11521 | #4主变本体轻瓦斯信号 |  | digital
N2DCS.21CHA05EH113 | 11522 | #4主变绕组温度高信号 |  | digital
N2DCS.21CHA05EH114 | 11523 | #4主变油位异常信号 |  | digital
N2DCS.21CHA05EH115 | 11524 | #4主变压力释放信号 |  | digital
N2DCS.21CHA05EH128 | 11525 | #4发变组非电量保护控制回路断线 |  | digital
N2DCS.21CHA05EH129 | 11526 | #4发变组非电量保护控制回路断线 |  | digital
N2DCS.21CHA05EH130 | 11527 | #4发变组非电量保护第一出口跳闸 |  | digital
N2DCS.21CHA05EH131 | 11528 | #4发变组非电量保护第二出口跳闸 |  | digital
N2DCS.21CHA05EH132 | 11529 | #4主变断路器位置不一致 |  | digital
N2DCS.21CHA05EH133 | 11530 | #4机失步解列跳闸 |  | digital
N2DCS.20CBQ01EH213A | 11531 | 6KV 2B段快切装置切换启允许 |  | digital
N2DCS.20AGCFVFRP | 11532 | Ovation Control Builder |  | digital
N2DCS.20RDIGI20007GT | 11533 | Ovation Control Builder |  | digital
N2DCS.22CBP01EJ_TQPMT | 11534 |  |  | digital
N2DCS.AGCOFFFVFRPOFF | 11535 | Ovation Control Builder |  | digital
N2DCS.APSAUTOMODE | 11536 | APS自动模式已投入 |  | digital
N2DCS.APSMODEOFF | 11537 | APS模式已退出 |  | digital
N2DCS.APSMODEON | 11538 | APS模式已投入 |  | digital
N2DCS.APSMODEPMT | 11539 | APS模式投入允许 |  | digital
N2DCS.APSSPBP1_BYPASS | 11540 | 降负荷断点旁路 |  | digital
N2DCS.APSSPBP1_TIMINGPMT | 11541 | 降负荷断点同步条件 |  | digital
N2DCS.APSSPBP1FINISH | 11542 | 降负荷断点完成 |  | digital
N2DCS.APSSPBP1FINISH1 | 11543 | 降负荷断点完成1 |  | digital
N2DCS.APSSPBP1PMTACK | 11544 | APS停机相关系统检查卡确认 |  | digital
N2DCS.APSSPBP2_BYPASS | 11545 | #4机打闸断点旁路 |  | digital
N2DCS.APSSPBP2_TIMINGPMT | 11546 | #4机打闸断点同步条件 |  | digital
N2DCS.APSSPBP2FINISH | 11547 | #4机打闸断点完成 |  | digital
N2DCS.APSSPBP2FINISH1 | 11548 | 燃机打闸断点完成1 |  | digital
N2DCS.APSSPBP3_BYPASS | 11549 | #1余热锅炉停止断点旁路 |  | digital
N2DCS.APSSPBP3_TIMINGPMT | 11550 | #1余热锅炉停止断点同步条件 |  | digital
N2DCS.APSSPBP3FINISH | 11551 | #1余热锅炉停止断点完成 |  | digital
N2DCS.APSSPBP3FINISH1 | 11552 | #1余热锅炉停止断点完成1 |  | digital
N2DCS.APSSPBP4_BYPASS | 11553 | #2机组停运断点旁路 |  | digital
N2DCS.APSSPBP4_TIMINGPMT | 11554 | #2机组停运断点同步条件 |  | digital
N2DCS.APSSPBP4FINISH | 11555 | #2机组停运断点完成 |  | digital
N2DCS.APSSPBP4FINISH1 | 11556 | #2机组停运断点完成1 |  | digital
N2DCS.APSSPRUNNING | 11557 | APS停止进行中 |  | digital
N2DCS.APSSTARTMODE | 11558 | APS启机模式已投入 |  | digital
N2DCS.APSSTBP1_BYPASS | 11559 | 系统准备断点旁路 |  | digital
N2DCS.APSSTBP1_TIMINGPMT | 11560 | 系统准备断点同步条件 |  | digital
N2DCS.APSSTBP1FINISH | 11561 | 系统准备断点完成 |  | digital
N2DCS.APSSTBP1FINISH1 | 11562 | 系统准备断点完成1 |  | digital
N2DCS.APSSTBP1PMTACK | 11563 | APS启机相关系统检查卡确认 |  | digital
N2DCS.APSSTBP2_BYPASS | 11564 | #2机组上水断点旁路 |  | digital
N2DCS.APSSTBP2_TIMINGPMT | 11565 | #2机组上水断点同步条件 |  | digital
N2DCS.APSSTBP2FINISH | 11566 | #2机组上水断点完成 |  | digital
N2DCS.APSSTBP2FINISH1 | 11567 | #2机组上水断点完成1 |  | digital
N2DCS.APSSTBP3_BYPASS | 11568 | #4机启动断点旁路 |  | digital
N2DCS.APSSTBP3_TIMINGPMT | 11569 | #4机启动断点同步条件 |  | digital
N2DCS.APSSTBP3FINISH | 11570 | #4机点火断点完成 |  | digital
N2DCS.APSSTBP3FINISH1 | 11571 | #4机点火断点完成1 |  | digital
N2DCS.APSSTBP4_BYPASS | 11572 | #3机并网断点旁路 |  | digital
N2DCS.APSSTBP4_TIMINGPMT | 11573 | #3机并网断点同步条件 |  | digital
N2DCS.APSSTBP4FINISH | 11574 | #3机并网断点已完成 |  | digital
N2DCS.APSSTBP4FINISH1 | 11575 | #3机并网断点已完成 |  | digital
N2DCS.APSSTBP5_BYPASS | 11576 | 升负荷断点旁路 |  | digital
N2DCS.APSSTBP5_TIMINGPMT | 11577 | 升负荷断点同步条件 |  | digital
N2DCS.APSSTBP5FINISH | 11578 | 升负荷断点已完成 |  | digital
N2DCS.APSSTOPMODE | 11579 | APS停机模式已投入 |  | digital
N2DCS.APSSTRUNNING | 11580 | APS启机进行中 |  | digital
N2DCS.BOTHCNDCPSTOP | 11581 | 余热锅炉停止断点已完成 |  | digital
N2DCS.BOTHHPWFSTOP | 11582 | #3炉高压给水泵全停 |  | digital
N2DCS.BOTHIPWFSTOP | 11583 | #3炉中压给水泵全停 |  | digital
N2DCS.CCSMODE | 11584 | Ovation Control Builder |  | digital
N2DCS.CPRESSAIR_SEQSTOK | 11585 |  |  | digital
N2DCS.GTALR | 11586 | Ovation Control Builder |  | digital
N2DCS.GTBRONACKOK | 11587 | #4机并网状态确认 |  | digital
N2DCS.GTBRONDMD | 11588 | #4机并网指令 |  | digital
N2DCS.GTCBON | 11589 | #4机负荷>7MW |  | digital
N2DCS.GTCCSOFF | 11590 | CCS已退出 |  | digital
N2DCS.GTCCSONDMD | 11591 | Ovation Control Builder |  | digital
N2DCS.GTCCSONDMDPMT | 11592 | Ovation Control Builder |  | digital
N2DCS.GTCCSPMT | 11593 | CCS投入允许条件1 |  | digital
N2DCS.GTLOADL155 | 11594 | #4机负荷<155MW |  | digital
N2DCS.GTREADY_SEQSTOK | 11595 | Ovation Control Builder |  | digital
N2DCS.GTREADYCTL | 11596 |  |  | digital
N2DCS.GTRUN | 11597 | #4机在运行 |  | digital
N2DCS.GTSTACKOK | 11598 | 手动确认#4机可以启动 |  | digital
N2DCS.HILBPVAUTO | 11599 | 高中低压旁路调阀均在自动模式 |  | digital
N2DCS.NOTCCSMODE | 11600 | Ovation Control Builder |  | digital
N2DCS.ONE12 | 11601 | 开关量1 |  | digital
N2DCS.REJECTION | 11602 | 甩负荷 |  | digital
N2DCS.SEQ134101 | 11603 | Ovation Control Builder |  | digital
N2DCS.SEQ134105 | 11604 | Ovation Control Builder |  | digital
N2DCS.STMODESEL | 11605 | #3机启动模式已选(冷、温、热、? |  | digital
N2DCS.TURBBRONACKOK | 11606 | 手动确认#3机准备并网指令 |  | digital
N2DCS.TURBBRONDMD | 11607 | APS顺控#3机并网指令 |  | digital
N2DCS.TURBDRNVLVCLS | 11608 | 疏水阀均在全关位 |  | digital
N2DCS.TURBDRNVLVOPN | 11609 | 疏水阀均在全开位 |  | digital
N2DCS.TURBSTACKOK | 11610 | 手动确认#3机准备启动指令 |  | digital
N2DCS.TURBSTACKPMT | 11611 | #3机启动允许 |  | digital
N2DCS.TURBSTACKPMT1 | 11612 | #3机启动允许 |  | digital
N2DCS.TURBTRIP | 11613 | #3机已遮断信号 |  | digital
N2DCS.TURBTRIPACKOK | 11614 | #3机手动打闸指令 |  | digital
N2DCS.TURBWARMFINISH | 11615 | #3机暖机完成 |  | digital
N2DCS.UNIT_START | 11616 | 机组启动（APS模式） |  | digital
N2DCS.ZERO12 | 11617 | 开关量0 |  | digital
N2DCS.10DCSFA002 | 11618 | Ovation Control Builder |  | digital
N2DCS.20DCSFA002 | 11619 | #3机冲转并网断点第1步已完成 |  | digital
N2DCS.20DCSFA009 | 11620 | Ovation Control Builder |  | digital
N2DCS.20DCSFA013 | 11621 | #3炉停止断点已完成 |  | digital
N2DCS.20DCSFA014 | 11622 | #3炉停止断点已完成 |  | digital
N2DCS.20DCSFA015 | 11623 | #3炉停止断点已完成 |  | digital
N2DCS.20LBA10CPNORMAL | 11624 | Ovation Control Builder |  | digital
N2DCS.20LBA30CPNORMAL | 11625 | Ovation Control Builder |  | digital
N2DCS.20TCSDO03 | 11626 | Ovation Control Builder |  | digital
N2DCS.20TCSDO04 | 11627 | Ovation Control Builder |  | digital
N2DCS.20TCSDO06 | 11628 | Ovation Control Builder |  | digital
N2DCS.20TCSDO08 | 11629 | Ovation Control Builder |  | digital
N2DCS.20TCSDO09 | 11630 | Ovation Control Builder |  | digital
N2DCS.22AVCAUTOOFF | 11631 | AVC在退出状态 |  | digital
N2DCS.APSMODEOFF_PLUSE | 11632 | APS模式已退出(脉冲) |  | digital
N2DCS.APSSPBP2FINISHNO | 11633 | Ovation Control Builder |  | digital
N2DCS.APSSTBP1FINISH1NO | 11634 | Ovation Control Builder |  | digital
N2DCS.APSSTBP3_SEQAUX1 | 11635 | Ovation Control Builder |  | digital
N2DCS.APSSTBP4_SEQAUX1 | 11636 | Ovation Control Builder |  | digital
N2DCS.APSSTBP4_SEQAUX2 | 11637 | Ovation Control Builder |  | digital
N2DCS.APSSTBP5FINISH1 | 11638 | 升负荷断点已完成 |  | digital
N2DCS.BOTHCIRPMP_SEQSTOK | 11639 | #3机低压蒸汽压力控制模式 |  | digital
N2DCS.BOTHCNDPMPSTOP | 11640 | 凝结水泵全停 |  | digital
N2DCS.CNDPMPSEQSTOPNO1 | 11641 | Ovation Control Builder |  | digital
N2DCS.CNDWTRFILLACKOK | 11642 | 凝泵密封及系统注水完成确认指令 |  | digital
N2DCS.CNSRCIRVLVOP | 11643 | 凝汽器循环水出水电动门均已全开 |  | digital
N2DCS.COLDORWARMON | 11644 | 汽机冷态/温态模式 |  | digital
N2DCS.D01P331_KBGB | 11645 | Ovation Control Builder |  | digital
N2DCS.D01P334 | 11646 | Ovation Control Builder |  | digital
N2DCS.DCS_DEH_DO1 | 11647 | #4机打闸断点第1步指令（至DEH |  | digital
N2DCS.DCS_DEH_DO2 | 11648 | #4机打闸断点第2步指令（至DEH |  | digital
N2DCS.DCS_DEH_DO3 | 11649 | #4机打闸断点第3步指令（至DEH |  | digital
N2DCS.ELC_OKGB | 11650 | 电气检查正常手动确认指令 |  | digital
N2DCS.GTBRONOK | 11651 | #4机已并网 |  | digital
N2DCS.GTH2SYSOK | 11652 | #4发电机氢气系统压力正常确认 |  | digital
N2DCS.GTLOAD15 | 11653 | #4机负荷>15MW |  | digital
N2DCS.GTOILSYSOK | 11654 | #4机滑油、密封油系统运行正常 |  | digital
N2DCS.GTSPEED3000 | 11655 | #4机转速3000rpm |  | digital
N2DCS.HILVLVHZERO | 11656 | Ovation Control Builder |  | digital
N2DCS.HRSGTRIPNONO | 11657 | Ovation Control Builder |  | digital
N2DCS.HXZSSYSOK | 11658 | 化水制水系统正常确认指令 |  | digital
N2DCS.IPIN | 11659 | #3机中压蒸汽压力控制模式 |  | digital
N2DCS.JYPMPACK | 11660 | 凝结水加压系统正常投运确认指令 |  | digital
N2DCS.LPCTLIN | 11661 | #3机低压蒸汽压力控制模式 |  | digital
N2DCS.MAINSTEAMPANDUAN | 11662 | 高压主蒸汽温度>最佳主蒸汽温度 |  | digital
N2DCS.QJSKJX | 11663 | #3机启顺控进行中 |  | digital
N2DCS.SEQ135101 | 11664 | Ovation Control Builder |  | digital
N2DCS.SEQ135102 | 11665 | Ovation Control Builder |  | digital
N2DCS.SEQ135103 | 11666 | Ovation Control Builder |  | digital
N2DCS.SEQ135104 | 11667 | Ovation Control Builder |  | digital
N2DCS.STHIGORV2 | 11668 | Ovation Control Builder |  | digital
N2DCS.STLOADLOW100 | 11669 | #3机负荷<100MW |  | digital
N2DCS.STLOADLOW5 | 11670 | #3机负荷<5MW |  | digital
N2DCS.STLOWORV2 | 11671 | Ovation Control Builder |  | digital
N2DCS.STMONORV2 | 11672 | Ovation Control Builder |  | digital
N2DCS.TBEHOILSYSOK | 11673 | #3机润滑油系统运行正常确认 |  | digital
N2DCS.TPIN | 11674 | #3机高压蒸汽压力控制模式 |  | digital
N2DCS.20CHA00EZ100_XK96 | 11675 | 汽机发电机跳闸 |  | digital
N2DCS.20CHA00EZ100_XV01 | 11676 | Ovation Control Builder |  | digital
N2DCS.20CHA00EZ100A_XK01 | 11677 | 发电机保护停机 1# |  | digital
N2DCS.20CHA00EZ100B_XK01 | 11678 | 发电机保护停机 2# |  | digital
N2DCS.20CHA00EZ100C_XK01 | 11679 | 发电机保护停机 3# |  | digital
N2DCS.20DROP41GW001_XM09 | 11680 | 机柜空开正常 |  | digital
N2DCS.20DROP41GW001_XM10 | 11681 | 机柜电源正常 |  | digital
N2DCS.20HYY01EY001_XK96 | 11682 | Ovation Control Builder |  | digital
N2DCS.20HYY01EY001_XV01 | 11683 | Ovation Control Builder |  | digital
N2DCS.20HYY01EY001A_XV10 | 11684 | 锅炉停机1 |  | digital
N2DCS.20HYY01EY001B_XV10 | 11685 | 锅炉停机2 |  | digital
N2DCS.20HYY01EY001C_XV10 | 11686 | 锅炉停机3 |  | digital
N2DCS.20LBA20EZ007_XV01 | 11687 | Ovation Control Builder |  | digital
N2DCS.20LBB50EZ007_XV01 | 11688 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101_XV01 | 11689 | Ovation Control Builder |  | digital
N2DCS.20LBD20AA001_XG04 | 11690 | 高压抽汽快关调节阀控制电源故障 |  | digital
N2DCS.20LBD40AA001_XG04 | 11691 | 中压抽汽快关调节阀控制电源故障 |  | digital
N2DCS.20LBS45AA001_XB01 | 11692 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_XB02 | 11693 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_XG04 | 11694 | 中压抽汽快关调节阀控制电源故障 |  | digital
N2DCS.20LBS45AA001_XG05A | 11695 | 中压抽汽快关调节阀油动机关闭电 |  | digital
N2DCS.20LBS45AA001_XG05B | 11696 | 中压抽汽快关调节阀油动机关闭电 |  | digital
N2DCS.20LBS45AA013_ZB21 | 11697 | 中压抽汽快关调节阀油动机关闭电 |  | digital
N2DCS.20LBS46AA001_XB01 | 11698 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_XB02 | 11699 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_XG04 | 11700 | 高压抽汽快关调节阀控制电源故障 |  | digital
N2DCS.20LBS46AA001_XG05A | 11701 | 高压抽汽快关调节阀油动机关闭电 |  | digital
N2DCS.20LBS46AA001_XG05B | 11702 | 高压抽汽快关调节阀油动机关闭电 |  | digital
N2DCS.20LBS46AA013_ZB21 | 11703 | 高压抽汽快关调节阀油动机关闭电 |  | digital
N2DCS.20MAA11AA011 | 11704 | 主汽门开启电磁阀 |  | digital
N2DCS.20MAA11AA013_XB01 | 11705 | Ovation Control Builder |  | digital
N2DCS.20MAA11AA013_XB02 | 11706 | Ovation Control Builder |  | digital
N2DCS.20MAA11AA013_ZB21A | 11707 | 主汽门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAA11AA013_ZB21AP | 11708 | 主汽门油动机关闭电磁阀#1监视（ |  | digital
N2DCS.20MAA11AA013_ZB21B | 11709 | 主汽门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAA11AA014_XB01 | 11710 | Ovation Control Builder |  | digital
N2DCS.20MAA11AA014_XB02 | 11711 | Ovation Control Builder |  | digital
N2DCS.20MAA11AA014_ZB21A | 11712 | 主汽门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAA11AA014_ZB21AP | 11713 | 主汽门油动机关闭电磁阀#2监视（ |  | digital
N2DCS.20MAA11AA014_ZB21B | 11714 | 主汽门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAA12AA013_XB01 | 11715 | Ovation Control Builder |  | digital
N2DCS.20MAA12AA013_XB02 | 11716 | Ovation Control Builder |  | digital
N2DCS.20MAA12AA013_ZB21A | 11717 | 高压调门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAA12AA013_ZB21AP | 11718 | 高压调门油动机关闭电磁阀#1监视 |  | digital
N2DCS.20MAA12AA013_ZB21B | 11719 | 高压调门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAA12AA014_XB01 | 11720 | Ovation Control Builder |  | digital
N2DCS.20MAA12AA014_XB02 | 11721 | Ovation Control Builder |  | digital
N2DCS.20MAA12AA014_ZB21A | 11722 | 高压调门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAA12AA014_ZB21AP | 11723 | 高压调门油动机关闭电磁阀#2监视 |  | digital
N2DCS.20MAA12AA014_ZB21B | 11724 | 高压调门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAA21AA013_ZB21 | 11725 | 主汽门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAA21AA014_ZB21 | 11726 | 主汽门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAA22AA013_ZB21 | 11727 | 高压调门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAA22AA014_ZB21 | 11728 | 高压调门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAA22SGFD1 | 11729 | 快关高调阀 |  | digital
N2DCS.20MAA50CT151A_XM20 | 11730 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT152A_XM20 | 11731 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT621A_XH01 | 11732 | #1高压排汽蒸汽温度>412℃ |  | digital
N2DCS.20MAA50CT621A_XH03 | 11733 | #1高压排汽蒸汽温度>384℃ |  | digital
N2DCS.20MAA50CT621A_XH52 | 11734 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT621A_XH54 | 11735 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT621A_XM20 | 11736 | #1高压排汽蒸汽温度坏点 |  | digital
N2DCS.20MAA50CT622A_XH01 | 11737 | #2高压排汽蒸汽温度>412℃ |  | digital
N2DCS.20MAA50CT622A_XH03 | 11738 | #2高压排汽蒸汽温度>384℃ |  | digital
N2DCS.20MAA50CT622A_XH52 | 11739 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT622A_XH54 | 11740 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT622A_XM20 | 11741 | #2高压排汽蒸汽温度坏点 |  | digital
N2DCS.20MAA50CT623A_XH01 | 11742 | #3高压排汽蒸汽温度>412℃ |  | digital
N2DCS.20MAA50CT623A_XH03 | 11743 | #3高压排汽蒸汽温度>384℃ |  | digital
N2DCS.20MAA50CT623A_XH52 | 11744 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT623A_XH54 | 11745 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT623A_XM20 | 11746 | #3高压排汽蒸汽温度坏点 |  | digital
N2DCS.20MAA50EZ111_XV01 | 11747 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ251_XK93 | 11748 | ＜4HZ时/中压外缸上下温差＞55K |  | digital
N2DCS.20MAA50EZ251_XK94 | 11749 | 中压外缸上下温差＞30K |  | digital
N2DCS.20MAA50EZ251_XK95 | 11750 | 并网120s后中压外缸上下温差>45K |  | digital
N2DCS.20MAA50EZ251_XK96 | 11751 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ251_XV01 | 11752 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ621_XK93 | 11753 | 高排温度测量存在故障 |  | digital
N2DCS.20MAA50EZ621_XK94 | 11754 | 高排温度大于计算报警值 |  | digital
N2DCS.20MAA50EZ621_XK96 | 11755 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ621_XM70 | 11756 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ621_XV01 | 11757 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ621E_XK93 | 11758 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ621E_XK94 | 11759 | 高排温度＞384℃ |  | digital
N2DCS.20MAA50EZ621E_XK96 | 11760 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ621E_XM70 | 11761 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ621E_XS96 | 11762 | 高排温度高高--抽汽解裂 |  | digital
N2DCS.20MAA50EZ621E_XV01 | 11763 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT251_XH02 | 11764 | 高压或中压缸上下壁温差>55℃ |  | digital
N2DCS.20MAA50FT251_XH04 | 11765 | 高压或中压缸上下壁温差>45℃ |  | digital
N2DCS.20MAA50FT251_XH05 | 11766 | 高压或中压缸上下壁温差>30℃ |  | digital
N2DCS.20MAA50FT621_XH01 | 11767 | 高压排汽蒸汽温度>450℃ |  | digital
N2DCS.20MAA50FT621A_DL12 | 11768 | 高压排汽蒸汽温度1/2偏差大 |  | digital
N2DCS.20MAA50FT621A_DL13 | 11769 | 高压排汽蒸汽温度1/3偏差大 |  | digital
N2DCS.20MAA50FT621A_DL23 | 11770 | 高压排汽蒸汽温度2/3偏差大 |  | digital
N2DCS.20MAA50FT621A_XM97 | 11771 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT621A_XM98 | 11772 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT621A_XM99 | 11773 | Ovation Control Builder |  | digital
N2DCS.20MAB11AA011 | 11774 | 中主门开启电磁阀 |  | digital
N2DCS.20MAB11AA013_XB01 | 11775 | Ovation Control Builder |  | digital
N2DCS.20MAB11AA013_XB02 | 11776 | Ovation Control Builder |  | digital
N2DCS.20MAB11AA013_ZB21A | 11777 | 再热主汽门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAB11AA013_ZB21AP | 11778 | 再热主汽门油动机关闭电磁阀#1监 |  | digital
N2DCS.20MAB11AA013_ZB21B | 11779 | 再热主汽门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAB11AA014_XB01 | 11780 | Ovation Control Builder |  | digital
N2DCS.20MAB11AA014_XB02 | 11781 | Ovation Control Builder |  | digital
N2DCS.20MAB11AA014_ZB21A | 11782 | 再热主汽门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAB11AA014_ZB21AP | 11783 | 再热主汽门油动机关闭电磁阀#2监 |  | digital
N2DCS.20MAB11AA014_ZB21B | 11784 | 再热主汽门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAB12AA013_XB01 | 11785 | Ovation Control Builder |  | digital
N2DCS.20MAB12AA013_XB02 | 11786 | Ovation Control Builder |  | digital
N2DCS.20MAB12AA013_ZB21A | 11787 | 中压调门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAB12AA013_ZB21AP | 11788 | 中压调门油动机关闭电磁阀#1监视 |  | digital
N2DCS.20MAB12AA013_ZB21B | 11789 | 中压调门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAB12AA014_XB01 | 11790 | Ovation Control Builder |  | digital
N2DCS.20MAB12AA014_XB02 | 11791 | Ovation Control Builder |  | digital
N2DCS.20MAB12AA014_ZB21A | 11792 | 中压调门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAB12AA014_ZB21AP | 11793 | 中压调门油动机关闭电磁阀#2监视 |  | digital
N2DCS.20MAB12AA014_ZB21B | 11794 | 中压调门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAB21AA013_ZB21 | 11795 | 再热主汽门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAB21AA014_ZB21 | 11796 | 再热主汽门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAB22AA013_ZB21 | 11797 | 中压调门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAB22AA014_ZB21 | 11798 | 中压调门油动机关闭电磁阀#2 |  | digital
N2DCS.20MAB22SGAF1 | 11799 | 快关中调阀1# |  | digital
N2DCS.20MAB50CT151A_XM20 | 11800 | Ovation Control Builder |  | digital
N2DCS.20MAB50CT152A_XM20 | 11801 | Ovation Control Builder |  | digital
N2DCS.20MAB50FT621_XH01 | 11802 | 中排温度＞305℃ |  | digital
N2DCS.20MAB50FT621_XH03 | 11803 | 中排温度＞323℃ |  | digital
N2DCS.20MAB50FT621_XK20 | 11804 | Ovation Control Builder |  | digital
N2DCS.20MAC10CT671_XH01 | 11805 | #1低压排汽支架温度>90℃ |  | digital
N2DCS.20MAC10CT671_XH03 | 11806 | #1低压排汽支架温度>70℃ |  | digital
N2DCS.20MAC10CT671_XM20 | 11807 | #1低压排汽支架温度坏点 |  | digital
N2DCS.20MAC10CT672_XH01 | 11808 | #2低压排汽支架温度>90℃ |  | digital
N2DCS.20MAC10CT672_XH03 | 11809 | #2低压排汽支架温度>70℃ |  | digital
N2DCS.20MAC10CT672_XM20 | 11810 | #2低压排汽支架温度坏点 |  | digital
N2DCS.20MAC10CT673_XH01 | 11811 | #3低压排汽支架温度>90℃ |  | digital
N2DCS.20MAC10CT673_XH03 | 11812 | #3低压排汽支架温度>70℃ |  | digital
N2DCS.20MAC10CT673_XM20 | 11813 | #3低压排汽支架温度坏点 |  | digital
N2DCS.20MAC10EZ671_XK93 | 11814 | 低排温度测量存在故障 |  | digital
N2DCS.20MAC10EZ671_XK94 | 11815 | 低排温度＞70℃ |  | digital
N2DCS.20MAC10EZ671_XK96 | 11816 | Ovation Control Builder |  | digital
N2DCS.20MAC10EZ671_XV01 | 11817 | Ovation Control Builder |  | digital
N2DCS.20MAC10FT611A_XH01 | 11818 | 低压缸末级叶片温度＞120℃ |  | digital
N2DCS.20MAC10FT611A_XH03 | 11819 | 低压缸末级叶片温度＞180℃ |  | digital
N2DCS.20MAC10FT611A_XH05 | 11820 | 低压缸末级叶片温度＞230℃ |  | digital
N2DCS.20MAC10FT611A_XH52 | 11821 | 低压缸末级叶片温度<100℃ |  | digital
N2DCS.20MAC10FT671_DL12 | 11822 | Ovation Control Builder |  | digital
N2DCS.20MAC10FT671_DL13 | 11823 | Ovation Control Builder |  | digital
N2DCS.20MAC10FT671_DL23 | 11824 | Ovation Control Builder |  | digital
N2DCS.20MAC10FT671_XH01 | 11825 | Ovation Control Builder |  | digital
N2DCS.20MAC10FT671_XH52 | 11826 | Ovation Control Builder |  | digital
N2DCS.20MAC10FT671A_XM97 | 11827 | Ovation Control Builder |  | digital
N2DCS.20MAC10FT671A_XM98 | 11828 | Ovation Control Builder |  | digital
N2DCS.20MAC10FT671A_XM99 | 11829 | Ovation Control Builder |  | digital
N2DCS.20MAC45AA001_XB01 | 11830 | Ovation Control Builder |  | digital
N2DCS.20MAC45AA001_XB02 | 11831 | Ovation Control Builder |  | digital
N2DCS.20MAC45AA001_XG04 | 11832 | 低压补汽主门油动机控制电源故障 |  | digital
N2DCS.20MAC45AA001_XG05A | 11833 | 低压补汽主门油动机关闭电磁阀输 |  | digital
N2DCS.20MAC45AA001_XG05B | 11834 | 低压补汽主门油动机关闭电磁阀输 |  | digital
N2DCS.20MAC45AA001_XG06 | 11835 | 低压主汽门活动性试验 |  | digital
N2DCS.20MAC45AA013_ZB21 | 11836 | 低压补汽主门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAC46AA001_XB01 | 11837 | Ovation Control Builder |  | digital
N2DCS.20MAC46AA001_XB02 | 11838 | Ovation Control Builder |  | digital
N2DCS.20MAC46AA001_XG04 | 11839 | 低压补汽调阀油动机控制电源故障 |  | digital
N2DCS.20MAC46AA001_XG05A | 11840 | 低压补汽调门油动机关闭电磁阀输 |  | digital
N2DCS.20MAC46AA001_XG05B | 11841 | 低压补汽调门油动机关闭电磁阀输 |  | digital
N2DCS.20MAC46AA013_ZB21 | 11842 | 低压补汽调门油动机关闭电磁阀#1 |  | digital
N2DCS.20MAD00EZ111_XK96 | 11843 | Ovation Control Builder |  | digital
N2DCS.20MAD00EZ111_XV01 | 11844 | Ovation Control Builder |  | digital
N2DCS.20MAD01EZ111_XK96 | 11845 | Ovation Control Builder |  | digital
N2DCS.20MAD01EZ111_XV01 | 11846 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114A_XH01 | 11847 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114A_XH03 | 11848 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114A_XM20 | 11849 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114B_XH01 | 11850 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114B_XH03 | 11851 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114B_XM20 | 11852 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114C_XH01 | 11853 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114C_XH03 | 11854 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT114C_XM20 | 11855 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118A_XH01 | 11856 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118A_XH03 | 11857 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118A_XM20 | 11858 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118B_XH01 | 11859 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118B_XH03 | 11860 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118B_XM20 | 11861 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118C_XH01 | 11862 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118C_XH03 | 11863 | Ovation Control Builder |  | digital
N2DCS.20MAD11CT118C_XM20 | 11864 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY021_XM71 | 11865 | #1径向轴承壳振1正常 |  | digital
N2DCS.20MAD11CY022_XM71 | 11866 | #1径向轴承壳振2正常 |  | digital
N2DCS.20MAD11CY121_MAX1 | 11867 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY121_MAX2 | 11868 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY121_XH01 | 11869 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY121_XH03 | 11870 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY121_XM71 | 11871 | #1径向轴承壳振1正常 |  | digital
N2DCS.20MAD11CY121_XM72 | 11872 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY121_XV20 | 11873 | #1轴瓦振动通道故障1 |  | digital
N2DCS.20MAD11CY122_MAX1 | 11874 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY122_MAX2 | 11875 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY122_XH01 | 11876 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY122_XH03 | 11877 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY122_XM71 | 11878 | #1径向轴承壳振2正常 |  | digital
N2DCS.20MAD11CY122_XM72 | 11879 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY122_XV20 | 11880 | #1轴瓦振动通道故障2 |  | digital
N2DCS.20MAD11EZ121_XK93 | 11881 | #1轴承座振动存在故障 |  | digital
N2DCS.20MAD11EZ121_XK94 | 11882 | #1轴承座振动＞9.3mm/s |  | digital
N2DCS.20MAD11EZ121_XK96 | 11883 | Ovation Control Builder |  | digital
N2DCS.20MAD11EZ214_XK93 | 11884 | #1轴承径向轴瓦金属测点1故障 |  | digital
N2DCS.20MAD11EZ214_XK94 | 11885 | #1轴承径向轴瓦金属温度1＞90℃ |  | digital
N2DCS.20MAD11EZ214_XK96 | 11886 | Ovation Control Builder |  | digital
N2DCS.20MAD11EZ218_XK93 | 11887 | #1轴承径向轴瓦金属测点2故障 |  | digital
N2DCS.20MAD11EZ218_XK94 | 11888 | #1轴承径向轴瓦金属温度2＞90℃ |  | digital
N2DCS.20MAD11EZ218_XK96 | 11889 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT114A_XM97 | 11890 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT114B_XM98 | 11891 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT114C_XM99 | 11892 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT118A_XM97 | 11893 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT118B_XM98 | 11894 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT118C_XM99 | 11895 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT214A_DL12 | 11896 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT214A_DL13 | 11897 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT214A_DL23 | 11898 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT218A_DL12 | 11899 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT218A_DL13 | 11900 | Ovation Control Builder |  | digital
N2DCS.20MAD11FT218A_DL23 | 11901 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111A_XH01 | 11902 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111A_XH03 | 11903 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111A_XM20 | 11904 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111B_XH01 | 11905 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111B_XH03 | 11906 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111B_XM20 | 11907 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111C_XH01 | 11908 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111C_XH03 | 11909 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT111C_XM20 | 11910 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112A_XH01 | 11911 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112A_XH03 | 11912 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112A_XM20 | 11913 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112B_XH01 | 11914 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112B_XH03 | 11915 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112B_XM20 | 11916 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112C_XH01 | 11917 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112C_XH03 | 11918 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT112C_XM20 | 11919 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113A_XH01 | 11920 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113A_XH03 | 11921 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113A_XM20 | 11922 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113B_XH01 | 11923 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113B_XH03 | 11924 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113B_XM20 | 11925 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113C_XH01 | 11926 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113C_XH03 | 11927 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT113C_XM20 | 11928 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114A_XH01 | 11929 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114A_XH03 | 11930 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114A_XM20 | 11931 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114B_XH01 | 11932 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114B_XH03 | 11933 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114B_XM20 | 11934 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114C_XH01 | 11935 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114C_XH03 | 11936 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT114C_XM20 | 11937 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131A_XH01 | 11938 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131A_XH03 | 11939 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131A_XM20 | 11940 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131B_XH01 | 11941 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131B_XH03 | 11942 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131B_XM20 | 11943 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131C_XH01 | 11944 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131C_XH03 | 11945 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT131C_XM20 | 11946 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132A_XH01 | 11947 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132A_XH03 | 11948 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132A_XM20 | 11949 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132B_XH01 | 11950 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132B_XH03 | 11951 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132B_XM20 | 11952 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132C_XH01 | 11953 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132C_XH03 | 11954 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT132C_XM20 | 11955 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133A_XH01 | 11956 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133A_XH03 | 11957 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133A_XM20 | 11958 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133B_XH01 | 11959 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133B_XH03 | 11960 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133B_XM20 | 11961 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133C_XH01 | 11962 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133C_XH03 | 11963 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT133C_XM20 | 11964 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134A_XH01 | 11965 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134A_XH03 | 11966 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134A_XM20 | 11967 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134B_XH01 | 11968 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134B_XH03 | 11969 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134B_XM20 | 11970 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134C_XH01 | 11971 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134C_XH03 | 11972 | Ovation Control Builder |  | digital
N2DCS.20MAD12CT134C_XM20 | 11973 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY011_XM71 | 11974 | 轴位移1#正常 |  | digital
N2DCS.20MAD12CY012_XM71 | 11975 | 轴位移2#正常 |  | digital
N2DCS.20MAD12CY013_XM71 | 11976 | 轴向位移3#OK |  | digital
N2DCS.20MAD12CY021_XM71 | 11977 | #2径向轴承壳振1正常 |  | digital
N2DCS.20MAD12CY022_XM71 | 11978 | #2径向轴承壳振2正常 |  | digital
N2DCS.20MAD12CY111_XH01 | 11979 | #1轴向位移坏点>1mm |  | digital
N2DCS.20MAD12CY111_XH03 | 11980 | #1轴向位移坏点>0.5mm |  | digital
N2DCS.20MAD12CY111_XH52 | 11981 | #1轴向位移坏点<-1mm |  | digital
N2DCS.20MAD12CY111_XH54 | 11982 | #1轴向位移坏点<-0.5mm |  | digital
N2DCS.20MAD12CY111_XM20 | 11983 | #1轴向位移坏点 |  | digital
N2DCS.20MAD12CY111_XM71 | 11984 | 轴位移1#正常 |  | digital
N2DCS.20MAD12CY111_XM72 | 11985 | 轴位移通道故障1 |  | digital
N2DCS.20MAD12CY112_XH01 | 11986 | #2轴向位移坏点>1mm |  | digital
N2DCS.20MAD12CY112_XH03 | 11987 | #2轴向位移坏点>0.5mm |  | digital
N2DCS.20MAD12CY112_XH52 | 11988 | #2轴向位移坏点<-1mm |  | digital
N2DCS.20MAD12CY112_XH54 | 11989 | #2轴向位移坏点<-0.5mm |  | digital
N2DCS.20MAD12CY112_XM20 | 11990 | #2轴向位移坏点 |  | digital
N2DCS.20MAD12CY112_XM71 | 11991 | 轴位移2#正常 |  | digital
N2DCS.20MAD12CY112_XM72 | 11992 | 轴位移通道故障2 |  | digital
N2DCS.20MAD12CY113_XH01 | 11993 | #3轴向位移坏点>1mm |  | digital
N2DCS.20MAD12CY113_XH03 | 11994 | #3轴向位移坏点>0.5mm |  | digital
N2DCS.20MAD12CY113_XH52 | 11995 | #3轴向位移坏点<-1mm |  | digital
N2DCS.20MAD12CY113_XH54 | 11996 | #3轴向位移坏点<-0.5mm |  | digital
N2DCS.20MAD12CY113_XM20 | 11997 | #3轴向位移坏点 |  | digital
N2DCS.20MAD12CY113_XM72 | 11998 | 轴位移通道故障3 |  | digital
N2DCS.20MAD12CY121_MAX1 | 11999 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY121_MAX2 | 12000 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY121_XH01 | 12001 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY121_XH03 | 12002 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY121_XM71 | 12003 | #2径向轴承壳振1正常 |  | digital
N2DCS.20MAD12CY121_XM72 | 12004 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY121_XV20 | 12005 | #2轴瓦振动通道故障1 |  | digital
N2DCS.20MAD12CY122_MAX1 | 12006 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY122_MAX2 | 12007 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY122_XH01 | 12008 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY122_XH03 | 12009 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY122_XM71 | 12010 | #2径向轴承壳振2正常 |  | digital
N2DCS.20MAD12CY122_XM72 | 12011 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY122_XV20 | 12012 | #2轴瓦振动通道故障2 |  | digital
N2DCS.20MAD12EZ111_XK93 | 12013 | 轴向位移测量存在故障 |  | digital
N2DCS.20MAD12EZ111_XK94 | 12014 | 轴向位移＜-0.5mm |  | digital
N2DCS.20MAD12EZ111_XK95 | 12015 | 轴向位移＞0.5mm |  | digital
N2DCS.20MAD12EZ111_XK96 | 12016 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ111_XV01 | 12017 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ121_XK93 | 12018 | #2轴承座振动存在故障 |  | digital
N2DCS.20MAD12EZ121_XK94 | 12019 | #2轴承座振动＞9.3mm/s |  | digital
N2DCS.20MAD12EZ121_XK96 | 12020 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ211_XK93 | 12021 | #2轴承径向轴瓦金属测点1故障 |  | digital
N2DCS.20MAD12EZ211_XK94 | 12022 | #2轴承径向轴瓦金属温度1＞90℃ |  | digital
N2DCS.20MAD12EZ211_XK96 | 12023 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ212_XK93 | 12024 | #2轴承径向轴瓦金属测点2故障 |  | digital
N2DCS.20MAD12EZ212_XK94 | 12025 | #2轴承径向轴瓦金属温度2＞90℃ |  | digital
N2DCS.20MAD12EZ212_XK96 | 12026 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ213_XK93 | 12027 | #2轴承径向轴瓦金属测点3故障 |  | digital
N2DCS.20MAD12EZ213_XK94 | 12028 | #2轴承径向轴瓦金属温度3＞90℃ |  | digital
N2DCS.20MAD12EZ213_XK96 | 12029 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ214_XK93 | 12030 | #2轴承径向轴瓦金属测点4故障 |  | digital
N2DCS.20MAD12EZ214_XK94 | 12031 | #2轴承径向轴瓦金属温度4＞90℃ |  | digital
N2DCS.20MAD12EZ214_XK96 | 12032 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ231_XK93 | 12033 | #2轴承推力轴瓦金属测点1故障 |  | digital
N2DCS.20MAD12EZ231_XK94 | 12034 | #2轴承推力轴瓦金属温度1＞90℃ |  | digital
N2DCS.20MAD12EZ231_XK96 | 12035 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ232_XK93 | 12036 | #2轴承推力轴瓦金属温度2故障 |  | digital
N2DCS.20MAD12EZ232_XK94 | 12037 | #2轴承推力轴瓦金属温度2＞90℃ |  | digital
N2DCS.20MAD12EZ232_XK96 | 12038 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ233_XK93 | 12039 | #2轴承推力轴瓦金属温度3故障 |  | digital
N2DCS.20MAD12EZ233_XK94 | 12040 | #2轴承推力轴瓦金属温度3＞90℃ |  | digital
N2DCS.20MAD12EZ233_XK96 | 12041 | Ovation Control Builder |  | digital
N2DCS.20MAD12EZ234_XK93 | 12042 | #2轴承推力轴瓦金属温度4故障 |  | digital
N2DCS.20MAD12EZ234_XK94 | 12043 | #2轴承推力轴瓦金属温度4＞90℃ |  | digital
N2DCS.20MAD12EZ234_XK96 | 12044 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT111A_DL12 | 12045 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT111A_DL13 | 12046 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT111A_DL23 | 12047 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT111A_XM97 | 12048 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT111B_XM98 | 12049 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT111C_XM99 | 12050 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT112A_DL12 | 12051 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT112A_DL13 | 12052 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT112A_DL23 | 12053 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT112A_XM97 | 12054 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT112B_XM98 | 12055 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT112C_XM99 | 12056 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT113A_DL12 | 12057 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT113A_DL13 | 12058 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT113A_DL23 | 12059 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT113A_XM97 | 12060 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT113B_XM98 | 12061 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT113C_XM99 | 12062 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT114A_DL12 | 12063 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT114A_DL13 | 12064 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT114A_DL23 | 12065 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT114A_XM97 | 12066 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT114B_XM98 | 12067 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT114C_XM99 | 12068 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT131A_DL12 | 12069 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT131A_DL13 | 12070 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT131A_DL23 | 12071 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT131A_XM97 | 12072 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT131B_XM98 | 12073 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT131C_XM99 | 12074 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT132A_DL12 | 12075 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT132A_DL13 | 12076 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT132A_DL23 | 12077 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT132A_XM97 | 12078 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT132B_XM98 | 12079 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT132C_XM99 | 12080 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT133A_DL12 | 12081 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT133A_DL13 | 12082 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT133A_DL23 | 12083 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT133A_XM97 | 12084 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT133B_XM98 | 12085 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT133C_XM99 | 12086 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT134A_DL12 | 12087 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT134A_DL13 | 12088 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT134A_DL23 | 12089 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT134A_XM97 | 12090 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT134B_XM98 | 12091 | Ovation Control Builder |  | digital
N2DCS.20MAD12FT134C_XM99 | 12092 | Ovation Control Builder |  | digital
N2DCS.20MAD12FY111A_DL12 | 12093 | Ovation Control Builder |  | digital
N2DCS.20MAD12FY111A_DL13 | 12094 | Ovation Control Builder |  | digital
N2DCS.20MAD12FY111A_DL23 | 12095 | Ovation Control Builder |  | digital
N2DCS.20MAD12FY111A_XM97 | 12096 | Ovation Control Builder |  | digital
N2DCS.20MAD12FY111A_XM98 | 12097 | Ovation Control Builder |  | digital
N2DCS.20MAD12FY111A_XM99 | 12098 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT111A_XH01 | 12099 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT111A_XH03 | 12100 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT111A_XM20 | 12101 | #3支持轴承前左上温度A坏点 |  | digital
N2DCS.20MAD13CT111B_XH01 | 12102 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT111B_XH03 | 12103 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT111B_XM20 | 12104 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT111C_XH01 | 12105 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT111C_XH03 | 12106 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT111C_XM20 | 12107 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112A_XH01 | 12108 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112A_XH03 | 12109 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112A_XM20 | 12110 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112B_XH01 | 12111 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112B_XH03 | 12112 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112B_XM20 | 12113 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112C_XH01 | 12114 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112C_XH03 | 12115 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT112C_XM20 | 12116 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113A_XH01 | 12117 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113A_XH03 | 12118 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113A_XM20 | 12119 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113B_XH01 | 12120 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113B_XH03 | 12121 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113B_XM20 | 12122 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113C_XH01 | 12123 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113C_XH03 | 12124 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT113C_XM20 | 12125 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114A_XH01 | 12126 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114A_XH03 | 12127 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114A_XM20 | 12128 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114B_XH01 | 12129 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114B_XH03 | 12130 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114B_XM20 | 12131 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114C_XH01 | 12132 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114C_XH03 | 12133 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT114C_XM20 | 12134 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115A_XH01 | 12135 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115A_XH03 | 12136 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115A_XM20 | 12137 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115B_XH01 | 12138 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115B_XH03 | 12139 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115B_XM20 | 12140 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115C_XH01 | 12141 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115C_XH03 | 12142 | Ovation Control Builder |  | digital
N2DCS.20MAD13CT115C_XM20 | 12143 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY021_XM71 | 12144 | #3径向轴承壳振1正常 |  | digital
N2DCS.20MAD13CY022_XM71 | 12145 | #3径向轴承壳振2正常 |  | digital
N2DCS.20MAD13CY121_MAX1 | 12146 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY121_MAX2 | 12147 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY121_XH01 | 12148 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY121_XH03 | 12149 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY121_XM71 | 12150 | #3径向轴承壳振1正常 |  | digital
N2DCS.20MAD13CY121_XM72 | 12151 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY121_XV20 | 12152 | #3轴瓦振动通道故障1 |  | digital
N2DCS.20MAD13CY122_MAX1 | 12153 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY122_MAX2 | 12154 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY122_XH01 | 12155 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY122_XH03 | 12156 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY122_XM71 | 12157 | #3径向轴承壳振2正常 |  | digital
N2DCS.20MAD13CY122_XM72 | 12158 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY122_XV20 | 12159 | #3轴瓦振动通道故障2 |  | digital
N2DCS.20MAD13EZ121_XK93 | 12160 | #3轴承座振动存在故障 |  | digital
N2DCS.20MAD13EZ121_XK94 | 12161 | #3轴承座振动＞9.3mm/s |  | digital
N2DCS.20MAD13EZ121_XK96 | 12162 | Ovation Control Builder |  | digital
N2DCS.20MAD13EZ211_XK93 | 12163 | #3轴承径向轴瓦金属测点1故障 |  | digital
N2DCS.20MAD13EZ211_XK94 | 12164 | #3轴承径向轴瓦金属温度1＞90℃ |  | digital
N2DCS.20MAD13EZ211_XK96 | 12165 | Ovation Control Builder |  | digital
N2DCS.20MAD13EZ212_XK93 | 12166 | #3轴承径向轴瓦金属测点2故障 |  | digital
N2DCS.20MAD13EZ212_XK94 | 12167 | #3轴承径向轴瓦金属温度2＞90℃ |  | digital
N2DCS.20MAD13EZ212_XK96 | 12168 | Ovation Control Builder |  | digital
N2DCS.20MAD13EZ213_XK93 | 12169 | #3轴承径向轴瓦金属测点3故障 |  | digital
N2DCS.20MAD13EZ213_XK94 | 12170 | #3轴承径向轴瓦金属温度3＞90℃ |  | digital
N2DCS.20MAD13EZ213_XK96 | 12171 | Ovation Control Builder |  | digital
N2DCS.20MAD13EZ214_XK93 | 12172 | #3轴承径向轴瓦金属测点4故障 |  | digital
N2DCS.20MAD13EZ214_XK94 | 12173 | #3轴承径向轴瓦金属温度4＞90℃ |  | digital
N2DCS.20MAD13EZ214_XK96 | 12174 | Ovation Control Builder |  | digital
N2DCS.20MAD13EZ215_XK93 | 12175 | #3轴承径向轴瓦金属测点5故障 |  | digital
N2DCS.20MAD13EZ215_XK94 | 12176 | #3轴承径向轴瓦金属温度5＞90℃ |  | digital
N2DCS.20MAD13EZ215_XK96 | 12177 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT111A_DL12 | 12178 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT111A_DL13 | 12179 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT111A_DL23 | 12180 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT111A_XM97 | 12181 | #3支持轴承侧前左上温度A报警 |  | digital
N2DCS.20MAD13FT111B_XM98 | 12182 | #3支持轴承侧前左上温度B报警 |  | digital
N2DCS.20MAD13FT111C_XM99 | 12183 | #3支持轴承侧前左上温度C报警 |  | digital
N2DCS.20MAD13FT112A_DL12 | 12184 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT112A_DL13 | 12185 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT112A_DL23 | 12186 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT112A_XM97 | 12187 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT112B_XM98 | 12188 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT112C_XM99 | 12189 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT113A_DL12 | 12190 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT113A_DL13 | 12191 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT113A_DL23 | 12192 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT113A_XM97 | 12193 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT113B_XM98 | 12194 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT113C_XM99 | 12195 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT114A_DL12 | 12196 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT114A_DL13 | 12197 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT114A_DL23 | 12198 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT114A_XM97 | 12199 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT114B_XM98 | 12200 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT114C_XM99 | 12201 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT115A_DL12 | 12202 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT115A_DL13 | 12203 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT115A_DL23 | 12204 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT115A_XM97 | 12205 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT115B_XM98 | 12206 | Ovation Control Builder |  | digital
N2DCS.20MAD13FT115C_XM99 | 12207 | Ovation Control Builder |  | digital
N2DCS.20MAG01CP101_XH01 | 12208 | #1凝汽器真空>30kPa |  | digital
N2DCS.20MAG01CP101_XH03 | 12209 | #1凝汽器真空>20kPa |  | digital
N2DCS.20MAG01CP101_XH07 | 12210 | Ovation Control Builder |  | digital
N2DCS.20MAG01CP101_XM20 | 12211 | #1凝汽器真空坏点 |  | digital
N2DCS.20MAG01CP102_XH01 | 12212 | #2凝汽器真空>30kPa |  | digital
N2DCS.20MAG01CP102_XH03 | 12213 | #2凝汽器真空>20kPa |  | digital
N2DCS.20MAG01CP102_XH07 | 12214 | Ovation Control Builder |  | digital
N2DCS.20MAG01CP102_XM20 | 12215 | #2凝汽器真空坏点 |  | digital
N2DCS.20MAG01CP103_XH01 | 12216 | #3凝汽器真空>30kPa |  | digital
N2DCS.20MAG01CP103_XH03 | 12217 | #3凝汽器真空>20kPa |  | digital
N2DCS.20MAG01CP103_XH07 | 12218 | Ovation Control Builder |  | digital
N2DCS.20MAG01CP103_XM20 | 12219 | #3凝汽器真空坏点 |  | digital
N2DCS.20MAG01EZ101_VRA | 12220 | Ovation Control Builder |  | digital
N2DCS.20MAG01EZ101_XK20 | 12221 | Ovation Control Builder |  | digital
N2DCS.20MAG01EZ101_XK93 | 12222 | 真空保护相关探头存在故障 |  | digital
N2DCS.20MAG01EZ101_XK94 | 12223 | 真空大于计算报警值 |  | digital
N2DCS.20MAG01EZ101_XK96 | 12224 | Ovation Control Builder |  | digital
N2DCS.20MAG01EZ101_XV01 | 12225 | Ovation Control Builder |  | digital
N2DCS.20MAG01FP101A_DL12 | 12226 | #1/#2凝汽器真空偏差大 |  | digital
N2DCS.20MAG01FP101A_DL13 | 12227 | #1/#3凝汽器真空偏差大 |  | digital
N2DCS.20MAG01FP101A_DL23 | 12228 | #2/#3凝汽器真空偏差大 |  | digital
N2DCS.20MAG01FP101A_XM97 | 12229 | #1凝汽器真空测点故障 |  | digital
N2DCS.20MAG01FP101A_XM98 | 12230 | #2凝汽器真空测点故障 |  | digital
N2DCS.20MAG01FP101A_XM99 | 12231 | #3凝汽器真空测点故障 |  | digital
N2DCS.20MAG10FP101_XH51 | 12232 | 凝汽器真空>80kPa |  | digital
N2DCS.20MAG10FP101_XH52 | 12233 | Ovation Control Builder |  | digital
N2DCS.20MAG10FP101_XH53 | 12234 | 凝汽器真空>7kPa |  | digital
N2DCS.20MAG10FP101_XH58 | 12235 | 凝汽器真空<13kPa |  | digital
N2DCS.20MAV10CL121_XH01 | 12236 | #1润滑油箱液位>1050mm |  | digital
N2DCS.20MAV10CL121_XH03 | 12237 | #1润滑油箱液位>1000mm |  | digital
N2DCS.20MAV10CL121_XH52 | 12238 | #1润滑油箱液位<850mm |  | digital
N2DCS.20MAV10CL121_XH54 | 12239 | #1润滑油箱液位<900mm |  | digital
N2DCS.20MAV10CL121_XM20 | 12240 | #1润滑油箱液位坏点 |  | digital
N2DCS.20MAV10CL122_XH01 | 12241 | #2润滑油箱液位>1050mm |  | digital
N2DCS.20MAV10CL122_XH03 | 12242 | #2润滑油箱液位>1000mm |  | digital
N2DCS.20MAV10CL122_XH52 | 12243 | #2润滑油箱液位<850mm |  | digital
N2DCS.20MAV10CL122_XH54 | 12244 | #2润滑油箱液位<900mm |  | digital
N2DCS.20MAV10CL122_XM20 | 12245 | Ovation Control Builder |  | digital
N2DCS.20MAV10CL123_XH01 | 12246 | #3润滑油箱液位>1050mm |  | digital
N2DCS.20MAV10CL123_XH03 | 12247 | #3润滑油箱液位>1000mm |  | digital
N2DCS.20MAV10CL123_XH52 | 12248 | #3润滑油箱液位<850mm |  | digital
N2DCS.20MAV10CL123_XH54 | 12249 | #3润滑油箱液位<900mm |  | digital
N2DCS.20MAV10CL123_XM20 | 12250 | Ovation Control Builder |  | digital
N2DCS.20MAV10EZ121_XK93 | 12251 | 润滑油液位测量存在故障 |  | digital
N2DCS.20MAV10EZ121_XK94 | 12252 | 润滑油液位＜900mm |  | digital
N2DCS.20MAV10EZ121_XK95 | 12253 | 润滑油液位＞1000mm |  | digital
N2DCS.20MAV10EZ121_XK96 | 12254 | Ovation Control Builder |  | digital
N2DCS.20MAV10EZ121_XV01 | 12255 | Ovation Control Builder |  | digital
N2DCS.20MAV10FL121A_DL12 | 12256 | Ovation Control Builder |  | digital
N2DCS.20MAV10FL121A_DL13 | 12257 | Ovation Control Builder |  | digital
N2DCS.20MAV10FL121A_DL23 | 12258 | Ovation Control Builder |  | digital
N2DCS.20MAV10FL121A_XM97 | 12259 | Ovation Control Builder |  | digital
N2DCS.20MAV10FL121A_XM98 | 12260 | Ovation Control Builder |  | digital
N2DCS.20MAV10FL121A_XM99 | 12261 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP116_XH52 | 12262 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP116_XH54 | 12263 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP116_XM20 | 12264 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP117_XH52 | 12265 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP117_XH54 | 12266 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP117_XM20 | 12267 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP118_XH52 | 12268 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP118_XH54 | 12269 | Ovation Control Builder |  | digital
N2DCS.20MAV42CP118_XM20 | 12270 | Ovation Control Builder |  | digital
N2DCS.20MAV42EZ116_XK93 | 12271 | 润滑油压力测量存在故障 |  | digital
N2DCS.20MAV42EZ116_XK94 | 12272 | 润滑油压力＜0.25MPa |  | digital
N2DCS.20MAV42EZ116_XK96 | 12273 | Ovation Control Builder |  | digital
N2DCS.20MAV42EZ116_XV01 | 12274 | Ovation Control Builder |  | digital
N2DCS.20MAV42FP116_XH01 | 12275 | Ovation Control Builder |  | digital
N2DCS.20MAV42FP116_XH03 | 12276 | Ovation Control Builder |  | digital
N2DCS.20MAV42FP116A_DL12 | 12277 | Ovation Control Builder |  | digital
N2DCS.20MAV42FP116A_DL13 | 12278 | Ovation Control Builder |  | digital
N2DCS.20MAV42FP116A_DL23 | 12279 | Ovation Control Builder |  | digital
N2DCS.20MAV42FP116A_XM97 | 12280 | Ovation Control Builder |  | digital
N2DCS.20MAV42FP116A_XM98 | 12281 | Ovation Control Builder |  | digital
N2DCS.20MAV42FP116A_XM99 | 12282 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP101_XH52 | 12283 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP101_XH54 | 12284 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP101_XM20 | 12285 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP102_XH52 | 12286 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP102_XH54 | 12287 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP102_XM20 | 12288 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP103_XH52 | 12289 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP103_XH54 | 12290 | Ovation Control Builder |  | digital
N2DCS.20MAX01CP103_XM20 | 12291 | Ovation Control Builder |  | digital
N2DCS.20MAX01EZ103_XK93 | 12292 | 控制油压力测量存在故障 |  | digital
N2DCS.20MAX01EZ103_XK94 | 12293 | 控制油压力＜12MPa |  | digital
N2DCS.20MAX01EZ103_XK96 | 12294 | Ovation Control Builder |  | digital
N2DCS.20MAX01EZ103_XV01 | 12295 | Ovation Control Builder |  | digital
N2DCS.20MAX01FP103_XH01 | 12296 | Ovation Control Builder |  | digital
N2DCS.20MAX01FP103A_DL12 | 12297 | Ovation Control Builder |  | digital
N2DCS.20MAX01FP103A_DL13 | 12298 | Ovation Control Builder |  | digital
N2DCS.20MAX01FP103A_DL23 | 12299 | Ovation Control Builder |  | digital
N2DCS.20MAX01FP103A_XM97 | 12300 | Ovation Control Builder |  | digital
N2DCS.20MAX01FP103A_XM98 | 12301 | Ovation Control Builder |  | digital
N2DCS.20MAX01FP103A_XM99 | 12302 | Ovation Control Builder |  | digital
N2DCS.20MAY01EU001_XK96 | 12303 | Ovation Control Builder |  | digital
N2DCS.20MAY01EU001_XV01 | 12304 | Ovation Control Builder |  | digital
N2DCS.20MAY01EZ001_XK01 | 12305 | Ovation Control Builder |  | digital
N2DCS.20MAY01EZ001F_XK46 | 12306 | ETS首出信号未来 |  | digital
N2DCS.20MAY01EZ001F_XK96 | 12307 | ETS首出 |  | digital
N2DCS.20MAY01EZ003_RESET | 12308 | 复位跳闸首出(5S脉冲) |  | digital
N2DCS.20MAY01EZ003_XA01 | 12309 | Ovation Control Builder |  | digital
N2DCS.20MAY01EZ011_XK461 | 12310 | 汽机遮断系统已遮断1 |  | digital
N2DCS.20MAY01EZ011_XK4610 | 12311 | 汽机遮断系统已遮断10 |  | digital
N2DCS.20MAY01EZ011_XK4611 | 12312 | 汽机遮断系统已遮断11 |  | digital
N2DCS.20MAY01EZ011_XK4612 | 12313 | 汽机遮断系统已遮断12 |  | digital
N2DCS.20MAY01EZ011_XK4613 | 12314 | 汽机遮断系统已遮断13 |  | digital
N2DCS.20MAY01EZ011_XK4614 | 12315 | 汽机遮断系统已遮断14 |  | digital
N2DCS.20MAY01EZ011_XK4615 | 12316 | 汽机遮断系统已遮断15 |  | digital
N2DCS.20MAY01EZ011_XK4616 | 12317 | 汽机遮断系统已遮断16 |  | digital
N2DCS.20MAY01EZ011_XK4617 | 12318 | 汽机遮断系统已遮断17 |  | digital
N2DCS.20MAY01EZ011_XK4618 | 12319 | 汽机遮断系统已遮断18 |  | digital
N2DCS.20MAY01EZ011_XK462 | 12320 | 汽机遮断系统已遮断2 |  | digital
N2DCS.20MAY01EZ011_XK463_DEH | 12321 | 汽机遮断系统已遮断3 |  | digital
N2DCS.20MAY01EZ011_XK464_DEH | 12322 | 汽机遮断系统已遮断4 |  | digital
N2DCS.20MAY01EZ011_XK465_DEH | 12323 | 汽机遮断系统已遮断5 |  | digital
N2DCS.20MAY01EZ011_XK466_DEH | 12324 | 汽机遮断系统已遮断6 |  | digital
N2DCS.20MAY01EZ011_XK467_DEH | 12325 | 汽机遮断系统已遮断7 |  | digital
N2DCS.20MAY01EZ011_XK468_DEH | 12326 | 汽机遮断系统已遮断8 |  | digital
N2DCS.20MAY01EZ011_XK469_DEH | 12327 | 汽机遮断系统已遮断9 |  | digital
N2DCS.20MAY01EZ020_XK96 | 12328 | Ovation Control Builder |  | digital
N2DCS.20MAY01EZ020_XV01 | 12329 | Ovation Control Builder |  | digital
N2DCS.20MAY01EZ020_XG51 | 12330 | 汽轮机遮断按钮STRING1# |  | digital
N2DCS.20MAY01EZ020_XG52 | 12331 | 汽轮机遮断按钮STRING2# |  | digital
N2DCS.20MAY01EZ020_XG53 | 12332 | 汽轮机遮断按钮STRING3# |  | digital
N2DCS.20MAY01GS001_A | 12333 | 汽轮机遮断按钮1#常开接点 |  | digital
N2DCS.20MAY01GS001_B | 12334 | 汽轮机遮断按钮1#常闭接点 |  | digital
N2DCS.20MAY01GS001_C | 12335 | 汽轮机遮断按钮1#常闭接点 |  | digital
N2DCS.20MAY01GS001_D | 12336 | 汽轮机遮断按钮1#常闭接点 |  | digital
N2DCS.20MAY01GS001_E | 12337 | 汽轮机遮断按钮1#常闭接点 |  | digital
N2DCS.20MAY01GS001_XG02 | 12338 | 汽轮机遮断按钮控制室（常开接点 |  | digital
N2DCS.20MAY01GS002_A | 12339 | 汽轮机遮断按钮2#常开接点 |  | digital
N2DCS.20MAY01GS002_B | 12340 | 汽轮机遮断按钮2#常闭接点 |  | digital
N2DCS.20MAY01GS002_C | 12341 | 汽轮机遮断按钮2#常闭接点 |  | digital
N2DCS.20MAY01GS002_D | 12342 | 汽轮机遮断按钮2#常闭接点 |  | digital
N2DCS.20MAY01GS002_E | 12343 | 汽轮机遮断按钮2#常闭接点 |  | digital
N2DCS.20MAY01GS002_XG02 | 12344 | 汽轮机遮断按钮控制室（常开接点 |  | digital
N2DCS.20MAY01GS003_A | 12345 | 汽轮机遮断按钮3#常开接点 |  | digital
N2DCS.20MAY01GS003_B | 12346 | 汽轮机遮断按钮3#常闭接点 |  | digital
N2DCS.20MAY01GS003_C | 12347 | 汽轮机遮断按钮3#常闭接点 |  | digital
N2DCS.20MAY01GS003_D | 12348 | 汽轮机遮断按钮3#常闭接点 |  | digital
N2DCS.20MAY01GS003_XG02 | 12349 | 汽轮机遮断按钮（常开接点） |  | digital
N2DCS.20MKD11CT113A_XH01 | 12350 | Ovation Control Builder |  | digital
N2DCS.20MKD11CT113A_XH03 | 12351 | Ovation Control Builder |  | digital
N2DCS.20MKD11CT113A_XM20 | 12352 | #1汽轮发电机轴承左下温度A坏点 |  | digital
N2DCS.20MKD11CT113B_XH01 | 12353 | Ovation Control Builder |  | digital
N2DCS.20MKD11CT113B_XH03 | 12354 | Ovation Control Builder |  | digital
N2DCS.20MKD11CT113B_XM20 | 12355 | #1汽轮发电机轴承左下温度B坏点 |  | digital
N2DCS.20MKD11CT114B_XH01 | 12356 | Ovation Control Builder |  | digital
N2DCS.20MKD11CT114B_XH03 | 12357 | Ovation Control Builder |  | digital
N2DCS.20MKD11CT114B_XM20 | 12358 | #1汽轮发电机轴承右下温度B坏点 |  | digital
N2DCS.20MKD11CY021_XM71 | 12359 | #1汽轮发电机轴承壳振1正常 |  | digital
N2DCS.20MKD11CY022_XM71 | 12360 | #1汽轮发电机轴承壳振2正常 |  | digital
N2DCS.20MKD11CY121_MAX1 | 12361 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY121_MAX2 | 12362 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY121_XH01 | 12363 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY121_XH03 | 12364 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY121_XM71 | 12365 | #1汽轮发电机轴承壳振1正常 |  | digital
N2DCS.20MKD11CY121_XM72 | 12366 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY121_XV20 | 12367 | #4轴瓦振动通道故障1 |  | digital
N2DCS.20MKD11CY122_MAX1 | 12368 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY122_MAX2 | 12369 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY122_XH01 | 12370 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY122_XH03 | 12371 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY122_XM71 | 12372 | #1汽轮发电机轴承壳振2正常 |  | digital
N2DCS.20MKD11CY122_XM72 | 12373 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY122_XV20 | 12374 | #4轴瓦振动通道故障2 |  | digital
N2DCS.20MKD11EZ121_XK93 | 12375 | Ovation Control Builder |  | digital
N2DCS.20MKD11EZ121_XK94 | 12376 | Ovation Control Builder |  | digital
N2DCS.20MKD11EZ121_XK96 | 12377 | Ovation Control Builder |  | digital
N2DCS.20MKD11EZ201_XK93 | 12378 | 汽端发电机轴瓦温度测量存在故障 |  | digital
N2DCS.20MKD11EZ201_XK94 | 12379 | 汽端发电机轴瓦温度＞99℃ |  | digital
N2DCS.20MKD11EZ201_XK96 | 12380 | Ovation Control Builder |  | digital
N2DCS.20MKD12CT113A_XH01 | 12381 | Ovation Control Builder |  | digital
N2DCS.20MKD12CT113A_XH03 | 12382 | Ovation Control Builder |  | digital
N2DCS.20MKD12CT113A_XM20 | 12383 | Ovation Control Builder |  | digital
N2DCS.20MKD12CT113B_XH01 | 12384 | Ovation Control Builder |  | digital
N2DCS.20MKD12CT113B_XH03 | 12385 | Ovation Control Builder |  | digital
N2DCS.20MKD12CT113B_XM20 | 12386 | #2汽轮发电机轴承左下温度B坏点 |  | digital
N2DCS.20MKD12CT114B_XH01 | 12387 | Ovation Control Builder |  | digital
N2DCS.20MKD12CT114B_XH03 | 12388 | Ovation Control Builder |  | digital
N2DCS.20MKD12CT114B_XM20 | 12389 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY021_XM71 | 12390 | #2汽轮发电机轴承壳振1正常 |  | digital
N2DCS.20MKD12CY022_XM71 | 12391 | #2汽轮发电机轴承壳振2正常 |  | digital
N2DCS.20MKD12CY121_MAX1 | 12392 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY121_MAX2 | 12393 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY121_XH01 | 12394 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY121_XH03 | 12395 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY121_XM71 | 12396 | #2汽轮发电机轴承壳振1正常 |  | digital
N2DCS.20MKD12CY121_XM72 | 12397 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY121_XV20 | 12398 | #5轴瓦振动通道故障1 |  | digital
N2DCS.20MKD12CY122_MAX1 | 12399 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY122_MAX2 | 12400 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY122_XH01 | 12401 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY122_XH03 | 12402 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY122_XM71 | 12403 | #2汽轮发电机轴承壳振2正常 |  | digital
N2DCS.20MKD12CY122_XM72 | 12404 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY122_XV20 | 12405 | #5轴瓦振动通道故障2 |  | digital
N2DCS.20MKD12EZ121_XK93 | 12406 | Ovation Control Builder |  | digital
N2DCS.20MKD12EZ121_XK94 | 12407 | Ovation Control Builder |  | digital
N2DCS.20MKD12EZ121_XK96 | 12408 | Ovation Control Builder |  | digital
N2DCS.20MKD12EZ201_XK93 | 12409 | 励端发电机轴瓦温度测量存在故障 |  | digital
N2DCS.20MKD12EZ201_XK94 | 12410 | 励端发电机轴瓦温度＞99℃ |  | digital
N2DCS.20MKD12EZ201_XK96 | 12411 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG010_XT10 | 12412 | ENABLE CSI6300 #1 TRIP TEST |  | digital
N2DCS.20MYA01DG010_XT11 | 12413 | RESET CSI6300 #1 TRIP LATCHED |  | digital
N2DCS.20MYA01DG010_XT20 | 12414 | CSI6300 #1 TRIP MODULE A TEST |  | digital
N2DCS.20MYA01DG010_XT30 | 12415 | CSI6300 #1 TRIP MODULE B TEST |  | digital
N2DCS.20MYA01DG010_XT40 | 12416 | CSI6300 #1 TRIP MODULE C TEST |  | digital
N2DCS.20MYA01DG020_XT10 | 12417 | ENABLE CSI6300 #2 TRIP TEST |  | digital
N2DCS.20MYA01DG020_XT11 | 12418 | RESET CSI6300 #2 TRIP LATCHED |  | digital
N2DCS.20MYA01DG020_XT20 | 12419 | CSI6300 #2 TRIP MODULE A TEST |  | digital
N2DCS.20MYA01DG020_XT30 | 12420 | CSI6300 #2 TRIP MODULE B TEST |  | digital
N2DCS.20MYA01DG020_XT40 | 12421 | CSI6300 #2 TRIP MODULE C TEST |  | digital
N2DCS.20MYA01DG030_AFTEST | 12422 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG030_FD2TEST | 12423 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG030_FDTEST | 12424 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG030_TESTAFS | 12425 | 中压主汽门活动性试验 |  | digital
N2DCS.20MYA01DG030_TESTFDS | 12426 | 高压主汽门活动性试验 |  | digital
N2DCS.20MYA01DG030_TESTON | 12427 | Ovation Control Builder |  | digital
N2DCS.20MYA01EZ011_XK96 | 12428 | Ovation Control Builder |  | digital
N2DCS.20MYA01EZ011_XT22 | 12429 | Ovation Control Builder |  | digital
N2DCS.20MYA01EZ011_XV01 | 12430 | Ovation Control Builder |  | digital
N2DCS.20MYA01EZ011_XK61 | 12431 | 超速保护 CSI6300 1# A OUT2 |  | digital
N2DCS.20MYA01EZ011_XK62 | 12432 | 超速保护 CSI6300 1# B OUT2 |  | digital
N2DCS.20MYA01EZ011_XK63 | 12433 | 超速保护 CSI6300 1# C OUT2 |  | digital
N2DCS.20MYA01EZ011_XT12 | 12434 | 超速保护 CSI6300 1# MODULE A O |  | digital
N2DCS.20MYA01EZ011_XT14 | 12435 | 超速保护 CSI6300 1# MODULE B O |  | digital
N2DCS.20MYA01EZ011_XT16 | 12436 | 超速保护 CSI6300 1# MODULE C O |  | digital
N2DCS.20MYA01EZ011_XT21 | 12437 | CSI6300 1# System OK |  | digital
N2DCS.20MYA01EZ021_XK96 | 12438 | Ovation Control Builder |  | digital
N2DCS.20MYA01EZ021_XT22 | 12439 | Ovation Control Builder |  | digital
N2DCS.20MYA01EZ021_XV01 | 12440 | Ovation Control Builder |  | digital
N2DCS.20MYA01EZ021_XK61 | 12441 | 超速保护 CSI6300 2# A OUT2 |  | digital
N2DCS.20MYA01EZ021_XK62 | 12442 | 超速保护 CSI6300 2# B OUT2 |  | digital
N2DCS.20MYA01EZ021_XK63 | 12443 | 超速保护 CSI6300 2# C OUT2 |  | digital
N2DCS.20MYA01EZ021_XT21 | 12444 | CSI6300 2# System OK |  | digital
N2DCS.20MYA02EZ011_XT12 | 12445 | 超速保护 CSI6300 2# MODULE A O |  | digital
N2DCS.20MYA02EZ011_XT14 | 12446 | 超速保护 CSI6300 2# MODULE B O |  | digital
N2DCS.20MYA02EZ011_XT16 | 12447 | 超速保护 CSI6300 2# MODULE C O |  | digital
N2DCS.DROP41GW001_XM09 | 12448 | 机柜空开正常 |  | digital
N2DCS.DROP41GW001_XM10 | 12449 | 机柜电源正常 |  | digital
N2DCS.20MAD12CY145_XM72 | 12450 | 膨胀通道故障 |  | digital
N2DCS.20BAC01GS001H1 | 12451 | 发电机出口开关闭合(NO 接点1) |  | digital
N2DCS.20BAC01GS001H2 | 12452 | 发电机出口开关闭合(NO 接点2) |  | digital
N2DCS.20BAC01GS001H3 | 12453 | 发电机出口开关闭合(NO 接点3) |  | digital
N2DCS.20CBA00FU002_DEH | 12454 | 负荷遥控模式 |  | digital
N2DCS.20CBA00FU019 | 12455 | 自动同步控制（请求同期） |  | digital
N2DCS.20CJA06DU001_XT01 | 12456 | 负荷控制协调方式请求 |  | digital
N2DCS.20CJJ01EE001_XT09 | 12457 | 汽机疏水投自动 |  | digital
N2DCS.20LBA10CF001_XH10 | 12458 | 高压蒸汽流量>10% |  | digital
N2DCS.20LBA10CF001_XH15 | 12459 | 高压蒸汽流量>15% |  | digital
N2DCS.20LBA10CF001_XH20 | 12460 | Ovation Control Builder |  | digital
N2DCS.20LBA10CP901_ST1 | 12461 | 高压主汽门前蒸汽压力测点全坏 |  | digital
N2DCS.20LBA10CP901_XH01 | 12462 | 高压主汽门前蒸汽压力>2Mpa |  | digital
N2DCS.20LBA10CP901_XH02 | 12463 | 高压主汽门前蒸汽压力>0.5MPa |  | digital
N2DCS.20LBA10CP901_XH03 | 12464 | 高压主汽门前蒸汽压力>3Mpa |  | digital
N2DCS.20LBA10CP901_XM01 | 12465 | 高压主汽门前蒸汽压力测点全坏 |  | digital
N2DCS.20LBA90CP901_ST1 | 12466 | 低压主汽门前蒸汽压力测点全坏 |  | digital
N2DCS.20LBA90CP901_XH01 | 12467 | 低压主汽门前蒸汽压力>0.2MPa |  | digital
N2DCS.20LBA90CP901_XH02 | 12468 | 低压主汽门前蒸汽压力>0 |  | digital
N2DCS.20LBA90CP901_XH03 | 12469 | 低压主汽门前蒸汽压力>0 |  | digital
N2DCS.20LBA90CP901_XM01 | 12470 | 低压主汽门前蒸汽压力测点全坏 |  | digital
N2DCS.20LBB10CP901_ST1 | 12471 | 中压主汽门前蒸汽压力测点全坏 |  | digital
N2DCS.20LBB10CP901_XH03 | 12472 | 中压主汽门前蒸汽压力<0.1MPa |  | digital
N2DCS.20LBB10CP901_XH09 | 12473 | 中压主汽门前蒸汽压力>0.5MPa |  | digital
N2DCS.20LBC10AA001_XB01 | 12474 | 高排逆止阀关 |  | digital
N2DCS.20LBC10AA001_XB02 | 12475 | 高排逆止阀开 |  | digital
N2DCS.20LBC10AA001_XM20 | 12476 | 高排逆止门故障(全开全关均为1) |  | digital
N2DCS.20LBC40CP101_XM20 | 12477 | #1高压排汽蒸汽压力坏点 |  | digital
N2DCS.20LBC40CP102_XM20 | 12478 | #2高压排汽蒸汽压力坏点 |  | digital
N2DCS.20LBC40CP103_XM20 | 12479 | #3高压排汽蒸汽压力坏点 |  | digital
N2DCS.20LBC40FP101_XH01 | 12480 | 高排高高-抽汽解裂 |  | digital
N2DCS.20LBC40FP101_XH02 | 12481 | 高排低低-抽汽解裂 |  | digital
N2DCS.20LBC40FP101_XH03 | 12482 | 高压排汽蒸汽压力<0 |  | digital
N2DCS.20LBC40FP101_XH04 | 12483 | 高排低-抽汽报警 |  | digital
N2DCS.20LBC40FP101_XH05 | 12484 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101_XH52 | 12485 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101_XH54 | 12486 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101_XK96 | 12487 | Ovation Control Builder |  | digital
N2DCS.20LBC41AA001_XM20 | 12488 | 高排通风阀故障(全开全关均为1) |  | digital
N2DCS.20LBC41CG051B | 12489 | 高排通风阀开 |  | digital
N2DCS.20LBC41CG051C | 12490 | 高排通风阀关 |  | digital
N2DCS.20LBS44AA001_XG01 | 12491 | Ovation Control Builder |  | digital
N2DCS.20LBS44AA001_XG03 | 12492 | Ovation Control Builder |  | digital
N2DCS.20LBS44AA001_XM20 | 12493 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_IPEGO | 12494 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_IPEIN | 12495 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_IPEQSP | 12496 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_IPETM | 12497 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_LOWER | 12498 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_RAISE | 12499 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_TRACK | 12500 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_XG01 | 12501 | 中压抽汽快关调节阀就地控制允许 |  | digital
N2DCS.20LBS45CG001 | 12502 | 中压抽汽快关调节阀开反馈 |  | digital
N2DCS.20LBS45CG003 | 12503 | 中压抽汽快关调节阀关反馈 |  | digital
N2DCS.20LBS45CG151_XH01 | 12504 | Ovation Control Builder |  | digital
N2DCS.20LBS45CG151_XH51 | 12505 | Ovation Control Builder |  | digital
N2DCS.20LBS45CG151_XM20 | 12506 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_HPEGO | 12507 | 高排抽汽设定运行 |  | digital
N2DCS.20LBS46AA001_HPEIN | 12508 | 高排抽汽投入 |  | digital
N2DCS.20LBS46AA001_HPEQSP | 12509 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_HPETM | 12510 | 高排抽汽控制手动 |  | digital
N2DCS.20LBS46AA001_LOWER | 12511 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_RAISE | 12512 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_TRACK | 12513 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_XG01 | 12514 | 高压抽汽快关调节阀就地控制允许 |  | digital
N2DCS.20LBS46CG001 | 12515 | 高压抽汽快关调节阀开反馈 |  | digital
N2DCS.20LBS46CG003 | 12516 | 高压抽汽快关调节阀关反馈 |  | digital
N2DCS.20LBS46CG151_XH01 | 12517 | Ovation Control Builder |  | digital
N2DCS.20LBS46CG151_XH51 | 12518 | Ovation Control Builder |  | digital
N2DCS.20LBS46CG151_XM20 | 12519 | Ovation Control Builder |  | digital
N2DCS.20MAA11CG051_XG01 | 12520 | 主汽门已全开 |  | digital
N2DCS.20MAA11CG051_XG11 | 12521 | 主汽门关闭 |  | digital
N2DCS.20MAA11CG151_XH01 | 12522 | 高压主汽门全开反馈 |  | digital
N2DCS.20MAA11CG151_XH52 | 12523 | 高压主汽门全关位 |  | digital
N2DCS.20MAA11CG151_XM20 | 12524 | 高压主气门反馈坏点 |  | digital
N2DCS.20MAA12CG051_XG01 | 12525 | 高压调门开启状态 |  | digital
N2DCS.20MAA12CG051_XG11 | 12526 | 高调门关闭 |  | digital
N2DCS.20MAA12CG151_SBFD | 12527 | 高压调门阀位坏点 |  | digital
N2DCS.20MAA12CG151_XH02 | 12528 | 高压调门阀位反馈>3% |  | digital
N2DCS.20MAA12CG151_XH52 | 12529 | 高调门已关闭 |  | digital
N2DCS.20MAA12DG010_BFDNA | 12530 | 汽机未遮断(脉冲) |  | digital
N2DCS.20MAA12DG010_BFDZU | 12531 | 汽机已遮断(脉冲) |  | digital
N2DCS.20MAA12DG010_SPBFD | 12532 | Ovation Control Builder |  | digital
N2DCS.20MAA12DG010_TRACK | 12533 | Ovation Control Builder |  | digital
N2DCS.20MAA12DG010_TRACKN | 12534 | Ovation Control Builder |  | digital
N2DCS.20MAA12DG010_VLVTE | 12535 | 汽机未遮断 |  | digital
N2DCS.20MAA12DG010_XH01 | 12536 | 高调门阀限>104.5 |  | digital
N2DCS.20MAA12SGAF1 | 12537 | 快关中调阀 |  | digital
N2DCS.20MAA12SGAF2 | 12538 | Ovation Control Builder |  | digital
N2DCS.20MAA12SGFD1 | 12539 | 快关高调阀 |  | digital
N2DCS.20MAA12SGFD2 | 12540 | 高压调门快关激活 |  | digital
N2DCS.20MAA12SGZD2 | 12541 | 低压调阀快关激活 |  | digital
N2DCS.20MAA30EE001_SEALCV | 12542 | Ovation Control Builder |  | digital
N2DCS.20MAA30EE001_SEALESV | 12543 | Ovation Control Builder |  | digital
N2DCS.20MAA30EE001_SEALESVINH | 12544 | Ovation Control Builder |  | digital
N2DCS.20MAA50CP101_XM20 | 12545 | Ovation Control Builder |  | digital
N2DCS.20MAA50CP102_XM20 | 12546 | Ovation Control Builder |  | digital
N2DCS.20MAA50CP103_XM20 | 12547 | Ovation Control Builder |  | digital
N2DCS.20MAA50CP111_XM20 | 12548 | Ovation Control Builder |  | digital
N2DCS.20MAA50CP112_XM20 | 12549 | Ovation Control Builder |  | digital
N2DCS.20MAA50CP113_XM20 | 12550 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ111_XH52 | 12551 | 高压缸压比＜1.05 |  | digital
N2DCS.20MAA50EZ111_XH54 | 12552 | 高压缸压比＜1.08 |  | digital
N2DCS.20MAA50EZ111_XK20 | 12553 | Ovation Control Builder |  | digital
N2DCS.20MAA50EZ111_XK96 | 12554 | 高压缸压比保护 |  | digital
N2DCS.20MAA50FP011_XH03 | 12555 | 高调门阀后蒸汽压力>7MPa |  | digital
N2DCS.20MAA50FP011_XH05 | 12556 | 高调门阀后蒸汽压力>2.5MPa |  | digital
N2DCS.20MAA50FP011_XM23 | 12557 | 高调门阀后蒸汽压力测点全坏 |  | digital
N2DCS.20MAB11CG051_XG01 | 12558 | 再热主汽门已全开 |  | digital
N2DCS.20MAB11CG051_XG11 | 12559 | 再热主汽门关闭 |  | digital
N2DCS.20MAB11CG151_XH01 | 12560 | 中压主汽门全开反馈 |  | digital
N2DCS.20MAB11CG151_XH52 | 12561 | 中压主汽门全关位 |  | digital
N2DCS.20MAB11CG151_XM20 | 12562 | Ovation Control Builder |  | digital
N2DCS.20MAB12AA001_EGVIN | 12563 | 再热调门抽汽投入 |  | digital
N2DCS.20MAB12AA001_EGVOFF | 12564 | 再热调门抽汽退出 |  | digital
N2DCS.20MAB12CG051_XG01 | 12565 | 中压调门开启状态 |  | digital
N2DCS.20MAB12CG051_XG11 | 12566 | 中压调门关闭 |  | digital
N2DCS.20MAB12CG151_SBAF | 12567 | Ovation Control Builder |  | digital
N2DCS.20MAB12CG151_XH02 | 12568 | 中压调门阀位反馈>3% |  | digital
N2DCS.20MAB12CG151_XH52 | 12569 | 中调门已关闭 |  | digital
N2DCS.20MAB12CG151_XH53 | 12570 | 中压调门阀位>10% |  | digital
N2DCS.20MAB12DG010_XH01 | 12571 | 中调门阀限>104.5 |  | digital
N2DCS.20MAB50CP101_XM20 | 12572 | Ovation Control Builder |  | digital
N2DCS.20MAC10CP101_XM20 | 12573 | Ovation Control Builder |  | digital
N2DCS.20MAC10CP102_XM20 | 12574 | Ovation Control Builder |  | digital
N2DCS.20MAC10CP103_XM20 | 12575 | Ovation Control Builder |  | digital
N2DCS.20MAC10CP901_XH01 | 12576 | Ovation Control Builder |  | digital
N2DCS.20MAC10CP901_XH03 | 12577 | Ovation Control Builder |  | digital
N2DCS.20MAC10CP901_XH05 | 12578 | Ovation Control Builder |  | digital
N2DCS.20MAC10CP901_XH52 | 12579 | Ovation Control Builder |  | digital
N2DCS.20MAC10CP901_XH54 | 12580 | Ovation Control Builder |  | digital
N2DCS.20MAC11FF001_DEH | 12581 | 热网故障 |  | digital
N2DCS.20MAC45AA001_XM20 | 12582 | 补汽主汽门故障 |  | digital
N2DCS.20MAC45AA001_XB11 | 12583 | 开低压补汽主门油动机 |  | digital
N2DCS.20MAC45AA001_XB13 | 12584 | 关低压补汽主门油动机 |  | digital
N2DCS.20MAC45AA001_XG01 | 12585 | 低压补汽主门油动机就地控制允许 |  | digital
N2DCS.20MAC45AA001_XG05 | 12586 | 低压补汽主门油动机试验电磁阀动 |  | digital
N2DCS.20MAC45AA011_XB01 | 12587 | Ovation Control Builder |  | digital
N2DCS.20MAC45AA011_XB02 | 12588 | Ovation Control Builder |  | digital
N2DCS.20MAC45CG001 | 12589 | 补汽主汽门开反馈 |  | digital
N2DCS.20MAC45CG002 | 12590 | 补汽主汽门关反馈 |  | digital
N2DCS.20MAC46AA001_XG01 | 12591 | 低压补汽调门油动机就地控制允许 |  | digital
N2DCS.20MAC46CG001 | 12592 | 补汽调阀开反馈 |  | digital
N2DCS.20MAC46CG003 | 12593 | 补汽调阀关反馈 |  | digital
N2DCS.20MAC46CG151_SBZD | 12594 | 低压补汽调门阀位反馈坏点 |  | digital
N2DCS.20MAC46CG151_XH02 | 12595 | 低压补汽调门开启 |  | digital
N2DCS.20MAC46CG151_XH52 | 12596 | 低压补汽调门关闭 |  | digital
N2DCS.20MAC46DG010_XH01 | 12597 | Ovation Control Builder |  | digital
N2DCS.20MAL11AA051_XM20 | 12598 | 高压调门前疏水阀位反馈质量坏点 |  | digital
N2DCS.20MAL11AA051T_XV02 | 12599 | 高压主门疏水门指令反馈无偏差 |  | digital
N2DCS.20MAL11CG151_XH02 | 12600 | 高压调门前疏水阀位反馈大于98 |  | digital
N2DCS.20MAL11CG151_XH52 | 12601 | 高压调门前疏水阀位反馈<5.5% |  | digital
N2DCS.20MAL23AA051_XM20 | 12602 | 中压主汽门前疏水门故障 |  | digital
N2DCS.20MAL23AA051A_XT01 | 12603 | 中压主汽门前疏水门开指令 |  | digital
N2DCS.20MAL23AA051B_XG01 | 12604 | 中压主汽门前疏水门反馈开 |  | digital
N2DCS.20MAL23AA051C_XG01 | 12605 | 中压主汽门前疏水门反馈关 |  | digital
N2DCS.20MAL23CG051B_XG01 | 12606 | 中压主汽门前疏水门反馈开 |  | digital
N2DCS.20MAL23CG051C_XG01 | 12607 | 中压主汽门前疏水门反馈关 |  | digital
N2DCS.20MAL26AA051_XM20 | 12608 | 中压调节阀前疏水门故障 |  | digital
N2DCS.20MAL26AA051A_XT01 | 12609 | 中压调节阀前疏水门开指令 |  | digital
N2DCS.20MAL26AA051B_XG01 | 12610 | 中压调节阀前疏水门反馈开 |  | digital
N2DCS.20MAL26AA051C_XG01 | 12611 | 中压调节阀前疏水门反馈关 |  | digital
N2DCS.20MAL26CG051B_XG01 | 12612 | 中压调节阀前疏水门反馈开 |  | digital
N2DCS.20MAL26CG051C_XG01 | 12613 | 中压调节阀前疏水门反馈关 |  | digital
N2DCS.20MAV30EU001_XV01 | 12614 | Ovation Control Builder |  | digital
N2DCS.20MAV30EU001_XV04 | 12615 | Ovation Control Builder |  | digital
N2DCS.20MAW10EG003_XV01 | 12616 | Ovation Control Builder |  | digital
N2DCS.20MAY00EE001_XA01 | 12617 | 已释放蒸汽品质 |  | digital
N2DCS.20MAY00EE001_XA02 | 12618 | 未释放蒸汽品质 |  | digital
N2DCS.20MAY00EE002_XA01 | 12619 | 已释放额定转速 |  | digital
N2DCS.20MAY00EE002_XA02 | 12620 | 未释放额定转速 |  | digital
N2DCS.20MAY01CG151_XH51 | 12621 | 所有主汽门已关闭1(去发电机主保 |  | digital
N2DCS.20MAY01CG151_XH52 | 12622 | 所有主汽门已关闭1(去锅炉主保护 |  | digital
N2DCS.20MAY01CG151_XH53 | 12623 | 所有主汽门已关闭2(去发电机主保 |  | digital
N2DCS.20MAY01CG151_XH54 | 12624 | 所有主汽门已关闭2(去锅炉主保护 |  | digital
N2DCS.20MAY01EZ001_XK46 | 12625 | Ovation Control Builder |  | digital
N2DCS.20MAY01EZ001_XK96 | 12626 | 汽机已遮断 |  | digital
N2DCS.20MAY01EZ001A_XK46 | 12627 | 汽机遮断系统已遮断A |  | digital
N2DCS.20MAY01EZ001B_XK46 | 12628 | 汽机遮断系统已遮断B |  | digital
N2DCS.20MAY10EC001_14JT6 | 12629 | 汽轮机启动顺控跳至第6步 |  | digital
N2DCS.20MAY10EC001_AAUS | 12630 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_CLSESV | 12631 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_CVCLSD | 12632 | 高、中、低压调门均全关 |  | digital
N2DCS.20MAY10EC001_DFAIL | 12633 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_DFINISHED | 12634 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_ENOP | 12635 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_ESVCLSD | 12636 | 高、中、低压主门均全关 |  | digital
N2DCS.20MAY10EC001_ESVOPND | 12637 | 高、中、低压主汽门均全开 |  | digital
N2DCS.20MAY10EC001_EVSSVOK | 12638 | 高/中/低压暖管完成 |  | digital
N2DCS.20MAY10EC001_M01 | 12639 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_RELEASE | 12640 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S10OK | 12641 | 汽机顺控启动第十步完成反馈 |  | digital
N2DCS.20MAY10EC001_S11OK | 12642 | 汽机顺控启动第十一步完成反馈 |  | digital
N2DCS.20MAY10EC001_S12OK | 12643 | 汽机顺控启动第十二步完成反馈 |  | digital
N2DCS.20MAY10EC001_S13OK | 12644 | 汽机顺控启动第十三步完成反馈 |  | digital
N2DCS.20MAY10EC001_S14OK | 12645 | 汽机顺控启动第十四步完成反馈 |  | digital
N2DCS.20MAY10EC001_S15OK | 12646 | 汽机顺控第十五步完成反馈 |  | digital
N2DCS.20MAY10EC001_S16OK | 12647 | 汽机顺控第十六步完成反馈 |  | digital
N2DCS.20MAY10EC001_S17OK | 12648 | 汽机顺控第十七步完成反馈 |  | digital
N2DCS.20MAY10EC001_S18OK | 12649 | 汽机顺控第十八步完成反馈 |  | digital
N2DCS.20MAY10EC001_S19OK | 12650 | 汽机顺控第十九步完成反馈 |  | digital
N2DCS.20MAY10EC001_S1OK | 12651 | 汽机顺控启动第一步完成反馈 |  | digital
N2DCS.20MAY10EC001_S20OK | 12652 | 汽机顺控第二十步完成反馈 |  | digital
N2DCS.20MAY10EC001_S21OK | 12653 | 汽机顺控第二十一步完成反馈 |  | digital
N2DCS.20MAY10EC001_S22OK | 12654 | 汽机顺控第二十二步完成反馈 |  | digital
N2DCS.20MAY10EC001_S23OK | 12655 | 汽机顺控第二十三步完成反馈 |  | digital
N2DCS.20MAY10EC001_S24OK | 12656 | 汽机顺控第二十四步完成反馈 |  | digital
N2DCS.20MAY10EC001_S25OK | 12657 | 汽机顺控第二十五步完成反馈 |  | digital
N2DCS.20MAY10EC001_S2OK | 12658 | 汽机顺控启动第二步完成反馈 |  | digital
N2DCS.20MAY10EC001_S3OK | 12659 | 汽机顺控启动第三步完成反馈 |  | digital
N2DCS.20MAY10EC001_S4OK | 12660 | 汽机顺控启动第四步完成反馈 |  | digital
N2DCS.20MAY10EC001_S51OK | 12661 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S52OK | 12662 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S53OK | 12663 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S54OK | 12664 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S55OK | 12665 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S56OK | 12666 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S57OK | 12667 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S58OK | 12668 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S59OK | 12669 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S5OK | 12670 | 汽机顺控启动第五步完成反馈 |  | digital
N2DCS.20MAY10EC001_S60OK | 12671 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S61OK | 12672 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_S6OK | 12673 | 汽机顺控启动第六步完成反馈 |  | digital
N2DCS.20MAY10EC001_S7OK | 12674 | 汽机顺控启动第七步完成反馈 |  | digital
N2DCS.20MAY10EC001_S8OK | 12675 | 汽机顺控启动第八步完成反馈 |  | digital
N2DCS.20MAY10EC001_S9OK | 12676 | 汽机顺控启动第九步完成反馈 |  | digital
N2DCS.20MAY10EC001_SASTILL | 12677 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_UDONE | 12678 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_UFAIL | 12679 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS01 | 12680 | 汽机顺控启动第一步指令 |  | digital
N2DCS.20MAY10EC001_XS02 | 12681 | 汽机顺控启动第二步指令 |  | digital
N2DCS.20MAY10EC001_XS03 | 12682 | 汽机启动顺控第三步指令 |  | digital
N2DCS.20MAY10EC001_XS04 | 12683 | 汽机顺控启动第四步指令 |  | digital
N2DCS.20MAY10EC001_XS05 | 12684 | 汽机顺控启动第五步指令 |  | digital
N2DCS.20MAY10EC001_XS06 | 12685 | 汽机顺控启动第六步指令 |  | digital
N2DCS.20MAY10EC001_XS07 | 12686 | 汽机顺控启动第七步指令 |  | digital
N2DCS.20MAY10EC001_XS08 | 12687 | 汽机顺控启动第八步指令 |  | digital
N2DCS.20MAY10EC001_XS09 | 12688 | 汽机顺控启动第九步指令 |  | digital
N2DCS.20MAY10EC001_XS10 | 12689 | 汽机顺控启动第十步指令 |  | digital
N2DCS.20MAY10EC001_XS11 | 12690 | 汽机顺控启动第十一步指令 |  | digital
N2DCS.20MAY10EC001_XS12 | 12691 | 汽机顺控启动第十二步指令 |  | digital
N2DCS.20MAY10EC001_XS13 | 12692 | 汽机顺控启动第十三步指令 |  | digital
N2DCS.20MAY10EC001_XS14 | 12693 | 汽机顺控启动第十四步指令 |  | digital
N2DCS.20MAY10EC001_XS15 | 12694 | 汽机顺控启动第十五步指令 |  | digital
N2DCS.20MAY10EC001_XS16 | 12695 | 汽机顺控启动第十六步指令 |  | digital
N2DCS.20MAY10EC001_XS17 | 12696 | 汽机顺控启动第十七步指令 |  | digital
N2DCS.20MAY10EC001_XS18 | 12697 | 汽机顺控启动第十八步指令 |  | digital
N2DCS.20MAY10EC001_XS19 | 12698 | 汽机顺控启动第十九步指令 |  | digital
N2DCS.20MAY10EC001_XS20 | 12699 | 汽机顺控启动第二十步指令 |  | digital
N2DCS.20MAY10EC001_XS21 | 12700 | 汽机顺控启动第二十一步指令 |  | digital
N2DCS.20MAY10EC001_XS22 | 12701 | 汽机顺控启动第二十二步指令 |  | digital
N2DCS.20MAY10EC001_XS23 | 12702 | 汽机顺控启动第二十三步指令 |  | digital
N2DCS.20MAY10EC001_XS24 | 12703 | 汽机顺控启动第二十四步指令 |  | digital
N2DCS.20MAY10EC001_XS25 | 12704 | 汽机顺控启动第二十五步指令 |  | digital
N2DCS.20MAY10EC001_XS51 | 12705 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS52 | 12706 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS53 | 12707 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS54 | 12708 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS55 | 12709 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS56 | 12710 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS57 | 12711 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS58 | 12712 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS59 | 12713 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XS60 | 12714 | 汽机顺控启动第六十步指令 |  | digital
N2DCS.20MAY10EC001_XS61 | 12715 | 汽机顺控启动第六十一步指令 |  | digital
N2DCS.20MAY10EC001_XV01 | 12716 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XV03 | 12717 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XV04 | 12718 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC001_XV07 | 12719 | Ovation Control Builder |  | digital
N2DCS.20MAY10EC009_XT01 | 12720 | 润滑油控制油系统正常运行 |  | digital
N2DCS.20MAY10FT910_FINISHED | 12721 | 暖机计时完成 |  | digital
N2DCS.20MAY10FT910_NST | 12722 | Ovation Control Builder |  | digital
N2DCS.20MAY10FT910_SOFAB | 12723 | Ovation Control Builder |  | digital
N2DCS.20MAY10FT910_ST | 12724 | Ovation Control Builder |  | digital
N2DCS.20MKA01CE903_OPC | 12725 | OPC动作至DCS |  | digital
N2DCS.20MKA01CE903_XH01 | 12726 | 发电机功率大于42.21MW |  | digital
N2DCS.20MKA01CE903_XH02 | 12727 | 发电机功率大于14.07MW |  | digital
N2DCS.20MKA01CE903_XH03 | 12728 | 发电机功率大于28.14MW |  | digital
N2DCS.20MKA01CE903_XH52 | 12729 | 发电机功率<98.49MW |  | digital
N2DCS.20MKW11EU001_ZV03 | 12730 | Ovation Control Builder |  | digital
N2DCS.20MKY01DE011A | 12731 | 同步转速允许 |  | digital
N2DCS.20MKY01DE011C | 12732 | 同步转速升 |  | digital
N2DCS.20MKY01DE011D | 12733 | 同步转速降 |  | digital
N2DCS.20MYA01CS901_ANFABR | 12734 | 启动终止 |  | digital
N2DCS.20MYA01CS901_FGNF11 | 12735 | 汽机转速在临界转速区:6~14HZ |  | digital
N2DCS.20MYA01CS901_FGNF21 | 12736 | 汽机转速在临界转速区:16~47.5HZ |  | digital
N2DCS.20MYA01CS901_NTASP | 12737 | 汽机转速不在临界转速 |  | digital
N2DCS.20MYA01CS901_NTGRKL | 12738 | 汽机转速加速度过小 |  | digital
N2DCS.20MYA01CS901_X16C | 12739 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH05 | 12740 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH11 | 12741 | OPC |  | digital
N2DCS.20MYA01CS901_XH15 | 12742 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH19 | 12743 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH21 | 12744 | 汽轮机转速>6.5Hz |  | digital
N2DCS.20MYA01CS901_XH25 | 12745 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH33 | 12746 | 汽轮机转速>33Hz |  | digital
N2DCS.20MYA01CS901_XH37 | 12747 | 汽轮机转速>47.5Hz |  | digital
N2DCS.20MYA01CS901_XH38 | 12748 | 汽机转速>NWART |  | digital
N2DCS.20MYA01CS901_XH54 | 12749 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH63 | 12750 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH71 | 12751 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH87 | 12752 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XT02 | 12753 | 汽轮机已并网 |  | digital
N2DCS.20MYA01CS901_XT03 | 12754 | 汽轮机未并网 |  | digital
N2DCS.20MYA01CS901_ZV23 | 12755 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_ZV71 | 12756 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_ZV83 | 12757 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH02 | 12758 | 汽轮机转速大于2950RPM |  | digital
N2DCS.20MYA01DG010_ANABWT | 12759 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG010_FGSWF | 12760 | 非转速设定跟踪 |  | digital
N2DCS.20MYA01DG010_INTPELIN | 12761 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG010_OSABGL | 12762 | 进汽设定值达到信号 |  | digital
N2DCS.20MYA01DG010_OSK | 12763 | 负荷设定跟踪 |  | digital
N2DCS.20MYA01DG010_OSKN | 12764 | 负荷设定不跟踪 |  | digital
N2DCS.20MYA01DG010_OSNF | 12765 | 进汽设定值跟踪 |  | digital
N2DCS.20MYA01DG010_OSXE | 12766 | 负荷远程控制ON |  | digital
N2DCS.20MYA01DG010_P10 | 12767 | 负荷远程控制投入 |  | digital
N2DCS.20MYA01DG010_SET | 12768 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG010_SPSWF | 12769 | 转速设定跟踪 |  | digital
N2DCS.20MYA01DG010_STPNS | 12770 | 转速设定值控制停止 |  | digital
N2DCS.20MYA01DG010_STPSWF | 12771 | 转速-负荷设定停止 |  | digital
N2DCS.20MYA01DG010_XH01 | 12772 | 外部负荷设定>98% |  | digital
N2DCS.20MYA01DG010_XT52 | 12773 | 负荷控制投入(协调方式） |  | digital
N2DCS.20MYA01DG011_OSGE | 12774 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_A | 12775 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_AHIGH | 12776 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_ALOW | 12777 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_ASTOP | 12778 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_DOWN | 12779 | TAB下降 |  | digital
N2DCS.20MYA01DG020_RSTCV | 12780 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_RSTESV | 12781 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_SDMAN | 12782 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_SE_EINL | 12783 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_STOP | 12784 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_TIME | 12785 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_TRIP | 12786 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_TRIPCV | 12787 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_TRIPESV | 12788 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_TRIPN | 12789 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_UP | 12790 | TAB上升 |  | digital
N2DCS.20MYA01DG020_XH01 | 12791 | TAB>99% |  | digital
N2DCS.20MYA01DG020_XH03 | 12792 | TAB>62% |  | digital
N2DCS.20MYA01DG020_XH05 | 12793 | TAB>12.5 |  | digital
N2DCS.20MYA01DG020_XH175 | 12794 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XH225 | 12795 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XH275 | 12796 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XH325 | 12797 | TAB>32.5 |  | digital
N2DCS.20MYA01DG020_XH375 | 12798 | TAB<37.5 |  | digital
N2DCS.20MYA01DG020_XH425 | 12799 | TAB>42.5 |  | digital
N2DCS.20MYA01DG020_XH475 | 12800 | TAB<47.5 |  | digital
N2DCS.20MYA01DG020_XH52 | 12801 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XH53 | 12802 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XH75 | 12803 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XT07 | 12804 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XT12 | 12805 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XT17 | 12806 | 主汽门油动机关闭电磁阀失电指令 |  | digital
N2DCS.20MYA01DG020_XT22 | 12807 | 主汽门油动机关闭电磁阀带电指令 |  | digital
N2DCS.20MYA01DG020_XT27 | 12808 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XT32 | 12809 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XT37 | 12810 | TAB主汽门开启电磁阀得电指令 |  | digital
N2DCS.20MYA01DG020_XT42 | 12811 | 高中低主汽门开启电磁阀失电指令 |  | digital
N2DCS.20MYA01DP010_FDSXA | 12812 | 高压压力手动设定投入 |  | digital
N2DCS.20MYA01DP010_FDSXE | 12813 | 高压压力自动设定投入 |  | digital
N2DCS.20MYA01DP011_GDE | 12814 | 限压模式 |  | digital
N2DCS.20MYA01DP011_GDER | 12815 | Ovation Control Builder |  | digital
N2DCS.20MYA01DP011_OSNF | 12816 | 进汽设定值跟踪 |  | digital
N2DCS.20MYA01DP011_VDE | 12817 | 初压模式 |  | digital
N2DCS.20MYA01DP020_HZSXA | 12818 | 中压压力手动设定投入 |  | digital
N2DCS.20MYA01DP020_HZSXE | 12819 | 中压压力自动设定投入 |  | digital
N2DCS.20MYA01DP030_ZDSXA | 12820 | 低压压力手动设定投入 |  | digital
N2DCS.20MYA01DP030_ZDSXE | 12821 | 低压压力自动设定投入 |  | digital
N2DCS.20MYA01DP050_XT01 | 12822 | Ovation Control Builder |  | digital
N2DCS.20MYA01DP090_HVDRA | 12823 | 高压缸压比控制退出 |  | digital
N2DCS.20MYA01DP090_HVDRE | 12824 | 高压缸压比控制投入 |  | digital
N2DCS.20MYA01DP090_S | 12825 | Ovation Control Builder |  | digital
N2DCS.20MYA01DP090_S20Q | 12826 | Ovation Control Builder |  | digital
N2DCS.20MYA01DS010_C12 | 12827 | 同步转速升/降(匹配电网频率) |  | digital
N2DCS.20MYA01DS010_C15 | 12828 | Ovation Control Builder |  | digital
N2DCS.20MYA01DS010_N60Q | 12829 | 转速不在临界转速区时熱应力故障 |  | digital
N2DCS.20MYA01DS010_N90Q | 12830 | Ovation Control Builder |  | digital
N2DCS.20MYA01DS010_NSABGL | 12831 | 转速设定值达到 |  | digital
N2DCS.20MYA01DS010_NSGPE | 12832 | 超速试验过程中 |  | digital
N2DCS.20MYA01DS010_NSKQ | 12833 | 转速设定跟踪 |  | digital
N2DCS.20MYA01DS010_NSKQN | 12834 | 转速设定不跟踪 |  | digital
N2DCS.20MYA01DS010_NSNF | 12835 | 转速设定跟踪 |  | digital
N2DCS.20MYA01DS010_OPC | 12836 | OPC试验过程中 |  | digital
N2DCS.20MYA01DS010_PSSE | 12837 | 超速测试 |  | digital
N2DCS.20MYA01DS010_PSSEFL | 12838 | Ovation Control Builder |  | digital
N2DCS.20MYA01DS010_RSSE | 12839 | Ovation Control Builder |  | digital
N2DCS.20MYA01DS010_RSSEFL | 12840 | Ovation Control Builder |  | digital
N2DCS.20MYA01DS010_SYHT | 12841 | 同步转速升 |  | digital
N2DCS.20MYA01DS010_SYTT | 12842 | 同步转速降 |  | digital
N2DCS.20MYA01DS010_XH03 | 12843 | Ovation Control Builder |  | digital
N2DCS.20MYA01DS010_XH05 | 12844 | Ovation Control Builder |  | digital
N2DCS.20MYA01DT050_HATRA | 12845 | 高排温度控制退出 |  | digital
N2DCS.20MYA01DT050_HATRE | 12846 | 高排温度控制投入 |  | digital
N2DCS.20MYA01DT050_S | 12847 | Ovation Control Builder |  | digital
N2DCS.20MYA01DT050_S20Q | 12848 | Ovation Control Builder |  | digital
N2DCS.20MYA01DU010_XT02 | 12849 | 负荷控制投入 |  | digital
N2DCS.20MYA01DU011_VWQN | 12850 | 热应力计算退出 |  | digital
N2DCS.20MYA01DU011_W60Q | 12851 | Ovation Control Builder |  | digital
N2DCS.20MYA01DU011_WTE | 12852 | 热应力计算投入 |  | digital
N2DCS.20MYA01DU012_SWFQ | 12853 | 确认设定值控制信号 |  | digital
N2DCS.20MYA01DU012_WTS | 12854 | 热应力故障 |  | digital
N2DCS.20MYA01DU050_FREQE | 12855 | Ovation Control Builder |  | digital
N2DCS.20MYA01DU050_LB | 12856 | 汽轮机已并网 |  | digital
N2DCS.20MYA01DU050_LBQ | 12857 | 汽轮机未并网 |  | digital
N2DCS.20MYA01DU050_LBX | 12858 | 汽机并网且无OPC动作 |  | digital
N2DCS.20MYA01DU050_XH01 | 12859 | 转速/负荷控制器输出值>0.5% |  | digital
N2DCS.20MYA01DU050_XH51 | 12860 | Ovation Control Builder |  | digital
N2DCS.20MYA01DU060_FDPRIE | 12861 | 高压压力控制激活 |  | digital
N2DCS.20MYA01DU060_HATRIE | 12862 | 高排温度控制器激活 |  | digital
N2DCS.20MYA01DU060_HVDRIE | 12863 | 高压压比控制器激活 |  | digital
N2DCS.20MYA01DU060_HZPRIE | 12864 | 再热压力控制器激活 |  | digital
N2DCS.20MYA01DU060_NORIE | 12865 | 转速/负荷控制器激活 |  | digital
N2DCS.20MYA01DU060_NTRIE | 12866 | 转速控制器激活 |  | digital
N2DCS.20MYA01DU060_ORIE | 12867 | 进汽控制器激活 |  | digital
N2DCS.20MYA01DU060_TAB50 | 12868 | Ovation Control Builder |  | digital
N2DCS.20MYA01DU060_TABG0 | 12869 | Ovation Control Builder |  | digital
N2DCS.20MYA01DU060_TABGNF | 12870 | TAB跟踪限定值 |  | digital
N2DCS.20MYA01DU060_TABIE | 12871 | TAB控制器激活 |  | digital
N2DCS.20MYA01DU060_XT01 | 12872 | 转速控制激活 |  | digital
N2DCS.20MYA01DU060_XT02 | 12873 | 负荷控制激活 |  | digital
N2DCS.20MYA01DU060_ZDPRIE | 12874 | 低压进汽压力控制器激活 |  | digital
N2DCS.20MYA01EZ400_XT01 | 12875 | 冷态启动保护 |  | digital
N2DCS.20NAA01FP101_XH01 | 12876 | 冷再抽汽减压阀前压力<0.1MPa |  | digital
N2DCS.20NAA01FP101_XK20 | 12877 | 冷再抽汽减压阀前压力测点全坏 |  | digital
N2DCS.20NAA01FP101_XM20 | 12878 | 冷再抽汽减压阀前压力测点3坏2 |  | digital
N2DCS.20NAA02FP101_XH01 | 12879 | Ovation Control Builder |  | digital
N2DCS.20NAA02FP101_XK20 | 12880 | 热再抽汽减压阀前压力测点全坏 |  | digital
N2DCS.20NAA02FP101_XM20 | 12881 | 热再抽汽减压阀前压力测点3坏2 |  | digital
N2DCS.20SIM01SW001_SIMON | 12882 | 混仿 |  | digital
N2DCS.20SIM01SW002_SIMLB | 12883 | 仿真并网 |  | digital
N2DCS.20SIM01SW002_SIMVLV | 12884 | Ovation Control Builder |  | digital
N2DCS.20SIM01SW002_SIMVP | 12885 | 纯仿 |  | digital
N2DCS.21MAN10AC101ZC2 | 12886 | 锅炉高旁阀关闭 |  | digital
N2DCS.21MAN20AC101ZC2 | 12887 | 锅炉中旁阀关闭 |  | digital
N2DCS.2_1_7_COIL_1_KSERVO_ALM | 12888 | Ovation Control Builder |  | digital
N2DCS.2_1_7_COIL_2_KSERVO_ALM | 12889 | Ovation Control Builder |  | digital
N2DCS.2_1_8_COIL_1_KSERVO_ALM | 12890 | Ovation Control Builder |  | digital
N2DCS.2_1_8_COIL_2_KSERVO_ALM | 12891 | Ovation Control Builder |  | digital
N2DCS.DCS_AUXOK | 12892 | Ovation Control Builder |  | digital
N2DCS.DCS_DRNWTR | 12893 | Ovation Control Builder |  | digital
N2DCS.DCS_GEN_SEAL_OIL_OK | 12894 | Ovation Control Builder |  | digital
N2DCS.DCS_GLANDSTEAMON | 12895 | Ovation Control Builder |  | digital
N2DCS.DCS_LIFTPUMPS_2OF3ON | 12896 | Ovation Control Builder |  | digital
N2DCS.DCS_LIFTPUMPS_ALLOFF | 12897 | Ovation Control Builder |  | digital
N2DCS.DEH_OPNDRN | 12898 | Ovation Control Builder |  | digital
N2DCS.DEH_PASSWORD_IS_SET | 12899 | Ovation Control Builder |  | digital
N2DCS.DNTGR | 12900 | Ovation Control Builder |  | digital
N2DCS.ENOPC | 12901 | Ovation Control Builder |  | digital
N2DCS.FGNF1 | 12902 | Ovation Control Builder |  | digital
N2DCS.FGNF2 | 12903 | Ovation Control Builder |  | digital
N2DCS.GV_ARE | 12904 | Ovation Control Builder |  | digital
N2DCS.GV_CAL | 12905 | Ovation Control Builder |  | digital
N2DCS.GV_CARD_CNTIGENCY | 12906 | Ovation Control Builder |  | digital
N2DCS.GV_COIL_1_OPEN | 12907 | Ovation Control Builder |  | digital
N2DCS.GV_COIL_1_SHORT | 12908 | Ovation Control Builder |  | digital
N2DCS.GV_COIL_2_OPEN | 12909 | Ovation Control Builder |  | digital
N2DCS.GV_COIL_2_SHORT | 12910 | Ovation Control Builder |  | digital
N2DCS.GV_COIL_3_OPEN | 12911 | Ovation Control Builder |  | digital
N2DCS.GV_COIL_3_SHORT | 12912 | Ovation Control Builder |  | digital
N2DCS.GV_CONTINGENCY | 12913 | Ovation Control Builder |  | digital
N2DCS.GV_FATAL_ERROR | 12914 | Ovation Control Builder |  | digital
N2DCS.GV_LOCAL | 12915 | Ovation Control Builder |  | digital
N2DCS.GV_REDUNDANT_LINK | 12916 | Ovation Control Builder |  | digital
N2DCS.IV_ARE | 12917 | Ovation Control Builder |  | digital
N2DCS.IV_CAL | 12918 | Ovation Control Builder |  | digital
N2DCS.IV_CARD_CNTIGENCY | 12919 | Ovation Control Builder |  | digital
N2DCS.IV_COIL_1_OPEN | 12920 | Ovation Control Builder |  | digital
N2DCS.IV_COIL_1_SHORT | 12921 | Ovation Control Builder |  | digital
N2DCS.IV_COIL_2_OPEN | 12922 | Ovation Control Builder |  | digital
N2DCS.IV_COIL_2_SHORT | 12923 | Ovation Control Builder |  | digital
N2DCS.IV_COIL_3_OPEN | 12924 | Ovation Control Builder |  | digital
N2DCS.IV_COIL_3_SHORT | 12925 | Ovation Control Builder |  | digital
N2DCS.IV_CONTINGENCY | 12926 | Ovation Control Builder |  | digital
N2DCS.IV_FATAL_ERROR | 12927 | Ovation Control Builder |  | digital
N2DCS.IV_LOCAL | 12928 | Ovation Control Builder |  | digital
N2DCS.IV_REDUNDANT_LINK | 12929 | Ovation Control Builder |  | digital
N2DCS.MANUALL_MAL11 | 12930 | Ovation Control Builder |  | digital
N2DCS.NT_MRE | 12931 | Ovation Control Builder |  | digital
N2DCS.NT_XALM | 12932 | Ovation Control Builder |  | digital
N2DCS.PEL_MRE | 12933 | Ovation Control Builder |  | digital
N2DCS.PEL_XALM | 12934 | Ovation Control Builder |  | digital
N2DCS.PFD11_MRE | 12935 | Ovation Control Builder |  | digital
N2DCS.PFD11_XALM | 12936 | Ovation Control Builder |  | digital
N2DCS.PZD11_MRE | 12937 | Ovation Control Builder |  | digital
N2DCS.PZD11_XALM | 12938 | Ovation Control Builder |  | digital
N2DCS.SHUTDOWNSGCON | 12939 | Ovation Control Builder |  | digital
N2DCS.STARTSGCON | 12940 | Ovation Control Builder |  | digital
N2DCS.STNT1 | 12941 | Ovation Control Builder |  | digital
N2DCS.STNT2 | 12942 | Ovation Control Builder |  | digital
N2DCS.STNT3 | 12943 | Ovation Control Builder |  | digital
N2DCS.STPEL1 | 12944 | Ovation Control Builder |  | digital
N2DCS.STPEL2 | 12945 | Ovation Control Builder |  | digital
N2DCS.STPEL3 | 12946 | Ovation Control Builder |  | digital
N2DCS.STPFD1 | 12947 | Ovation Control Builder |  | digital
N2DCS.STPFD2 | 12948 | Ovation Control Builder |  | digital
N2DCS.STPFD3 | 12949 | Ovation Control Builder |  | digital
N2DCS.STPHZ1 | 12950 | Ovation Control Builder |  | digital
N2DCS.STPHZ2 | 12951 | Ovation Control Builder |  | digital
N2DCS.STPHZ3 | 12952 | Ovation Control Builder |  | digital
N2DCS.STPZD1 | 12953 | Ovation Control Builder |  | digital
N2DCS.STPZD2 | 12954 | Ovation Control Builder |  | digital
N2DCS.STPZD3 | 12955 | Ovation Control Builder |  | digital
N2DCS.VGBAFALM | 12956 | Ovation Control Builder |  | digital
N2DCS.VGBFDALM | 12957 | Ovation Control Builder |  | digital
N2DCS.VGBZDALM | 12958 | Ovation Control Builder |  | digital
N2DCS.VGFDSALM | 12959 | Ovation Control Builder |  | digital
N2DCS.VGHZSALM | 12960 | Ovation Control Builder |  | digital
N2DCS.VGNSALM | 12961 | Ovation Control Builder |  | digital
N2DCS.VGOSALM | 12962 | Ovation Control Builder |  | digital
N2DCS.VGOSGALM | 12963 | Ovation Control Builder |  | digital
N2DCS.VGTABALM | 12964 | Ovation Control Builder |  | digital
N2DCS.VGZDSALM | 12965 | Ovation Control Builder |  | digital
N2DCS.W150Q1 | 12966 | Ovation Control Builder |  | digital
N2DCS.W160Q1 | 12967 | Ovation Control Builder |  | digital
N2DCS.1_1_7_COIL_1_KSERVO_ALM | 12968 | Ovation Control Builder |  | digital
N2DCS.1_1_7_COIL_2_KSERVO_ALM | 12969 | Ovation Control Builder |  | digital
N2DCS.20MYA01CS901_XH53 | 12970 | Ovation Control Builder |  | digital
N2DCS.20MYA01DG020_XH40 | 12971 | TAB>40 |  | digital
N2DCS.20CBA00FU003_DEH | 12972 | 开高压疏水阀（10% LOAD关） |  | digital
N2DCS.20CBA00FU004_DEH | 12973 | 开中压疏水阀（20%LOAD关）24VDC |  | digital
N2DCS.20LBA20CT007_XH01 | 12974 | Ovation Control Builder |  | digital
N2DCS.20LBA20CT007_XH03 | 12975 | 主蒸汽温度过高 |  | digital
N2DCS.20LBA20CT007_XH04 | 12976 | 高压主汽门前蒸汽温度>350℃ |  | digital
N2DCS.20LBA20CT007_XH10 | 12977 | Ovation Control Builder |  | digital
N2DCS.20LBA20CT007_XM20 | 12978 | 高压主汽门前蒸汽温度测点全坏 |  | digital
N2DCS.20LBA20EZ007_XK96 | 12979 | Ovation Control Builder |  | digital
N2DCS.20LBA90CT001_XM20 | 12980 | 低压主汽门前蒸汽温度坏点 |  | digital
N2DCS.20LBB50CT007_XH01 | 12981 | Ovation Control Builder |  | digital
N2DCS.20LBB50CT007_XH03 | 12982 | 再热蒸汽温度过高 |  | digital
N2DCS.20LBB50CT007_XH07 | 12983 | 中压主汽门前蒸汽温度>330℃ |  | digital
N2DCS.20LBB50CT007_XM20 | 12984 | 中压主汽门前蒸汽温度测点全坏 |  | digital
N2DCS.20LBB50EZ007_XK96 | 12985 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP001_REL1 | 12986 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP001_REL2 | 12987 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP001_XK20 | 12988 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP001_XK93 | 12989 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP001_XK94 | 12990 | 高排过热度＜20K |  | digital
N2DCS.20LBC40FP001_XK96 | 12991 | 高排过热度＜10K |  | digital
N2DCS.20LBC40FP101_REL1 | 12992 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101_XK20 | 12993 | Ovation Control Builder |  | digital
N2DCS.20LBC41AA051A | 12994 | 高排通风阀电磁阀1 |  | digital
N2DCS.20LBC41AA051A_A_OFF | 12995 | Ovation Control Builder |  | digital
N2DCS.20LBC41AA051A_A_ON | 12996 | Ovation Control Builder |  | digital
N2DCS.20LBC41AA051B | 12997 | 高排通风阀电磁阀2 |  | digital
N2DCS.20MAA11CL011 | 12998 | 高压主汽门油动机油盘液位 |  | digital
N2DCS.20MAA11CT121A_XM20 | 12999 | Ovation Control Builder |  | digital
N2DCS.20MAA11CT122A_XM20 | 13000 | Ovation Control Builder |  | digital
N2DCS.20MAA12CL011 | 13001 | 高压调门油动机油盘液位 |  | digital
N2DCS.20MAA12CT121A_XM20 | 13002 | Ovation Control Builder |  | digital
N2DCS.20MAA12CT122A_XH52 | 13003 | 高压调节汽门中壁温度A(50%)<150 |  | digital
N2DCS.20MAA12CT122A_XM20 | 13004 | 高压调门中壁温度A（50%）坏点 |  | digital
N2DCS.20MAA12CT122A_XH54 | 13005 | Ovation Control Builder |  | digital
N2DCS.20MAA50CT131A_XM20 | 13006 | 高压缸内壁温度A（100%）坏点 |  | digital
N2DCS.20MAA50CT132A_XM20 | 13007 | 高压缸内壁温度A（50%）坏点 |  | digital
N2DCS.20MAA50CT141A_XM20 | 13008 | 高压缸外壁温（50%）坏点 |  | digital
N2DCS.20MAA50CT142A_XM20 | 13009 | 高压缸中壁温（50%）坏点 |  | digital
N2DCS.20MAA50CT143A_XM20 | 13010 | 高压缸内壁温（50%）坏点 |  | digital
N2DCS.20MAA50FT004A_DL12 | 13011 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT004A_DL13 | 13012 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT004A_DL23 | 13013 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT004A_XK20 | 13014 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT004A_XK93 | 13015 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_S/HTG+5 | 13016 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_S/HTG_20_A | 13017 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_S/HTG_20_B | 13018 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_S/HTG_5 | 13019 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_TEMP_OK | 13020 | 高压缸壁温质量无坏点 |  | digital
N2DCS.20MAA50FT051_TEMPOK | 13021 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_XH02 | 13022 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_XV01 | 13023 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_XV02 | 13024 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_XV03 | 13025 | 高压缸壁温条件满足 |  | digital
N2DCS.20MAA50FT051_XV06 | 13026 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_XV32 | 13027 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_XV51 | 13028 | 高压缸上中壁温条件满足 |  | digital
N2DCS.20MAA50FT051_XV52 | 13029 | 高压缸下中壁温条件满足 |  | digital
N2DCS.20MAA50FT051_XV54 | 13030 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV11 | 13031 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV12 | 13032 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV13 | 13033 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV21 | 13034 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV22 | 13035 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV23 | 13036 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV31 | 13037 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV32 | 13038 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV33 | 13039 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV41 | 13040 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV42 | 13041 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV43 | 13042 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT051_ZV53 | 13043 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT151_CT05_OK | 13044 | Ovation Control Builder |  | digital
N2DCS.20MAA50FT151_XM23 | 13045 | Ovation Control Builder |  | digital
N2DCS.20MAB11CL011 | 13046 | 中压主汽门油动机油盘液位 |  | digital
N2DCS.20MAB12CL011 | 13047 | 中压调门油动机油盘液位 |  | digital
N2DCS.20MAB50FT011A_DL12 | 13048 | Ovation Control Builder |  | digital
N2DCS.20MAB50FT011A_DL13 | 13049 | Ovation Control Builder |  | digital
N2DCS.20MAB50FT011A_DL23 | 13050 | Ovation Control Builder |  | digital
N2DCS.20MAB50FT011A_XK20 | 13051 | 中压内缸进汽口壁温无质量坏点 |  | digital
N2DCS.20MAB50FT011A_XK93 | 13052 | Ovation Control Builder |  | digital
N2DCS.20MAB50FT021_REL1 | 13053 | Ovation Control Builder |  | digital
N2DCS.20MAB50FT021_REL2 | 13054 | Ovation Control Builder |  | digital
N2DCS.20MAB50FT021_XK20 | 13055 | Ovation Control Builder |  | digital
N2DCS.20MAB50FT021_XK94 | 13056 | 中排过热度＜20K |  | digital
N2DCS.20MAB50FT021_XK96 | 13057 | 中排过热度＜10K |  | digital
N2DCS.20MAC01AA001A | 13058 | 低压缸喷水电磁阀1 |  | digital
N2DCS.20MAC01AA001A_ZV01 | 13059 | Ovation Control Builder |  | digital
N2DCS.20MAC01AA001A_ZV02 | 13060 | Ovation Control Builder |  | digital
N2DCS.20MAC01AA001A_ZV03 | 13061 | Ovation Control Builder |  | digital
N2DCS.20MAC01AA001A_ZV04 | 13062 | Ovation Control Builder |  | digital
N2DCS.20MAC01AA002A | 13063 | 低压缸喷水电磁阀2 |  | digital
N2DCS.20MAC10CT181A_XH01 | 13064 | Ovation Control Builder |  | digital
N2DCS.20MAC10CT181A_XH52 | 13065 | Ovation Control Builder |  | digital
N2DCS.20MAC10CT181A_XM20 | 13066 | Ovation Control Builder |  | digital
N2DCS.20MAC10CT182A_XH01 | 13067 | Ovation Control Builder |  | digital
N2DCS.20MAC10CT182A_XH52 | 13068 | Ovation Control Builder |  | digital
N2DCS.20MAC10CT182A_XM20 | 13069 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY041_XM71 | 13070 | #1径向轴承轴振通道X正常 |  | digital
N2DCS.20MAD11CY042_XM71 | 13071 | #1径向轴承轴振通道Y OK |  | digital
N2DCS.20MAD11CY141_MAX1 | 13072 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY141_MAX2 | 13073 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY141_XH01 | 13074 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY141_XH03 | 13075 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY141_XM71 | 13076 | #1径向轴承轴振通道X正常 |  | digital
N2DCS.20MAD11CY141_XM72 | 13077 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY141_XV20 | 13078 | #1轴瓦轴振X通道故障 |  | digital
N2DCS.20MAD11CY142_MAX1 | 13079 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY142_MAX2 | 13080 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY142_XH01 | 13081 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY142_XH03 | 13082 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY142_XM71 | 13083 | #1径向轴承轴振通道Y OK |  | digital
N2DCS.20MAD11CY142_XM72 | 13084 | Ovation Control Builder |  | digital
N2DCS.20MAD11CY142_XV20 | 13085 | #1轴瓦轴振Y通道故障 |  | digital
N2DCS.20MAD11EZ141_XK93 | 13086 | #1轴承转子振动测量存在故障 |  | digital
N2DCS.20MAD11EZ141_XK94 | 13087 | #1轴承转子振动＞83um |  | digital
N2DCS.20MAD11EZ141_XK96 | 13088 | #1轴承转子振动＞130um |  | digital
N2DCS.20MAD12CY041_XM71 | 13089 | #2径向轴承轴振通道X正常 |  | digital
N2DCS.20MAD12CY042_XM71 | 13090 | #2径向轴承轴振通道Y OK |  | digital
N2DCS.20MAD12CY141_MAX1 | 13091 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY141_MAX2 | 13092 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY141_XH01 | 13093 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY141_XH03 | 13094 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY141_XM71 | 13095 | #2径向轴承轴振通道X正常 |  | digital
N2DCS.20MAD12CY141_XM72 | 13096 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY141_XV20 | 13097 | #2轴瓦轴振X通道故障 |  | digital
N2DCS.20MAD12CY142_MAX1 | 13098 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY142_MAX2 | 13099 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY142_XH01 | 13100 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY142_XH03 | 13101 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY142_XM71 | 13102 | #2径向轴承轴振通道Y OK |  | digital
N2DCS.20MAD12CY142_XM72 | 13103 | Ovation Control Builder |  | digital
N2DCS.20MAD12CY142_XV20 | 13104 | #2轴瓦Y向轴振通道故障 |  | digital
N2DCS.20MAD12CY145_XM71 | 13105 | 膨胀通道OK |  | digital
N2DCS.20MAD12EZ141_XK93 | 13106 | #2轴承转子振动测量存在故障 |  | digital
N2DCS.20MAD12EZ141_XK94 | 13107 | #2轴承转子振动＞83um |  | digital
N2DCS.20MAD12EZ141_XK96 | 13108 | #2轴承转子振动＞130um |  | digital
N2DCS.20MAD13CY041_XM71 | 13109 | #3径向轴承轴振通道X正常 |  | digital
N2DCS.20MAD13CY042_XM71 | 13110 | #3径向轴承轴振通道Y OK |  | digital
N2DCS.20MAD13CY141_MAX1 | 13111 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY141_MAX2 | 13112 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY141_XH01 | 13113 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY141_XH03 | 13114 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY141_XM71 | 13115 | #3径向轴承轴振通道X正常 |  | digital
N2DCS.20MAD13CY141_XM72 | 13116 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY141_XV20 | 13117 | #3轴瓦轴振X通道故障 |  | digital
N2DCS.20MAD13CY142_MAX1 | 13118 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY142_MAX2 | 13119 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY142_XH01 | 13120 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY142_XH03 | 13121 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY142_XM71 | 13122 | #3径向轴承轴振通道Y OK |  | digital
N2DCS.20MAD13CY142_XM72 | 13123 | Ovation Control Builder |  | digital
N2DCS.20MAD13CY142_XV20 | 13124 | #3轴瓦轴振Y通道故障 |  | digital
N2DCS.20MAD13EZ141_XK93 | 13125 | #3轴承转子振动测量存在故障 |  | digital
N2DCS.20MAD13EZ141_XK94 | 13126 | #3轴承转子振动＞83um |  | digital
N2DCS.20MAD13EZ141_XK96 | 13127 | #3轴承转子振动＞130um |  | digital
N2DCS.20MAV51AA012VO | 13128 | 盘车三通阀（220VAC） |  | digital
N2DCS.20MAY01EP144_FAST | 13129 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP145_FAST | 13130 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_CV | 13131 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_ESV | 13132 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_HPC | 13133 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_HPS | 13134 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_IPS | 13135 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_RSTF | 13136 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_RSTN | 13137 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_RSTS | 13138 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_XH04 | 13139 | 上升温度裕度>20 |  | digital
N2DCS.20MAY01EP150_XH06 | 13140 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_XH09 | 13141 | 高主/高调上升温度裕度大于2.5 |  | digital
N2DCS.20MAY01EP150_XH52 | 13142 | 最小上升温度裕度<0 |  | digital
N2DCS.20MAY01EP150_XH54 | 13143 | 最小上升温度裕度<15 |  | digital
N2DCS.20MAY01EP150_XH55 | 13144 | 最小下降温度裕度<2 |  | digital
N2DCS.20MAY01EP150_XH57 | 13145 | 最小下降温度裕度<0 |  | digital
N2DCS.20MAY01EP150_XM01 | 13146 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_XT01 | 13147 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP150_XT21 | 13148 | Margin Mode Fast |  | digital
N2DCS.20MAY01EP150_XT22 | 13149 | Margin Mode Normal |  | digital
N2DCS.20MAY01EP150_XT23 | 13150 | Margin Mode Slow |  | digital
N2DCS.20MAY01EP151_XT01 | 13151 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP151_XT06 | 13152 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP151_XT07 | 13153 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP151_XT16 | 13154 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP151_XT17 | 13155 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP151_XT24 | 13156 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP151_XT25 | 13157 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP151_XTOR | 13158 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP152_XT01 | 13159 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP152_XT06 | 13160 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP152_XT07 | 13161 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP152_XT16 | 13162 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP152_XT17 | 13163 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP152_XT24 | 13164 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP152_XT25 | 13165 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP153_XT01 | 13166 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP153_XT06 | 13167 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP153_XT07 | 13168 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP153_XT16 | 13169 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP153_XT17 | 13170 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP153_XT24 | 13171 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP153_XT25 | 13172 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_DPSIM | 13173 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_STSIM | 13174 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_TGFH | 13175 | 高压转子温度3>610℃ |  | digital
N2DCS.20MAY01EP154_TGFL | 13176 | 高压转子温度3<10℃ |  | digital
N2DCS.20MAY01EP154_TSFH | 13177 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_TSFL | 13178 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_TSFTH | 13179 | 高压转子温度2>610℃ |  | digital
N2DCS.20MAY01EP154_TSFTL | 13180 | 高压转子温度2<10℃ |  | digital
N2DCS.20MAY01EP154_XH01 | 13181 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XH05 | 13182 | 高压转子温度3大于200℃ |  | digital
N2DCS.20MAY01EP154_XH07 | 13183 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XH08 | 13184 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XH53 | 13185 | 高压转子温度3<400℃ |  | digital
N2DCS.20MAY01EP154_XK20F | 13186 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XT01 | 13187 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XT02 | 13188 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XT06 | 13189 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XT07 | 13190 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XT16 | 13191 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XT17 | 13192 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XT24 | 13193 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP154_XT25 | 13194 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_DPSIM | 13195 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_STSIM | 13196 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_TGFH | 13197 | 高压转子温度3>610℃ |  | digital
N2DCS.20MAY01EP155_TGFL | 13198 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_TSFH | 13199 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_TSFL | 13200 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_TSFTH | 13201 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_TSFTL | 13202 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XH02 | 13203 | 中压转子温度2>20℃ |  | digital
N2DCS.20MAY01EP155_XH03 | 13204 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XH05 | 13205 | 中压转子温度3>200℃ |  | digital
N2DCS.20MAY01EP155_XH11 | 13206 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XH57 | 13207 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XK20F | 13208 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XT01 | 13209 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XT02 | 13210 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XT06 | 13211 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XT07 | 13212 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XT16 | 13213 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XT17 | 13214 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XT24 | 13215 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP155_XT25 | 13216 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP181_MINLO | 13217 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP181_S | 13218 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP181_STOP | 13219 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP182_MINLO | 13220 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP182_S | 13221 | Ovation Control Builder |  | digital
N2DCS.20MAY01EP182_STOP | 13222 | Ovation Control Builder |  | digital
N2DCS.20MAY01EZ011_XK46 | 13223 | 汽机遮断系统已遮断1 |  | digital
N2DCS.20MAY01EZ011_XK47 | 13224 | 汽机遮断系统已遮断2 |  | digital
N2DCS.20MAY10FT000_XM20 | 13225 | X准则计算故障 |  | digital
N2DCS.20MAY10FT001_XH02 | 13226 | 满足热应力准则X1 |  | digital
N2DCS.20MAY10FT001_XM20 | 13227 | 热应力准则X1故障 |  | digital
N2DCS.20MAY10FT002_XH51 | 13228 | 满足热应力准则X2 |  | digital
N2DCS.20MAY10FT002_XM20 | 13229 | 热应力准则X2故障 |  | digital
N2DCS.20MAY10FT004_XH02 | 13230 | 满足热应力准则X4 |  | digital
N2DCS.20MAY10FT004_XH52 | 13231 | Ovation Control Builder |  | digital
N2DCS.20MAY10FT004_XM20 | 13232 | 热应力准则X4故障 |  | digital
N2DCS.20MAY10FT005_XH02 | 13233 | 满足热应力准则X5 |  | digital
N2DCS.20MAY10FT005_XM20 | 13234 | 热应力准则X5故障 |  | digital
N2DCS.20MAY10FT006_XH02 | 13235 | 满足热应力准则X6 |  | digital
N2DCS.20MAY10FT006_XM20 | 13236 | 热应力准则X6故障 |  | digital
N2DCS.20MAY10FT007A_XH51 | 13237 | 满足热应力准则X7_A |  | digital
N2DCS.20MAY10FT007A_XM20 | 13238 | 热应力准则X7_A故障 |  | digital
N2DCS.20MAY10FT007B_XH51 | 13239 | 满足热应力准则X7_B |  | digital
N2DCS.20MAY10FT007B_XM20 | 13240 | 热应力准则X7_B故障 |  | digital
N2DCS.20MAY10FT008_XH51 | 13241 | 满足热应力准则X8 |  | digital
N2DCS.20MAY10FT008_XM20 | 13242 | 热应力准则X8故障 |  | digital
N2DCS.20MAY10FT010_XM20 | 13243 | Z准则计算故障 |  | digital
N2DCS.20MAY10FT011_XH02 | 13244 | 满足热应力准则Z1-CRIT |  | digital
N2DCS.20MAY10FT011_XM20 | 13245 | Z1准则计算故障 |  | digital
N2DCS.20MAY10FT012_XH02 | 13246 | 满足热应力准则Z2-CRIT |  | digital
N2DCS.20MAY10FT012_XM20 | 13247 | Z2准则计算故障 |  | digital
N2DCS.20MAY10FT013_XH02 | 13248 | 满足热应力准则Z3-CRIT |  | digital
N2DCS.20MAY10FT013_XH52 | 13249 | 高压主汽门前蒸汽过热度<15 |  | digital
N2DCS.20MAY10FT013_XM20 | 13250 | Z3准则计算故障 |  | digital
N2DCS.20MAY10FT014_XH02 | 13251 | 满足热应力准则Z4-CRIT |  | digital
N2DCS.20MAY10FT014_XH04 | 13252 | 中压主汽门前蒸汽过热度>10℃ |  | digital
N2DCS.20MAY10FT014_XH52 | 13253 | 中压主汽门前蒸汽过热度<20℃ |  | digital
N2DCS.20MAY10FT014_XM20 | 13254 | Z4准则计算故障 |  | digital
N2DCS.20MAY10FT015_XH02 | 13255 | 满足热应力准则Z5-CRIT |  | digital
N2DCS.20MAY10FT015_XM20 | 13256 | Z5准则计算故障 |  | digital
N2DCS.20MKD11CY041_XM71 | 13257 | #1汽轮发电机轴承轴振通道X正常 |  | digital
N2DCS.20MKD11CY042_XM71 | 13258 | #1汽轮发电机轴承轴振通道Y正常 |  | digital
N2DCS.20MKD11CY141_MAX1 | 13259 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY141_MAX2 | 13260 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY141_XH01 | 13261 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY141_XH03 | 13262 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY141_XM71 | 13263 | #1汽轮发电机轴承轴振通道X正常 |  | digital
N2DCS.20MKD11CY141_XM72 | 13264 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY141_XV20 | 13265 | #4轴瓦轴振X通道故障 |  | digital
N2DCS.20MKD11CY142_MAX1 | 13266 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY142_MAX2 | 13267 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY142_XH01 | 13268 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY142_XH03 | 13269 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY142_XM71 | 13270 | #1汽轮发电机轴承轴振通道Y正常 |  | digital
N2DCS.20MKD11CY142_XM72 | 13271 | Ovation Control Builder |  | digital
N2DCS.20MKD11CY142_XV20 | 13272 | #4轴瓦轴振Y通道故障 |  | digital
N2DCS.20MKD11EZ141_XK93 | 13273 | 发电机后轴承转子振动测量故障 |  | digital
N2DCS.20MKD11EZ141_XK94 | 13274 | 发电机后轴承转子振动＞83um |  | digital
N2DCS.20MKD11EZ141_XK96 | 13275 | 发电机后轴承转子振动>130μm |  | digital
N2DCS.20MKD12CY041_XM71 | 13276 | #2汽轮发电机轴承轴振通道X正常 |  | digital
N2DCS.20MKD12CY042_XM71 | 13277 | #2汽轮发电机轴承轴振通道Y正常 |  | digital
N2DCS.20MKD12CY141_MAX1 | 13278 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY141_MAX2 | 13279 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY141_XH01 | 13280 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY141_XH03 | 13281 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY141_XM71 | 13282 | #2汽轮发电机轴承轴振通道X正常 |  | digital
N2DCS.20MKD12CY141_XM72 | 13283 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY141_XV20 | 13284 | #5轴瓦轴振X通道故障 |  | digital
N2DCS.20MKD12CY142_MAX1 | 13285 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY142_MAX2 | 13286 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY142_XH01 | 13287 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY142_XH03 | 13288 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY142_XM71 | 13289 | #2汽轮发电机轴承轴振通道Y正常 |  | digital
N2DCS.20MKD12CY142_XM72 | 13290 | Ovation Control Builder |  | digital
N2DCS.20MKD12CY142_XV20 | 13291 | #5轴瓦轴振Y通道故障 |  | digital
N2DCS.20MKD12EZ141_XK93 | 13292 | 励磁机后轴承转子振动测量故障 |  | digital
N2DCS.20MKD12EZ141_XK94 | 13293 | 励磁机后轴承转子振动＞83um |  | digital
N2DCS.20MKD12EZ141_XK96 | 13294 | 励磁机后轴承转子振动>130μm |  | digital
N2DCS.21CJA00EA001_XS53 | 13295 | DCS启动DEH启动顺控 |  | digital
N2DCS.21CJA00EA001_XS54 | 13296 | DCS启动DEH停机顺控 |  | digital
N2DCS.PK1_NORM | 13297 | Ovation Control Builder |  | digital
N2DCS.PK2_SLOW | 13298 | Ovation Control Builder |  | digital
N2DCS.PK3_FAST | 13299 | Ovation Control Builder |  | digital
N2DCS.20LBA10AA402_LP | 13300 | #3机高压主汽母管疏水气动门1 |  | digital
N2DCS.20LBA10AA404_LP | 13301 | #3机高压主汽母管疏水气动门2 |  | digital
N2DCS.20LBA20AA402_LP | 13302 | #3机低压主汽门前疏水气动门 |  | digital
N2DCS.20LBA20AA406_LP | 13303 | #3机低压主汽母管疏水气动门 |  | digital
N2DCS.20LBA20CP_LP | 13304 | #3机低压蒸汽母管压力 |  | digital
N2DCS.20LBB10AA402_LP | 13305 | #3机高温再热蒸汽母管疏水气动门 |  | digital
N2DCS.20LBB10AA404_LP | 13306 | #3机中旁阀前疏水气动门 |  | digital
N2DCS.20LBB10CP_LP | 13307 | #3机高温再热蒸汽压力 |  | digital
N2DCS.20LBC10AA001_LP | 13308 | #3机高排逆止门 |  | digital
N2DCS.20LBC10AA404_LP | 13309 | #3机高排逆止门后疏水气动门 |  | digital
N2DCS.20LBC10AA406_LP | 13310 | #3机冷再疏水气动门 |  | digital
N2DCS.20LBH10AA101_LP | 13311 | 高排通风门 |  | int32
N2DCS.20LBH10AA402_LP | 13312 | #3机高排通风阀前疏水气动门 |  | digital
N2DCS.20MAL11AA051_LP | 13313 | 高压主汽门后疏水门 |  | int32
N2DCS.20MAL23AA051_LP | 13314 | 中压主汽门上疏水门 |  | int32
N2DCS.20MAL26AA051_LP | 13315 | 中压主汽门后疏水门 |  | int32
N2DCS.20MAL65AA051_LP | 13316 | #3机高排逆止门前疏水气动门 |  | digital
N2DCS.20MAN10AA001_LP | 13317 | #3机高旁减温水气动隔离门 |  | digital
N2DCS.20MAN10AA101_LP | 13318 | 高压旁路门 |  | int32
N2DCS.20MAN10AA101_MODE | 13319 | #3机高旁阀 |  | digital
N2DCS.20MAN10AA102_LP | 13320 | 高压旁路减温水调节门 |  | int32
N2DCS.20MAN10AA102_MODE | 13321 | #3机高旁减温水调节阀 |  | digital
N2DCS.20MAN10AA102MODE | 13322 | Ovation Control Builder |  | int32
N2DCS.20MAN10CP_LP | 13323 | #3机高旁阀后蒸汽压力 |  | digital
N2DCS.20MAN10CT_LP | 13324 | #3机高旁阀后蒸汽温度 |  | digital
N2DCS.20MAN10GH001R1_LP | 13325 | #3机高压旁路油站#1油泵 |  | digital
N2DCS.20MAN10GH001R2_LP | 13326 | #3机高压旁路油站#2油泵 |  | digital
N2DCS.20MAN20AA101_LP | 13327 | 中压旁路门 |  | int32
N2DCS.20MAN20AA101_MODE | 13328 | #3机中旁阀 |  | digital
N2DCS.20MAN20CP_LP | 13329 | #3机中旁阀后蒸汽压力 |  | digital
N2DCS.20MAN20CT_LP | 13330 | #3机中旁阀后蒸汽温度 |  | digital
N2DCS.20MAN20GH001R1_LP | 13331 | #3机中低压旁路油站#1油泵 |  | digital
N2DCS.20MAN20GH001R2_LP | 13332 | #3机中低压旁路油站#2油泵 |  | digital
N2DCS.20MAP10AA101_LP | 13333 | 低压旁路门 |  | int32
N2DCS.20MAP10AA101_MODE | 13334 | #3机低旁阀 |  | digital
N2DCS.20MAP10AA404_LP | 13335 | #3机低旁阀前疏水气动门 |  | digital
N2DCS.20MAP10CP_LP | 13336 | #3机低旁阀后蒸汽压力 |  | digital
N2DCS.20MAP10CT_LP | 13337 | #3机低旁阀后蒸汽温度 |  | digital
N2DCS.HOILSTNOILP_BYLP | 13338 | #3机高压旁路油站油泵 |  | digital
N2DCS.ILOILSTNOILP_BYLP | 13339 | #3机中低压旁路油站油泵 |  | digital
N2DCS.TURBDRNHPCP_LP1 | 13340 | #3机高压疏水阀组1关闭状态 |  | digital
N2DCS.TURBDRNHPCP_LP2 | 13341 | #3机高压疏水阀组2关闭状态 |  | digital
N2DCS.TURBDRNHPOP_LP1 | 13342 | #3机高压疏水阀组1打开状态 |  | digital
N2DCS.TURBDRNHPOP_LP2 | 13343 | #3机高压疏水阀组2打开状态 |  | digital
N2DCS.TURBDRNIPCP_LP | 13344 | #3机中压疏水阀组关闭状态 |  | digital
N2DCS.TURBDRNIPOP_LP | 13345 | #3机中压疏水阀组打开状态 |  | digital
N2DCS.TURBDRNLPCP_LP | 13346 | #3机低压疏水阀组关闭状态 |  | digital
N2DCS.TURBDRNLPOP_LP | 13347 | #3机低压疏水阀组打开状态 |  | digital
N2DCS.GTLOADMODE1 | 13348 | #4机负荷设定方式 |  | digital
N2DCS.LOADGOHOLD1 | 13349 | 机组总负荷增闭锁信号 |  | digital
N2DCS.LOADSPMODE1 | 13350 | 机组总负荷设定方式 |  | digital
N2DCS.RB_TRIP | 13351 | #4机RB动作 |  | digital
N2DCS.STTRIPLP | 13352 | #3机跳闸信号 |  | digital
N2DCS.STTRIPTAGLP | 13353 | 锅炉联跳汽机保护解除信号 |  | digital
N2DCS.TEST_MODE | 13354 | Ovation Control Builder |  | int32
N2DCS.20LBD20AA001_LP | 13355 | #3机冷再供热电动门 |  | digital
N2DCS.20LBD20AA002_LP | 13356 | #3机冷再供热逆止门后电动门 |  | digital
N2DCS.20LBD20AA402_LP | 13357 | #3机冷再供热母管气动疏水门 |  | digital
N2DCS.20LBD20AC001MODE | 13358 | #3机冷再供热减温减压器 |  | digital
N2DCS.20LBD40AA001_LP | 13359 | #3机热再供热电动门 |  | digital
N2DCS.20LBD40AA002_LP | 13360 | #3机热再供热逆止门后电动门 |  | digital
N2DCS.20LBD40AA402_LP | 13361 | #3机热再供热母管气动疏水门 |  | digital
N2DCS.20LBD40AC001MODE | 13362 | #3机热再供热减温减压器 |  | digital
N2DCS.20LBD60AA001_LP | 13363 | #3机供热母管电动门 |  | digital
N2DCS.20LBD80AA001_LP | 13364 | #3机冷再抽汽至预留中压电动门 |  | digital
N2DCS.20LBD80AA402_LP | 13365 | 冷再抽汽至预留中压管道疏水门 |  | digital
N2DCS.20LBG11AA007_LP | 13366 | #3机高排至辅汽母管供汽电动门 |  | digital
N2DCS.20LBG11AC001MODE | 13367 | 高排至辅汽母管供汽减温减压器 |  | digital
N2DCS.20LBG21AA001_LP | 13368 | 辅汽母管至#3机轴封供汽电动门 |  | digital
N2DCS.20LBG22AA001_LP | 13369 | 辅汽至#3机蒸汽喷射装置电动门 |  | digital
N2DCS.20LCE11AA001_LP | 13370 | #3机凝结水至辅汽减温水电动门 |  | digital
N2DCS.20LCE11AA101MODE | 13371 | #3机凝结水至辅汽减温水电动调阀 |  | digital
N2DCS.20LCE12AA001_LP | 13372 | #3机凝结水至低旁减温水气动门 |  | digital
N2DCS.20LCE12AA101_LP | 13373 | 低压旁路喷水调节门 |  | int32
N2DCS.20LCE12AA101_MODE | 13374 | #3机凝结水至低旁减温水调节阀 |  | digital
N2DCS.20LCE12AA101MODE | 13375 | Ovation Control Builder |  | int32
N2DCS.20LCE13AA001_LP | 13376 | #3机凝结水至热再减温水电动门 |  | digital
N2DCS.20LCE13AA101MODE | 13377 | #3机凝结水至热再减温水电动调阀 |  | digital
N2DCS.20LCE15AA001_LP | 13378 | #3机凝结水至中旁减温水气动门 |  | digital
N2DCS.20LCE15AA101_LP | 13379 | 中压旁路喷水调节门 |  | int32
N2DCS.20LCE15AA101_MODE | 13380 | #3机凝结水至中旁减温水调节阀 |  | digital
N2DCS.20LCE15AA101MODE | 13381 | Ovation Control Builder |  | int32
N2DCS.20LCE17AA001_LP | 13382 | #3机凝结水至冷再减温水电动门 |  | digital
N2DCS.20LCE17AA101MODE | 13383 | #3机凝结水至冷再减温水电动调阀 |  | digital
N2DCS.20LCE18AA052_LP | 13384 | 轴封减温水电磁阀 |  | int32
N2DCS.20LCE18AA152MODE | 13385 | #3机凝结水至轴封减温水气动调阀 |  | digital
N2DCS.20LCE19AA101_LP | 13386 | 凝结水至凝汽器水幕喷水气动阀 |  | digital
N2DCS.20LCE19AA101MODE | 13387 | 凝结水至凝汽器水幕喷水气动调阀 |  | digital
N2DCS.20LCE20AA101MODE | 13388 | 凝结水至疏水扩容器减温水调节阀 |  | digital
N2DCS.20LCM40AP001_LP | 13389 | #3机#1疏水泵 |  | digital
N2DCS.20LCM40AP002_LP | 13390 | #3机#2疏水泵 |  | digital
N2DCS.20MAL22AA051_LP | 13391 | #3机高压缸气动疏水门1 |  | digital
N2DCS.20MAL22AA053_LP | 13392 | #3机高压缸气动疏水门2 |  | digital
N2DCS.20MAL22AA054_LP | 13393 | #3机高压缸气动疏水门3 |  | digital
N2DCS.20MAL35AA051_LP | 13394 | 中压缸气动疏水门1 |  | int32
N2DCS.20MAL36AA051_LP | 13395 | 中压缸气动疏水门2 |  | int32
N2DCS.20MAL50AA051_LP | 13396 | 低压缸气动疏水门 |  | int32
N2DCS.20MAW10AA151MODE | 13397 | 辅汽至#3机高、中压轴封气动调阀 |  | digital
N2DCS.20MAW13AA151MODE | 13398 | 辅汽至#3机低压轴封气动调节阀 |  | digital
N2DCS.20MAW50AA151MODE | 13399 | #3机轴封供汽溢流阀 |  | digital
N2DCS.20MAW65AA051_LP | 13400 | 高压缸轴封漏汽至中压缸气动门 |  | digital
N2DCS.20MAW65AA052_LP | 13401 | 高压缸轴封漏汽至低压后缸气动门 |  | digital
N2DCS.20MAW80AN001_LP | 13402 | #3机#1轴封风机 |  | digital
N2DCS.20MAW80AN002_LP | 13403 | #3机#2轴封风机 |  | digital
N2DCS.AUXSTMSYS_SEQST | 13404 | 辅汽系统启顺控 |  | digital
N2DCS.AUXSTMSYS_SEQSTAUX | 13405 | 辅汽系统启顺控辅助点 |  | digital
N2DCS.AUXSTMSYS_SEQSTAUX0 | 13406 | 辅汽系统启顺控启允许条件 |  | digital
N2DCS.AUXSTMSYS_SEQSTAUX1 | 13407 | 辅汽系统启顺控第1步完成条件 |  | digital
N2DCS.AUXSTMSYS_SEQSTAUX2 | 13408 | 辅汽系统启顺控第2步完成条件 |  | digital
N2DCS.AUXSTMSYS_SEQSTAUX3 | 13409 | 辅汽系统启顺控第3步完成条件 |  | digital
N2DCS.AUXSTMSYS_SEQSTLP | 13410 | 辅汽系统启顺控状态 |  | digital
N2DCS.GLDCLREGF_BYLP | 13411 | #3机轴封风机 |  | digital
N2DCS.GLDSTMSYS_SEQSP | 13412 | 轴封系统停顺控 |  | digital
N2DCS.GLDSTMSYS_SEQSP2 | 13413 | Ovation Control Builder |  | int32
N2DCS.GLDSTMSYS_SEQSPAUX | 13414 | 轴封系统停顺控辅助点 |  | digital
N2DCS.GLDSTMSYS_SEQSPAUX0 | 13415 | 轴封系统停顺控启允许条件 |  | digital
N2DCS.GLDSTMSYS_SEQSPAUX1 | 13416 | 轴封系统停顺控第1步完成条件 |  | digital
N2DCS.GLDSTMSYS_SEQSPAUX2 | 13417 | 轴封系统停顺控第2步完成条件 |  | digital
N2DCS.GLDSTMSYS_SEQSPAUX3 | 13418 | 轴封系统停顺控第3步完成条件 |  | digital
N2DCS.GLDSTMSYS_SEQSPLP | 13419 | 轴封系统停顺控状态 |  | digital
N2DCS.GLDSTMSYS_SEQST | 13420 | 轴封系统启顺控 |  | digital
N2DCS.GLDSTMSYS_SEQSTAUX | 13421 | 轴封系统启顺控辅助点 |  | digital
N2DCS.GLDSTMSYS_SEQSTAUX0 | 13422 | 轴封系统启顺控启允许条件 |  | digital
N2DCS.GLDSTMSYS_SEQSTAUX1 | 13423 | 轴封系统启顺控第1步完成条件 |  | digital
N2DCS.GLDSTMSYS_SEQSTAUX2 | 13424 | 轴封系统启顺控第2步完成条件 |  | digital
N2DCS.GLDSTMSYS_SEQSTAUX3 | 13425 | 轴封系统启顺控第3步完成条件 |  | digital
N2DCS.GLDSTMSYS_SEQSTAUX4 | 13426 | 轴封系统启顺控第4步完成条件 |  | digital
N2DCS.GLDSTMSYS_SEQSTLP | 13427 | 轴封系统启顺控状态 |  | digital
N2DCS.J0LBG10CP_LP | 13428 | 辅汽母管压力 |  | digital
N2DCS.J0LBG10CT_LP | 13429 | 辅汽母管温度 |  | digital
N2DCS.20LCM40AA403_LP | 13430 | #3机#1疏水泵出口真空电动门 |  | digital
N2DCS.20LCM40AA406_LP | 13431 | #3机#2疏水泵出口真空电动门 |  | digital
N2DCS.20LCM40AA407_LP | 13432 | 疏水扩容器放水至凝泵坑电动门 |  | digital
N2DCS.GLDSTMSYS_SEQSTAUX5 | 13433 | 轴封系统启顺控第5步完成条件 |  | digital
N2DCS.SHUSHUIPMP_BYLP | 13434 | #3机疏水泵 |  | digital
N2DCS.20LCA11AA001_LP | 13435 | #3机#1凝结水泵进口真空电动门 |  | digital
N2DCS.20LCA11AA003_LP | 13436 | #3机#1凝结水泵出口真空电动门 |  | digital
N2DCS.20LCA30AA101MODE | 13437 | #3机凝结水再循环气动调节阀 |  | digital
N2DCS.20LCA40AA002_LP | 13438 | #3机凝结水无压放水电动门 |  | digital
N2DCS.20LCB11AP001_LP | 13439 | #3机#1凝结水泵 |  | digital
N2DCS.20LCB11GH001_MODE | 13440 | #3机#1凝结水泵永磁控制器 |  | digital
N2DCS.20LCB11GH0011_LP | 13441 | #1凝结水泵水泵 |  | int32
N2DCS.20LCB11GH0012_LP | 13442 | #2凝结水泵水泵 |  | int32
N2DCS.20LCE01AA001_LP | 13443 | #3机凝结水杂用水母管电动门 |  | digital
N2DCS.20LCE16AA101MODE | 13444 | 凝结水至闭式水箱补水电动调节阀 |  | digital
N2DCS.20LCR10AA001_LP | 13445 | 第二套机组除盐水补水电动门 |  | digital
N2DCS.20LCR10AA101MODE | 13446 | #3机凝汽器正常补水电动调节阀 |  | digital
N2DCS.20LCR10AA102MODE | 13447 | #3机凝汽器启动补水电动调节阀 |  | digital
N2DCS.20LCR14AA001_LP | 13448 | 除盐水至#3机闭式水箱注水电动门 |  | digital
N2DCS.20PAB11AA001_LP | 13449 | #3机凝汽器循环水进水#1电动门 |  | digital
N2DCS.20PAB21AA001_LP | 13450 | #3机凝汽器循环水#1出水电动门 |  | digital
N2DCS.20PAH11AA002_LP | 13451 | #3机凝汽器#1胶球泵出口电动门 |  | digital
N2DCS.20PAH11AP001_LP | 13452 | #3机凝汽器#1胶球泵 |  | digital
N2DCS.20PAH11AT001_LP | 13453 | #3机凝汽器#1收球网 |  | digital
N2DCS.20PAH11BB001_LP | 13454 | #3机凝汽器#1装球室 |  | digital
N2DCS.20PCB10AA001_LP | 13455 | #3机开式水电动过滤器进水电动门 |  | digital
N2DCS.20PCB10AA002_LP | 13456 | #3机开式水电动过滤器出水电动门 |  | digital
N2DCS.20PCB10AA003_LP | 13457 | #3机开式水电动过滤器旁路电动门 |  | digital
N2DCS.20PCB10GH501_LP | 13458 | #3机开式水电动过滤器 |  | digital
N2DCS.20PCB11AA001_LP | 13459 | #3机#1开式冷却水泵进口电动门 |  | digital
N2DCS.20PCB11AA002_LP | 13460 | #3机#1开式冷却水泵出口电动门 |  | digital
N2DCS.20PCB11AP001_LP | 13461 | #3机#1开式冷却水泵 |  | digital
N2DCS.20PCB13AA011_LP | 13462 | #1真空泵冷却器开式水进水电动门 |  | digital
N2DCS.20PCB21AA001_LP | 13463 | #1热交换器开式冷却水进水电动门 |  | digital
N2DCS.20PCB23AA011_LP | 13464 | #1真空泵冷却器开式水出水电动门 |  | digital
N2DCS.20PCB31AA001_LP | 13465 | #1热交换器开式冷却水出水电动门 |  | digital
N2DCS.20PGA11AA001_LP | 13466 | #3机#1闭式冷却水泵进口电动门 |  | digital
N2DCS.20PGA11AA003_LP | 13467 | #3机#1闭式冷却水泵出口电动门 |  | digital
N2DCS.20PGA11AP001_LP | 13468 | #3机#1闭式冷却水泵 |  | digital
N2DCS.20PGA21AA001_LP | 13469 | #1热交换器闭式水进口电动门 |  | digital
N2DCS.20PGA21AA002_LP | 13470 | #1热交换器闭式水出口电动门 |  | digital
N2DCS.CIRWTR_SEQST | 13471 | 开式冷却水系统启顺控 |  | digital
N2DCS.CIRWTR_SEQSTAUX | 13472 | 开始循环水系统启顺控辅助 |  | int32
N2DCS.CIRWTR_SEQSTLP | 13473 | Ovation Control Builder |  | int32
N2DCS.CLCLGPMP_BYLP | 13474 | #3机闭式冷却水泵 |  | digital
N2DCS.CLCLGPMPA_PMTLP | 13475 | #3机闭式冷却水泵启允许条件 |  | digital
N2DCS.CLCLGPMPA_SEQAUX | 13476 | 闭式循环冷却水泵A程控 |  | int32
N2DCS.CLCLGPMPA_SEQAUX0 | 13477 | Ovation Control Builder |  | int32
N2DCS.CLCLGPMPA_SEQAUX1 | 13478 | Ovation Control Builder |  | int32
N2DCS.CLCLGPMPA_SEQAUX10 | 13479 | Ovation Control Builder |  | int32
N2DCS.CLCLGPMPA_SEQAUX11 | 13480 | Ovation Control Builder |  | int32
N2DCS.CLCLGPMPA_SEQAUX2 | 13481 | Ovation Control Builder |  | int32
N2DCS.CLCLGPMPA_SEQAUX3 | 13482 | Ovation Control Builder |  | int32
N2DCS.CLCLGPMPA_SEQAUX9 | 13483 | Ovation Control Builder |  | int32
N2DCS.CLCLGPMPA_SEQSP | 13484 | #1闭式水泵停顺控 |  | digital
N2DCS.CLCLGPMPA_SEQSPAUX | 13485 | #1闭式水泵停顺控辅助点 |  | digital
N2DCS.CLCLGPMPA_SEQSPAUX0 | 13486 | #1闭式水泵停顺控启允许条件 |  | digital
N2DCS.CLCLGPMPA_SEQSPAUX1 | 13487 | #1闭式水泵停顺控第1步完成条件 |  | digital
N2DCS.CLCLGPMPA_SEQSPAUX2 | 13488 | #1闭式水泵停顺控第2步完成条件 |  | digital
N2DCS.CLCLGPMPA_SEQSPLP | 13489 | #1闭式水泵停顺控状态 |  | digital
N2DCS.CLCLGPMPA_SEQST | 13490 | #1闭式水泵启顺控 |  | digital
N2DCS.CLCLGPMPA_SEQSTAUX | 13491 | #1闭式水泵启顺控辅助点 |  | digital
N2DCS.CLCLGPMPA_SEQSTAUX0 | 13492 | #1闭式水泵启顺控启允许条件 |  | digital
N2DCS.CLCLGPMPA_SEQSTAUX1 | 13493 | #1闭式水泵启顺控第1步完成条件 |  | digital
N2DCS.CLCLGPMPA_SEQSTAUX2 | 13494 | #1闭式水泵启顺控第2步完成条件 |  | digital
N2DCS.CLCLGPMPA_SEQSTAUX3 | 13495 | #1闭式水泵启顺控第3步完成条件 |  | digital
N2DCS.CLCLGPMPA_SEQSTLP | 13496 | #1闭式水泵启顺控状态 |  | digital
N2DCS.CLCLGPMPA_TRIP | 13497 | #1闭式水泵跳闸条件 |  | digital
N2DCS.CLCLGPMPA_TRIPTAG | 13498 | #1闭式水泵跳闸条件解除信号 |  | digital
N2DCS.CLCLGWTR_SEQST | 13499 | 闭式水系统启顺控 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX | 13500 | 闭式水系统启顺控辅助点 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX0 | 13501 | 闭式水系统启顺控启允许条件 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX1 | 13502 | 闭式水系统启顺控第1步完成条件 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX2 | 13503 | 闭式水系统启顺控第2步完成条件 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX3 | 13504 | 闭式水系统启顺控第3步完成条件 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX4 | 13505 | 闭式水系统启顺控第4步完成条件 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX5 | 13506 | 闭式水系统启顺控第5步完成条件 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX6 | 13507 | 闭式水系统启顺控第6步完成条件 |  | digital
N2DCS.CLCLGWTR_SEQSTAUX7 | 13508 | 闭式水系统启顺控第7步完成条件 |  | digital
N2DCS.CLCLGWTR_SEQSTLP | 13509 | 闭式水系统启顺控状态 |  | digital
N2DCS.CLCLGWTR_SEQSTOK | 13510 | 闭式水系统启顺控第8步完成条件 |  | digital
N2DCS.CNDHWLVL_LP | 13511 | #3机凝汽器热井液位 |  | digital
N2DCS.CNDPA_SEQSP | 13512 | #3机#1凝结水泵停顺控 |  | digital
N2DCS.CNDPA_SEQSPAUX | 13513 | #3机#1凝结水泵停顺控辅助点 |  | digital
N2DCS.CNDPA_SEQSPAUX0 | 13514 | #1凝结水泵停顺控启允许条件 |  | int32
N2DCS.CNDPA_SEQSPAUX1 | 13515 | #1凝结水泵停顺控第1步完成条件 |  | digital
N2DCS.CNDPA_SEQSPAUX2 | 13516 | #1凝结水泵停顺控第2步完成条件 |  | digital
N2DCS.CNDPA_SEQSPAUX3 | 13517 | #1凝结水泵停顺控第3步完成条件 |  | digital
N2DCS.CNDPA_SEQSPAUX4 | 13518 | 第4步成功完成条件 |  | int32
N2DCS.CNDPA_SEQST | 13519 | #1凝结水泵启顺控 |  | int32
N2DCS.CNDPA_SEQSTAUX | 13520 | #1凝结水泵启顺控辅助点 |  | digital
N2DCS.CNDPA_SEQSTAUX0 | 13521 | #1凝结水泵启顺控启允许条件 |  | int32
N2DCS.CNDPA_SEQSTAUX1 | 13522 | #1凝结水泵启顺控第1步完成条件 |  | digital
N2DCS.CNDPA_SEQSTAUX2 | 13523 | #1凝结水泵启顺控第2步完成条件 |  | digital
N2DCS.CNDPA_SEQSTAUX3 | 13524 | #1凝结水泵启顺控第3步完成条件 |  | digital
N2DCS.CNDPA_SEQSTAUX4 | 13525 | 第4步成功完成条件 |  | int32
N2DCS.CNDPAPA_SEQSPLP | 13526 | #1凝结水泵停顺控状态 |  | digital
N2DCS.CNDPAPA_SEQSTLP | 13527 | #1凝结水泵启顺控状态 |  | digital
N2DCS.CNDPMP_BYLP | 13528 | #3机凝结水泵 |  | digital
N2DCS.CNDPMPA_STPMTLP | 13529 | #3机#1凝结水泵启允许条件 |  | digital
N2DCS.CNDPMPA_TRIP | 13530 | #3机#1凝结水泵跳闸条件 |  | digital
N2DCS.CNDPMPA_TRIPTAG | 13531 | #3机#1凝结水泵跳闸条件解除信号 |  | digital
N2DCS.CNDWTRSYS_SEQST | 13532 | 凝结水系统启顺控 |  | int32
N2DCS.CNDWTRSYS_SEQSTAUX | 13533 | 凝结水系统启顺控辅助点 |  | digital
N2DCS.CNDWTRSYS_SEQSTAUX0 | 13534 | 凝结水系统启顺控启允许条件 |  | int32
N2DCS.CNDWTRSYS_SEQSTAUX1 | 13535 | 凝结水系统启顺控第1步完成条件 |  | digital
N2DCS.CNDWTRSYS_SEQSTAUX2 | 13536 | 凝结水系统启顺控第2步完成条件 |  | digital
N2DCS.CNDWTRSYS_SEQSTAUX3 | 13537 | 凝结水系统启顺控第3步完成条件 |  | digital
N2DCS.CNDWTRSYS_SEQSTAUX4 | 13538 | 第4步成功完成条件 |  | int32
N2DCS.CNDWTRSYS_SEQSTLP | 13539 | 凝结水系统启顺控状态 |  | digital
N2DCS.CNDWTRSYS_SEQSTREY | 13540 | 凝结水系统准备顺控 |  | digital
N2DCS.CNDWTRSYS_SEQSTREYAUX | 13541 | 凝结水系统准备顺控辅助点 |  | digital
N2DCS.CNDWTRSYS_SEQSTREYAUX0 | 13542 | 凝结水系统准备顺控启允许条件 |  | digital
N2DCS.CNDWTRSYS_SEQSTREYAUX1 | 13543 | 凝结水系统准备顺控1步完成条件 |  | digital
N2DCS.CNDWTRSYS_SEQSTREYAUX2 | 13544 | 凝结水系统准备顺控2步完成条件 |  | digital
N2DCS.CNDWTRSYS_SEQSTREYAUX3 | 13545 | 凝结水系统准备顺控3步完成条件 |  | digital
N2DCS.CNDWTRSYS_SEQSTREYAUX4 | 13546 | 凝结水系统准备顺控4步完成条件 |  | digital
N2DCS.CNDWTRSYS_SEQSTREYLP | 13547 | 凝结水系统准备顺控状态 |  | digital
N2DCS.CNSRLVL_LP | 13548 | #3机凝汽器热井液位 |  | digital
N2DCS.OPNCIRPMPA_PMTLP | 13549 | #3机#1开式水泵启允许条件 |  | digital
N2DCS.OPNCIRPMPA_SEQAUX | 13550 | Ovation Control Builder |  | int32
N2DCS.OPNCIRPMPA_SEQAUX0 | 13551 | Ovation Control Builder |  | int32
N2DCS.OPNCIRPMPA_SEQAUX1 | 13552 | Ovation Control Builder |  | int32
N2DCS.OPNCIRPMPA_SEQAUX2 | 13553 | Ovation Control Builder |  | int32
N2DCS.OPNCIRPMPA_SEQAUX3 | 13554 | Ovation Control Builder |  | int32
N2DCS.OPNCIRPMPA_SEQAUX4 | 13555 | Ovation Control Builder |  | int32
N2DCS.OPNCIRPMPA_SEQAUX5 | 13556 | Ovation Control Builder |  | int32
N2DCS.OPNCIRPMPA_SEQSP | 13557 | #3机#1开式水泵停顺控 |  | digital
N2DCS.OPNCIRPMPA_SEQSPAUX | 13558 | #3机#1开式水泵停顺控辅助点 |  | digital
N2DCS.OPNCIRPMPA_SEQSPAUX1 | 13559 | #1开式水泵停顺控第1步完成条件 |  | digital
N2DCS.OPNCIRPMPA_SEQSPAUX2 | 13560 | #1开式水泵停顺控第2步完成条件 |  | digital
N2DCS.OPNCIRPMPA_SEQSPLP | 13561 | #3机#1开式水泵停顺控状态 |  | digital
N2DCS.OPNCIRPMPA_SEQST | 13562 | #3机#1开式水泵启顺控 |  | digital
N2DCS.OPNCIRPMPA_SEQSTAUX | 13563 | #3机#1开式水泵启顺控辅助点 |  | digital
N2DCS.OPNCIRPMPA_SEQSTAUX0 | 13564 | #3机#1开式水泵启顺控启允许条件 |  | digital
N2DCS.OPNCIRPMPA_SEQSTAUX1 | 13565 | #1开式水泵启顺控第1步完成条件 |  | digital
N2DCS.OPNCIRPMPA_SEQSTAUX2 | 13566 | #1开式水泵启顺控第2步完成条件 |  | digital
N2DCS.OPNCIRPMPA_SEQSTAUX3 | 13567 | #1开式水泵启顺控第3步完成条件 |  | digital
N2DCS.OPNCIRPMPA_SEQSTLP | 13568 | #3机#1开式水泵启顺控状态 |  | digital
N2DCS.OPNCIRPMPA_TRIP | 13569 | #3机#1开式水泵跳闸条件 |  | digital
N2DCS.OPNCIRPMPA_TRIPTAG | 13570 | #3机#1开式水泵跳闸条件解除信号 |  | digital
N2DCS.OPNCIRWTR_SEQST | 13571 | 开式水系统启顺控 |  | digital
N2DCS.OPNCIRWTR_SEQSTAUX | 13572 | 开式水系统启顺控辅助点 |  | digital
N2DCS.OPNCIRWTR_SEQSTAUX0 | 13573 | 开式水系统启顺控启允许条件 |  | digital
N2DCS.OPNCIRWTR_SEQSTAUX1 | 13574 | 开式水系统启顺控第1步完成条件 |  | digital
N2DCS.OPNCIRWTR_SEQSTAUX2 | 13575 | 开式水系统启顺控第2步完成条件 |  | digital
N2DCS.OPNCIRWTR_SEQSTAUX3 | 13576 | 开式水系统启顺控第3步完成条件 |  | digital
N2DCS.OPNCIRWTR_SEQSTAUX4 | 13577 | 开式水系统启顺控第4步完成条件 |  | digital
N2DCS.OPNCIRWTR_SEQSTLP | 13578 | 开式水系统启顺控状态 |  | digital
N2DCS.OPNCIRWTRPMP_BYLP | 13579 | #3机开式冷却水泵 |  | digital
N2DCS.RBBRBALLA_SEQAUX | 13580 | A侧胶球系统辅助 |  | int32
N2DCS.RBBRBALLA_SEQAUX1 | 13581 | Ovation Control Builder |  | int32
N2DCS.RBBRBALLA_SEQAUX10 | 13582 | Ovation Control Builder |  | int32
N2DCS.RBBRBALLA_SEQAUX2 | 13583 | Ovation Control Builder |  | int32
N2DCS.RBBRBALLA_SEQAUX3 | 13584 | Ovation Control Builder |  | int32
N2DCS.RBBRBALLA_SEQAUX4 | 13585 | Ovation Control Builder |  | int32
N2DCS.RBBRBALLA_SEQAUX7 | 13586 | Ovation Control Builder |  | int32
N2DCS.RBBRBALLA_SEQAUX8 | 13587 | Ovation Control Builder |  | int32
N2DCS.RBBRBALLA_SEQAUX9 | 13588 | Ovation Control Builder |  | int32
N2DCS.RBBRBALLA_SEQSP | 13589 | 凝汽器#1胶球收球顺控 |  | digital
N2DCS.RBBRBALLA_SEQSPAUX | 13590 | 凝汽器#1胶球收球顺控辅助点 |  | digital
N2DCS.RBBRBALLA_SEQSPAUX1 | 13591 | #1胶球收球顺控第1步完成条件 |  | digital
N2DCS.RBBRBALLA_SEQSPAUX2 | 13592 | #1胶球收球顺控第2步完成条件 |  | digital
N2DCS.RBBRBALLA_SEQSPAUX3 | 13593 | #1胶球收球顺控第3步完成条件 |  | digital
N2DCS.RBBRBALLA_SEQSPAUX4 | 13594 | #1胶球收球顺控第4步完成条件 |  | digital
N2DCS.RBBRBALLA_SEQSPLP | 13595 | 凝汽器#1胶球收球顺控状态 |  | digital
N2DCS.RBBRBALLA_SEQST | 13596 | 凝汽器#1胶球投球顺控 |  | digital
N2DCS.RBBRBALLA_SEQSTAUX | 13597 | 凝汽器#1胶球投球顺控辅助点 |  | digital
N2DCS.RBBRBALLA_SEQSTAUX0 | 13598 | 凝汽器#1胶球投球顺控启允许条件 |  | digital
N2DCS.RBBRBALLA_SEQSTAUX1 | 13599 | #1胶球投球顺控第1步完成条件 |  | digital
N2DCS.RBBRBALLA_SEQSTAUX2 | 13600 | #1胶球投球顺控第2步完成条件 |  | digital
N2DCS.RBBRBALLA_SEQSTAUX3 | 13601 | #1胶球投球顺控第3步完成条件 |  | digital
N2DCS.RBBRBALLA_SEQSTAUX4 | 13602 | #1胶球投球顺控第4步完成条件 |  | digital
N2DCS.RBBRBALLA_SEQSTLP | 13603 | 凝汽器#1胶球投球顺控状态 |  | digital
N2DCS.20LDK10AA003_LP | 13604 | #3机除铁过滤器升压气动门 |  | digital
N2DCS.20LDK10AA004_LP | 13605 | #3机除铁过滤器出水电动门 |  | digital
N2DCS.CNDWTRSYS_SEQSTREYAUX5 | 13606 | 凝结水系统准备顺控5步完成条件 |  | digital
N2DCS.20LCA12AA001_LP | 13607 | #3机#2凝结水泵进口真空电动门 |  | digital
N2DCS.20LCA12AA003_LP | 13608 | #3机#2凝结水泵出口真空电动门 |  | digital
N2DCS.20LCB12AP001_LP | 13609 | #3机#2凝结水泵 |  | digital
N2DCS.20LCB12AP002_LP | 13610 | #3机#2凝结水泵 |  | digital
N2DCS.20LCB12GH001_LP | 13611 | #2凝结水泵#1永磁调速水泵 |  | digital
N2DCS.20LCB12GH0011_LP | 13612 | #2凝结水泵 |  | int32
N2DCS.20LCB12GH0012_LP | 13613 | #2凝结水泵#2永磁调速水泵 |  | digital
N2DCS.20PAB12AA001_LP | 13614 | #3机凝汽器循环水进水#2电动门 |  | digital
N2DCS.20PAB22AA001_LP | 13615 | #3机凝汽器循环水#2出水电动门 |  | digital
N2DCS.20PAH12AA002_LP | 13616 | #3机凝汽器#2胶球泵出口电动门 |  | digital
N2DCS.20PAH12AP001_LP | 13617 | #3机凝汽器#2胶球泵 |  | digital
N2DCS.20PAH12AT001_LP | 13618 | #3机凝汽器#2收球网 |  | digital
N2DCS.20PAH12BB001_LP | 13619 | #3机凝汽器#2装球室 |  | digital
N2DCS.20PCB11AA003_LP | 13620 | #3机#2开式冷却水泵进口电动门 |  | digital
N2DCS.20PCB11AA004_LP | 13621 | #3机#2开式冷却水泵出口电动门 |  | digital
N2DCS.20PCB11AP002_LP | 13622 | #3机#2开式冷却水泵 |  | digital
N2DCS.20PCB13AA012_LP | 13623 | #2真空泵冷却器开式水进水电动门 |  | digital
N2DCS.20PCB22AA001_LP | 13624 | #2热交换器开式冷却水进水电动门 |  | digital
N2DCS.20PCB23AA012_LP | 13625 | #2真空泵冷却器开式水出水电动门 |  | digital
N2DCS.20PCB32AA001_LP | 13626 | #2热交换器开式冷却水出水电动门 |  | digital
N2DCS.20PGA12AA001_LP | 13627 | #3机#2闭式冷却水泵进口电动门 |  | digital
N2DCS.20PGA12AA003_LP | 13628 | #3机#2闭式冷却水泵出口电动门 |  | digital
N2DCS.20PGA12AP001_LP | 13629 | #3机#2闭式冷却水泵 |  | digital
N2DCS.20PGA22AA001_LP | 13630 | #2热交换器闭式水进口电动门 |  | digital
N2DCS.20PGA22AA002_LP | 13631 | #2热交换器闭式水出口电动门 |  | digital
N2DCS.20PGA26AA101MODE | 13632 | #4发电机定冷水进水电动调节阀 |  | digital
N2DCS.20PGA26AA102MODE | 13633 | #4发电机氢冷器进水电动调节阀 |  | digital
N2DCS.20PGA26AA103MODE | 13634 | #4机润滑油冷却器进水电动调节阀 |  | digital
N2DCS.20PGA32AA101MODE | 13635 | #3机EH油冷却器进水电动调节阀 |  | digital
N2DCS.20PGA33AA101MODE | 13636 | #3机润滑油冷却器进水电动调节阀 |  | digital
N2DCS.20PGA34AA101MODE | 13637 | #3发电机空冷器进水电动调节阀 |  | digital
N2DCS.CLCLGPMPB_PMTLP | 13638 | #3机闭式冷却水泵启允许条件 |  | digital
N2DCS.CLCLGPMPB_SEQSP | 13639 | #2闭式水泵停顺控 |  | digital
N2DCS.CLCLGPMPB_SEQSPAUX | 13640 | #2闭式水泵停顺控辅助点 |  | digital
N2DCS.CLCLGPMPB_SEQSPAUX0 | 13641 | #2闭式水泵停顺控启允许条件 |  | digital
N2DCS.CLCLGPMPB_SEQSPAUX1 | 13642 | #2闭式水泵停顺控第1步完成条件 |  | digital
N2DCS.CLCLGPMPB_SEQSPAUX2 | 13643 | #2闭式水泵停顺控第2步完成条件 |  | digital
N2DCS.CLCLGPMPB_SEQSPLP | 13644 | #2闭式水泵停顺控状态 |  | digital
N2DCS.CLCLGPMPB_SEQST | 13645 | #2闭式水泵启顺控 |  | digital
N2DCS.CLCLGPMPB_SEQSTAUX | 13646 | #2闭式水泵启顺控辅助点 |  | digital
N2DCS.CLCLGPMPB_SEQSTAUX0 | 13647 | #2闭式水泵启顺控启允许条件 |  | digital
N2DCS.CLCLGPMPB_SEQSTAUX1 | 13648 | #2闭式水泵启顺控第1步完成条件 |  | digital
N2DCS.CLCLGPMPB_SEQSTAUX2 | 13649 | #2闭式水泵启顺控第2步完成条件 |  | digital
N2DCS.CLCLGPMPB_SEQSTAUX3 | 13650 | #2闭式水泵启顺控第3步完成条件 |  | digital
N2DCS.CLCLGPMPB_SEQSTLP | 13651 | #2闭式水泵启顺控状态 |  | digital
N2DCS.CLCLGPMPB_TRIP | 13652 | #2闭式水泵跳闸条件 |  | digital
N2DCS.CLCLGPMPB_TRIPTAG | 13653 | #2闭式水泵跳闸条件解除信号 |  | digital
N2DCS.CNDPAPB_SEQSPLP | 13654 | #2凝结水泵停顺控状态 |  | digital
N2DCS.CNDPAPB_SEQSTLP | 13655 | #2凝结水泵启顺控状态 |  | digital
N2DCS.CNDPB_SEQSP | 13656 | #2凝结水泵停顺控 |  | int32
N2DCS.CNDPB_SEQSPAUX | 13657 | #2凝结水泵停顺控辅助点 |  | digital
N2DCS.CNDPB_SEQSPAUX0 | 13658 | #2凝结水泵停顺控启运行条件 |  | int32
N2DCS.CNDPB_SEQSPAUX1 | 13659 | #2凝结水泵停顺控第1步完成条件 |  | digital
N2DCS.CNDPB_SEQSPAUX2 | 13660 | #2凝结水泵停顺控第2步完成条件 |  | digital
N2DCS.CNDPB_SEQSPAUX3 | 13661 | 第3步成功完成条件 |  | int32
N2DCS.CNDPB_SEQSPAUX4 | 13662 | 第4步成功完成条件 |  | int32
N2DCS.CNDPB_SEQST | 13663 | #2凝结水泵启顺控 |  | int32
N2DCS.CNDPB_SEQSTAUX | 13664 | #2凝结水泵启顺控辅助点 |  | digital
N2DCS.CNDPB_SEQSTAUX0 | 13665 | #2凝结水泵启顺控启允许条件 |  | digital
N2DCS.CNDPB_SEQSTAUX1 | 13666 | #2凝结水泵启顺控第1步完成条件 |  | digital
N2DCS.CNDPB_SEQSTAUX2 | 13667 | #2凝结水泵启顺控第2步完成条件 |  | digital
N2DCS.CNDPB_SEQSTAUX3 | 13668 | #2凝结水泵启顺控第3步完成条件 |  | digital
N2DCS.CNDPB_SEQSTAUX4 | 13669 | #2凝结水泵启顺控第4步完成条件 |  | digital
N2DCS.CNDPMPB_STPMTLP | 13670 | #3机#2凝结水泵启允许条件 |  | digital
N2DCS.CNDPMPB_TRIP | 13671 | #3机#2凝结水泵跳闸条件 |  | digital
N2DCS.CNDPMPB_TRIPTAG | 13672 | #3机#2凝结水泵跳闸条件解除信号 |  | digital
N2DCS.OPNCIRPMPB_PMTLP | 13673 | #3机#2开式水泵启允许条件 |  | digital
N2DCS.OPNCIRPMPB_SEQSP | 13674 | #3机#2开式水泵停顺控 |  | digital
N2DCS.OPNCIRPMPB_SEQSPAUX | 13675 | #3机#2开式水泵停顺控辅助点 |  | digital
N2DCS.OPNCIRPMPB_SEQSPAUX1 | 13676 | #2开式水泵停顺控第1步完成条件 |  | digital
N2DCS.OPNCIRPMPB_SEQSPAUX2 | 13677 | #2开式水泵停顺控第2步完成条件 |  | digital
N2DCS.OPNCIRPMPB_SEQSPLP | 13678 | #3机#2开式水泵停顺控状态 |  | digital
N2DCS.OPNCIRPMPB_SEQST | 13679 | #3机#2开式水泵启顺控 |  | digital
N2DCS.OPNCIRPMPB_SEQSTAUX | 13680 | #3机#2开式水泵启顺控辅助点 |  | digital
N2DCS.OPNCIRPMPB_SEQSTAUX0 | 13681 | #3机#2开式水泵启顺控启允许条件 |  | digital
N2DCS.OPNCIRPMPB_SEQSTAUX1 | 13682 | #2开式水泵启顺控第1步完成条件 |  | digital
N2DCS.OPNCIRPMPB_SEQSTAUX2 | 13683 | #2开式水泵启顺控第2步完成条件 |  | digital
N2DCS.OPNCIRPMPB_SEQSTAUX3 | 13684 | #2开式水泵启顺控第3步完成条件 |  | digital
N2DCS.OPNCIRPMPB_SEQSTLP | 13685 | #3机#2开式水泵启顺控状态 |  | digital
N2DCS.OPNCIRPMPB_TRIP | 13686 | #3机#2开式水泵跳闸条件 |  | digital
N2DCS.OPNCIRPMPB_TRIPTAG | 13687 | #3机#2开式水泵跳闸条件解除信号 |  | digital
N2DCS.RBBRBALLB_SEQSP | 13688 | 凝汽器#2胶球收球顺控 |  | digital
N2DCS.RBBRBALLB_SEQSPAUX | 13689 | 凝汽器#2胶球收球顺控辅助点 |  | digital
N2DCS.RBBRBALLB_SEQSPAUX1 | 13690 | #2胶球收球顺控第1步完成条件 |  | digital
N2DCS.RBBRBALLB_SEQSPAUX2 | 13691 | #2胶球收球顺控第2步完成条件 |  | digital
N2DCS.RBBRBALLB_SEQSPAUX3 | 13692 | #2胶球收球顺控第3步完成条件 |  | digital
N2DCS.RBBRBALLB_SEQSPAUX4 | 13693 | #2胶球收球顺控第4步完成条件 |  | digital
N2DCS.RBBRBALLB_SEQSPLP | 13694 | 凝汽器#2胶球收球顺控状态 |  | digital
N2DCS.RBBRBALLB_SEQST | 13695 | 凝汽器#2胶球投球顺控 |  | digital
N2DCS.RBBRBALLB_SEQSTAUX | 13696 | 凝汽器#2胶球投球顺控辅助点 |  | digital
N2DCS.RBBRBALLB_SEQSTAUX0 | 13697 | 凝汽器#2胶球投球顺控启允许条件 |  | digital
N2DCS.RBBRBALLB_SEQSTAUX1 | 13698 | #2胶球投球顺控第1步完成条件 |  | digital
N2DCS.RBBRBALLB_SEQSTAUX2 | 13699 | #2胶球投球顺控第2步完成条件 |  | digital
N2DCS.RBBRBALLB_SEQSTAUX3 | 13700 | #2胶球投球顺控第3步完成条件 |  | digital
N2DCS.RBBRBALLB_SEQSTAUX4 | 13701 | #2胶球投球顺控第4步完成条件 |  | digital
N2DCS.RBBRBALLB_SEQSTLP | 13702 | 凝汽器#2胶球投球顺控状态 |  | digital
N2DCS.20LCB12GH001MODE | 13703 | #2凝结水泵永磁调速控制器 |  | digital
N2DCS.20LDB10AA501_LP | 13704 | 凝结水除铁过滤器#1排气气动门 |  | digital
N2DCS.20LDB10AA502_LP | 13705 | 凝结水除铁过滤器#2排气气动门 |  | digital
N2DCS.20LDK10AA002_LP | 13706 | 凝结水除铁过滤器进口电动门 |  | digital
N2DCS.20LDK20AA002_LP | 13707 | 凝结水除铁过滤器旁路电动门 |  | digital
N2DCS.CNDYCPMP_BYLP | 13708 | #2凝结水泵永磁调速冷却水泵 |  | digital
N2DCS.CTGLQ_BYLP | 13709 | 除铁过滤器主、旁路预选 |  | digital
N2DCS.HXCTQ_SEQSP | 13710 | 除铁过滤器停顺控 |  | digital
N2DCS.HXCTQ_SEQSPAUX | 13711 | 除铁过滤器停顺控辅助点 |  | digital
N2DCS.HXCTQ_SEQSPAUX0 | 13712 | 除铁过滤器停顺控启允许条件 |  | digital
N2DCS.HXCTQ_SEQSPAUX1 | 13713 | 除铁过滤器停顺控第1步完成条件 |  | digital
N2DCS.HXCTQ_SEQSPAUX2 | 13714 | 除铁过滤器停顺控第2步完成条件 |  | digital
N2DCS.HXCTQ_SEQSPAUX3 | 13715 | 除铁过滤器停顺控第3步完成条件 |  | digital
N2DCS.HXCTQ_SEQSPLP | 13716 | 除铁过滤器停顺控状态 |  | digital
N2DCS.HXCTQ_SEQST | 13717 | 除铁过滤器启顺控 |  | digital
N2DCS.HXCTQ_SEQSTAUX | 13718 | 除铁过滤器启顺控辅助点 |  | digital
N2DCS.HXCTQ_SEQSTAUX0 | 13719 | 除铁过滤器启顺控启允许条件 |  | digital
N2DCS.HXCTQ_SEQSTAUX1 | 13720 | 除铁过滤器启顺控第1步完成条件 |  | digital
N2DCS.HXCTQ_SEQSTAUX2 | 13721 | 除铁过滤器启顺控第2步完成条件 |  | digital
N2DCS.HXCTQ_SEQSTAUX3 | 13722 | 除铁过滤器启顺控第3步完成条件 |  | digital
N2DCS.HXCTQ_SEQSTAUX4 | 13723 | 除铁过滤器启顺控第4步完成条件 |  | digital
N2DCS.HXCTQ_SEQSTAUX5 | 13724 | 除铁过滤器启顺控第5步完成条件 |  | digital
N2DCS.HXCTQ_SEQSTLP | 13725 | 除铁过滤器启顺控状态 |  | digital
N2DCS.20MA101AP001_LP | 13726 | #1EH油泵 |  | int32
N2DCS.20MA101AP011_LP | 13727 | #1EH油循环泵 |  | int32
N2DCS.20MAJ21AA001_LP | 13728 | #3机#1真空泵进口气动门2 |  | digital
N2DCS.20MAJ21AA007_LP | 13729 | #1真空泵汽水分离器补水电磁阀 |  | digital
N2DCS.20MAJ21AA011_LP | 13730 | #3机#1真空泵进口气动门1 |  | digital
N2DCS.20MAJ21AP001_LP | 13731 | #3机#1真空泵 |  | digital
N2DCS.20MAJ23AA009_LP | 13732 | #3机蒸汽喷射装置进口气动门 |  | digital
N2DCS.20MAJ23AA014_LP | 13733 | 蒸汽喷射装置换热器放水气动门 |  | digital
N2DCS.20MAJ23AA016_LP | 13734 | 蒸汽喷射装置换热器汽侧出口气门 |  | int32
N2DCS.20MAJ23AA101_MODE | 13735 | #3机蒸汽喷射装置压力调节阀 |  | digital
N2DCS.20MAJ23AA101MODE | 13736 | Ovation Control Builder |  | int32
N2DCS.20MAJ30AA002_LP | 13737 | #3机凝汽器真空破坏气动门 |  | digital
N2DCS.20MAV10AH001_LP | 13738 | #3机润滑油箱#1电加热器 |  | digital
N2DCS.20MAV10AH002_LP | 13739 | #3机润滑油箱#2电加热器 |  | digital
N2DCS.20MAV21AP021_LP | 13740 | #3机#1润滑油泵 |  | digital
N2DCS.20MAV31AP001_LP | 13741 | #3机#1顶轴油泵 |  | digital
N2DCS.20MAV82AN001_LP | 13742 | #3机#1润滑油风机 |  | digital
N2DCS.20MAX01AP001_LP | 13743 | #3机#1EH油泵 |  | digital
N2DCS.20MAX01AP011_LP | 13744 | #3机#1EH油循环泵 |  | digital
N2DCS.20PAA11AA001_LP | 13745 | #1旋转滤网冲洗水电动门 |  | digital
N2DCS.20PAB11AA002_LP | 13746 | #3循环水泵出口液控蝶阀 |  | digital
N2DCS.20PAB11AT001_LP | 13747 | #1旋转滤网 |  | digital
N2DCS.20PAB41AP001_LP | 13748 | #3循环水泵冷却水#1加压泵 |  | digital
N2DCS.20PAB42AP001_LP | 13749 | #3循环水泵冷却水#2加压泵 |  | digital
N2DCS.20PAB61AA001_LP | 13750 | 生活水至#3循环水泵冷却水电磁阀 |  | digital
N2DCS.20PAC11AP001_LP | 13751 | #3循环水泵 |  | int32
N2DCS.20PAC11AP001H_LP | 13752 | #3循环水泵高速 |  | int32
N2DCS.20PAC11AP001L_LP | 13753 | #3循环水泵低速 |  | int32
N2DCS.20PSA01AP001_LP | 13754 | #2冷却塔排水池#1排污泵 |  | digital
N2DCS.ACLUBOILP_BYLP | 13755 | #3机润滑油泵 |  | digital
N2DCS.CIRPMPA_STPMTLP | 13756 | #3循环水泵启允许条件 |  | digital
N2DCS.CIRPMPA_TRIP | 13757 | #3循环水泵跳闸条件 |  | digital
N2DCS.CIRPMPA_TRIPTAG | 13758 | #3循环水泵跳闸条件解除信号 |  | digital
N2DCS.CIRWTRPMP_BYLP | 13759 | 循环水泵 |  | int32
N2DCS.CIRWTRPMP_SEQSPAUX | 13760 | Ovation Control Builder |  | int32
N2DCS.CIRWTRPMPA_SEQSP | 13761 | #3循环水泵停顺控 |  | int32
N2DCS.CIRWTRPMPA_SEQSPAUX | 13762 | #3循环水泵停顺控辅助点 |  | digital
N2DCS.CIRWTRPMPA_SEQSPAUX1 | 13763 | #3循环水泵停顺控第1步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSPAUX2 | 13764 | #3循环水泵停顺控第2步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSPAUX3 | 13765 | #3循环水泵停顺控第3步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSPAUX4 | 13766 | #3循环水泵停顺控第4步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSPAUX5 | 13767 | 第5步成功完成条件 |  | int32
N2DCS.CIRWTRPMPA_SEQSPLP | 13768 | #3循环水泵停顺控状态 |  | digital
N2DCS.CIRWTRPMPA_SEQST | 13769 | #3循环水泵启顺控 |  | int32
N2DCS.CIRWTRPMPA_SEQSTAUX | 13770 | #3循环水泵停顺控辅助点 |  | digital
N2DCS.CIRWTRPMPA_SEQSTAUX0 | 13771 | #3循环水泵停顺控启允许条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSTAUX1 | 13772 | #3循环水泵停顺控第1步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSTAUX2 | 13773 | #3循环水泵停顺控第2步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSTAUX3 | 13774 | #3循环水泵停顺控第3步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSTAUX4 | 13775 | #3循环水泵停顺控第4步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSTAUX5 | 13776 | #3循环水泵停顺控第5步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSTAUX6 | 13777 | #3循环水泵停顺控第6步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSTAUX7 | 13778 | #3循环水泵停顺控第7步完成条件 |  | digital
N2DCS.CIRWTRPMPA_SEQSTLP | 13779 | #3循环水泵启顺控状态 |  | digital
N2DCS.CIRWTRSYS_SEQST | 13780 | 循环水系统启顺控 |  | int32
N2DCS.CIRWTRSYS_SEQSTAUX | 13781 | 循环水系统启顺控辅助点 |  | digital
N2DCS.CIRWTRSYS_SEQSTAUX0 | 13782 | 循环水系统启顺控启允许条件 |  | int32
N2DCS.CIRWTRSYS_SEQSTAUX1 | 13783 | 循环水系统启顺控第1步完成条件 |  | digital
N2DCS.CIRWTRSYS_SEQSTAUX2 | 13784 | 循环水系统启顺控第2步完成条件 |  | digital
N2DCS.CIRWTRSYS_SEQSTAUX3 | 13785 | 循环水系统启顺控第3步完成条件 |  | digital
N2DCS.CIRWTRSYS_SEQSTAUX4 | 13786 | 循环水系统启顺控第4步完成条件 |  | digital
N2DCS.CIRWTRSYS_SEQSTAUX5 | 13787 | 第5步成功完成条件 |  | int32
N2DCS.CIRWTRSYS_SEQSTLP | 13788 | 循环水系统启顺控状态 |  | digital
N2DCS.CNSRVACM_LP | 13789 | #3机凝汽器真空压力 |  | digital
N2DCS.EHMAINOILP_BYLP | 13790 | EH油泵 |  | digital
N2DCS.EHOILCIRP_BYLP | 13791 | EH油循环泵 |  | digital
N2DCS.EHOILSYS_SEQSP | 13792 | EH油系统停顺控 |  | int32
N2DCS.EHOILSYS_SEQSPAUX | 13793 | EH油系统停顺控辅助点 |  | digital
N2DCS.EHOILSYS_SEQSPAUX0 | 13794 | EH油系统停顺控启允许条件 |  | int32
N2DCS.EHOILSYS_SEQSPAUX1 | 13795 | EH油系统停顺控第1步完成条件 |  | digital
N2DCS.EHOILSYS_SEQSPAUX2 | 13796 | EH油系统停顺控第2步完成条件 |  | digital
N2DCS.EHOILSYS_SEQSPLP | 13797 | EH油系统停顺控第3步完成条件 |  | digital
N2DCS.EHOILSYS_SEQST | 13798 | EH油系统启顺控 |  | int32
N2DCS.EHOILSYS_SEQSTAUX | 13799 | EH油系统启顺控辅助点 |  | digital
N2DCS.EHOILSYS_SEQSTAUX0 | 13800 | EH油系统启顺控启允许条件 |  | int32
N2DCS.EHOILSYS_SEQSTAUX1 | 13801 | EH油系统启顺控第1步完成条件 |  | digital
N2DCS.EHOILSYS_SEQSTAUX2 | 13802 | EH油系统启顺控第2步完成条件 |  | digital
N2DCS.EHOILSYS_SEQSTAUX3 | 13803 | 第3步成功完成条件 |  | int32
N2DCS.EHOILSYS_SEQSTLP | 13804 | EH油系统启顺控状态 |  | digital
N2DCS.EHOILSYS_SEQSTOKLP | 13805 | EH油系统启顺控第3步完成条件 |  | digital
N2DCS.JACKOILP_BYLP | 13806 | 顶轴油泵 |  | int32
N2DCS.LUBOILEGF_BYLP | 13807 | #3机润滑油风机 |  | digital
N2DCS.LUBOILHTR_BYLP | 13808 | #3机润滑油箱电加热器 |  | digital
N2DCS.LUBWTINPREPMPA_BYLP | 13809 | #3循环水泵冷却水加压泵 |  | digital
N2DCS.ROTFLTRA_SEQST | 13810 | #1旋转滤网冲洗顺控 |  | digital
N2DCS.ROTFLTRA_SEQSTAUX | 13811 | #1旋转滤网冲洗顺控辅助点 |  | digital
N2DCS.ROTFLTRA_SEQSTLP | 13812 | #1旋转滤网冲洗顺控状态 |  | digital
N2DCS.TURBDRNALLCP_LP1 | 13813 | #3机本体疏水阀组1关闭状态 |  | digital
N2DCS.TURBDRNALLCP_LP2 | 13814 | #3机本体疏水阀组2关闭状态 |  | digital
N2DCS.TURBDRNALLOP_LP1 | 13815 | #3机本体疏水阀组1打开状态 |  | digital
N2DCS.TURBDRNALLOP_LP2 | 13816 | #3机本体疏水阀组2打开状态 |  | digital
N2DCS.TURBOILSYS_SEQST | 13817 | #3机润滑油系统启顺控 |  | digital
N2DCS.TURBOILSYS_SEQSTAUX | 13818 | #3机润滑油系统启顺控辅助点 |  | digital
N2DCS.TURBOILSYS_SEQSTAUX0 | 13819 | #3机润滑油系统启顺控启允许条件 |  | digital
N2DCS.TURBOILSYS_SEQSTAUX1 | 13820 | 润滑油系统启顺控第1步完成条件 |  | digital
N2DCS.TURBOILSYS_SEQSTAUX2 | 13821 | 润滑油系统启顺控第2步完成条件 |  | digital
N2DCS.TURBOILSYS_SEQSTAUX3 | 13822 | 润滑油系统启顺控第3步完成条件 |  | digital
N2DCS.TURBOILSYS_SEQSTAUX4 | 13823 | 润滑油系统启顺控第4步完成条件 |  | digital
N2DCS.TURBOILSYS_SEQSTAUX5 | 13824 | 润滑油系统启顺控第5步完成条件 |  | digital
N2DCS.TURBOILSYS_SEQSTLP | 13825 | #3机润滑油系统启顺控状态 |  | digital
N2DCS.TURBOILSYS_SEQSTOKLP | 13826 | 润滑油系统启顺控第6步完成条件 |  | digital
N2DCS.VACM_SEQSP | 13827 | Ovation Control Builder |  | int32
N2DCS.VACMPMP_BYLP | 13828 | #3机真空泵 |  | digital
N2DCS.VACMPMPA_PMTLP | 13829 | #1真空泵启允许条件 |  | digital
N2DCS.VACMPMPA_SEQSP | 13830 | #1真空泵停顺控 |  | int32
N2DCS.VACMPMPA_SEQSPAUX | 13831 | #1真空泵停顺控辅助点 |  | digital
N2DCS.VACMPMPA_SEQSPAUX1 | 13832 | #1真空泵停顺控第1步完成条件 |  | digital
N2DCS.VACMPMPA_SEQSPAUX2 | 13833 | #1真空泵停顺控第2步完成条件 |  | digital
N2DCS.VACMPMPA_SEQSPAUX3 | 13834 | 第3步成功完成条件 |  | int32
N2DCS.VACMPMPA_SEQSPLP | 13835 | #1真空泵停顺控状态 |  | digital
N2DCS.VACMPMPA_SEQST | 13836 | #1真空泵启顺控 |  | int32
N2DCS.VACMPMPA_SEQSTAUX | 13837 | #1真空泵启顺控辅助点 |  | digital
N2DCS.VACMPMPA_SEQSTAUX0 | 13838 | #1真空泵启顺控启允许条件 |  | int32
N2DCS.VACMPMPA_SEQSTAUX1 | 13839 | #1真空泵启顺控第1步完成条件 |  | digital
N2DCS.VACMPMPA_SEQSTAUX2 | 13840 | #1真空泵启顺控第2步完成条件 |  | digital
N2DCS.VACMPMPA_SEQSTAUX3 | 13841 | #1真空泵启顺控第3步完成条件 |  | digital
N2DCS.VACMPMPA_SEQSTLP | 13842 | #1真空泵启顺控状态 |  | digital
N2DCS.VACMPMPA_TRIP | 13843 | #1真空泵跳闸条件 |  | int32
N2DCS.VACMPMPA_TRIPTAG | 13844 | #1真空泵跳闸条件解除信号 |  | digital
N2DCS.VACMSYS_SEQSP | 13845 | 抽真空系统停顺控 |  | int32
N2DCS.VACMSYS_SEQSPAUX | 13846 | 抽真空系统停顺控辅助点 |  | digital
N2DCS.VACMSYS_SEQSPLP | 13847 | 抽真空系统停顺控状态 |  | digital
N2DCS.VACMSYS_SEQST | 13848 | 抽真空系统启顺控 |  | int32
N2DCS.VACMSYS_SEQSTAUX | 13849 | 抽真空系统启顺控辅助点 |  | digital
N2DCS.VACMSYS_SEQSTAUX0 | 13850 | 抽真空系统启顺控启允许条件 |  | int32
N2DCS.VACMSYS_SEQSTAUX1 | 13851 | 抽真空系统启顺控第1步完成条件 |  | digital
N2DCS.VACMSYS_SEQSTAUX2 | 13852 | 抽真空系统启顺控第2步完成条件 |  | digital
N2DCS.VACMSYS_SEQSTAUX3 | 13853 | 抽真空系统启顺控第3步完成条件 |  | digital
N2DCS.VACMSYS_SEQSTAUX4 | 13854 | 抽真空系统启顺控第4步完成条件 |  | digital
N2DCS.VACMSYS_SEQSTAUX5 | 13855 | 抽真空系统启顺控第5步完成条件 |  | digital
N2DCS.VACMSYS_SEQSTAUX6 | 13856 | 第6步成功完成条件 |  | int32
N2DCS.VACMSYS_SEQSTLP | 13857 | 抽真空系统启顺控状态 |  | digital
N2DCS.20MA101AP002_LP | 13858 | #2EH油泵 |  | int32
N2DCS.20MA101AP012_LP | 13859 | #2EH油循环油泵 |  | int32
N2DCS.20MAJ22AA001_LP | 13860 | #3机#2真空泵进口气动门2 |  | digital
N2DCS.20MAJ22AA007_LP | 13861 | #2真空泵汽水分离器补水电磁阀 |  | digital
N2DCS.20MAJ22AA011_LP | 13862 | #3机#2真空泵进口气动门1 |  | digital
N2DCS.20MAJ22AP001_LP | 13863 | #3机#2真空泵 |  | digital
N2DCS.20MAV10AH003_LP | 13864 | #3机润滑油箱#3电加热器 |  | digital
N2DCS.20MAV10AH004_LP | 13865 | #3机润滑油箱#4电加热器 |  | digital
N2DCS.20MAV21AA321_LP | 13866 | #3机润滑油泵出口试验电磁阀 |  | digital
N2DCS.20MAV21AP022_LP | 13867 | #3机#2润滑油泵 |  | digital
N2DCS.20MAV24AP001_LP | 13868 | #3机润滑油应急油泵 |  | digital
N2DCS.20MAV32AP001_LP | 13869 | #3机#2顶轴油泵 |  | digital
N2DCS.20MAV42AA322_LP | 13870 | #3机润滑油母管试验电磁阀1 |  | digital
N2DCS.20MAV42AA329_LP | 13871 | #3机润滑油母管试验电磁阀2 |  | digital
N2DCS.20MAV82AN002_LP | 13872 | #3机#2润滑油风机 |  | digital
N2DCS.20MAX01AP002_LP | 13873 | #3机#2EH油泵 |  | digital
N2DCS.20MAX01AP012_LP | 13874 | #3机#2EH油循环泵 |  | digital
N2DCS.20PAA12AA001_LP | 13875 | #2旋转滤网冲洗水电动门 |  | digital
N2DCS.20PAB10AA001_LP | 13876 | 循环水母管电动联络门 |  | digital
N2DCS.20PAB11AA001H_LP | 13877 | #3循环水泵出口门 |  | int32
N2DCS.20PAB12AA002_LP | 13878 | #4循环水泵出口液控蝶阀 |  | digital
N2DCS.20PAB12AT001_LP | 13879 | #2旋转滤网 |  | digital
N2DCS.20PAB31AA002_LP | 13880 | 循环水母管至循泵冷却水电动门 |  | digital
N2DCS.20PAB41AA001_LP | 13881 | #4循环水泵出口门 |  | int32
N2DCS.20PAB51AP001_LP | 13882 | #4循环水泵冷却水#1加压泵 |  | digital
N2DCS.20PAB52AP001_LP | 13883 | #4循环水泵冷却水#2加压泵 |  | digital
N2DCS.20PAB62AA001_LP | 13884 | 生活水至#4循环水泵冷却水电磁阀 |  | digital
N2DCS.20PAC12AP001_LP | 13885 | #4循环水泵 |  | int32
N2DCS.20PAC12AP001H_LP | 13886 | #4循环水泵高速 |  | int32
N2DCS.20PAC12AP001L_LP | 13887 | #4循环水泵低速 |  | int32
N2DCS.20PAR01AA001_LP | 13888 | 净水站至#2冷却塔进口电动门 |  | digital
N2DCS.20PAR01AA002MODE | 13889 | #2冷却塔进水流量电动调节阀 |  | digital
N2DCS.20PSA02AP001_LP | 13890 | #2冷却塔排水池#2排污泵 |  | digital
N2DCS.CIRPMPB_STPMTLP | 13891 | #4循环水泵启允许条件 |  | digital
N2DCS.CIRPMPB_TRIP | 13892 | #4循环水泵跳闸条件 |  | digital
N2DCS.CIRPMPB_TRIPTAG | 13893 | #4循环水泵跳闸条件解除信号 |  | digital
N2DCS.CIRWTRPMPB_SEQSP | 13894 | #4循环水泵停顺控 |  | int32
N2DCS.CIRWTRPMPB_SEQSPAUX | 13895 | #4循环水泵停顺控辅助点 |  | digital
N2DCS.CIRWTRPMPB_SEQSPAUX1 | 13896 | #4循环水泵停顺控第1步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSPAUX2 | 13897 | #4循环水泵停顺控第2步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSPAUX3 | 13898 | #4循环水泵停顺控第3步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSPAUX4 | 13899 | #4循环水泵停顺控第4步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSPAUX5 | 13900 | 第5步成功完成条件 |  | int32
N2DCS.CIRWTRPMPB_SEQSPLP | 13901 | #4循环水泵停顺控状态 |  | digital
N2DCS.CIRWTRPMPB_SEQST | 13902 | #4循环水泵启顺控 |  | int32
N2DCS.CIRWTRPMPB_SEQSTAUX | 13903 | #4循环水泵启顺控辅助点 |  | digital
N2DCS.CIRWTRPMPB_SEQSTAUX0 | 13904 | #4循环水泵启顺控启允许条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSTAUX1 | 13905 | #4循环水泵启顺控第1步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSTAUX2 | 13906 | #4循环水泵启顺控第2步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSTAUX3 | 13907 | #4循环水泵启顺控第3步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSTAUX4 | 13908 | #4循环水泵启顺控第4步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSTAUX5 | 13909 | #4循环水泵启顺控第5步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSTAUX6 | 13910 | #4循环水泵启顺控第6步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSTAUX7 | 13911 | #4循环水泵启顺控第7步完成条件 |  | digital
N2DCS.CIRWTRPMPB_SEQSTLP | 13912 | #4循环水泵启顺控状态 |  | digital
N2DCS.LUBWTINPREPMPB_BYLP | 13913 | #4循环水泵冷却水加压泵 |  | digital
N2DCS.ROTFLTRB_SEQST | 13914 | #2旋转滤网冲洗顺控 |  | digital
N2DCS.ROTFLTRB_SEQSTAUX | 13915 | #2旋转滤网冲洗顺控辅助点 |  | digital
N2DCS.ROTFLTRB_SEQSTLP | 13916 | #2旋转滤网冲洗顺控状态 |  | digital
N2DCS.VACMPMPAB_PMTLP | 13917 | #2真空泵启允许条件 |  | int32
N2DCS.VACMPMPB_PMTLP | 13918 | #2真空泵启动允许条件 |  | int32
N2DCS.VACMPMPB_SEQSP | 13919 | #2真空泵停顺控 |  | int32
N2DCS.VACMPMPB_SEQSPAUX | 13920 | #2真空泵停顺控辅助点 |  | digital
N2DCS.VACMPMPB_SEQSPAUX1 | 13921 | #2真空泵停顺控第1步完成条件 |  | digital
N2DCS.VACMPMPB_SEQSPAUX2 | 13922 | #2真空泵停顺控第2步完成条件 |  | digital
N2DCS.VACMPMPB_SEQSPAUX3 | 13923 | 第3步成功完成条件 |  | int32
N2DCS.VACMPMPB_SEQSPLP | 13924 | #2真空泵停顺控状态 |  | digital
N2DCS.VACMPMPB_SEQST | 13925 | #2真空泵启顺控 |  | int32
N2DCS.VACMPMPB_SEQSTAUX | 13926 | #2真空泵启顺控辅助点 |  | digital
N2DCS.VACMPMPB_SEQSTAUX0 | 13927 | #2真空泵启顺控启允许条件 |  | int32
N2DCS.VACMPMPB_SEQSTAUX1 | 13928 | #2真空泵启顺控第1步完成条件 |  | digital
N2DCS.VACMPMPB_SEQSTAUX2 | 13929 | #2真空泵启顺控第2步完成条件 |  | digital
N2DCS.VACMPMPB_SEQSTAUX3 | 13930 | #2真空泵启顺控第3步完成条件 |  | digital
N2DCS.VACMPMPB_SEQSTLP | 13931 | #2真空泵启顺控状态 |  | digital
N2DCS.VACMPMPB_TRIP | 13932 | #2真空泵跳闸条件 |  | int32
N2DCS.VACMPMPB_TRIPTAG | 13933 | #2真空泵跳闸条件解除信号 |  | digital
N2DCS.20HAD74AA401_LP | 13934 | #3炉低压蒸发器排污至定排电动门 |  | digital
N2DCS.20HAD75AA001_LP | 13935 | #3炉低压汽包连排电动门 |  | digital
N2DCS.20HAD75AA101_MODE | 13936 | #3炉低压汽包连排电动调节门 |  | digital
N2DCS.20HAD76AA001_LP | 13937 | #3炉低压汽包启动放水电动门 |  | digital
N2DCS.20HAD76AA002_LP | 13938 | #2炉低压汽包启动放水电动调节门 |  | digital
N2DCS.20HAH70AA502_LP | 13939 | #3炉低压饱和蒸汽放空电动门 |  | digital
N2DCS.20HAJ80AA502_LP | 13940 | 一级再热器进口集箱放空门 |  | digital
N2DCS.20HAJ80AA504_LP | 13941 | 一级再热器出口集箱放空电动门 |  | digital
N2DCS.20HAJ81AA402_LP | 13942 | #3炉一级再热器连接管疏水电动门 |  | digital
N2DCS.20HAJ81AA404_LP | 13943 | #3炉二级再热器进口管疏水电动门 |  | digital
N2DCS.20LAA70AA501_LP | 13944 | #3炉除氧头放空电动门 |  | digital
N2DCS.20LAB70AA101_MODE | 13945 | #3炉低压给水调节阀 |  | digital
N2DCS.20LAF80AA002_LP | 13946 | #3炉一级再热器减温水电动门 |  | digital
N2DCS.20LAF80AA004_LP | 13947 | #3炉二级再热器减温水电动门 |  | digital
N2DCS.20LAF80AA101_MODE | 13948 | #3炉一级再热器减温水气动调节阀 |  | digital
N2DCS.20LAF80AA102_MODE | 13949 | #3炉二级再热器减温水气动调节阀 |  | digital
N2DCS.20LBA70AA402_LP | 13950 | #3炉低压过热器出口疏水电动门 |  | digital
N2DCS.20LBA70AA502_LP | 13951 | #3炉低压过热器启动排汽电动门 |  | digital
N2DCS.20LBB80AA502_LP | 13952 | #3炉热再主蒸汽启动排气电动门 |  | digital
N2DCS.20LBC80AA402_LP | 13953 | #3炉冷再进口疏水罐疏水电动门 |  | digital
N2DCS.20LBG70AA002_LP | 13954 | 辅汽至#3炉除氧头电动门 |  | digital
N2DCS.20LBG70AA101_MODE | 13955 | 辅汽至#3炉除氧头气动调节阀 |  | digital
N2DCS.20LCC70AA502_LP | 13956 | #3炉低压省煤器放空电动门 |  | digital
N2DCS.20LCC71AA101_MODE | 13957 | 低压省煤器再循环泵出口气动调阀 |  | digital
N2DCS.20LCC72AA003_LP | 13958 | 低压省煤器#1再循环泵出口电动门 |  | digital
N2DCS.20LCC72AP001_LP | 13959 | #3炉低压省煤器#1再循环泵 |  | digital
N2DCS.20LCC72AP001DY_LP | 13960 | 低压省煤器#1再循环泵电机电加热 |  | digital
N2DCS.20LCC73AA003_LP | 13961 | 低压省煤器#2再循环泵出口电动门 |  | digital
N2DCS.20LCC73AP001_LP | 13962 | #3炉低压省煤器#2再循环泵 |  | digital
N2DCS.20LCC73AP001DY_LP | 13963 | 低压省煤器#1再循环泵电机电加热 |  | digital
N2DCS.20LCQ74AA101_MODE | 13964 | #3炉连排至定排气动调节阀 |  | digital
N2DCS.LPDRUMCP_LP | 13965 | #3炉低压汽包压力 |  | digital
N2DCS.LPDRUMCTD_LP | 13966 | #3炉低压汽包下壁温 |  | digital
N2DCS.LPDRUMCTU_LP | 13967 | #3炉低压汽包上壁温 |  | digital
N2DCS.LPDRUMLVL_DIFLP | 13968 | Ovation Control Builder |  | int32
N2DCS.LPDRUMLVL_LP | 13969 | #3炉低压汽包液位 |  | digital
N2DCS.LPDSTCF_LP | 13970 | #3炉低压主蒸汽流量 |  | digital
N2DCS.LPDSTCP_LP | 13971 | #3炉低压主蒸汽压力 |  | digital
N2DCS.LPDSTCT_LP | 13972 | #3炉低压主蒸汽温度 |  | digital
N2DCS.LPDWTCF_LP | 13973 | #3炉低压汽包给水流量 |  | digital
N2DCS.LPDWTCT_LP | 13974 | #3炉低压汽包给水温度 |  | digital
N2DCS.LPECON_SEQST | 13975 | 低压省煤器再循环系统启顺控 |  | digital
N2DCS.LPECON_SEQSTAUX | 13976 | 低省再循环系统启顺控辅助点 |  | digital
N2DCS.LPECON_SEQSTLP | 13977 | 低压省煤器再循环系统启顺控状态 |  | digital
N2DCS.LPECONP_BYLP | 13978 | 低压省煤器再循环泵 |  | digital
N2DCS.LPECONPA_SEQSP | 13979 | #1低省再循环泵停顺控 |  | digital
N2DCS.LPECONPA_SEQSPAUX | 13980 | #1低省再循环泵停顺控辅助点 |  | digital
N2DCS.LPECONPA_SEQSPLP | 13981 | #1低省再循环泵停顺控状态 |  | digital
N2DCS.LPECONPA_SEQST | 13982 | #1低省再循环泵启顺控 |  | digital
N2DCS.LPECONPA_SEQSTAUX | 13983 | #1低省再循环泵启顺控辅助点 |  | digital
N2DCS.LPECONPA_SEQSTLP | 13984 | #1低省再循环泵启顺控状态 |  | digital
N2DCS.LPECONPA_STRPEM_LP | 13985 | #1低省再循环泵启允许条件 |  | digital
N2DCS.LPECONPA_TRIP | 13986 | #1低省再循环泵跳闸条件 |  | digital
N2DCS.LPECONPA_TRIPTAG | 13987 | #1低省再循环泵跳闸条件解除 |  | digital
N2DCS.LPECONPB_SEQSP | 13988 | #2低省再循环泵停顺控 |  | digital
N2DCS.LPECONPB_SEQSPAUX | 13989 | #2低省再循环泵停顺控辅助点 |  | digital
N2DCS.LPECONPB_SEQSPLP | 13990 | #2低省再循环泵停顺控状态 |  | digital
N2DCS.LPECONPB_SEQST | 13991 | #2低省再循环泵启顺控 |  | digital
N2DCS.LPECONPB_SEQSTAUX | 13992 | #2低省再循环泵启顺控辅助点 |  | digital
N2DCS.LPECONPB_SEQSTLP | 13993 | #2低省再循环泵启顺控状态 |  | digital
N2DCS.LPECONPB_STRPEM_LP | 13994 | #2低省再循环泵启允许条件 |  | digital
N2DCS.LPECONPB_TRIP | 13995 | #2低省再循环泵跳闸条件 |  | digital
N2DCS.LPECONPB_TRIPTAG | 13996 | #2低省再循环泵跳闸条件解除 |  | digital
N2DCS.LPFW_SEQST | 13997 | 低压汽包上水顺控 |  | int32
N2DCS.LPFW_SEQSTAUX | 13998 | 低压汽包上水顺控辅助点 |  | digital
N2DCS.LPFW_SEQSTAUX0 | 13999 | 低压汽包上水顺控启允许条件 |  | digital
N2DCS.LPFW_SEQSTAUX1 | 14000 | 低压汽包上水顺控第1步完成条件 |  | digital
N2DCS.LPFW_SEQSTAUX2 | 14001 | 低压汽包上水顺控第2步完成条件 |  | digital
N2DCS.LPFW_SEQSTAUX3 | 14002 | 低压汽包上水顺控第3步完成条件 |  | digital
N2DCS.LPFW_SEQSTAUX5 | 14003 | 低压汽包上水顺控第5步完成条件 |  | digital
N2DCS.LPFW_SEQSTLP | 14004 | 低压汽包上水顺控状态 |  | digital
N2DCS.LPMS_SEQST | 14005 | 低压主蒸汽升温升压顺控 |  | int32
N2DCS.LPMS_SEQSTAUX | 14006 | 低压主蒸汽升温升压顺控辅助点 |  | digital
N2DCS.LPMS_SEQSTAUX4 | 14007 | 低压主汽升温升压顺控第4步完成 |  | digital
N2DCS.LPMS_SEQSTLP | 14008 | 低压主蒸汽升温升压顺控状态 |  | digital
N2DCS.RH2INSTCT_LP | 14009 | #3炉一级再热器减温器后温度 |  | digital
N2DCS.RH2OUTSTCP_LP | 14010 | #3炉一级再热器减温器后压力 |  | digital
N2DCS.RH2OUTSTCT_LP | 14011 | #3炉热再主蒸汽温度 |  | digital
N2DCS.SEQTEST_SEQST | 14012 | Ovation Control Builder |  | int32
N2DCS.SEQTEST_SEQSTAUX | 14013 | Ovation Control Builder |  | int32
N2DCS.SEQTEST_SEQSTLP | 14014 | Ovation Control Builder |  | int32
N2DCS.LPFW_SEQSTAUX4 | 14015 | 低压汽包上水顺控第4步完成条件 |  | digital
N2DCS.20HAD84AA401_LP | 14016 | #3炉中压蒸发器排污至定排电动门 |  | digital
N2DCS.20HAD85AA001_LP | 14017 | #3炉中压汽包连排电动门 |  | digital
N2DCS.20HAD85AA101_MODE | 14018 | #3炉中压汽包连排气动调节阀 |  | digital
N2DCS.20HAD86AA001_LP | 14019 | #3炉中压汽包启动放水电动门 |  | digital
N2DCS.20HAD86AA002_LP | 14020 | #3炉中压汽包启动放水电动调节门 |  | digital
N2DCS.20HAH80AA502_LP | 14021 | #3炉中压饱和蒸汽放空电动门 |  | digital
N2DCS.20HNE70AA001_LP | 14022 | #3炉烟囱出口挡板 |  | digital
N2DCS.20LAB81AA001_LP | 14023 | #3炉#1中压给水泵出口电动门 |  | digital
N2DCS.20LAB81AP001_LP | 14024 | #3炉#1中压给水泵 |  | digital
N2DCS.20LAB83AA101_MODE | 14025 | #3炉中压给水气动调节阀 |  | digital
N2DCS.20LAB91AA001_LP | 14026 | #3炉#1高压给水泵出口电动门 |  | digital
N2DCS.20LAB91AP001_LP | 14027 | #3炉#1高压给水泵 |  | digital
N2DCS.20LAC91AP001_LP | 14028 | #1高压给水泵 |  | int32
N2DCS.20LBA80AA001_LP | 14029 | #3炉中压主蒸汽电动门 |  | digital
N2DCS.20LBA80AA402_LP | 14030 | #3炉中压主蒸汽疏水至定排电动门 |  | digital
N2DCS.20LBA80AA502_LP | 14031 | #3炉中压主蒸汽启动排汽电动门 |  | digital
N2DCS.20XAV91GH001_LP | 14032 | #1高压给水泵稀油站 |  | int32
N2DCS.20XAV91GH001AP_BYLP | 14033 | #1高压给水泵稀油站油泵 |  | digital
N2DCS.20XAV91GH001AP1_LP | 14034 | #3炉#1稀油站#1润滑油泵 |  | digital
N2DCS.20XAV91GH001AP2_LP | 14035 | #3炉#1稀油站#2润滑油泵 |  | digital
N2DCS.20XAV91GH001HT_LP | 14036 | #3炉#1稀油站电加热器 |  | digital
N2DCS.HPFWPA_SEQSP | 14037 | #1高压给水泵停顺控 |  | int32
N2DCS.HPFWPA_SEQSPAUX | 14038 | #1高压给水泵停顺控辅助点 |  | digital
N2DCS.HPFWPA_SEQSPAUX0 | 14039 | #1高压给水泵停顺控启允许条件 |  | int32
N2DCS.HPFWPA_SEQSPLP | 14040 | #1高压给水泵停顺控状态 |  | digital
N2DCS.HPFWPA_SEQST | 14041 | #1高压给水泵启顺控 |  | int32
N2DCS.HPFWPA_SEQSTAUX | 14042 | #1高压给水泵启顺控辅助点 |  | digital
N2DCS.HPFWPA_SEQSTLP | 14043 | #1高压给水泵启顺控状态 |  | digital
N2DCS.HPFWPA_STRPEM_LP | 14044 | #1高压给水泵启允许条件 |  | digital
N2DCS.HPFWPA_TRIP | 14045 | #1高压给水泵跳闸条件 |  | int32
N2DCS.HPFWPA_TRIPTAG | 14046 | #1高压给水泵跳闸条件解除信号 |  | digital
N2DCS.HPFWPATCUT | 14047 | #1高给泵超温保护报警解除信号 |  | digital
N2DCS.IPDRUMCP_LP | 14048 | #3炉中压汽包压力 |  | digital
N2DCS.IPDRUMCTD_LP | 14049 | #3炉中压汽包下壁温 |  | digital
N2DCS.IPDRUMCTU_LP | 14050 | #3炉中压汽包上壁温 |  | digital
N2DCS.IPDRUMLVL_DIFLP | 14051 | 中压汽包液位偏差 |  | int32
N2DCS.IPDRUMLVL_LP | 14052 | #3炉中压汽包液位（计算后） |  | digital
N2DCS.IPDSTCF_LP | 14053 | #3炉中压主蒸汽流量 |  | digital
N2DCS.IPDSTCP_LP | 14054 | #3炉中压主蒸汽压力 |  | digital
N2DCS.IPDSTCT_LP | 14055 | #3炉中压主蒸汽温度 |  | digital
N2DCS.IPDWTCF_LP | 14056 | #3炉中压给水流量（计算后） |  | digital
N2DCS.IPDWTCT_LP | 14057 | #3炉中压给水温度 |  | digital
N2DCS.IPFW_SEQST | 14058 | 中压汽包上水顺控 |  | int32
N2DCS.IPFW_SEQSTAUX | 14059 | 中压汽包上水顺控辅助点 |  | digital
N2DCS.IPFW_SEQSTAUX0 | 14060 | 中压汽包上水顺控启允许条件 |  | int32
N2DCS.IPFW_SEQSTAUX1 | 14061 | 中压汽包上水顺控第1步完成条件 |  | digital
N2DCS.IPFW_SEQSTAUX2 | 14062 | 中压汽包上水顺控第2步完成条件 |  | digital
N2DCS.IPFW_SEQSTAUX3 | 14063 | 中压汽包上水顺控第3步完成条件 |  | digital
N2DCS.IPFW_SEQSTAUX6 | 14064 | 第6步成功完成条件 |  | int32
N2DCS.IPFW_SEQSTLP | 14065 | 中压汽包上水顺控状态 |  | digital
N2DCS.IPFWP_BYLP | 14066 | #3炉中压给水泵备用 |  | digital
N2DCS.IPFWPA_SEQSP | 14067 | #1中压给水泵停顺控 |  | int32
N2DCS.IPFWPA_SEQSPAUX | 14068 | #1中压给水泵停顺控辅助点 |  | digital
N2DCS.IPFWPA_SEQSPAUX0 | 14069 | #1中压给水泵停顺控启允许条件 |  | int32
N2DCS.IPFWPA_SEQSPLP | 14070 | #1中压给水泵停顺控状态 |  | digital
N2DCS.IPFWPA_SEQST | 14071 | #1中压给水泵启顺控 |  | int32
N2DCS.IPFWPA_SEQSTAUX | 14072 | #1中压给水泵启顺控辅助点 |  | digital
N2DCS.IPFWPA_SEQSTLP | 14073 | #1中压给水泵启顺控状态 |  | digital
N2DCS.IPFWPA_STRPEM_LP | 14074 | #1中压给水泵启顺控启允许条件 |  | digital
N2DCS.IPFWPA_TRIP | 14075 | #1中压给水泵跳闸条件 |  | int32
N2DCS.IPFWPA_TRIPTAG | 14076 | #1中压给水泵跳闸条件解除信号 |  | digital
N2DCS.IPFWPATCUT | 14077 | #1中给泵超温保护报警解除信号 |  | digital
N2DCS.IPMS_SEQST | 14078 | 中压主蒸汽升温升压顺控 |  | int32
N2DCS.IPMS_SEQSTAUX | 14079 | 中压主蒸汽升温升压顺控辅助点 |  | digital
N2DCS.IPMS_SEQSTAUX2 | 14080 | 中压主汽升温升压顺控第2步完成 |  | digital
N2DCS.IPMS_SEQSTAUX3 | 14081 | 第3步成功完成条件 |  | int32
N2DCS.IPMS_SEQSTAUX6 | 14082 | 中压主汽升温升压顺控第6步完成 |  | digital
N2DCS.IPMS_SEQSTAUX7 | 14083 | 中压主汽升温升压顺控第7步完成 |  | digital
N2DCS.IPMS_SEQSTLP | 14084 | 中压主蒸汽升温升压顺控状态 |  | digital
N2DCS.LPMS_SEQSTAUX2 | 14085 | 第2步成功完成条件 |  | int32
N2DCS.HPFWPA_SEQBPST | 14086 | #1高压给水泵变频启顺控 |  | digital
N2DCS.HPFWPA_SEQBPSTAUX | 14087 | #1高压给水泵变频启顺控辅助点 |  | digital
N2DCS.HPFWPA_SEQBPSTAUX0 | 14088 | #1高给泵变频启顺控启允许条件 |  | digital
N2DCS.HPFWPA_SEQBPSTAUX1 | 14089 | #1高给泵变频启顺控1步完成条件 |  | digital
N2DCS.HPFWPA_SEQBPSTAUX2 | 14090 | #1高给泵变频启顺控2步完成条件 |  | digital
N2DCS.HPFWPA_SEQBPSTAUX3 | 14091 | #1高给泵变频启顺控3步完成条件 |  | digital
N2DCS.HPFWPA_SEQBPSTAUX4 | 14092 | #1高给泵变频启顺控4步完成条件 |  | digital
N2DCS.HPFWPA_SEQBPSTLP | 14093 | #1高压给水泵变频启顺控系统 |  | digital
N2DCS.HPFWPA_SEQSPAUX1 | 14094 | #1高压给水泵停顺控1步完成条件 |  | digital
N2DCS.HPFWPA_SEQSPAUX2 | 14095 | #1高压给水泵停顺控2步完成条件 |  | digital
N2DCS.HPFWPA_SEQSTAUX0 | 14096 | #1高给泵工频启顺控启允许条件 |  | digital
N2DCS.HPFWPA_SEQSTAUX1 | 14097 | #1高给泵工频启顺控1步完成条件 |  | digital
N2DCS.HPFWPA_SEQSTAUX2 | 14098 | #1高给泵工频启顺控2步完成条件 |  | digital
N2DCS.HPFWPA_SEQSTAUX3 | 14099 | #1高给泵工频启顺控3步完成条件 |  | digital
N2DCS.HPFWPA_SEQSTAUX4 | 14100 | #1高给泵工频启顺控4步完成条件 |  | digital
N2DCS.IPFW_SEQSTAUX4 | 14101 | 中压汽包上水顺控第4步完成条件 |  | digital
N2DCS.IPFW_SEQSTAUX5 | 14102 | 中压汽包上水顺控第5步完成条件 |  | digital
N2DCS.IPMS_SEQSTAUX4 | 14103 | 中压主汽升温升压顺控第4步完成 |  | digital
N2DCS.IPMS_SEQSTAUX8 | 14104 | 中压主汽升温升压顺控第8步完成 |  | digital
N2DCS.20HAC90AA502_LP | 14105 | #3炉高压省煤器放空电动门 |  | digital
N2DCS.20HAD91AA405_LP | 14106 | #3炉高压蒸发器排污至定排电动门 |  | digital
N2DCS.20HAD95AA001_LP | 14107 | #3炉高压汽包连排电动门 |  | digital
N2DCS.20HAD95AA101_MODE | 14108 | #3炉高压汽包连排气动调节阀 |  | digital
N2DCS.20HAD96AA001_LP | 14109 | #3炉高压汽包启动放水电动门 |  | digital
N2DCS.20HAD96AA002_LP | 14110 | #3炉高压汽包启动放水电动调节门 |  | digital
N2DCS.20HAH90AA402_LP | 14111 | 高压一级过热器出口疏水电动门 |  | digital
N2DCS.20HAH90AA412_LP | 14112 | 高压二级过热器出口疏水电动门 |  | int32
N2DCS.20HAH90AA502_LP | 14113 | #3炉高压饱和蒸汽放空电动门 |  | digital
N2DCS.20HAH90AA504_LP | 14114 | 高压二级过热器出口放空电动门 |  | digital
N2DCS.20LAB82AA001_LP | 14115 | #3炉#2中压给水泵出口电动门 |  | digital
N2DCS.20LAB82AP001_LP | 14116 | #3炉#2中压给水泵 |  | digital
N2DCS.20LAB90AA101_MODE | 14117 | #3炉高压给水气动调节阀 |  | digital
N2DCS.20LAB92AA001_LP | 14118 | #3炉#2高压给水泵出口电动门 |  | digital
N2DCS.20LAB92AP001_LP | 14119 | #3炉#2高压给水泵 |  | digital
N2DCS.20LAC91GX0001_LP | 14120 | 高压给水泵变频器 |  | digital
N2DCS.20LAC91GX0001_MODE | 14121 | 高压给水泵变频器频率控制 |  | digital
N2DCS.20LAC92AP001_LP | 14122 | #2高压给水泵 |  | int32
N2DCS.20LAE90AA002_LP | 14123 | #3炉高压二级过热器减温水电动门 |  | digital
N2DCS.20LAE90AA004_LP | 14124 | #3炉高压主蒸汽减温水电动门 |  | digital
N2DCS.20LAE90AA101_MODE | 14125 | 高压二级过热器减温水气动调节阀 |  | digital
N2DCS.20LAE90AA102_MODE | 14126 | #3炉高压主蒸汽减温水气动调节阀 |  | digital
N2DCS.20LAE91AA101_MODE | 14127 | #3炉高压省煤器旁路气动调节阀 |  | digital
N2DCS.20LBA90AA502_LP | 14128 | #3炉高压主蒸汽启动排汽电动门 |  | digital
N2DCS.20LBG90AA001_LP | 14129 | 辅汽至#3炉高压蒸发器电动门 |  | digital
N2DCS.20XAV92GH001_LP | 14130 | #2高压给水泵稀油站 |  | int32
N2DCS.20XAV92GH001AP_BYLP | 14131 | #2高压给水泵稀油站油泵 |  | digital
N2DCS.20XAV92GH001AP1_LP | 14132 | #3炉#2稀油站#1润滑油泵 |  | digital
N2DCS.20XAV92GH001AP2_LP | 14133 | #3炉#2稀油站#2润滑油泵 |  | digital
N2DCS.20XAV92GH001HT_LP | 14134 | #3炉#2稀油站电加热器 |  | digital
N2DCS.GYSJGRQJKWD_LP | 14135 | #3炉高压三级过热器进口温度 |  | digital
N2DCS.HPDRUMCP_LP | 14136 | #3炉高压汽包压力 |  | digital
N2DCS.HPDRUMCTD_LP | 14137 | #3炉高压汽包下外壁温 |  | digital
N2DCS.HPDRUMCTU_LP | 14138 | #3炉高压汽包上外壁温 |  | digital
N2DCS.HPDRUMCTU2_LP | 14139 | #3炉高压汽包上内壁温 |  | digital
N2DCS.HPDRUMLVL_DIFLP | 14140 | 高压汽包液位偏差 |  | int32
N2DCS.HPDRUMLVL_LP | 14141 | #3炉高压汽包液位 |  | digital
N2DCS.HPDSTCF_LP | 14142 | #3炉高压主蒸汽流量（计算后） |  | digital
N2DCS.HPDSTCP_LP | 14143 | #3炉高压主蒸汽压力 |  | digital
N2DCS.HPDSTCT_LP | 14144 | #3炉高压主蒸汽温度 |  | digital
N2DCS.HPDWTCF_LP | 14145 | #3炉高压给水流量（计算后） |  | digital
N2DCS.HPDWTCT_LP | 14146 | #3炉高压给水温度（计算后） |  | digital
N2DCS.HPFW_SEQST | 14147 | 高压汽包上水顺控 |  | int32
N2DCS.HPFW_SEQSTAUX | 14148 | 高压汽包上水顺控辅助点 |  | digital
N2DCS.HPFW_SEQSTAUX0 | 14149 | 高压汽包上水顺控启允许条件 |  | int32
N2DCS.HPFW_SEQSTAUX1 | 14150 | 高压汽包上水顺控第1步完成条件 |  | digital
N2DCS.HPFW_SEQSTAUX2 | 14151 | 高压汽包上水顺控第2步完成条件 |  | digital
N2DCS.HPFW_SEQSTAUX3 | 14152 | 高压汽包上水顺控第3步完成条件 |  | digital
N2DCS.HPFW_SEQSTAUX6 | 14153 | 高压汽包上水顺控第6步完成条件 |  | digital
N2DCS.HPFW_SEQSTLP | 14154 | 高压汽包上水顺控状态 |  | digital
N2DCS.HPFWP_BYLP | 14155 | #3炉高压给水泵 |  | digital
N2DCS.HPFWPB_SEQSP | 14156 | #2高压给水泵停顺控 |  | int32
N2DCS.HPFWPB_SEQSPAUX | 14157 | #2高压给水泵停顺控辅助点 |  | digital
N2DCS.HPFWPB_SEQSPAUX0 | 14158 | #2高压给水泵停顺控启允许条件 |  | int32
N2DCS.HPFWPB_SEQSPLP | 14159 | #2高压给水泵停顺控状态 |  | digital
N2DCS.HPFWPB_SEQST | 14160 | #2高压给水泵启顺控 |  | int32
N2DCS.HPFWPB_SEQSTAUX | 14161 | #2高压给水泵启顺控辅助点 |  | digital
N2DCS.HPFWPB_SEQSTLP | 14162 | #2高压给水泵启顺控状态 |  | digital
N2DCS.HPFWPB_STRPEM_LP | 14163 | #2高压给水泵启允许条件 |  | digital
N2DCS.HPFWPB_TRIP | 14164 | #2高压给水泵跳闸条件 |  | int32
N2DCS.HPFWPB_TRIPTAG | 14165 | #2高压给水泵跳闸条件解除信号 |  | digital
N2DCS.HPFWPBTCUT | 14166 | #2高给泵超温保护报警解除信号 |  | digital
N2DCS.HPMS_SEQST | 14167 | 高压主蒸汽升温升压顺控 |  | int32
N2DCS.HPMS_SEQSTAUX | 14168 | 高压主蒸汽升温升压顺控辅助点 |  | digital
N2DCS.HPMS_SEQSTAUX1 | 14169 | 高压主蒸汽升温升压顺控1步完成 |  | digital
N2DCS.HPMS_SEQSTAUX2 | 14170 | 高压主蒸汽升温升压顺控2步完成 |  | digital
N2DCS.HPMS_SEQSTAUX3 | 14171 | 高压主蒸汽升温升压顺控3步完成 |  | digital
N2DCS.HPMS_SEQSTAUX4 | 14172 | 高压主蒸汽升温升压顺控4步完成 |  | digital
N2DCS.HPMS_SEQSTLP | 14173 | 高压主蒸汽升温升压顺控状态 |  | digital
N2DCS.IPFWPB_SEQSP | 14174 | #2中压给水泵停顺控 |  | int32
N2DCS.IPFWPB_SEQSPAUX | 14175 | #2中压给水泵停顺控辅助点 |  | digital
N2DCS.IPFWPB_SEQSPAUX0 | 14176 | #2中压给水泵停顺控启允许条件 |  | int32
N2DCS.IPFWPB_SEQSPLP | 14177 | #2中压给水泵停顺控状态 |  | digital
N2DCS.IPFWPB_SEQST | 14178 | #2中压给水泵启顺控 |  | int32
N2DCS.IPFWPB_SEQSTAUX | 14179 | #2中压给水泵启顺控辅助点 |  | digital
N2DCS.IPFWPB_SEQSTLP | 14180 | #2中压给水泵启顺控状态 |  | digital
N2DCS.IPFWPB_STRPEM_LP | 14181 | #2中压给水泵启顺控启允许条件 |  | digital
N2DCS.IPFWPB_TRIP | 14182 | #2中压给水泵跳闸条件 |  | int32
N2DCS.IPFWPB_TRIPTAG | 14183 | #2中压给水泵跳闸条件解除信号 |  | digital
N2DCS.IPFWPBTCUT | 14184 | #2中给泵超温保护报警解除信号 |  | digital
N2DCS.20LBA90AA192_LP | 14185 | #3炉高压主蒸汽出口PCV阀 |  | digital
N2DCS.HPDRUMCT_LP | 14186 | #3炉高压汽包下壁温 |  | digital
N2DCS.HPFW_SEQSTAUX4 | 14187 | 高压汽包上水顺控第4步完成条件 |  | digital
N2DCS.HPFW_SEQSTAUX5 | 14188 | 高压汽包上水顺控第5步完成条件 |  | digital
N2DCS.HPFWPB_SEQBPST | 14189 | #2高压给水泵变频启顺控 |  | digital
N2DCS.HPFWPB_SEQBPSTAUX | 14190 | #2高压给水泵变频启顺控辅助点 |  | digital
N2DCS.HPFWPB_SEQBPSTAUX0 | 14191 | #2高给泵变频启顺控启允许条件 |  | digital
N2DCS.HPFWPB_SEQBPSTAUX1 | 14192 | #2高给泵变频启顺控1步完成条件 |  | digital
N2DCS.HPFWPB_SEQBPSTAUX2 | 14193 | #2高给泵变频启顺控2步完成条件 |  | digital
N2DCS.HPFWPB_SEQBPSTAUX3 | 14194 | #2高给泵变频启顺控3步完成条件 |  | digital
N2DCS.HPFWPB_SEQBPSTAUX4 | 14195 | #2高给泵变频启顺控4步完成条件 |  | digital
N2DCS.HPFWPB_SEQBPSTLP | 14196 | #2高压给水泵变频启顺控系统 |  | digital
N2DCS.HPFWPB_SEQSPAUX1 | 14197 | #2高压给水泵停顺控1步完成条件 |  | digital
N2DCS.HPFWPB_SEQSPAUX2 | 14198 | #2高压给水泵停顺控2步完成条件 |  | digital
N2DCS.HPFWPB_SEQSTAUX0 | 14199 | #2高给泵工频启顺控启允许条件 |  | digital
N2DCS.HPFWPB_SEQSTAUX1 | 14200 | #2高给泵工频启顺控1步完成条件 |  | digital
N2DCS.HPFWPB_SEQSTAUX2 | 14201 | #2高给泵工频启顺控2步完成条件 |  | digital
N2DCS.HPFWPB_SEQSTAUX3 | 14202 | #2高给泵工频启顺控3步完成条件 |  | digital
N2DCS.HPFWPB_SEQSTAUX4 | 14203 | #2高给泵工频启顺控4步完成条件 |  | digital
N2DCS.HPMS_SEQSTAUX5 | 14204 | 高压主蒸汽升温升压顺控5步完成 |  | digital
N2DCS.HRSGTP | 14205 | 余热锅炉保护跳闸条件 |  | int32
N2DCS.20BBA00GS001_LP | 14206 | 6KV 2A段工作电源开关62A01 |  | digital
N2DCS.20BBB00GS002_LP | 14207 | 6KV 2B段备用电源开关62B02 |  | digital
N2DCS.20BFA00GS103_LP | 14208 | 工作PC IIA段至保安段开关42A104 |  | int32
N2DCS.20BFA00GS201_LP | 14209 | 工作PC 2A段至保安段开关42A104 |  | digital
N2DCS.20BFB00GS001_LP | 14210 | 380V工作PC段分段开关42B021 |  | digital
N2DCS.20BFT10GS101_LP | 14211 | 工作1A变6kV侧开关62A10 |  | int32
N2DCS.20BFT10GS102_LP | 14212 | 工作1A变380V侧开关42A011 |  | int32
N2DCS.20BJD00GS201_LP | 14213 | 工作PC 2A至#4机MCC A开关42A032 |  | digital
N2DCS.20BJE00GS201_LP | 14214 | 工作PC 2A至#4机MCC B开关42A042 |  | digital
N2DCS.20BNA00GS201_LP | 14215 | 保安段至#4机EMCC段开关42E015 |  | digital
N2DCS.QJBW_SEQST | 14216 | #3机并网顺控 |  | digital
N2DCS.QJBW_SEQSTAUX | 14217 | #3机并网顺控辅助点 |  | digital
N2DCS.QJBW_SEQSTAUX0 | 14218 | #3机并网顺控启允许条件 |  | digital
N2DCS.QJBW_SEQSTAUX1 | 14219 | #3机并网顺控第1步完成条件 |  | digital
N2DCS.QJBW_SEQSTAUX2 | 14220 | #3机并网顺控第2步完成条件 |  | digital
N2DCS.QJBW_SEQSTAUX3 | 14221 | #3机并网顺控第3步完成条件 |  | digital
N2DCS.QJBW_SEQSTAUX4 | 14222 | #3机并网顺控第4步完成条件 |  | digital
N2DCS.QJBW_SEQSTAUX5 | 14223 | #3机并网顺控第5步完成条件 |  | digital
N2DCS.QJBW_SEQSTLP | 14224 | #3机并网顺控状态 |  | digital
N2DCS.20BBA00GS002_LP | 14225 | 6kV 2A段备用电源进线开关62A02 |  | digital
N2DCS.20BBB00GS001_LP | 14226 | 6kV 2B段工作电源进线开关62B01 |  | digital
N2DCS.20BFB00GS103_LP | 14227 | 工作PC IIB段至保安段开关42B103 |  | int32
N2DCS.20BFB00GS201_LP | 14228 | 工作PC 2B段至保安段开关42B103 |  | digital
N2DCS.20BFT20GS101_LP | 14229 | 工作2B变6kV侧开关62B10 |  | digital
N2DCS.20BFT20GS102_LP | 14230 | 工作2B变380V侧开关42B011 |  | digital
N2DCS.20BJD00GS202_LP | 14231 | 工作PC 2B至#4机MCC A开关42B032 |  | digital
N2DCS.20BJE00GS202_LP | 14232 | 工作PC 2B至#4机MCC B开关42B042 |  | digital
N2DCS.20BMA00GS001_LP | 14233 | 柴油发电机至保安段开关42E092 |  | digital
N2DCS.20BMA00GS002_LP | 14234 | 保安段工作电源K12开关42E101 |  | digital
N2DCS.20BMA00GS003_LP | 14235 | 保安段工作电源K13开关42E111 |  | digital
N2DCS.20BNA00GS202_LP | 14236 | 工作2B段至#4机EMCC段开关42B051 |  | digital
N2DCS.APSSPBP1_SEQ | 14237 | 降负荷断点1命令 |  | digital
N2DCS.APSSPBP1_SEQAUX | 14238 | 降负荷断点1辅助点 |  | digital
N2DCS.APSSPBP1_SEQLP | 14239 | 降负荷断点 |  | int32
N2DCS.APSSPBP2_SEQ | 14240 | #4机打闸断点命令 |  | digital
N2DCS.APSSPBP2_SEQAUX | 14241 | #4机打闸断点辅助点 |  | digital
N2DCS.APSSPBP2_SEQLP | 14242 | 燃机打闸断点 |  | int32
N2DCS.APSSPBP3_SEQ | 14243 | 余热锅炉停止断点命令 |  | int32
N2DCS.APSSPBP3_SEQAUX | 14244 | 余热锅炉停止断点辅助点 |  | int32
N2DCS.APSSPBP3_SEQLP | 14245 | 余热锅炉停止断点 |  | int32
N2DCS.APSSPBP4_SEQ | 14246 | 机组停运断点命令 |  | int32
N2DCS.APSSPBP4_SEQAUX | 14247 | 机组停运断点辅助点 |  | int32
N2DCS.APSSPBP4_SEQLP | 14248 | 机组停运断点 |  | int32
N2DCS.APSSTBP1_SEQ | 14249 | 系统准备断点命令 |  | int32
N2DCS.APSSTBP1_SEQAUX | 14250 | 系统准备断点辅助点 |  | int32
N2DCS.APSSTBP1_SEQLP | 14251 | 系统准备断点 |  | int32
N2DCS.APSSTBP2_SEQ | 14252 | 机组上水断点命令 |  | int32
N2DCS.APSSTBP2_SEQAUX | 14253 | 机组上水断点辅助点 |  | int32
N2DCS.APSSTBP2_SEQLP | 14254 | 机组上水断点 |  | int32
N2DCS.APSSTBP3_SEQ | 14255 | #4机点火断点指令 |  | digital
N2DCS.APSSTBP3_SEQAUX | 14256 | #4机点火断点辅助点 |  | digital
N2DCS.APSSTBP3_SEQLP | 14257 | 燃机点火断点 |  | int32
N2DCS.APSSTBP4_SEQ | 14258 | #3机并网断点指令 |  | digital
N2DCS.APSSTBP4_SEQAUX | 14259 | #3机并网断点辅助点 |  | digital
N2DCS.APSSTBP4_SEQLP | 14260 | 汽机并网断点 |  | int32
N2DCS.APSSTBP5_SEQ | 14261 | 升负荷断点指令 |  | int32
N2DCS.APSSTBP5_SEQAUX | 14262 | 升负荷断点辅助点 |  | int32
N2DCS.APSSTBP5_SEQLP | 14263 | 升负荷断点 |  | int32
N2DCS.AUXSYS_SEQST | 14264 | Ovation Control Builder |  | int32
N2DCS.AUXSYS_SEQSTAUX | 14265 | Ovation Control Builder |  | int32
N2DCS.AUXSYS_SEQSTLP | 14266 | Ovation Control Builder |  | int32
N2DCS.HRSGFW_SEQST | 14267 | 余热锅炉上水顺控 |  | int32
N2DCS.HRSGFW_SEQSTAUX | 14268 | 余热锅炉上水顺控辅助 |  | int32
N2DCS.HRSGFW_SEQSTLP | 14269 | Ovation Control Builder |  | int32
N2DCS.APSSPBP1_SEQ2 | 14270 | 降负荷断点2命令 |  | digital
N2DCS.APSSPBP1_SEQDV06 | 14271 | Ovation Control Builder |  | int32
N2DCS.APSSPBP1_SEQDV07 | 14272 | Ovation Control Builder |  | int32
N2DCS.APSSPBP1_SEQDV08 | 14273 | Ovation Control Builder |  | int32
N2DCS.APSSPBP1_SEQDV09 | 14274 | Ovation Control Builder |  | int32
N2DCS.APSSPBP1_SEQDV10 | 14275 | Ovation Control Builder |  | int32
N2DCS.APSSPBP2_SEQ2 | 14276 | Ovation Control Builder |  | int32
N2DCS.APSSPBP2_SEQDV06 | 14277 | Ovation Control Builder |  | int32
N2DCS.APSSPBP2_SEQDV07 | 14278 | Ovation Control Builder |  | int32
N2DCS.APSSPBP2_SEQDV08 | 14279 | Ovation Control Builder |  | int32
N2DCS.APSSPBP2_SEQDV09 | 14280 | Ovation Control Builder |  | int32
N2DCS.APSSPBP2_SEQDV10 | 14281 | Ovation Control Builder |  | int32
N2DCS.APSSPBP3_SEQ2 | 14282 | Ovation Control Builder |  | int32
N2DCS.APSSPBP3_SEQDV06 | 14283 | Ovation Control Builder |  | int32
N2DCS.APSSPBP3_SEQDV07 | 14284 | Ovation Control Builder |  | int32
N2DCS.APSSPBP3_SEQDV08 | 14285 | Ovation Control Builder |  | int32
N2DCS.APSSPBP3_SEQDV09 | 14286 | Ovation Control Builder |  | int32
N2DCS.APSSPBP3_SEQDV10 | 14287 | Ovation Control Builder |  | int32
N2DCS.APSSPBP4_SEQ2 | 14288 | Ovation Control Builder |  | int32
N2DCS.APSSPBP4_SEQDV06 | 14289 | Ovation Control Builder |  | int32
N2DCS.APSSPBP4_SEQDV07 | 14290 | Ovation Control Builder |  | int32
N2DCS.APSSPBP4_SEQDV08 | 14291 | Ovation Control Builder |  | int32
N2DCS.APSSPBP4_SEQDV09 | 14292 | Ovation Control Builder |  | int32
N2DCS.APSSPBP4_SEQDV10 | 14293 | Ovation Control Builder |  | int32
N2DCS.APSSTBP1_SEQ2 | 14294 | Ovation Control Builder |  | int32
N2DCS.APSSTBP1_SEQDV06 | 14295 | Ovation Control Builder |  | int32
N2DCS.APSSTBP2_SEQ2 | 14296 | Ovation Control Builder |  | int32
N2DCS.APSSTBP2_SEQDV06 | 14297 | Ovation Control Builder |  | int32
N2DCS.APSSTBP2_SEQDV07 | 14298 | Ovation Control Builder |  | int32
N2DCS.APSSTBP2_SEQDV08 | 14299 | Ovation Control Builder |  | int32
N2DCS.APSSTBP2_SEQDV09 | 14300 | Ovation Control Builder |  | int32
N2DCS.APSSTBP2_SEQDV10 | 14301 | Ovation Control Builder |  | int32
N2DCS.APSSTBP3_SEQ2 | 14302 | Ovation Control Builder |  | int32
N2DCS.APSSTBP3_SEQDV06 | 14303 | Ovation Control Builder |  | int32
N2DCS.APSSTBP3_SEQDV07 | 14304 | Ovation Control Builder |  | int32
N2DCS.APSSTBP3_SEQDV08 | 14305 | Ovation Control Builder |  | int32
N2DCS.APSSTBP3_SEQDV09 | 14306 | Ovation Control Builder |  | int32
N2DCS.APSSTBP3_SEQDV10 | 14307 | Ovation Control Builder |  | int32
N2DCS.APSSTBP4_SEQ2 | 14308 | Ovation Control Builder |  | int32
N2DCS.APSSTBP4_SEQDV06 | 14309 | Ovation Control Builder |  | int32
N2DCS.APSSTBP4_SEQDV07 | 14310 | Ovation Control Builder |  | int32
N2DCS.APSSTBP4_SEQDV08 | 14311 | Ovation Control Builder |  | int32
N2DCS.APSSTBP4_SEQDV09 | 14312 | Ovation Control Builder |  | int32
N2DCS.APSSTBP4_SEQDV10 | 14313 | Ovation Control Builder |  | int32
N2DCS.APSSTBP5_SEQ2 | 14314 | Ovation Control Builder |  | int32
N2DCS.APSSTBP5_SEQDV06 | 14315 | Ovation Control Builder |  | int32
N2DCS.APSSTBP5_SEQDV07 | 14316 | Ovation Control Builder |  | int32
N2DCS.APSSTBP5_SEQDV08 | 14317 | Ovation Control Builder |  | int32
N2DCS.APSSTBP5_SEQDV09 | 14318 | Ovation Control Builder |  | int32
N2DCS.APSSTBP5_SEQDV10 | 14319 | Ovation Control Builder |  | int32
N2DCS.20LBS45AA001_LP | 14320 | Ovation Control Builder |  | int32
N2DCS.20LBS46AA001_LP | 14321 | Ovation Control Builder |  | int32
N2DCS.20MAA11AA011_LP | 14322 | Ovation Control Builder |  | int32
N2DCS.20MAA11AA013_LP | 14323 | Ovation Control Builder |  | int32
N2DCS.20MAA11AA014_LP | 14324 | Ovation Control Builder |  | int32
N2DCS.20MAA12AA013_LP | 14325 | Ovation Control Builder |  | int32
N2DCS.20MAA12AA014_LP | 14326 | Ovation Control Builder |  | int32
N2DCS.20MAB11AA011_LP | 14327 | Ovation Control Builder |  | int32
N2DCS.20MAB11AA013_LP | 14328 | Ovation Control Builder |  | int32
N2DCS.20MAB11AA014_LP | 14329 | Ovation Control Builder |  | int32
N2DCS.20MAB12AA013_LP | 14330 | Ovation Control Builder |  | int32
N2DCS.20MAB12AA014_LP | 14331 | Ovation Control Builder |  | int32
N2DCS.20MAC45AA001_LP | 14332 | Ovation Control Builder |  | int32
N2DCS.20MAC46AA001_LP | 14333 | Ovation Control Builder |  | int32
N2DCS.20MAC45AA011_LP | 14334 | Ovation Control Builder |  | int32
N2DCS.20MAL23AA051A_LP | 14335 | Ovation Control Builder |  | int32
N2DCS.20MAL26AA051A_LP | 14336 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV51 | 14337 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV52 | 14338 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV53 | 14339 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV54 | 14340 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV55 | 14341 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV56 | 14342 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV57 | 14343 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV58 | 14344 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV59 | 14345 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV60 | 14346 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_DDV61 | 14347 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV01 | 14348 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV02 | 14349 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV03 | 14350 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV04 | 14351 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV05 | 14352 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV06 | 14353 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV07 | 14354 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV08 | 14355 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV09 | 14356 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV10 | 14357 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV11 | 14358 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV12 | 14359 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV13 | 14360 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV14 | 14361 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV15 | 14362 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV16 | 14363 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV17 | 14364 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV18 | 14365 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV19 | 14366 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV20 | 14367 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV21 | 14368 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV22 | 14369 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV23 | 14370 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV24 | 14371 | Ovation Control Builder |  | int32
N2DCS.20MAY10EC001_UDV25 | 14372 | Ovation Control Builder |  | int32
N2DCS.GV_CMD | 14373 | Ovation Control Builder |  | int32
N2DCS.GV_COIL_FAILUE | 14374 | Ovation Control Builder |  | int32
N2DCS.GV_MODE | 14375 | Ovation Control Builder |  | int32
N2DCS.GV_STAT | 14376 | Ovation Control Builder |  | int32
N2DCS.IV_CMD | 14377 | Ovation Control Builder |  | int32
N2DCS.IV_COIL_FAILUE | 14378 | Ovation Control Builder |  | int32
N2DCS.IV_MODE | 14379 | Ovation Control Builder |  | int32
N2DCS.IV_STAT | 14380 | Ovation Control Builder |  | int32
N2DCS.SHUTDOWN_MODE | 14381 | Ovation Control Builder |  | int32
N2DCS.STARTUP_MODE | 14382 | Ovation Control Builder |  | int32
N2DCS.TEST_LP | 14383 |  |  | digital
N2DCS.20MAL23AA051_XG01_LP | 14384 | Ovation Control Builder |  | int32
N2DCS.20LBC41AA051A_LP | 14385 | Ovation Control Builder |  | int32
N2DCS.20LBC41AA051B_LP | 14386 | Ovation Control Builder |  | int32
N2DCS.20MAC01AA001A_LP | 14387 | Ovation Control Builder |  | int32
N2DCS.20MAC01AA002A_LP | 14388 | Ovation Control Builder |  | int32
N2DCS.20MAV51AA012_LP_DEH | 14389 | Ovation Control Builder |  | int32
N2DCS.20MAV51AA012_LP | 14390 | Ovation Control Builder |  | int32
N1DCS.NPPC_W_G_T | 14391 | 全厂总负荷 | MW | float32
CALC.N1PS_P_atm | 14392 | 大气压力kPa | kPa | float32
CALC.N1PS_T_atm | 14393 | 大气温度 | ℃ | float32
CALC.N1PS_R_Humidity | 14394 | 相对湿度 | % | float32
CALC.N1GS_FuelVCH4 | 14395 | 天然气CH4含量% | % | float32
CALC.N1GS_FuelVC2H6 | 14396 | 天然气C2H6含量% | % | float32
CALC.N1GS_FuelVC3H8 | 14397 | 天然气C3H8含量% | % | float32
CALC.N1GS_FuelVCO2 | 14398 | 天然气CO2含量% | % | float32
CALC.N1GS_FuelVN1 | 14399 | 天然气N2含量% | % | float32
CALC.N1GS_Den_Fuel | 14400 | 燃料密度kg/m3 | kg/Nm3 | float32
CALC.N1GS_Qnetar | 14401 | 燃料低热值kJ/kg | kJ/kg | float32
CALC.N1GS_FuelVCO | 14402 | 天然气CO含量% | % | float32
CALC.N1GS_FuelVH2 | 14403 | 天然气H2含量% | % | float32
CALC.N1GS_FuelVC2H4 | 14404 | 天然气C2H4含量% | % | float32
CALC.N1GS_FuelVO2 | 14405 | 天然气O2含量% | % | float32
CALC.N1GS_FuelVH2S | 14406 | 天然气H2S含量% | % | float32
CALC.N1BS_P_StkGasIn | 14407 | 余热锅炉入口烟气压力 | kPa | float32
CALC.N1BS_T_StkGasIn | 14408 | 余热锅炉入口烟气温度 | ℃ | float32
CALC.N1BS_StkO2 | 14409 | 余热锅炉烟囱烟气O2含量 | % | float32
CALC.N1BS_StkCO2 | 14410 | 余热锅炉烟囱烟气CO2含量 | % | float32
CALC.N1BS_StkN2 | 14411 | 余热锅炉烟囱烟气N2含量 | % | float32
CALC.N1BS_StkH2O | 14412 | 余热锅炉烟囱烟气H2O含量 | % | float32
CALC.N1BS_T_StkGasOut | 14413 | 余热锅炉烟囱出口烟气温度 | ℃ | float32
CALC.N1BS_P_StkGasOut | 14414 | 余热锅炉烟囱出口烟气压力 | kPa | float32
CALC.N1BS_F_StkGas | 14415 | 余热锅炉烟囱烟气流量 | t/h | float32
CALC.N1BS_StkSO2 | 14416 | 余热锅炉烟囱烟气SO2含量 | % | float32
CALC.N1BS_T_HPEVAGasIn | 14417 | 高压蒸发器入口烟气温度 | kPa | float32
CALC.N1BS_T_HPEVAGasOut | 14418 | 高压蒸发器出口烟气温度 | ℃ | float32
CALC.N1BS_T_IPEVAGasIn | 14419 | 中压蒸发器入口烟气温度 | % | float32
CALC.N1BS_T_IPEVAGasOut | 14420 | 中压蒸发器出口烟气温度 | % | float32
CALC.N1BS_T_LPEVAGasIn | 14421 | 低压蒸发器入口烟气温度 | % | float32
CALC.N1BS_T_LPEVAGasOut | 14422 | 低压蒸发器出口烟气温度 | % | float32
CALC.N1BS_T_HPSHOut | 14423 | 余热锅炉高压过热蒸汽温度 | ℃ | float32
CALC.N1BS_P_HPSHOut | 14424 | 余热锅炉高压过热蒸汽压力 | MPa | float32
CALC.N1BS_F_HPSHOut | 14425 | 余热锅炉高压过热汽蒸汽流量 | t/h | float32
CALC.N1BS_T_IPSHOut | 14426 | 余热锅炉中压过热蒸汽温度 | ℃ | float32
CALC.N1BS_P_IPSHOut | 14427 | 余热锅炉中压过热蒸汽压力 | MPa | float32
CALC.N1BS_F_IPSHOut | 14428 | 余热锅炉中压过热汽蒸汽流量 | t/h | float32
CALC.N1BS_T_LPSHOut | 14429 | 余热锅炉低压过热蒸汽温度 | ℃ | float32
CALC.N1BS_P_LPSHOut | 14430 | 余热锅炉低压过热蒸汽压力 | MPa | float32
CALC.N1BS_F_LPSHOut | 14431 | 余热锅炉低压过热蒸汽流量 | t/h | float32
CALC.N1BS_T_RHStm | 14432 | 冷再热蒸汽温度 | ℃ | float32
CALC.N1BS_P_RHStm | 14433 | 冷再热蒸汽压力 | MPa | float32
CALC.N1BS_F_RHStm | 14434 | 冷再热流量 | t/h | float32
CALC.N1BS_F_HPFeed | 14435 | 余热锅炉高压给水流量 | t/h | float32
CALC.N1BS_F_IPFeed | 14436 | 余热锅炉中压给水流量 | t/h | float32
CALC.N1BS_F_LPFeed | 14437 | 余热锅炉低压给水流量 | t/h | float32
CALC.N1BS_F_FuelHeaterWt | 14438 | 余热锅炉燃料加热器给水流量 | t/h | float32
CALC.N1BS_F_DEHPWtr | 14439 | 余热锅炉高压过热汽减温水流量 | t/h | float32
CALC.N1BS_T_HPFeed | 14440 | 余热锅炉高压给水温度 | ℃ | float32
CALC.N1BS_P_HPFeed | 14441 | 余热锅炉高压给水压力 | MPa | float32
CALC.N1BS_T_IPFeed | 14442 | 余热锅炉中压给水温度 | ℃ | float32
CALC.N1BS_P_IPFeed | 14443 | 余热锅炉中压给水压力 | MPa | float32
CALC.N1BS_P_HPDrum | 14444 | 余热锅炉高压汽包压力 | MPa | float32
CALC.N1BS_P_IPDrum | 14445 | 余热锅炉中压汽包压力 | MPa | float32
CALC.N1BS_P_LPDrum | 14446 | 余热锅炉低压汽包压力 | MPa | float32
CALC.N1BS_T_LPECOIn | 14447 | 余热锅炉低压省煤器入口温度 | ℃ | float32
CALC.N1BS_P_LPECOIn | 14448 | 余热锅炉低压省煤器入口压力 | MPa | float32
CALC.N1BS_T_LPECOOut | 14449 | 余热锅炉低压省煤器出口温度 | ℃ | float32
CALC.N1BS_P_LPECOOut | 14450 | 余热锅炉低压省煤器出口压力 | MPa | float32
CALC.N1BS_T_HPECOOut | 14451 | 余热锅炉高压省煤器出口温度 | ℃ | float32
CALC.N1BS_T_IPECOOut | 14452 | 余热锅炉中压省煤器出口温度 | ℃ | float32
CALC.N1BS_F_TCACooler | 14453 | TCA冷却器流量 | t/h | float32
CALC.N1BS_T_TCACoolerOut | 14454 | TCA冷却器出口温度 | ℃ | float32
CALC.N1BS_P_TCACoolerOut | 14455 | TCA冷却器出口压力 | MPa | float32
CALC.N1BS_P_HPECOOut | 14456 | 余热锅炉高压省煤器出口压力 | ℃ | float32
CALC.N1BS_P_IPECOOut | 14457 | 余热锅炉中压省煤器出口压力 | ℃ | float32
CALC.N1BS_T_CNDIn | 14458 | 给水温度 | ℃ | float32
CALC.N1BS_P_CNDIn | 14459 | 给水压力 | ℃ | float32
CALC.N1BS_F_DERHWtr | 14460 | 余热锅炉再减温水流量 | t/h | float32
CALC.N1TS_P_HPStmIn | 14461 | 高压缸进汽压力 | MPa | float32
CALC.N1TS_T_HPStmIn | 14462 | 高压缸进汽温度 | ℃ | float32
CALC.N1TS_P_IPStmIn | 14463 | 中压缸进汽压力 | MPa | float32
CALC.N1TS_T_IPStmIn | 14464 | 中压缸进汽温度 | ℃ | float32
CALC.N1TS_P_LPex | 14465 | 低压缸排汽压力 | kPa | float32
CALC.N1TS_P_LPStmIn | 14466 | 低压缸进汽压力 | ℃ | float32
CALC.N1TS_T_LPStmIn | 14467 | 低压缸进汽温度 | ℃ | float32
CALC.N1TS_T_LPex | 14468 | 低压缸排汽温度 | ℃ | float32
CALC.N1TS_F_IPStmIn | 14469 | 中压缸蒸汽流量 | t/h | float32
CALC.N1TS_F_HPStmIn | 14470 | 高压缸蒸汽流量 | t/h | float32
CALC.N1TS_F_LPStmIn | 14471 | 低压缸蒸汽流量 | t/h | float32
CALC.N1TS_P_HPStmOut | 14472 | 高压缸排汽压力 | MPa | float32
CALC.N1TS_T_HPStmOut | 14473 | 高压缸排汽温度 | ℃ | float32
CALC.N1TS_F_RHStm | 14474 | 冷再热流量 | ℃ | float32
CALC.N1TS_P_IPStmOut | 14475 | 中压缸排汽压力 | ℃ | float32
CALC.N1TS_T_IPStmOut | 14476 | 中压缸排汽温度 | ℃ | float32
CALC.N1TS_P_LPexAST | 14477 | 低压缸排汽压力(绝对值) | kPa | float32
CALC.N1TS_T_CicWi | 14478 | 凝汽器循环水进水温度 | ℃ | float32
CALC.N1TS_T_CicWo | 14479 | 凝汽器循环水出水温度 | ℃ | float32
CALC.N1TS_T_CNDIn | 14480 | 凝结水加热器入口混合段前温度 | ℃ | float32
CALC.N1TS_P_CNDIn | 14481 | 凝结水加热器入口混合段前压力 | MPa | float32
CALC.N1TS_F_GStmCnd | 14482 | 汽封冷却器出口凝结水流量 | t/h | float32
CALC.N1TS_F_WaterRep | 14483 | 凝结水热井补给水流量 | t/h | float32
CALC.N1TS_T_HwLCo | 14484 | 热井出水温度 | ℃ | float32
CALC.N1TS_F_SupplyHeat | 14485 | 蒸汽轮机供热抽汽流量 | t/h | float32
CALC.N1TS_T_SupplyHeat | 14486 | 蒸汽轮机供热抽汽温度 | ℃ | float32
CALC.N1TS_P_SupplyHeat | 14487 | 蒸汽轮机供热抽汽压力 | MPa | float32
CALC.N1TS_F_GRWaterRep | 14488 | 蒸汽轮机供热补水流量 | t/h | float32
CALC.N1TS_T_GRWaterRep | 14489 | 蒸汽轮机供热补水温度 | ℃ | float32
CALC.N1TS_P_GRWaterRep | 14490 | 蒸汽轮机供热补水压力 | MPa | float32
CALC.N1TS_T_ShuWater | 14491 | 采暖抽汽疏水温度 | ℃ | float32
CALC.N1TS_P_ShuWater | 14492 | 采暖抽汽疏水压力 | MPa | float32
CALC.N1TS_W_CGB | 14493 | 汽机厂高变功率 | MW | float32
CALC.N1TS_W_QBB | 14494 | 启备变功率 | MW | float32
CALC.N1TS_W_LCB | 14495 | 励磁变功率 | MW | float32
CALC.N1GS_W_G | 14496 | 燃机输出功率 | ℃ | float32
CALC.N1TS_W_G | 14497 | 汽机功率 | MW | float32
CALC.N1GS_S_G | 14498 | 机组运行状态 |  | digital
CALC.N1GS_W_ZB | 14499 | 燃机主变输出功率 | MW | float32
CALC.N1PS_W_G | 14500 | 联合循环发电机功率 | MW | float32
CALC.N1GS_E_Frequency | 14501 | 发电机频率 | Hz | float32
CALC.N1TS_W_ZB | 14502 | 汽机主变输出功率 | MW | float32
CALC.N1GS_W_QBB | 14503 | 启备变功率 | MW | float32
CALC.N1GS_W_CGB | 14504 | 燃机厂高变功率 | MW | float32
CALC.N1PS_W_CGB | 14505 | 厂高变功率 | MW | float32
CALC.N1PS_W_QBB | 14506 | 启备变功率 | MW | float32
CALC.N1PS_W_ZB | 14507 | 主变输出功率 | MW | float32
CALC.N1TS_S_G | 14508 | 机组运行状态 |  | digital
CALC.N1TS_A_CoaguPumpA | 14509 | 凝结水泵A电流 | A | float32
CALC.N1TS_A_CoaguPumpB | 14510 | 凝结水泵B电流 | A | float32
CALC.N1TS_A_CoaguPumpC | 14511 | 凝结水泵C电流 | A | float32
CALC.N1TS_A_CirPumpA | 14512 | 循环水泵A电流 | A | float32
CALC.N1TS_A_CirPumpB | 14513 | 循环水泵B电流 | A | float32
CALC.N1BS_V_6KV | 14514 | 6kV电压 | kV | float32
CALC.N1TS_S_CoaguPumpA | 14515 | 凝结水泵A运行状态 |  | digital
CALC.N1TS_S_CoaguPumpB | 14516 | 凝结水泵B运行状态 |  | digital
CALC.N1TS_S_CoaguPumpC | 14517 | 凝结水泵C运行状态 |  | digital
CALC.N1TS_S_CirPumpA | 14518 | 循环水泵A运行状态 |  | digital
CALC.N1TS_S_CirPumpB | 14519 | 循环水泵B运行状态 |  | digital
CALC.N1GS_P_COMPIn | 14520 | 压气机进口压力P1 | kPa | float32
CALC.N1GS_T_COMPIn | 14521 | 压气机进口温度T1 | ℃ | float32
CALC.N1GS_P_COMPOut | 14522 | 压气机出口压力P2 | kPa | float32
CALC.N1GS_T_COMPOut | 14523 | 压气机出口温度T2 | ℃ | float32
CALC.N1GS_T_FuelIn | 14524 | 进入燃烧室燃料温度Tf | ℃ | float32
CALC.N1GS_F_FuelIn | 14525 | 进入燃烧室燃料流量Qf | t/h | float32
CALC.N1GS_P_GASTIn | 14526 | 燃气轮机进口压力P3 | kPa | float32
CALC.N1GS_P_GASTOut | 14527 | 燃气轮机出口压力P4 | ℃ | float32
CALC.N1GS_T_GASTOut | 14528 | 燃气轮机出口温度T4 | ℃ | float32
CALC.N1GS_F_GASIn | 14529 | 进入透平的燃气流量Qt | t/h | float32
CALC.N1GS_F_COMPIn | 14530 | 压气机进口空气流量Qc | t/h | float32
CALC.N1BS_F_HPFPA_In | 14531 | 高压给水泵A进口流量 | t/h | float32
CALC.N1BS_P_HPFPA_In | 14532 | 高压给水泵A进口压力 | MPa | float32
CALC.N1BS_T_HPFPA_In | 14533 | 高压给水泵A进口温度 | ℃ | float32
CALC.N1BS_P_HPFPA_Out | 14534 | 高压给水泵A出口压力 | MPa | float32
CALC.N1BS_T_HPFPA_Out | 14535 | 高压给水泵A出口温度 | ℃ | float32
CALC.N1BS_F_HPFPB_In | 14536 | 高压给水泵B进口流量 | t/h | float32
CALC.N1BS_P_HPFPB_In | 14537 | 高压给水泵B进口压力 | MPa | float32
CALC.N1BS_T_HPFPB_In | 14538 | 高压给水泵B进口温度 | ℃ | float32
CALC.N1BS_P_HPFPB_Out | 14539 | 高压给水泵B出口压力 | MPa | float32
CALC.N1BS_T_HPFPB_Out | 14540 | 高压给水泵B出口温度 | ℃ | float32
CALC.N1BS_F_IPFPA_In | 14541 | 中压给水泵A进口流量 | t/h | float32
CALC.N1BS_P_IPFPA_In | 14542 | 中压给水泵A进口压力 | MPa | float32
CALC.N1BS_T_IPFPA_In | 14543 | 中压给水泵A进口温度 | ℃ | float32
CALC.N1BS_P_IPFPA_Out | 14544 | 中压给水泵A出口压力 | MPa | float32
CALC.N1BS_T_IPFPA_Out | 14545 | 中压给水泵A出口温度 | ℃ | float32
CALC.N1BS_F_IPFPB_In | 14546 | 中压给水泵B进口流量 | t/h | float32
CALC.N1BS_P_IPFPB_In | 14547 | 中压给水泵B进口压力 | MPa | float32
CALC.N1BS_T_IPFPB_In | 14548 | 中压给水泵B进口温度 | ℃ | float32
CALC.N1BS_P_IPFPB_Out | 14549 | 中压给水泵B出口压力 | MPa | float32
CALC.N1BS_T_IPFPB_Out | 14550 | 中压给水泵B出口温度 | ℃ | float32
CALC.N1BS_R_HPFPA | 14551 | 高压给水泵A转速 | rpm | float32
CALC.N1BS_R_HPFPB | 14552 | 高压给水泵B转速 | rpm | float32
CALC.N1BS_R_IPFPA | 14553 | 中压给水泵A转速 | rpm | float32
CALC.N1BS_R_IPFPB | 14554 | 中压给水泵B转速 | rpm | float32
CALC.N1BC_Han_StkGasIn | 14555 | 余热锅炉入口烟气焓 | kJ/kg | float32
CALC.N1BC_Han_StkGasOut | 14556 | 余热锅炉出口烟气焓 | kJ/kg | float32
CALC.N1BC_Han_HPStmIn | 14557 | 锅炉高压主蒸汽焓 | kJ/kg | float32
CALC.N1BC_Han_IPStmIn | 14558 | 锅炉中压主蒸汽焓 | kJ/kg | float32
CALC.N1BC_Han_LPStmIn | 14559 | 锅炉低压主蒸汽焓 | kJ/kg | float32
CALC.N1BC_Han_HPStmOut | 14560 | 锅炉冷再热汽焓 | kJ/kg | float32
CALC.N1BC_Han_HPFeed | 14561 | 高压给水焓 | kJ/kg | float32
CALC.N1BC_Han_IPFeed | 14562 | 中压给水焓 | kJ/kg | float32
CALC.N1BC_Han_HPECOOut | 14563 | 高压省煤器出口焓 | kJ/kg | float32
CALC.N1BC_Han_IPECOOut | 14564 | 中压省煤器出口焓 | kJ/kg | float32
CALC.N1BC_Han_TCACoolerOut | 14565 | TCA冷却器出口焓 | kJ/kg | float32
CALC.N1BC_Q_STM | 14566 | 余热锅炉蒸汽侧吸热量 | MJ/h | float32
CALC.N1BC_EFF_BOILER | 14567 | 余热锅炉热效率 | % | float32
CALC.N1BC_F_STKGAS | 14568 | 烟囱烟气流量 | t/h | float32
CALC.N1BC_Q_GAS | 14569 | 余热锅炉烟气侧放热量 | MJ/h | float32
CALC.N1BC_P_GasDiff | 14570 | 余热锅炉烟气压损 | kPa | float32
CALC.N1BC_T_HPRdDiff | 14571 | 余热锅炉热端温差 | ℃ | float32
CALC.N1BC_T_LPEVADIFF | 14572 | 低压蒸发器节点温差 | ℃ | float32
CALC.N1BC_T_IPEVADIFF | 14573 | 中压蒸发器节点温差 | ℃ | float32
CALC.N1BC_T_HPEVADIFF | 14574 | 高压蒸发器节点温差 | ℃ | float32
CALC.N1BC_T_LPECODIFF | 14575 | 低压省煤器接近点温差 | ℃ | float32
CALC.N1BC_TS_LPECO | 14576 | 低压省煤器出口压力对应饱和水温度 | ℃ | float32
CALC.N1BC_T_IPECODIFF | 14577 | 中压省煤器接近点温差 | ℃ | float32
CALC.N1BC_TS_IPECO | 14578 | 中压省煤器出口压力对应饱和水温度 | ℃ | float32
CALC.N1BC_T_HPECODIFF | 14579 | 高压省煤器接近点温差 | ℃ | float32
CALC.N1BC_TS_HPECO | 14580 | 高压省煤器出口压力对应饱和水温度 | ℃ | float32
CALC.N1BC_H_HPFPA | 14581 | 高压给水泵A扬程 | m | float32
CALC.N1BC_H_HPFPA_CORR | 14582 | 高压给水泵A修正扬程 | m | float32
CALC.N1BC_F_HPFPA_OUT | 14583 | 高压给水泵A出口流量 | t/h | float32
CALC.N1BC_F_HPFPA_OUT_CORR | 14584 | 高压给水泵A出口修正流量 | t/h | float32
CALC.N1BC_W_HPFPA_Shaft | 14585 | 高压给水泵A轴功率 | kW | float32
CALC.N1BC_W_HPFPA_Shaft_CORR | 14586 | 高压给水泵A修正轴功率 | kW | float32
CALC.N1BC_EFF_HPFPNA | 14587 | 高压给水泵A效率 | % | float32
CALC.N1BC_EFF_HPFPNA_CORR | 14588 | 高压给水泵A修正效率 | % | float32
CALC.N1BC_H_HPFPB | 14589 | 高压给水泵B扬程 | m | float32
CALC.N1BC_H_HPFPB_CORR | 14590 | 高压给水泵B修正扬程 | m | float32
CALC.N1BC_F_HPFPB_OUT | 14591 | 高压给水泵B出口流量 | t/h | float32
CALC.N1BC_F_HPFPB_OUT_CORR | 14592 | 高压给水泵B出口修正流量 | t/h | float32
CALC.N1BC_W_HPFPB_Shaft | 14593 | 高压给水泵B轴功率 | kW | float32
CALC.N1BC_W_HPFPB_Shaft_CORR | 14594 | 高压给水泵B修正轴功率 | kW | float32
CALC.N1BC_EFF_HPFPNB | 14595 | 高压给水泵B效率 | % | float32
CALC.N1BC_EFF_HPFPNB_CORR | 14596 | 高压给水泵B修正效率 | % | float32
CALC.N1BC_H_IPFPA | 14597 | 中压给水泵A扬程 | m | float32
CALC.N1BC_H_IPFPA_CORR | 14598 | 中压给水泵A修正扬程 | m | float32
CALC.N1BC_F_IPFPA_OUT | 14599 | 中压给水泵A出口流量 | t/h | float32
CALC.N1BC_F_IPFPA_OUT_CORR | 14600 | 中压给水泵A出口修正流量 | t/h | float32
CALC.N1BC_W_IPFPA_Shaft | 14601 | 中压给水泵A轴功率 | kW | float32
CALC.N1BC_W_IPFPA_Shaft_CORR | 14602 | 中压给水泵A修正轴功率 | kW | float32
CALC.N1BC_EFF_IPFPNA | 14603 | 中压给水泵A效率 | % | float32
CALC.N1BC_EFF_IPFPNA_CORR | 14604 | 中压给水泵A修正效率 | % | float32
CALC.N1BC_H_IPFPB | 14605 | 中压给水泵B扬程 | m | float32
CALC.N1BC_H_IPFPB_CORR | 14606 | 中压给水泵B修正扬程 | m | float32
CALC.N1BC_F_IPFPB_OUT | 14607 | 中压给水泵B出口流量 | t/h | float32
CALC.N1BC_F_IPFPB_OUT_CORR | 14608 | 中压给水泵B出口修正流量 | t/h | float32
CALC.N1BC_W_IPFPB_Shaft | 14609 | 中压给水泵B轴功率 | kW | float32
CALC.N1BC_W_IPFPB_Shaft_CORR | 14610 | 中压给水泵B修正轴功率 | kW | float32
CALC.N1BC_EFF_IPFPNB | 14611 | 中压给水泵B效率 | % | float32
CALC.N1BC_EFF_IPFPNB_CORR | 14612 | 中压给水泵B修正效率 | % | float32
CALC.N1BC_EFF_BOILER_T | 14613 | 主蒸汽温度(目标) | ℃ | float32
CALC.N1BC_F_STKGAS_T | 14614 | 烟气流量(目标) | ℃ | float32
CALC.N1BC_T_StkGasIn_T | 14615 | 余热锅炉入口烟气温度(目标) | ℃ | float32
CALC.N1BC_StkH2O_T | 14616 | 烟囱烟气H2O含量(目标) | ℃ | float32
CALC.N1BC_P_LPSHOut_T | 14617 | 余热锅炉低压过热蒸汽压力(目标) | ℃ | float32
CALC.N1TC_T_HPStmOut_T | 14618 | 高压缸排汽温度(目标) | ℃ | float32
CALC.N1TC_T_CNDIn_T | 14619 | 凝结水加热器入口混合段前温度(目标) | ℃ | float32
CALC.N1BC_CV_EFF_Boiler_NUM | 14620 | 锅炉效率曲线(目标)_Num |  | float32
CALC.N1BC_CV_EFF_Boiler_X01 | 14621 | 锅炉效率曲线(目标)_X01 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y01 | 14622 | 锅炉效率曲线(目标)_Y01 |  | float32
CALC.N1BC_CV_EFF_Boiler_X02 | 14623 | 锅炉效率曲线(目标)_X02 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y02 | 14624 | 锅炉效率曲线(目标)_Y02 |  | float32
CALC.N1BC_CV_EFF_Boiler_X03 | 14625 | 锅炉效率曲线(目标)_X03 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y03 | 14626 | 锅炉效率曲线(目标)_Y03 |  | float32
CALC.N1BC_CV_EFF_Boiler_X04 | 14627 | 锅炉效率曲线(目标)_X04 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y04 | 14628 | 锅炉效率曲线(目标)_Y04 |  | float32
CALC.N1BC_CV_EFF_Boiler_X05 | 14629 | 锅炉效率曲线(目标)_X05 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y05 | 14630 | 锅炉效率曲线(目标)_Y05 |  | float32
CALC.N1BC_CV_EFF_Boiler_X06 | 14631 | 锅炉效率曲线(目标)_X06 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y06 | 14632 | 锅炉效率曲线(目标)_Y06 |  | float32
CALC.N1BC_CV_EFF_Boiler_X07 | 14633 | 锅炉效率曲线(目标)_X07 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y07 | 14634 | 锅炉效率曲线(目标)_Y07 |  | float32
CALC.N1BC_CV_EFF_Boiler_X08 | 14635 | 锅炉效率曲线(目标)_X08 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y08 | 14636 | 锅炉效率曲线(目标)_Y08 |  | float32
CALC.N1BC_CV_EFF_Boiler_X09 | 14637 | 锅炉效率曲线(目标)_X09 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y09 | 14638 | 锅炉效率曲线(目标)_Y09 |  | float32
CALC.N1BC_CV_EFF_Boiler_X10 | 14639 | 锅炉效率曲线(目标)_X10 |  | float32
CALC.N1BC_CV_EFF_Boiler_Y10 | 14640 | 锅炉效率曲线(目标)_Y10 |  | float32
CALC.N1BC_CV_F_STKGAS_NUM | 14641 | 烟气流量曲线(目标)_Num |  | float32
CALC.N1BC_CV_F_STKGAS_X01 | 14642 | 烟气流量曲线(目标)_X01 |  | float32
CALC.N1BC_CV_F_STKGAS_Y01 | 14643 | 烟气流量曲线(目标)_Y01 |  | float32
CALC.N1BC_CV_F_STKGAS_X02 | 14644 | 烟气流量曲线(目标)_X02 |  | float32
CALC.N1BC_CV_F_STKGAS_Y02 | 14645 | 烟气流量曲线(目标)_Y02 |  | float32
CALC.N1BC_CV_F_STKGAS_X03 | 14646 | 烟气流量曲线(目标)_X03 |  | float32
CALC.N1BC_CV_F_STKGAS_Y03 | 14647 | 烟气流量曲线(目标)_Y03 |  | float32
CALC.N1BC_CV_F_STKGAS_X04 | 14648 | 烟气流量曲线(目标)_X04 |  | float32
CALC.N1BC_CV_F_STKGAS_Y04 | 14649 | 烟气流量曲线(目标)_Y04 |  | float32
CALC.N1BC_CV_F_STKGAS_X05 | 14650 | 烟气流量曲线(目标)_X05 |  | float32
CALC.N1BC_CV_F_STKGAS_Y05 | 14651 | 烟气流量曲线(目标)_Y05 |  | float32
CALC.N1BC_CV_F_STKGAS_X06 | 14652 | 烟气流量曲线(目标)_X06 |  | float32
CALC.N1BC_CV_F_STKGAS_Y06 | 14653 | 烟气流量曲线(目标)_Y06 |  | float32
CALC.N1BC_CV_F_STKGAS_X07 | 14654 | 烟气流量曲线(目标)_X07 |  | float32
CALC.N1BC_CV_F_STKGAS_Y07 | 14655 | 烟气流量曲线(目标)_Y07 |  | float32
CALC.N1BC_CV_F_STKGAS_X08 | 14656 | 烟气流量曲线(目标)_X08 |  | float32
CALC.N1BC_CV_F_STKGAS_Y08 | 14657 | 烟气流量曲线(目标)_Y08 |  | float32
CALC.N1BC_CV_F_STKGAS_X09 | 14658 | 烟气流量曲线(目标)_X09 |  | float32
CALC.N1BC_CV_F_STKGAS_Y09 | 14659 | 烟气流量曲线(目标)_Y09 |  | float32
CALC.N1BC_CV_F_STKGAS_X10 | 14660 | 烟气流量曲线(目标)_X10 |  | float32
CALC.N1BC_CV_F_STKGAS_Y10 | 14661 | 烟气流量曲线(目标)_Y10 |  | float32
CALC.N1BC_COHPSHOutF_StkGasF | 14662 | 高压蒸汽流量随排气流量修正系数 |  | float32
CALC.N1BC_COHPSHOutF_StkGasT | 14663 | 高压蒸汽流量随排气温度修正系数 |  | float32
CALC.N1BC_COHPSHOutF_CNDInT | 14664 | 高压蒸汽流量随给水温度修正系数 |  | float32
CALC.N1BC_COHPSHOutF_StkH2O | 14665 | 高压蒸汽流量随含水率修正系数 |  | float32
CALC.N1BC_COHPSHOutF_HPStmOutT | 14666 | 高压蒸汽流量随高压缸排汽温度修正系数 |  | float32
CALC.N1BC_COHPSHOutF | 14667 | 高压蒸汽流量总修正系数 |  | float32
CALC.N1BC_F_HPSHOut_GC | 14668 | 修正后高压过热蒸汽流量 | t/h | float32
CALC.N1BC_COHPSHOutT_StkGasF | 14669 | 高压蒸汽温度随排气流量修正系数 |  | float32
CALC.N1BC_COHPSHOutT_StkGasT | 14670 | 高压蒸汽温度随排气温度修正系数 |  | float32
CALC.N1BC_COHPSHOutT_CNDInT | 14671 | 高压蒸汽温度随给水温度修正系数 |  | float32
CALC.N1BC_COHPSHOutT_StkH2O | 14672 | 高压蒸汽温度随含水率修正系数 |  | float32
CALC.N1BC_COHPSHOutT_HPStmOutT | 14673 | 高压蒸汽温度随高压缸排汽温度修正系数 |  | float32
CALC.N1BC_COHPSHOutT | 14674 | 高压蒸汽温度总修正系数 |  | float32
CALC.N1BC_T_HPSHOut_GC | 14675 | 修正后高压蒸汽温度 | ℃ | float32
CALC.N1BC_COIPSHOutF_StkGasF | 14676 | 再热蒸汽流量随排气流量修正系数 |  | float32
CALC.N1BC_COIPSHOutF_StkGasT | 14677 | 再热蒸汽流量随排气温度修正系数 |  | float32
CALC.N1BC_COIPSHOutF_CNDInT | 14678 | 再热蒸汽流量随给水温度修正系数 |  | float32
CALC.N1BC_COIPSHOutF_StkH2O | 14679 | 再热蒸汽流量随含水率修正系数 |  | float32
CALC.N1BC_COIPSHOutF_HPStmOutT | 14680 | 再热蒸汽流量随高压缸排汽温度修正系数 |  | float32
CALC.N1BC_COIPSHOutF | 14681 | 再热蒸汽流量总修正系数 |  | float32
CALC.N1BC_F_IPSHOut_GC | 14682 | 修正后再热蒸汽流量 | t/h | float32
CALC.N1BC_COIPSHOutT_StkGasF | 14683 | 再热蒸汽温度随排气流量修正系数 |  | float32
CALC.N1BC_COIPSHOutT_StkGasT | 14684 | 再热蒸汽温度随排气温度修正系数 |  | float32
CALC.N1BC_COIPSHOutT_CNDInT | 14685 | 再热蒸汽温度随给水温度修正系数 |  | float32
CALC.N1BC_COIPSHOutT_StkH2O | 14686 | 再热蒸汽温度随含水率修正系数 |  | float32
CALC.N1BC_COIPSHOutT_HPStmOutT | 14687 | 再热蒸汽温度随高压缸排汽温度修正系数 |  | float32
CALC.N1BC_COIPSHOutT | 14688 | 再热蒸汽温度总修正系数 |  | float32
CALC.N1BC_T_IPSHOut_GC | 14689 | 修正后再热蒸汽温度 | ℃ | float32
CALC.N1BC_COLPSHOutF_StkGasF | 14690 | 低压蒸汽流量随排气流量修正系数 |  | float32
CALC.N1BC_COLPSHOutF_StkGasT | 14691 | 低压蒸汽流量随排气温度修正系数 |  | float32
CALC.N1BC_COLPSHOutF_CNDInT | 14692 | 低压蒸汽流量随给水温度修正系数 |  | float32
CALC.N1BC_COLPSHOutF_StkH2O | 14693 | 低压蒸汽流量随含水率修正系数 |  | float32
CALC.N1BC_COLPSHOutF_HPStmOutT | 14694 | 低压蒸汽流量随高压缸排汽温度修正系数 |  | float32
CALC.N1BC_COLPSHOutF | 14695 | 低压蒸汽流量总修正系数 |  | float32
CALC.N1BC_F_LPSHOut_GC | 14696 | 修正后低压蒸汽流量 | t/h | float32
CALC.N1BC_COLPSHOutF_LPSHOutP | 14697 | 低压蒸汽流量随低压蒸汽压力修正系数 |  | float32
CALC.N1BC_COLPSHOutT_StkGasF | 14698 | 低压蒸汽温度随排气流量修正系数 |  | float32
CALC.N1BC_COLPSHOutT_StkGasT | 14699 | 低压蒸汽温度随排气温度修正系数 |  | float32
CALC.N1BC_COLPSHOutT_CNDInT | 14700 | 低压蒸汽温度随给水温度修正系数 |  | float32
CALC.N1BC_COLPSHOutT_StkH2O | 14701 | 低压蒸汽温度随含水率修正系数 |  | float32
CALC.N1BC_COLPSHOutT_HPStmOutT | 14702 | 低压蒸汽温度随高压缸排汽温度修正系数 |  | float32
CALC.N1BC_COLPSHOutT | 14703 | 低压蒸汽温度总修正系数 |  | float32
CALC.N1BC_T_LPSHOut_GC | 14704 | 修正后低压蒸汽温度 | ℃ | float32
CALC.N1BC_CEFB_StkGasF | 14705 | 余热锅炉效率随排气流量修正系数 |  | float32
CALC.N1BC_CEFB_StkGasT | 14706 | 余热锅炉效率随排气温度修正系数 |  | float32
CALC.N1BC_CEFB_CNDInT | 14707 | 余热锅炉效率随给水温度修正系数 |  | float32
CALC.N1BC_CEFB_StkH2O | 14708 | 余热锅炉效率随含水率修正系数 |  | float32
CALC.N1BC_CEFB_HPStmOutT | 14709 | 余热锅炉效率随高压缸排汽温度修正系数 |  | float32
CALC.N1BC_CEFB_BOILER | 14710 | 余热锅炉效率总修正系数 |  | float32
CALC.N1BC_EFF_BOILER_GC | 14711 | 修正后余热锅炉效率 | % | float32
CALC.N1BC_CEFB_LPSHOutP | 14712 | 余热锅炉效率随低压蒸汽压力修正系数 |  | float32
CALC.N1BC_COGasDiffP_StkGasF | 14713 | 排气压降随排气流量修正系数 |  | float32
CALC.N1BC_COGasDiffP_StkGasT | 14714 | 排气压降随排气温度修正系数 |  | float32
CALC.N1BC_COGasDiffP | 14715 | 排气压降总修正系数 |  | float32
CALC.N1BC_P_GasDiff_GC | 14716 | 修正后排气压降 | kPa | float32
CALC.N1TC_Han_HPStmIn | 14717 | 高压缸入口蒸汽焓值 | kJ/kg | float32
CALC.N1TC_Han_HPStmOut | 14718 | 高压缸出口蒸汽焓值 | kJ/kg | float32
CALC.N1TC_Eff_HP | 14719 | 高压缸效率 | % | float32
CALC.N1TC_Han_IPStmIn | 14720 | 中压缸入口蒸汽焓值 | kJ/kg | float32
CALC.N1TC_Han_IPStmOut | 14721 | 中压缸出口蒸汽焓值 | kJ/kg | float32
CALC.N1TC_Eff_IP | 14722 | 中压缸效率 | % | float32
CALC.N1TC_Han_LPStmIn | 14723 | 低压缸入口蒸汽焓值 | kJ/kg | float32
CALC.N1TC_Han_CNDIn | 14724 | 给水焓值 | kJ/kg | float32
CALC.N1TC_Han_SupplyHeat | 14725 | 采暖蒸汽焓值 | kJ/kg | float32
CALC.N1TC_Han_ShuWater | 14726 | 热网加热器疏水焓 | kJ/kg | float32
CALC.N1TS_Q_SupplyHeat | 14727 | 热负荷功率 | MW | float32
CALC.N1TC_HeatRate | 14728 | 汽轮机热耗率 | kJ/kwh | float32
CALC.N1TC_EFF_Turbine | 14729 | 汽轮机电效率 | % | float32
CALC.N1TC_SteamRate | 14730 | 汽轮机汽耗率 | kg/kWh | float32
CALC.N1TC_RW_SupplyHeat | 14731 | 供热比 | % | float32
CALC.N1TC_RW_HeatToEle | 14732 | 热电比 | GJ/MWh | float32
CALC.N1TC_R_WaterRep | 14733 | 补水率 | % | float32
CALC.N1TC_R_WaterRepHeat | 14734 | 供热补水率 | % | float32
CALC.N1TC_Eff_SupplyHeat | 14735 | 供热热效率 | % | float32
CALC.N1TC_Eff_Fuel | 14736 | 燃料利用系数 | % | float32
CALC.N1TC_W_PEC | 14737 | 厂用电功率 | MW | float32
CALC.N1TC_RW_PEC | 14738 | 厂用电率 | % | float32
CALC.N1TC_R_FuelExpendGE | 14739 | 供电气耗 | Nm3/kWh | float32
CALC.N1TC_R_FuelExpend | 14740 | 发电气耗率 | Nm3/kWh | float32
CALC.N1TC_R_FuelExpendHE | 14741 | 供热气耗 | Nm3/GJ | float32
CALC.N1TC_CoalRate | 14742 | 供电煤耗 | g/kWh | float32
CALC.N1TC_CoalRate_GE | 14743 | 发电煤耗 | g/kWh | float32
CALC.N1TC_CoalRateHeatHE | 14744 | 供热煤耗 | kg/GJ | float32
CALC.N1TC_N_HetLoad | 14745 | 凝汽器热负荷 | t/h | float32
CALC.N1TC_N_AdLoad | 14746 | 凝汽器附加热负荷 | % | float32
CALC.N1TC_DT_CirWater | 14747 | 循环水温升 | t/h | float32
CALC.N1TC_C_HetTrs | 14748 | 凝汽器传热系数 | t/h | float32
CALC.N1TC_ConWaterSC | 14749 | 凝结水过冷度 | t/h | float32
CALC.N1TC_TTD_Con | 14750 | 凝汽器端差 | t/h | float32
CALC.N1TC_TS_LPex | 14751 | 低压缸排汽压力对应饱和温度 | t/h | float32
CALC.N1TC_P_LPEX_COE | 14752 | 真空度 | t/h | float32
CALC.N1TC_Eff_LP | 14753 | 低压缸效率 | % | float32
CALC.N1TC_X_LPex | 14754 | 汽轮机排汽干度 |  | float32
CALC.N1TC_Han_LPex | 14755 | 低压缸出口蒸汽焓值 | kJ/kg | float32
CALC.N1TS_T_MS_T | 14756 | 主蒸汽温度(目标) | ℃ | float32
CALC.N1TS_P_MS_T | 14757 | 主蒸汽压力(目标) | MPa | float32
CALC.N1TS_T_HRh_T | 14758 | 再热蒸汽温度(目标) | ℃ | float32
CALC.N1TC_Eff_HP_T | 14759 | 高压缸效率(目标) | % | float32
CALC.N1TC_Eff_IP_T | 14760 | 中压缸效率(目标) | % | float32
CALC.N1TS_P_LPex_T | 14761 | 低排压力(目标) | kPa | float32
CALC.N1TC_HeatRate_T | 14762 | 汽机热耗率(目标) | kJ/kWh | float32
CALC.N1TS_P_LPexAST_T | 14763 | 低压缸排汽压力(目标)(绝对值) |  | float32
CALC.N1TC_CV_T_MS_NUM | 14764 | 主蒸汽温度曲线(目标)_Num |  | float32
CALC.N1TC_CV_T_MS_X01 | 14765 | 主蒸汽温度曲线(目标)_X01 |  | float32
CALC.N1TC_CV_T_MS_Y01 | 14766 | 主蒸汽温度曲线(目标)_Y01 |  | float32
CALC.N1TC_CV_T_MS_X02 | 14767 | 主蒸汽温度曲线(目标)_X02 |  | float32
CALC.N1TC_CV_T_MS_Y02 | 14768 | 主蒸汽温度曲线(目标)_Y02 |  | float32
CALC.N1TC_CV_T_MS_X03 | 14769 | 主蒸汽温度曲线(目标)_X03 |  | float32
CALC.N1TC_CV_T_MS_Y03 | 14770 | 主蒸汽温度曲线(目标)_Y03 |  | float32
CALC.N1TC_CV_T_MS_X04 | 14771 | 主蒸汽温度曲线(目标)_X04 |  | float32
CALC.N1TC_CV_T_MS_Y04 | 14772 | 主蒸汽温度曲线(目标)_Y04 |  | float32
CALC.N1TC_CV_T_MS_X05 | 14773 | 主蒸汽温度曲线(目标)_X05 |  | float32
CALC.N1TC_CV_T_MS_Y05 | 14774 | 主蒸汽温度曲线(目标)_Y05 |  | float32
CALC.N1TC_CV_T_MS_X06 | 14775 | 主蒸汽温度曲线(目标)_X06 |  | float32
CALC.N1TC_CV_T_MS_Y06 | 14776 | 主蒸汽温度曲线(目标)_Y06 |  | float32
CALC.N1TC_CV_T_MS_X07 | 14777 | 主蒸汽温度曲线(目标)_X07 |  | float32
CALC.N1TC_CV_T_MS_Y07 | 14778 | 主蒸汽温度曲线(目标)_Y07 |  | float32
CALC.N1TC_CV_T_MS_X08 | 14779 | 主蒸汽温度曲线(目标)_X08 |  | float32
CALC.N1TC_CV_T_MS_Y08 | 14780 | 主蒸汽温度曲线(目标)_Y08 |  | float32
CALC.N1TC_CV_T_MS_X09 | 14781 | 主蒸汽温度曲线(目标)_X09 |  | float32
CALC.N1TC_CV_T_MS_Y09 | 14782 | 主蒸汽温度曲线(目标)_Y09 |  | float32
CALC.N1TC_CV_T_MS_X10 | 14783 | 主蒸汽温度曲线(目标)_X10 |  | float32
CALC.N1TC_CV_T_MS_Y10 | 14784 | 主蒸汽温度曲线(目标)_Y10 |  | float32
CALC.N1TC_CV_P_MS_NUM | 14785 | 主蒸汽压力曲线(目标)_Num |  | float32
CALC.N1TC_CV_P_MS_X01 | 14786 | 主蒸汽压力曲线(目标)_X01 |  | float32
CALC.N1TC_CV_P_MS_Y01 | 14787 | 主蒸汽压力曲线(目标)_Y01 |  | float32
CALC.N1TC_CV_P_MS_X02 | 14788 | 主蒸汽压力曲线(目标)_X02 |  | float32
CALC.N1TC_CV_P_MS_Y02 | 14789 | 主蒸汽压力曲线(目标)_Y02 |  | float32
CALC.N1TC_CV_P_MS_X03 | 14790 | 主蒸汽压力曲线(目标)_X03 |  | float32
CALC.N1TC_CV_P_MS_Y03 | 14791 | 主蒸汽压力曲线(目标)_Y03 |  | float32
CALC.N1TC_CV_P_MS_X04 | 14792 | 主蒸汽压力曲线(目标)_X04 |  | float32
CALC.N1TC_CV_P_MS_Y04 | 14793 | 主蒸汽压力曲线(目标)_Y04 |  | float32
CALC.N1TC_CV_P_MS_X05 | 14794 | 主蒸汽压力曲线(目标)_X05 |  | float32
CALC.N1TC_CV_P_MS_Y05 | 14795 | 主蒸汽压力曲线(目标)_Y05 |  | float32
CALC.N1TC_CV_P_MS_X06 | 14796 | 主蒸汽压力曲线(目标)_X06 |  | float32
CALC.N1TC_CV_P_MS_Y06 | 14797 | 主蒸汽压力曲线(目标)_Y06 |  | float32
CALC.N1TC_CV_P_MS_X07 | 14798 | 主蒸汽压力曲线(目标)_X07 |  | float32
CALC.N1TC_CV_P_MS_Y07 | 14799 | 主蒸汽压力曲线(目标)_Y07 |  | float32
CALC.N1TC_CV_P_MS_X08 | 14800 | 主蒸汽压力曲线(目标)_X08 |  | float32
CALC.N1TC_CV_P_MS_Y08 | 14801 | 主蒸汽压力曲线(目标)_Y08 |  | float32
CALC.N1TC_CV_P_MS_X09 | 14802 | 主蒸汽压力曲线(目标)_X09 |  | float32
CALC.N1TC_CV_P_MS_Y09 | 14803 | 主蒸汽压力曲线(目标)_Y09 |  | float32
CALC.N1TC_CV_P_MS_X10 | 14804 | 主蒸汽压力曲线(目标)_X10 |  | float32
CALC.N1TC_CV_P_MS_Y10 | 14805 | 主蒸汽压力曲线(目标)_Y10 |  | float32
CALC.N1TC_CV_T_HRH_NUM | 14806 | 再热蒸汽温度曲线(目标)_Num |  | float32
CALC.N1TC_CV_T_HRH_X01 | 14807 | 再热蒸汽温度曲线(目标)_X01 |  | float32
CALC.N1TC_CV_T_HRH_Y01 | 14808 | 再热蒸汽温度曲线(目标)_Y01 |  | float32
CALC.N1TC_CV_T_HRH_X02 | 14809 | 再热蒸汽温度曲线(目标)_X02 |  | float32
CALC.N1TC_CV_T_HRH_Y02 | 14810 | 再热蒸汽温度曲线(目标)_Y02 |  | float32
CALC.N1TC_CV_T_HRH_X03 | 14811 | 再热蒸汽温度曲线(目标)_X03 |  | float32
CALC.N1TC_CV_T_HRH_Y03 | 14812 | 再热蒸汽温度曲线(目标)_Y03 |  | float32
CALC.N1TC_CV_T_HRH_X04 | 14813 | 再热蒸汽温度曲线(目标)_X04 |  | float32
CALC.N1TC_CV_T_HRH_Y04 | 14814 | 再热蒸汽温度曲线(目标)_Y04 |  | float32
CALC.N1TC_CV_T_HRH_X05 | 14815 | 再热蒸汽温度曲线(目标)_X05 |  | float32
CALC.N1TC_CV_T_HRH_Y05 | 14816 | 再热蒸汽温度曲线(目标)_Y05 |  | float32
CALC.N1TC_CV_T_HRH_X06 | 14817 | 再热蒸汽温度曲线(目标)_X06 |  | float32
CALC.N1TC_CV_T_HRH_Y06 | 14818 | 再热蒸汽温度曲线(目标)_Y06 |  | float32
CALC.N1TC_CV_T_HRH_X07 | 14819 | 再热蒸汽温度曲线(目标)_X07 |  | float32
CALC.N1TC_CV_T_HRH_Y07 | 14820 | 再热蒸汽温度曲线(目标)_Y07 |  | float32
CALC.N1TC_CV_T_HRH_X08 | 14821 | 再热蒸汽温度曲线(目标)_X08 |  | float32
CALC.N1TC_CV_T_HRH_Y08 | 14822 | 再热蒸汽温度曲线(目标)_Y08 |  | float32
CALC.N1TC_CV_T_HRH_X09 | 14823 | 再热蒸汽温度曲线(目标)_X09 |  | float32
CALC.N1TC_CV_T_HRH_Y09 | 14824 | 再热蒸汽温度曲线(目标)_Y09 |  | float32
CALC.N1TC_CV_T_HRH_X10 | 14825 | 再热蒸汽温度曲线(目标)_X10 |  | float32
CALC.N1TC_CV_T_HRH_Y10 | 14826 | 再热蒸汽温度曲线(目标)_Y10 |  | float32
CALC.N1TC_CV_EFF_HP_NUM | 14827 | 高压缸效率曲线(目标)_Num |  | float32
CALC.N1TC_CV_EFF_HP_X01 | 14828 | 高压缸效率曲线(目标)_X01 |  | float32
CALC.N1TC_CV_EFF_HP_Y01 | 14829 | 高压缸效率曲线(目标)_Y01 |  | float32
CALC.N1TC_CV_EFF_HP_X02 | 14830 | 高压缸效率曲线(目标)_X02 |  | float32
CALC.N1TC_CV_EFF_HP_Y02 | 14831 | 高压缸效率曲线(目标)_Y02 |  | float32
CALC.N1TC_CV_EFF_HP_X03 | 14832 | 高压缸效率曲线(目标)_X03 |  | float32
CALC.N1TC_CV_EFF_HP_Y03 | 14833 | 高压缸效率曲线(目标)_Y03 |  | float32
CALC.N1TC_CV_EFF_HP_X04 | 14834 | 高压缸效率曲线(目标)_X04 |  | float32
CALC.N1TC_CV_EFF_HP_Y04 | 14835 | 高压缸效率曲线(目标)_Y04 |  | float32
CALC.N1TC_CV_EFF_HP_X05 | 14836 | 高压缸效率曲线(目标)_X05 |  | float32
CALC.N1TC_CV_EFF_HP_Y05 | 14837 | 高压缸效率曲线(目标)_Y05 |  | float32
CALC.N1TC_CV_EFF_HP_X06 | 14838 | 高压缸效率曲线(目标)_X06 |  | float32
CALC.N1TC_CV_EFF_HP_Y06 | 14839 | 高压缸效率曲线(目标)_Y06 |  | float32
CALC.N1TC_CV_EFF_HP_X07 | 14840 | 高压缸效率曲线(目标)_X07 |  | float32
CALC.N1TC_CV_EFF_HP_Y07 | 14841 | 高压缸效率曲线(目标)_Y07 |  | float32
CALC.N1TC_CV_EFF_HP_X08 | 14842 | 高压缸效率曲线(目标)_X08 |  | float32
CALC.N1TC_CV_EFF_HP_Y08 | 14843 | 高压缸效率曲线(目标)_Y08 |  | float32
CALC.N1TC_CV_EFF_HP_X09 | 14844 | 高压缸效率曲线(目标)_X09 |  | float32
CALC.N1TC_CV_EFF_HP_Y09 | 14845 | 高压缸效率曲线(目标)_Y09 |  | float32
CALC.N1TC_CV_EFF_HP_X10 | 14846 | 高压缸效率曲线(目标)_X10 |  | float32
CALC.N1TC_CV_EFF_HP_Y10 | 14847 | 高压缸效率曲线(目标)_Y10 |  | float32
CALC.N1TC_CV_EFF_IP_NUM | 14848 | 中压缸效率曲线(目标)_Num |  | float32
CALC.N1TC_CV_EFF_IP_X01 | 14849 | 中压缸效率曲线(目标)_X01 |  | float32
CALC.N1TC_CV_EFF_IP_Y01 | 14850 | 中压缸效率曲线(目标)_Y01 |  | float32
CALC.N1TC_CV_EFF_IP_X02 | 14851 | 中压缸效率曲线(目标)_X02 |  | float32
CALC.N1TC_CV_EFF_IP_Y02 | 14852 | 中压缸效率曲线(目标)_Y02 |  | float32
CALC.N1TC_CV_EFF_IP_X03 | 14853 | 中压缸效率曲线(目标)_X03 |  | float32
CALC.N1TC_CV_EFF_IP_Y03 | 14854 | 中压缸效率曲线(目标)_Y03 |  | float32
CALC.N1TC_CV_EFF_IP_X04 | 14855 | 中压缸效率曲线(目标)_X04 |  | float32
CALC.N1TC_CV_EFF_IP_Y04 | 14856 | 中压缸效率曲线(目标)_Y04 |  | float32
CALC.N1TC_CV_EFF_IP_X05 | 14857 | 中压缸效率曲线(目标)_X05 |  | float32
CALC.N1TC_CV_EFF_IP_Y05 | 14858 | 中压缸效率曲线(目标)_Y05 |  | float32
CALC.N1TC_CV_EFF_IP_X06 | 14859 | 中压缸效率曲线(目标)_X06 |  | float32
CALC.N1TC_CV_EFF_IP_Y06 | 14860 | 中压缸效率曲线(目标)_Y06 |  | float32
CALC.N1TC_CV_EFF_IP_X07 | 14861 | 中压缸效率曲线(目标)_X07 |  | float32
CALC.N1TC_CV_EFF_IP_Y07 | 14862 | 中压缸效率曲线(目标)_Y07 |  | float32
CALC.N1TC_CV_EFF_IP_X08 | 14863 | 中压缸效率曲线(目标)_X08 |  | float32
CALC.N1TC_CV_EFF_IP_Y08 | 14864 | 中压缸效率曲线(目标)_Y08 |  | float32
CALC.N1TC_CV_EFF_IP_X09 | 14865 | 中压缸效率曲线(目标)_X09 |  | float32
CALC.N1TC_CV_EFF_IP_Y09 | 14866 | 中压缸效率曲线(目标)_Y09 |  | float32
CALC.N1TC_CV_EFF_IP_X10 | 14867 | 中压缸效率曲线(目标)_X10 |  | float32
CALC.N1TC_CV_EFF_IP_Y10 | 14868 | 中压缸效率曲线(目标)_Y10 |  | float32
CALC.N1TC_CV_HEATRATE_NUM | 14869 | 热耗率曲线(目标)_Num |  | float32
CALC.N1TC_CV_HEATRATE_X01 | 14870 | 热耗率曲线(目标)_X01 |  | float32
CALC.N1TC_CV_HEATRATE_Y01 | 14871 | 热耗率曲线(目标)_Y01 |  | float32
CALC.N1TC_CV_HEATRATE_X02 | 14872 | 热耗率曲线(目标)_X02 |  | float32
CALC.N1TC_CV_HEATRATE_Y02 | 14873 | 热耗率曲线(目标)_Y02 |  | float32
CALC.N1TC_CV_HEATRATE_X03 | 14874 | 热耗率曲线(目标)_X03 |  | float32
CALC.N1TC_CV_HEATRATE_Y03 | 14875 | 热耗率曲线(目标)_Y03 |  | float32
CALC.N1TC_CV_HEATRATE_X04 | 14876 | 热耗率曲线(目标)_X04 |  | float32
CALC.N1TC_CV_HEATRATE_Y04 | 14877 | 热耗率曲线(目标)_Y04 |  | float32
CALC.N1TC_CV_HEATRATE_X05 | 14878 | 热耗率曲线(目标)_X05 |  | float32
CALC.N1TC_CV_HEATRATE_Y05 | 14879 | 热耗率曲线(目标)_Y05 |  | float32
CALC.N1TC_CV_HEATRATE_X06 | 14880 | 热耗率曲线(目标)_X06 |  | float32
CALC.N1TC_CV_HEATRATE_Y06 | 14881 | 热耗率曲线(目标)_Y06 |  | float32
CALC.N1TC_CV_P_LPEX_NUM | 14882 | 低排压力曲线(目标)_Num |  | float32
CALC.N1TC_CV_P_LPEX_X01 | 14883 | 低排压力曲线(目标)_X01 |  | float32
CALC.N1TC_CV_P_LPEX_Y01 | 14884 | 低排压力曲线(目标)_Y01 |  | float32
CALC.N1TC_CV_P_LPEX_X02 | 14885 | 低排压力曲线(目标)_X02 |  | float32
CALC.N1TC_CV_P_LPEX_Y02 | 14886 | 低排压力曲线(目标)_Y02 |  | float32
CALC.N1TC_CV_P_LPEX_X03 | 14887 | 低排压力曲线(目标)_X03 |  | float32
CALC.N1TC_CV_P_LPEX_Y03 | 14888 | 低排压力曲线(目标)_Y03 |  | float32
CALC.N1TC_CV_P_LPEX_X04 | 14889 | 低排压力曲线(目标)_X04 |  | float32
CALC.N1TC_CV_P_LPEX_Y04 | 14890 | 低排压力曲线(目标)_Y04 |  | float32
CALC.N1TC_CV_P_LPEX_X05 | 14891 | 低排压力曲线(目标)_X05 |  | float32
CALC.N1TC_CV_P_LPEX_Y05 | 14892 | 低排压力曲线(目标)_Y05 |  | float32
CALC.N1TC_CV_P_LPEX_X06 | 14893 | 低排压力曲线(目标)_X06 |  | float32
CALC.N1TC_CV_P_LPEX_Y06 | 14894 | 低排压力曲线(目标)_Y06 |  | float32
CALC.N1TC_CV_P_LPEX_X07 | 14895 | 低排压力曲线(目标)_X07 |  | float32
CALC.N1TC_CV_P_LPEX_Y07 | 14896 | 低排压力曲线(目标)_Y07 |  | float32
CALC.N1TC_CV_P_LPEX_X08 | 14897 | 低排压力曲线(目标)_X08 |  | float32
CALC.N1TC_CV_P_LPEX_Y08 | 14898 | 低排压力曲线(目标)_Y08 |  | float32
CALC.N1TC_CV_P_LPEX_X09 | 14899 | 低排压力曲线(目标)_X09 |  | float32
CALC.N1TC_CV_P_LPEX_Y09 | 14900 | 低排压力曲线(目标)_Y09 |  | float32
CALC.N1TC_CV_P_LPEX_X10 | 14901 | 低排压力曲线(目标)_X10 |  | float32
CALC.N1TC_CV_P_LPEX_Y10 | 14902 | 低排压力曲线(目标)_Y10 |  | float32
CALC.N1TC_CV_HEATRT_D_NUM | 14903 | 热耗率曲线(未修正)_Num |  | float32
CALC.N1TC_CV_HEATRT_D_X01 | 14904 | 热耗率曲线(未修正)_X01 |  | float32
CALC.N1TC_CV_HEATRT_D_Y01 | 14905 | 热耗率曲线(未修正)_Y01 |  | float32
CALC.N1TC_CV_HEATRT_D_X02 | 14906 | 热耗率曲线(未修正)_X02 |  | float32
CALC.N1TC_CV_HEATRT_D_Y02 | 14907 | 热耗率曲线(未修正)_Y02 |  | float32
CALC.N1TC_CV_HEATRT_D_X03 | 14908 | 热耗率曲线(未修正)_X03 |  | float32
CALC.N1TC_CV_HEATRT_D_Y03 | 14909 | 热耗率曲线(未修正)_Y03 |  | float32
CALC.N1TC_CV_HEATRT_D_X04 | 14910 | 热耗率曲线(未修正)_X04 |  | float32
CALC.N1TC_CV_HEATRT_D_Y04 | 14911 | 热耗率曲线(未修正)_Y04 |  | float32
CALC.N1TC_CV_HEATRT_D_X05 | 14912 | 热耗率曲线(未修正)_X05 |  | float32
CALC.N1TC_CV_HEATRT_D_Y05 | 14913 | 热耗率曲线(未修正)_Y05 |  | float32
CALC.N1TC_CV_HEATRT_D_X06 | 14914 | 热耗率曲线(未修正)_X06 |  | float32
CALC.N1TC_CV_HEATRT_D_Y06 | 14915 | 热耗率曲线(未修正)_Y06 |  | float32
CALC.N1TC_CV_HEATRT_D_X07 | 14916 | 热耗率曲线(未修正)_X07 |  | float32
CALC.N1TC_CV_HEATRT_D_Y07 | 14917 | 热耗率曲线(未修正)_Y07 |  | float32
CALC.N1TC_CV_HEATRT_D_X08 | 14918 | 热耗率曲线(未修正)_X08 |  | float32
CALC.N1TC_CV_HEATRT_D_Y08 | 14919 | 热耗率曲线(未修正)_Y08 |  | float32
CALC.N1TC_CV_HEATRT_D_X09 | 14920 | 热耗率曲线(未修正)_X09 |  | float32
CALC.N1TC_CV_HEATRT_D_Y09 | 14921 | 热耗率曲线(未修正)_Y09 |  | float32
CALC.N1TC_CV_HEATRT_D_X10 | 14922 | 热耗率曲线(未修正)_X10 |  | float32
CALC.N1TC_CV_HEATRT_D_Y10 | 14923 | 热耗率曲线(未修正)_Y10 |  | float32
CALC.N1TC_CPR_P_HPStmIn | 14924 | 高压蒸汽压力对功率的修正系数 |  | float32
CALC.N1TC_CPR_T_HPStmIn | 14925 | 高压蒸汽温度对功率的修正系数 |  | float32
CALC.N1TC_CPR_T_IPStmIn | 14926 | 中压蒸汽温度对功率的修正系数 |  | float32
CALC.N1TC_CPR_T_LPStmIn | 14927 | 低压蒸汽温度对功率的修正系数 |  | float32
CALC.N1TC_CPR_P_Lpex | 14928 | 蒸汽轮机背压对功率的修正系数 |  | float32
CALC.N1TC_CPR_F_LPStmIn | 14929 | 低压蒸汽流量对功率的修正系数 |  | float32
CALC.N1TC_CPR_W_G | 14930 | 汽轮机功率总修正系数 |  | float32
CALC.N1TC_W_G_GC | 14931 | 汽轮机功率(修正) | MW | float32
CALC.N1TC_Han_GRWaterRep | 14932 | 供热补水焓 | kJ/kg | float32
CALC.N1GC_R_CToH | 14933 | 碳氢比 |  | float32
CALC.N1GC_MT_FUEL | 14934 | 燃料分子量 | kg/kmol | float32
CALC.N1GC_Qnetar | 14935 | 燃料低热值(计算)kJ/kg | kJ/kg | float32
CALC.N1GC_MT_GAS | 14936 | 燃气分子量 | kg/kmol | float32
CALC.N1GC_R_P2VsP1 | 14937 | 压气机压比P2/P1 |  | float32
CALC.N1GC_Eff_COMP | 14938 | 压气机内效率 | % | float32
CALC.N1GC_R_FuelToAir | 14939 | 燃料空气比(不考虑冷却) |  | float32
CALC.N1GC_T_GASTInISO | 14940 | 燃机入口温度T3(ISO) | ℃ | float32
CALC.N1GC_R_INLET | 14941 | 实际燃料空气比(考虑冷却) |  | float32
CALC.N1GC_R_T3VsT1 | 14942 | 燃气轮机装置温比T3/T1 |  | float32
CALC.N1GC_W_GAST | 14943 | 燃气透平功率 | MW | float32
CALC.N1GC_W_COMPA | 14944 | 压气机耗功率 | MW | float32
CALC.N1GC_T_GASTIn | 14945 | 燃气轮机进口温度T3 | ℃ | float32
CALC.N1GC_Eff_GAST | 14946 | 燃气轮机内效率 | % | float32
CALC.N1GC_R_FuelExpend | 14947 | 燃机发电气耗率 | Nm3/kWh | float32
CALC.N1GC_GASTHeatRate | 14948 | 燃机热耗率 | kJ/kWh | float32
CALC.N1GC_Eff_GASTUnit | 14949 | 燃机发电效率 | % | float32
CALC.N1GC_W_PEC | 14950 | 厂用电功率 | MW | float32
CALC.N1GC_RW_PEC | 14951 | 厂用电率 | % | float32
CALC.N1GC_R_FuelExpendGE | 14952 | 燃机供电气耗 | Nm3/kWh | float32
CALC.N1GC_CoalRate_GE | 14953 | 燃机发电煤耗 | g/kWh | float32
CALC.N1GC_CoalRate | 14954 | 燃机供电煤耗 | g/kWh | float32
CALC.N1GC_Eff_COMP_T | 14955 | 压气机效率(目标) | ℃ | float32
CALC.N1GC_Eff_GAST_T | 14956 | 燃机效率(目标) | ℃ | float32
CALC.N1GC_T_GASTOut_T | 14957 | 燃机出口温度(目标) | ℃ | float32
CALC.N1GC_CV_Eff_COMP_NUM | 14958 | 压气机效率曲线(目标)_Num |  | float32
CALC.N1GC_CV_Eff_COMP_X01 | 14959 | 压气机效率曲线(目标)_X01 |  | float32
CALC.N1GC_CV_Eff_COMP_Y01 | 14960 | 压气机效率曲线(目标)_Y01 |  | float32
CALC.N1GC_CV_Eff_COMP_X02 | 14961 | 压气机效率曲线(目标)_X02 |  | float32
CALC.N1GC_CV_Eff_COMP_Y02 | 14962 | 压气机效率曲线(目标)_Y02 |  | float32
CALC.N1GC_CV_Eff_COMP_X03 | 14963 | 压气机效率曲线(目标)_X03 |  | float32
CALC.N1GC_CV_Eff_COMP_Y03 | 14964 | 压气机效率曲线(目标)_Y03 |  | float32
CALC.N1GC_CV_Eff_COMP_X04 | 14965 | 压气机效率曲线(目标)_X04 |  | float32
CALC.N1GC_CV_Eff_COMP_Y04 | 14966 | 压气机效率曲线(目标)_Y04 |  | float32
CALC.N1GC_CV_Eff_COMP_X05 | 14967 | 压气机效率曲线(目标)_X05 |  | float32
CALC.N1GC_CV_Eff_COMP_Y05 | 14968 | 压气机效率曲线(目标)_Y05 |  | float32
CALC.N1GC_CV_Eff_COMP_X06 | 14969 | 压气机效率曲线(目标)_X06 |  | float32
CALC.N1GC_CV_Eff_COMP_Y06 | 14970 | 压气机效率曲线(目标)_Y06 |  | float32
CALC.N1GC_CV_Eff_COMP_X07 | 14971 | 压气机效率曲线(目标)_X07 |  | float32
CALC.N1GC_CV_Eff_COMP_Y07 | 14972 | 压气机效率曲线(目标)_Y07 |  | float32
CALC.N1GC_CV_Eff_COMP_X08 | 14973 | 压气机效率曲线(目标)_X08 |  | float32
CALC.N1GC_CV_Eff_COMP_Y08 | 14974 | 压气机效率曲线(目标)_Y08 |  | float32
CALC.N1GC_CV_Eff_COMP_X09 | 14975 | 压气机效率曲线(目标)_X09 |  | float32
CALC.N1GC_CV_Eff_COMP_Y09 | 14976 | 压气机效率曲线(目标)_Y09 |  | float32
CALC.N1GC_CV_Eff_COMP_X10 | 14977 | 压气机效率曲线(目标)_X10 |  | float32
CALC.N1GC_CV_Eff_COMP_Y10 | 14978 | 压气机效率曲线(目标)_Y10 |  | float32
CALC.N1GC_CV_Eff_GAST_NUM | 14979 | 燃机效率曲线(目标)_Num |  | float32
CALC.N1GC_CV_Eff_GAST_X01 | 14980 | 燃机效率曲线(目标)_X01 |  | float32
CALC.N1GC_CV_Eff_GAST_Y01 | 14981 | 燃机效率曲线(目标)_Y01 |  | float32
CALC.N1GC_CV_Eff_GAST_X02 | 14982 | 燃机效率曲线(目标)_X02 |  | float32
CALC.N1GC_CV_Eff_GAST_Y02 | 14983 | 燃机效率曲线(目标)_Y02 |  | float32
CALC.N1GC_CV_Eff_GAST_X03 | 14984 | 燃机效率曲线(目标)_X03 |  | float32
CALC.N1GC_CV_Eff_GAST_Y03 | 14985 | 燃机效率曲线(目标)_Y03 |  | float32
CALC.N1GC_CV_Eff_GAST_X04 | 14986 | 燃机效率曲线(目标)_X04 |  | float32
CALC.N1GC_CV_Eff_GAST_Y04 | 14987 | 燃机效率曲线(目标)_Y04 |  | float32
CALC.N1GC_CV_Eff_GAST_X05 | 14988 | 燃机效率曲线(目标)_X05 |  | float32
CALC.N1GC_CV_Eff_GAST_Y05 | 14989 | 燃机效率曲线(目标)_Y05 |  | float32
CALC.N1GC_CV_Eff_GAST_X06 | 14990 | 燃机效率曲线(目标)_X06 |  | float32
CALC.N1GC_CV_Eff_GAST_Y06 | 14991 | 燃机效率曲线(目标)_Y06 |  | float32
CALC.N1GC_CV_Eff_GAST_X07 | 14992 | 燃机效率曲线(目标)_X07 |  | float32
CALC.N1GC_CV_Eff_GAST_Y07 | 14993 | 燃机效率曲线(目标)_Y07 |  | float32
CALC.N1GC_CV_Eff_GAST_X08 | 14994 | 燃机效率曲线(目标)_X08 |  | float32
CALC.N1GC_CV_Eff_GAST_Y08 | 14995 | 燃机效率曲线(目标)_Y08 |  | float32
CALC.N1GC_CV_Eff_GAST_X09 | 14996 | 燃机效率曲线(目标)_X09 |  | float32
CALC.N1GC_CV_Eff_GAST_Y09 | 14997 | 燃机效率曲线(目标)_Y09 |  | float32
CALC.N1GC_CV_Eff_GAST_X10 | 14998 | 燃机效率曲线(目标)_X10 |  | float32
CALC.N1GC_CV_Eff_GAST_Y10 | 14999 | 燃机效率曲线(目标)_Y10 |  | float32
CALC.N1GC_CV_T_GASTOut_NUM | 15000 | 燃机出口温度曲线(目标)_Num |  | float32
CALC.N1GC_CV_T_GASTOut_X01 | 15001 | 燃机出口温度曲线(目标)_X01 |  | float32
CALC.N1GC_CV_T_GASTOut_Y01 | 15002 | 燃机出口温度曲线(目标)_Y01 |  | float32
CALC.N1GC_CV_T_GASTOut_X02 | 15003 | 燃机出口温度曲线(目标)_X02 |  | float32
CALC.N1GC_CV_T_GASTOut_Y02 | 15004 | 燃机出口温度曲线(目标)_Y02 |  | float32
CALC.N1GC_CV_T_GASTOut_X03 | 15005 | 燃机出口温度曲线(目标)_X03 |  | float32
CALC.N1GC_CV_T_GASTOut_Y03 | 15006 | 燃机出口温度曲线(目标)_Y03 |  | float32
CALC.N1GC_CV_T_GASTOut_X04 | 15007 | 燃机出口温度曲线(目标)_X04 |  | float32
CALC.N1GC_CV_T_GASTOut_Y04 | 15008 | 燃机出口温度曲线(目标)_Y04 |  | float32
CALC.N1GC_CV_T_GASTOut_X05 | 15009 | 燃机出口温度曲线(目标)_X05 |  | float32
CALC.N1GC_CV_T_GASTOut_Y05 | 15010 | 燃机出口温度曲线(目标)_Y05 |  | float32
CALC.N1GC_CV_T_GASTOut_X06 | 15011 | 燃机出口温度曲线(目标)_X06 |  | float32
CALC.N1GC_CV_T_GASTOut_Y06 | 15012 | 燃机出口温度曲线(目标)_Y06 |  | float32
CALC.N1GC_CV_T_GASTOut_X07 | 15013 | 燃机出口温度曲线(目标)_X07 |  | float32
CALC.N1GC_CV_T_GASTOut_Y07 | 15014 | 燃机出口温度曲线(目标)_Y07 |  | float32
CALC.N1GC_CV_T_GASTOut_X08 | 15015 | 燃机出口温度曲线(目标)_X08 |  | float32
CALC.N1GC_CV_T_GASTOut_Y08 | 15016 | 燃机出口温度曲线(目标)_Y08 |  | float32
CALC.N1GC_CV_T_GASTOut_X09 | 15017 | 燃机出口温度曲线(目标)_X09 |  | float32
CALC.N1GC_CV_T_GASTOut_Y09 | 15018 | 燃机出口温度曲线(目标)_Y09 |  | float32
CALC.N1GC_CV_T_GASTOut_X10 | 15019 | 燃机出口温度曲线(目标)_X10 |  | float32
CALC.N1GC_CV_T_GASTOut_Y10 | 15020 | 燃机出口温度曲线(目标)_Y10 |  | float32
CALC.N1PC_R_STToGT | 15021 | 联合循环蒸燃功比 | % | float32
CALC.N1PC_R_STToUnit | 15022 | 联合循环蒸功百分率 | % | float32
CALC.N1PC_HeatRate | 15023 | 联合循环热耗率 | kJ/kWh | float32
CALC.N1PC_Eff_Unit | 15024 | 联合循环电效率 | % | float32
CALC.N1PC_W_PEC | 15025 | 厂用电功率 | MW | float32
CALC.N1PC_RW_PEC | 15026 | 厂用电率 | % | float32
CALC.N1PC_CoalRate_GE | 15027 | 联合循环发电煤耗 | g/kWh | float32
CALC.N1PC_CoalRate | 15028 | 联合循环供电煤耗 | g/kWh | float32
CALC.N1PC_Eff_Fuel | 15029 | 燃料利用系数 | % | float32
CALC.N1PC_RW_HeatToEle | 15030 | 热电比 | GJ/MWh | float32
CALC.N1PC_RW_SupplyHeat | 15031 | 供热比 | % | float32
CALC.N1PC_Eff_SupplyHeat | 15032 | 供热热效率 | % | float32
CALC.N1PC_RW_PECHeat | 15033 | 供热用厂用电率 | kWh/GJ | float32
CALC.N1PC_R_FuelExpendHE | 15034 | 联合循环供热气耗 | Nm3/GJ | float32
CALC.N1PC_R_FuelExpend | 15035 | 联合循环发电气耗率 | Nm3/kWh | float32
CALC.N1PC_R_FuelExpendGE | 15036 | 联合循环供电气耗 | Nm3/kWh | float32
CALC.N1PC_RW_PECEle | 15037 | 发电用厂用电率 | Nm3/GJ | float32
CALC.N1PC_CoalRateHeatHE | 15038 | 联合循环供热煤耗 | % | float32
CALC.N1PS_Qnetar | 15039 | 燃料低热值 | % | float32
CALC.N1PC_CHR_P_atm | 15040 | 大气压力对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_P_atm | 15041 | 大气压力对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CHR_T_atm | 15042 | 大气温度对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_T_atm | 15043 | 大气温度对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CHR_Qnetar | 15044 | 燃料低热值对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_Qnetar | 15045 | 燃料低热值对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CHR_Humidity | 15046 | 相对湿度对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_Humidity | 15047 | 相对湿度对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CHR_P_Lpex | 15048 | 蒸汽轮机背压对联合热耗修正系数 |  | float32
CALC.N1PC_HR_P_Lpex | 15049 | 蒸汽轮机背压对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CHR_R_WaterRep | 15050 | 补给水率对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_R_WaterRep | 15051 | 补给水率对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CHR_Frequency | 15052 | 发电机频率对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_Frequency | 15053 | 发电机频率对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CHR_SupplyHeat | 15054 | 热负荷对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_SupplyHeat | 15055 | 热负荷对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CHR_Runtime | 15056 | 老化对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_Runtime | 15057 | 老化对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_HeatRate_GC | 15058 | 联合循环热耗率(基准工况) | kJ/kWh | float32
CALC.N1PC_CPR_P_atm | 15059 | 大气压力对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_P_atm | 15060 | 大气压力对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPR_T_atm | 15061 | 大气温度对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_T_atm | 15062 | 大气温度对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPR_Qnetar | 15063 | 燃料低热值对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_Qnetar | 15064 | 燃料低热值对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPR_Humidity | 15065 | 相对湿度对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_Humidity | 15066 | 相对湿度对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPR_P_Lpex | 15067 | 蒸汽轮机背压对联合功率修正系数 |  | float32
CALC.N1PC_PR_P_Lpex | 15068 | 蒸汽轮机背压对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPR_R_WaterRep | 15069 | 补给水率对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_R_WaterRep | 15070 | 补给水率对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPR_Frequency | 15071 | 发电机频率对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_Frequency | 15072 | 发电机频率对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPR_SupplyHeat | 15073 | 热负荷对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_SupplyHeat | 15074 | 热负荷对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPR_Runtime | 15075 | 老化对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_Runtime | 15076 | 老化对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_W_G_GC | 15077 | 联合循环发电机功率(基准工况) | MW | float32
CALC.N1PC_W_GT | 15078 | 联合循环发电机理论功率 | MW | float32
CALC.N1PC_CV_HEATRATE_NUM | 15079 | 热耗率曲线(目标)_Num |  | float32
CALC.N1PC_CV_HEATRATE_X01 | 15080 | 热耗率曲线(目标)_X01 |  | float32
CALC.N1PC_CV_HEATRATE_Y01 | 15081 | 热耗率曲线(目标)_Y01 |  | float32
CALC.N1PC_CV_HEATRATE_X02 | 15082 | 热耗率曲线(目标)_X02 |  | float32
CALC.N1PC_CV_HEATRATE_Y02 | 15083 | 热耗率曲线(目标)_Y02 |  | float32
CALC.N1PC_CV_HEATRATE_X03 | 15084 | 热耗率曲线(目标)_X03 |  | float32
CALC.N1PC_CV_HEATRATE_Y03 | 15085 | 热耗率曲线(目标)_Y03 |  | float32
CALC.N1PC_CV_HEATRATE_X04 | 15086 | 热耗率曲线(目标)_X04 |  | float32
CALC.N1PC_CV_HEATRATE_Y04 | 15087 | 热耗率曲线(目标)_Y04 |  | float32
CALC.N1PC_CV_HEATRATE_X05 | 15088 | 热耗率曲线(目标)_X05 |  | float32
CALC.N1PC_CV_HEATRATE_Y05 | 15089 | 热耗率曲线(目标)_Y05 |  | float32
CALC.N1PC_CV_HEATRATE_X06 | 15090 | 热耗率曲线(目标)_X06 |  | float32
CALC.N1PC_CV_HEATRATE_Y06 | 15091 | 热耗率曲线(目标)_Y06 |  | float32
CALC.N1PC_CV_HEATRATE_X07 | 15092 | 热耗率曲线(目标)_X07 |  | float32
CALC.N1PC_CV_HEATRATE_Y07 | 15093 | 热耗率曲线(目标)_Y07 |  | float32
CALC.N1PC_CV_HEATRATE_X08 | 15094 | 热耗率曲线(目标)_X08 |  | float32
CALC.N1PC_CV_HEATRATE_Y08 | 15095 | 热耗率曲线(目标)_Y08 |  | float32
CALC.N1PC_CV_HEATRATE_X09 | 15096 | 热耗率曲线(目标)_X09 |  | float32
CALC.N1PC_CV_HEATRATE_Y09 | 15097 | 热耗率曲线(目标)_Y09 |  | float32
CALC.N1PC_CV_HEATRATE_X10 | 15098 | 热耗率曲线(目标)_X10 |  | float32
CALC.N1PC_CV_HEATRATE_Y10 | 15099 | 热耗率曲线(目标)_Y10 |  | float32
CALC.N1PC_HeatRate_GC_T | 15100 | 联合循环热耗率(基准工况目标) |  | float32
CALC.N1PC_CPH_P_atm | 15101 | 大气压力对热负荷修正系数 |  | float32
CALC.N1PC_PH_P_atm | 15102 | 大气压力对热负荷的影响 | kJ/kWh | float32
CALC.N1PC_CPH_T_atm | 15103 | 大气温度对热负荷修正系数 |  | float32
CALC.N1PC_PH_T_atm | 15104 | 大气温度对热负荷的影响 | kJ/kWh | float32
CALC.N1PC_CPH_Qnetar | 15105 | 燃料低热值对热负荷修正系数 |  | float32
CALC.N1PC_PH_Qnetar | 15106 | 燃料低热值对热负荷的影响 | kJ/kWh | float32
CALC.N1PC_CPH_Humidity | 15107 | 相对湿度对热负荷修正系数 |  | float32
CALC.N1PC_PH_Humidity | 15108 | 相对湿度对热负荷的影响 | kJ/kWh | float32
CALC.N1PC_CPH_P_Lpex | 15109 | 蒸汽轮机背压对热负荷修正系数 |  | float32
CALC.N1PC_PH_P_Lpex | 15110 | 蒸汽轮机背压对热负荷的影响 | kJ/kWh | float32
CALC.N1PC_CPH_R_WaterRep | 15111 | 补给水率对热负荷修正系数 |  | float32
CALC.N1PC_PH_R_WaterRep | 15112 | 补给水率对热负荷的影响 | kJ/kWh | float32
CALC.N1PC_CPH_Frequency | 15113 | 发电机频率对热负荷修正系数 |  | float32
CALC.N1PC_PH_Frequency | 15114 | 发电机频率对热负荷的影响 | kJ/kWh | float32
CALC.N1PC_CPH_SupplyHeat | 15115 | 热负荷对热负荷修正系数 |  | float32
CALC.N1PC_PH_SupplyHeat | 15116 | 热负荷对热负荷的影响 | kJ/kWh | float32
CALC.N1PC_CPH_Runtime | 15117 | 老化对热负荷修正系数 |  | float32
CALC.N1PC_PH_Runtime | 15118 | 老化对热负荷的影响 | kJ/kWh | float32
CALC.NPGC_W_G | 15119 | 全厂燃机功率 | MW | float32
CALC.NPTC_W_G | 15120 | 全厂蒸汽轮机功率 | MW | float32
CALC.NPPC_F_GRCQ | 15121 | 供热抽汽流量 | t/h | float32
CALC.NPPC_Q_SupplyHeat | 15122 | 供热量 | MW | float32
CALC.NPPC_W_GT | 15123 | 全厂最大理论容量 | MW | float32
CALC.NPPC_W_G | 15124 | 全厂负荷 | MW | float32
CALC.NPPC_HeatRate | 15125 | 全厂联合循环热耗率 | kJ/kWh | float32
CALC.NPPC_Eff_Unit | 15126 | 全厂联合循环电效率 | % | float32
CALC.NPPC_R_STToGT | 15127 | 联合循环蒸燃功比 | % | float32
CALC.NPPC_R_STToUnit | 15128 | 联合循环蒸功百分率 | % | float32
CALC.NPPC_RW_PEC | 15129 | 厂用电率 | % | float32
CALC.NPPC_RW_PECEle | 15130 | 供电厂用电率 | % | float32
CALC.NPPC_RW_PECHeat | 15131 | 供热厂用电率 | kWh/GJ | float32
CALC.NPPC_RW_SupplyHeat | 15132 | 供热比 | % | float32
CALC.NPPC_RW_HeatToEle | 15133 | 热电比 | % | float32
CALC.NPPC_Eff_SupplyHeat | 15134 | 供热热效率 | % | float32
CALC.NPPC_R_FuelExpend | 15135 | 联合循环发电气耗率 | Nm3/kWh | float32
CALC.NPPC_R_FuelExpendGE | 15136 | 联合循环供电气耗 | Nm3/kWh | float32
CALC.NPPC_R_FuelExpendHE | 15137 | 联合循环供热气耗 | Nm3/kWh | float32
CALC.NPPC_CoalRate_GE | 15138 | 联合循环发电煤耗 | g/kWh | float32
CALC.NPPC_CoalRate | 15139 | 联合循环供电煤耗 | g/kWh | float32
CALC.NPPC_CoalRateHeatHE | 15140 | 联合循环供热煤耗 | GJ/kg | float32
CALC.NPPC_F_FuelIn | 15141 | 燃料流量 | t/h | float32
CALC.NPPC_F_SupplyHeat | 15142 | 供热抽汽流量 | t/h | float32
CALC.N1PC_HeatRate_PS | 15143 | 联合循环供电热耗率 | kJ/kWh | float32
CALC.N1PC_Eff_Unit_PS | 15144 | 联合循环供电效率 | % | float32
CALC.NPPC_HeatRate_PS | 15145 | 联合循环供电热耗率 | kJ/kWh | float32
CALC.NPPC_Eff_Unit_PS | 15146 | 联合循环供电效率 | % | float32
CALC.N1TC_HeatRate_PS | 15147 | 汽轮机供电热耗率 | kJ/kWh | float32
CALC.N1TC_EFF_Turbine_PS | 15148 | 汽轮机供电效率 | % | float32
CALC.N1GC_GASTHeatRate_PS | 15149 | 燃机供电热耗率 | kJ/kWh | float32
CALC.N1GC_Eff_GASTUnit_PS | 15150 | 燃机供电效率 | % | float32
CALC.N1BS_A_HPFPA | 15151 | 高压给水泵A电流 | A | float32
CALC.N1BS_A_HPFPB | 15152 | 高压给水泵B电流 | A | float32
CALC.N1BS_A_IPFPA | 15153 | 中压给水泵A电流 | A | float32
CALC.N1BS_A_IPFPB | 15154 | 中压给水泵B电流 | A | float32
CALC.N1GS_FuelVN2 | 15155 | 天然气N2含量% | % | float32
CALC.N2PS_P_atm | 15156 | 大气压力kPa | kPa | float32
CALC.N2PS_T_atm | 15157 | 大气温度 | ℃ | float32
CALC.N2PS_R_Humidity | 15158 | 相对湿度 | % | float32
CALC.N2GS_FuelVCH4 | 15159 | 天然气CH4含量% | % | float32
CALC.N2GS_FuelVC2H6 | 15160 | 天然气C2H6含量% | % | float32
CALC.N2GS_FuelVC3H8 | 15161 | 天然气C3H8含量% | % | float32
CALC.N2GS_FuelVCO2 | 15162 | 天然气CO2含量% | % | float32
CALC.N2GS_FuelVN2 | 15163 | 天然气N2含量% | % | float32
CALC.N2GS_Den_Fuel | 15164 | 燃料密度kg/m3 | kg/Nm3 | float32
CALC.N2GS_Qnetar | 15165 | 燃料低热值kJ/kg | kJ/kg | float32
CALC.N2GS_FuelVCO | 15166 | 天然气CO含量% | % | float32
CALC.N2GS_FuelVH2 | 15167 | 天然气H2含量% | % | float32
CALC.N2GS_FuelVC2H4 | 15168 | 天然气C2H4含量% | % | float32
CALC.N2GS_FuelVO2 | 15169 | 天然气O2含量% | % | float32
CALC.N2GS_FuelVH2S | 15170 | 天然气H2S含量% | % | float32
CALC.N2BS_P_StkGasIn | 15171 | 余热锅炉入口烟气压力 | kPa | float32
CALC.N2BS_T_StkGasIn | 15172 | 余热锅炉入口烟气温度 | ℃ | float32
CALC.N2BS_StkO2 | 15173 | 余热锅炉烟囱烟气O2含量 | % | float32
CALC.N2BS_StkCO2 | 15174 | 余热锅炉烟囱烟气CO2含量 | % | float32
CALC.N2BS_StkN2 | 15175 | 余热锅炉烟囱烟气N2含量 | % | float32
CALC.N2BS_StkH2O | 15176 | 余热锅炉烟囱烟气H2O含量 | % | float32
CALC.N2BS_T_StkGasOut | 15177 | 余热锅炉烟囱出口烟气温度 | ℃ | float32
CALC.N2BS_P_StkGasOut | 15178 | 余热锅炉烟囱出口烟气压力 | kPa | float32
CALC.N2BS_F_StkGas | 15179 | 余热锅炉烟囱烟气流量 | t/h | float32
CALC.N2BS_StkSO2 | 15180 | 余热锅炉烟囱烟气SO2含量 | % | float32
CALC.N2BS_T_HPEVAGasIn | 15181 | 高压蒸发器入口烟气温度 | kPa | float32
CALC.N2BS_T_HPEVAGasOut | 15182 | 高压蒸发器出口烟气温度 | ℃ | float32
CALC.N2BS_T_IPEVAGasIn | 15183 | 中压蒸发器入口烟气温度 | % | float32
CALC.N2BS_T_IPEVAGasOut | 15184 | 中压蒸发器出口烟气温度 | % | float32
CALC.N2BS_T_LPEVAGasIn | 15185 | 低压蒸发器入口烟气温度 | % | float32
CALC.N2BS_T_LPEVAGasOut | 15186 | 低压蒸发器出口烟气温度 | % | float32
CALC.N2BS_T_HPSHOut | 15187 | 余热锅炉高压过热蒸汽温度 | ℃ | float32
CALC.N2BS_P_HPSHOut | 15188 | 余热锅炉高压过热蒸汽压力 | MPa | float32
CALC.N2BS_F_HPSHOut | 15189 | 余热锅炉高压过热汽蒸汽流量 | t/h | float32
CALC.N2BS_T_IPSHOut | 15190 | 余热锅炉中压过热蒸汽温度 | ℃ | float32
CALC.N2BS_P_IPSHOut | 15191 | 余热锅炉中压过热蒸汽压力 | MPa | float32
CALC.N2BS_F_IPSHOut | 15192 | 余热锅炉中压过热汽蒸汽流量 | t/h | float32
CALC.N2BS_T_LPSHOut | 15193 | 余热锅炉低压过热蒸汽温度 | ℃ | float32
CALC.N2BS_P_LPSHOut | 15194 | 余热锅炉低压过热蒸汽压力 | MPa | float32
CALC.N2BS_F_LPSHOut | 15195 | 余热锅炉低压过热蒸汽流量 | t/h | float32
CALC.N2BS_T_RHStm | 15196 | 冷再热蒸汽温度 | ℃ | float32
CALC.N2BS_P_RHStm | 15197 | 冷再热蒸汽压力 | MPa | float32
CALC.N2BS_F_RHStm | 15198 | 冷再热流量 | t/h | float32
CALC.N2BS_F_HPFeed | 15199 | 余热锅炉高压给水流量 | t/h | float32
CALC.N2BS_F_IPFeed | 15200 | 余热锅炉中压给水流量 | t/h | float32
CALC.N2BS_F_LPFeed | 15201 | 余热锅炉低压给水流量 | t/h | float32
CALC.N2BS_F_FuelHeaterWt | 15202 | 余热锅炉燃料加热器给水流量 | t/h | float32
CALC.N2BS_F_DEHPWtr | 15203 | 余热锅炉高压过热汽减温水流量 | t/h | float32
CALC.N2BS_T_HPFeed | 15204 | 余热锅炉高压给水温度 | ℃ | float32
CALC.N2BS_P_HPFeed | 15205 | 余热锅炉高压给水压力 | MPa | float32
CALC.N2BS_T_IPFeed | 15206 | 余热锅炉中压给水温度 | ℃ | float32
CALC.N2BS_P_IPFeed | 15207 | 余热锅炉中压给水压力 | MPa | float32
CALC.N2BS_P_HPDrum | 15208 | 余热锅炉高压汽包压力 | MPa | float32
CALC.N2BS_P_IPDrum | 15209 | 余热锅炉中压汽包压力 | MPa | float32
CALC.N2BS_P_LPDrum | 15210 | 余热锅炉低压汽包压力 | MPa | float32
CALC.N2BS_T_LPECOIn | 15211 | 余热锅炉低压省煤器入口温度 | ℃ | float32
CALC.N2BS_P_LPECOIn | 15212 | 余热锅炉低压省煤器入口压力 | MPa | float32
CALC.N2BS_T_LPECOOut | 15213 | 余热锅炉低压省煤器出口温度 | ℃ | float32
CALC.N2BS_P_LPECOOut | 15214 | 余热锅炉低压省煤器出口压力 | MPa | float32
CALC.N2BS_T_HPECOOut | 15215 | 余热锅炉高压省煤器出口温度 | ℃ | float32
CALC.N2BS_T_IPECOOut | 15216 | 余热锅炉中压省煤器出口温度 | ℃ | float32
CALC.N2BS_F_TCACooler | 15217 | TCA冷却器流量 | t/h | float32
CALC.N2BS_T_TCACoolerOut | 15218 | TCA冷却器出口温度 | ℃ | float32
CALC.N2BS_P_TCACoolerOut | 15219 | TCA冷却器出口压力 | MPa | float32
CALC.N2BS_P_HPECOOut | 15220 | 余热锅炉高压省煤器出口压力 | ℃ | float32
CALC.N2BS_P_IPECOOut | 15221 | 余热锅炉中压省煤器出口压力 | ℃ | float32
CALC.N2BS_T_CNDIn | 15222 | 给水温度 | ℃ | float32
CALC.N2BS_P_CNDIn | 15223 | 给水压力 | ℃ | float32
CALC.N2BS_F_DERHWtr | 15224 | 余热锅炉再减温水流量 | t/h | float32
CALC.N2TS_P_HPStmIn | 15225 | 高压缸进汽压力 | MPa | float32
CALC.N2TS_T_HPStmIn | 15226 | 高压缸进汽温度 | ℃ | float32
CALC.N2TS_P_IPStmIn | 15227 | 中压缸进汽压力 | MPa | float32
CALC.N2TS_T_IPStmIn | 15228 | 中压缸进汽温度 | ℃ | float32
CALC.N2TS_P_LPex | 15229 | 低压缸排汽压力 | kPa | float32
CALC.N2TS_P_LPStmIn | 15230 | 低压缸进汽压力 | ℃ | float32
CALC.N2TS_T_LPStmIn | 15231 | 低压缸进汽温度 | ℃ | float32
CALC.N2TS_T_LPex | 15232 | 低压缸排汽温度 | ℃ | float32
CALC.N2TS_F_IPStmIn | 15233 | 中压缸蒸汽流量 | t/h | float32
CALC.N2TS_F_HPStmIn | 15234 | 高压缸蒸汽流量 | t/h | float32
CALC.N2TS_F_LPStmIn | 15235 | 低压缸蒸汽流量 | t/h | float32
CALC.N2TS_P_HPStmOut | 15236 | 高压缸排汽压力 | MPa | float32
CALC.N2TS_T_HPStmOut | 15237 | 高压缸排汽温度 | ℃ | float32
CALC.N2TS_F_RHStm | 15238 | 冷再热流量 | ℃ | float32
CALC.N2TS_P_IPStmOut | 15239 | 中压缸排汽压力 | ℃ | float32
CALC.N2TS_T_IPStmOut | 15240 | 中压缸排汽温度 | ℃ | float32
CALC.N2TS_P_LPexAST | 15241 | 低压缸排汽压力(绝对值) | kPa | float32
CALC.N2TS_T_CicWi | 15242 | 凝汽器循环水进水温度 | ℃ | float32
CALC.N2TS_T_CicWo | 15243 | 凝汽器循环水出水温度 | ℃ | float32
CALC.N2TS_T_CNDIn | 15244 | 凝结水加热器入口混合段前温度 | ℃ | float32
CALC.N2TS_P_CNDIn | 15245 | 凝结水加热器入口混合段前压力 | MPa | float32
CALC.N2TS_F_GStmCnd | 15246 | 汽封冷却器出口凝结水流量 | t/h | float32
CALC.N2TS_F_WaterRep | 15247 | 凝结水热井补给水流量 | t/h | float32
CALC.N2TS_T_HwLCo | 15248 | 热井出水温度 | ℃ | float32
CALC.N2TS_F_SupplyHeat | 15249 | 蒸汽轮机供热抽汽流量 | t/h | float32
CALC.N2TS_T_SupplyHeat | 15250 | 蒸汽轮机供热抽汽温度 | ℃ | float32
CALC.N2TS_P_SupplyHeat | 15251 | 蒸汽轮机供热抽汽压力 | MPa | float32
CALC.N2TS_F_GRWaterRep | 15252 | 蒸汽轮机供热补水流量 | t/h | float32
CALC.N2TS_T_GRWaterRep | 15253 | 蒸汽轮机供热补水温度 | ℃ | float32
CALC.N2TS_P_GRWaterRep | 15254 | 蒸汽轮机供热补水压力 | MPa | float32
CALC.N2TS_T_ShuWater | 15255 | 采暖抽汽疏水温度 | ℃ | float32
CALC.N2TS_P_ShuWater | 15256 | 采暖抽汽疏水压力 | MPa | float32
CALC.N2TS_W_CGB | 15257 | 汽机厂高变功率 | MW | float32
CALC.N2TS_W_QBB | 15258 | 启备变功率 | MW | float32
CALC.N2TS_W_LCB | 15259 | 励磁变功率 | MW | float32
CALC.N2GS_W_G | 15260 | 燃机输出功率 | ℃ | float32
CALC.N2TS_W_G | 15261 | 汽机功率 | MW | float32
CALC.N2GS_S_G | 15262 | 机组运行状态 |  | digital
CALC.N2GS_W_ZB | 15263 | 燃机主变输出功率 | MW | float32
CALC.N2PS_W_G | 15264 | 联合循环发电机功率 | MW | float32
CALC.N2GS_E_Frequency | 15265 | 发电机频率 | Hz | float32
CALC.N2TS_W_ZB | 15266 | 汽机主变输出功率 | MW | float32
CALC.N2GS_W_QBB | 15267 | 启备变功率 | MW | float32
CALC.N2GS_W_CGB | 15268 | 燃机厂高变功率 | MW | float32
CALC.N2PS_W_CGB | 15269 | 厂高变功率 | MW | float32
CALC.N2PS_W_QBB | 15270 | 启备变功率 | MW | float32
CALC.N2PS_W_ZB | 15271 | 主变输出功率 | MW | float32
CALC.N2TS_S_G | 15272 | 机组运行状态 |  | digital
CALC.N2TS_A_CoaguPumpA | 15273 | 凝结水泵A电流 | A | float32
CALC.N2TS_A_CoaguPumpB | 15274 | 凝结水泵B电流 | A | float32
CALC.N2TS_A_CoaguPumpC | 15275 | 凝结水泵C电流 | A | float32
CALC.N2TS_A_CirPumpA | 15276 | 循环水泵A电流 | A | float32
CALC.N2TS_A_CirPumpB | 15277 | 循环水泵B电流 | A | float32
CALC.N2BS_V_6KV | 15278 | 6kV电压 | kV | float32
CALC.N2TS_S_CoaguPumpA | 15279 | 凝结水泵A运行状态 |  | digital
CALC.N2TS_S_CoaguPumpB | 15280 | 凝结水泵B运行状态 |  | digital
CALC.N2TS_S_CoaguPumpC | 15281 | 凝结水泵C运行状态 |  | digital
CALC.N2TS_S_CirPumpA | 15282 | 循环水泵A运行状态 |  | digital
CALC.N2TS_S_CirPumpB | 15283 | 循环水泵B运行状态 |  | digital
CALC.N2GS_P_COMPIn | 15284 | 压气机进口压力P1 | kPa | float32
CALC.N2GS_T_COMPIn | 15285 | 压气机进口温度T1 | ℃ | float32
CALC.N2GS_P_COMPOut | 15286 | 压气机出口压力P2 | kPa | float32
CALC.N2GS_T_COMPOut | 15287 | 压气机出口温度T2 | ℃ | float32
CALC.N2GS_T_FuelIn | 15288 | 进入燃烧室燃料温度Tf | ℃ | float32
CALC.N2GS_F_FuelIn | 15289 | 进入燃烧室燃料流量Qf | t/h | float32
CALC.N2GS_P_GASTIn | 15290 | 燃气轮机进口压力P3 | kPa | float32
CALC.N2GS_P_GASTOut | 15291 | 燃气轮机出口压力P4 | ℃ | float32
CALC.N2GS_T_GASTOut | 15292 | 燃气轮机出口温度T4 | ℃ | float32
CALC.N2GS_F_GASIn | 15293 | 进入透平的燃气流量Qt | t/h | float32
CALC.N2GS_F_COMPIn | 15294 | 压气机进口空气流量Qc | t/h | float32
CALC.N2BS_F_HPFPA_In | 15295 | 高压给水泵A进口流量 | t/h | float32
CALC.N2BS_P_HPFPA_In | 15296 | 高压给水泵A进口压力 | MPa | float32
CALC.N2BS_T_HPFPA_In | 15297 | 高压给水泵A进口温度 | ℃ | float32
CALC.N2BS_P_HPFPA_Out | 15298 | 高压给水泵A出口压力 | MPa | float32
CALC.N2BS_T_HPFPA_Out | 15299 | 高压给水泵A出口温度 | ℃ | float32
CALC.N2BS_F_HPFPB_In | 15300 | 高压给水泵B进口流量 | t/h | float32
CALC.N2BS_P_HPFPB_In | 15301 | 高压给水泵B进口压力 | MPa | float32
CALC.N2BS_T_HPFPB_In | 15302 | 高压给水泵B进口温度 | ℃ | float32
CALC.N2BS_P_HPFPB_Out | 15303 | 高压给水泵B出口压力 | MPa | float32
CALC.N2BS_T_HPFPB_Out | 15304 | 高压给水泵B出口温度 | ℃ | float32
CALC.N2BS_F_IPFPA_In | 15305 | 中压给水泵A进口流量 | t/h | float32
CALC.N2BS_P_IPFPA_In | 15306 | 中压给水泵A进口压力 | MPa | float32
CALC.N2BS_T_IPFPA_In | 15307 | 中压给水泵A进口温度 | ℃ | float32
CALC.N2BS_P_IPFPA_Out | 15308 | 中压给水泵A出口压力 | MPa | float32
CALC.N2BS_T_IPFPA_Out | 15309 | 中压给水泵A出口温度 | ℃ | float32
CALC.N2BS_F_IPFPB_In | 15310 | 中压给水泵B进口流量 | t/h | float32
CALC.N2BS_P_IPFPB_In | 15311 | 中压给水泵B进口压力 | MPa | float32
CALC.N2BS_T_IPFPB_In | 15312 | 中压给水泵B进口温度 | ℃ | float32
CALC.N2BS_P_IPFPB_Out | 15313 | 中压给水泵B出口压力 | MPa | float32
CALC.N2BS_T_IPFPB_Out | 15314 | 中压给水泵B出口温度 | ℃ | float32
CALC.N2BS_R_HPFPA | 15315 | 高压给水泵A转速 | rpm | float32
CALC.N2BS_R_HPFPB | 15316 | 高压给水泵B转速 | rpm | float32
CALC.N2BS_R_IPFPA | 15317 | 中压给水泵A转速 | rpm | float32
CALC.N2BS_R_IPFPB | 15318 | 中压给水泵B转速 | rpm | float32
CALC.N2BC_Han_StkGasIn | 15319 | 余热锅炉入口烟气焓 | kJ/kg | float32
CALC.N2BC_Han_StkGasOut | 15320 | 余热锅炉出口烟气焓 | kJ/kg | float32
CALC.N2BC_Han_HPStmIn | 15321 | 锅炉高压主蒸汽焓 | kJ/kg | float32
CALC.N2BC_Han_IPStmIn | 15322 | 锅炉中压主蒸汽焓 | kJ/kg | float32
CALC.N2BC_Han_LPStmIn | 15323 | 锅炉低压主蒸汽焓 | kJ/kg | float32
CALC.N2BC_Han_HPStmOut | 15324 | 锅炉冷再热汽焓 | kJ/kg | float32
CALC.N2BC_Han_HPFeed | 15325 | 高压给水焓 | kJ/kg | float32
CALC.N2BC_Han_IPFeed | 15326 | 中压给水焓 | kJ/kg | float32
CALC.N2BC_Han_HPECOOut | 15327 | 高压省煤器出口焓 | kJ/kg | float32
CALC.N2BC_Han_IPECOOut | 15328 | 中压省煤器出口焓 | kJ/kg | float32
CALC.N2BC_Han_TCACoolerOut | 15329 | TCA冷却器出口焓 | kJ/kg | float32
CALC.N2BC_Q_STM | 15330 | 余热锅炉蒸汽侧吸热量 | MJ/h | float32
CALC.N2BC_EFF_BOILER | 15331 | 余热锅炉热效率 | % | float32
CALC.N2BC_F_STKGAS | 15332 | 烟囱烟气流量 | t/h | float32
CALC.N2BC_Q_GAS | 15333 | 余热锅炉烟气侧放热量 | MJ/h | float32
CALC.N2BC_P_GasDiff | 15334 | 余热锅炉烟气压损 | kPa | float32
CALC.N2BC_T_HPRdDiff | 15335 | 余热锅炉热端温差 | ℃ | float32
CALC.N2BC_T_LPEVADIFF | 15336 | 低压蒸发器节点温差 | ℃ | float32
CALC.N2BC_T_IPEVADIFF | 15337 | 中压蒸发器节点温差 | ℃ | float32
CALC.N2BC_T_HPEVADIFF | 15338 | 高压蒸发器节点温差 | ℃ | float32
CALC.N2BC_T_LPECODIFF | 15339 | 低压省煤器接近点温差 | ℃ | float32
CALC.N2BC_TS_LPECO | 15340 | 低压省煤器出口压力对应饱和水温度 | ℃ | float32
CALC.N2BC_T_IPECODIFF | 15341 | 中压省煤器接近点温差 | ℃ | float32
CALC.N2BC_TS_IPECO | 15342 | 中压省煤器出口压力对应饱和水温度 | ℃ | float32
CALC.N2BC_T_HPECODIFF | 15343 | 高压省煤器接近点温差 | ℃ | float32
CALC.N2BC_TS_HPECO | 15344 | 高压省煤器出口压力对应饱和水温度 | ℃ | float32
CALC.N2BC_H_HPFPA | 15345 | 高压给水泵A扬程 | m | float32
CALC.N2BC_H_HPFPA_CORR | 15346 | 高压给水泵A修正扬程 | m | float32
CALC.N2BC_F_HPFPA_OUT | 15347 | 高压给水泵A出口流量 | t/h | float32
CALC.N2BC_F_HPFPA_OUT_CORR | 15348 | 高压给水泵A出口修正流量 | t/h | float32
CALC.N2BC_W_HPFPA_Shaft | 15349 | 高压给水泵A轴功率 | kW | float32
CALC.N2BC_W_HPFPA_Shaft_CORR | 15350 | 高压给水泵A修正轴功率 | kW | float32
CALC.N2BC_EFF_HPFPNA | 15351 | 高压给水泵A效率 | % | float32
CALC.N2BC_EFF_HPFPNA_CORR | 15352 | 高压给水泵A修正效率 | % | float32
CALC.N2BC_H_HPFPB | 15353 | 高压给水泵B扬程 | m | float32
CALC.N2BC_H_HPFPB_CORR | 15354 | 高压给水泵B修正扬程 | m | float32
CALC.N2BC_F_HPFPB_OUT | 15355 | 高压给水泵B出口流量 | t/h | float32
CALC.N2BC_F_HPFPB_OUT_CORR | 15356 | 高压给水泵B出口修正流量 | t/h | float32
CALC.N2BC_W_HPFPB_Shaft | 15357 | 高压给水泵B轴功率 | kW | float32
CALC.N2BC_W_HPFPB_Shaft_CORR | 15358 | 高压给水泵B修正轴功率 | kW | float32
CALC.N2BC_EFF_HPFPNB | 15359 | 高压给水泵B效率 | % | float32
CALC.N2BC_EFF_HPFPNB_CORR | 15360 | 高压给水泵B修正效率 | % | float32
CALC.N2BC_H_IPFPA | 15361 | 中压给水泵A扬程 | m | float32
CALC.N2BC_H_IPFPA_CORR | 15362 | 中压给水泵A修正扬程 | m | float32
CALC.N2BC_F_IPFPA_OUT | 15363 | 中压给水泵A出口流量 | t/h | float32
CALC.N2BC_F_IPFPA_OUT_CORR | 15364 | 中压给水泵A出口修正流量 | t/h | float32
CALC.N2BC_W_IPFPA_Shaft | 15365 | 中压给水泵A轴功率 | kW | float32
CALC.N2BC_W_IPFPA_Shaft_CORR | 15366 | 中压给水泵A修正轴功率 | kW | float32
CALC.N2BC_EFF_IPFPNA | 15367 | 中压给水泵A效率 | % | float32
CALC.N2BC_EFF_IPFPNA_CORR | 15368 | 中压给水泵A修正效率 | % | float32
CALC.N2BC_H_IPFPB | 15369 | 中压给水泵B扬程 | m | float32
CALC.N2BC_H_IPFPB_CORR | 15370 | 中压给水泵B修正扬程 | m | float32
CALC.N2BC_F_IPFPB_OUT | 15371 | 中压给水泵B出口流量 | t/h | float32
CALC.N2BC_F_IPFPB_OUT_CORR | 15372 | 中压给水泵B出口修正流量 | t/h | float32
CALC.N2BC_W_IPFPB_Shaft | 15373 | 中压给水泵B轴功率 | kW | float32
CALC.N2BC_W_IPFPB_Shaft_CORR | 15374 | 中压给水泵B修正轴功率 | kW | float32
CALC.N2BC_EFF_IPFPNB | 15375 | 中压给水泵B效率 | % | float32
CALC.N2BC_EFF_IPFPNB_CORR | 15376 | 中压给水泵B修正效率 | % | float32
CALC.N2BC_EFF_BOILER_T | 15377 | 主蒸汽温度(目标) | ℃ | float32
CALC.N2BC_F_STKGAS_T | 15378 | 烟气流量(目标) | ℃ | float32
CALC.N2BC_T_StkGasIn_T | 15379 | 余热锅炉入口烟气温度(目标) | ℃ | float32
CALC.N2BC_StkH2O_T | 15380 | 烟囱烟气H2O含量(目标) | ℃ | float32
CALC.N2BC_P_LPSHOut_T | 15381 | 余热锅炉低压过热蒸汽压力(目标) | ℃ | float32
CALC.N2TC_T_HPStmOut_T | 15382 | 高压缸排汽温度(目标) | ℃ | float32
CALC.N2TC_T_CNDIn_T | 15383 | 凝结水加热器入口混合段前温度(目标) | ℃ | float32
CALC.N2BC_CV_EFF_Boiler_NUM | 15384 | 锅炉效率曲线(目标)_Num |  | float32
CALC.N2BC_CV_EFF_Boiler_X01 | 15385 | 锅炉效率曲线(目标)_X01 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y01 | 15386 | 锅炉效率曲线(目标)_Y01 |  | float32
CALC.N2BC_CV_EFF_Boiler_X02 | 15387 | 锅炉效率曲线(目标)_X02 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y02 | 15388 | 锅炉效率曲线(目标)_Y02 |  | float32
CALC.N2BC_CV_EFF_Boiler_X03 | 15389 | 锅炉效率曲线(目标)_X03 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y03 | 15390 | 锅炉效率曲线(目标)_Y03 |  | float32
CALC.N2BC_CV_EFF_Boiler_X04 | 15391 | 锅炉效率曲线(目标)_X04 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y04 | 15392 | 锅炉效率曲线(目标)_Y04 |  | float32
CALC.N2BC_CV_EFF_Boiler_X05 | 15393 | 锅炉效率曲线(目标)_X05 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y05 | 15394 | 锅炉效率曲线(目标)_Y05 |  | float32
CALC.N2BC_CV_EFF_Boiler_X06 | 15395 | 锅炉效率曲线(目标)_X06 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y06 | 15396 | 锅炉效率曲线(目标)_Y06 |  | float32
CALC.N2BC_CV_EFF_Boiler_X07 | 15397 | 锅炉效率曲线(目标)_X07 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y07 | 15398 | 锅炉效率曲线(目标)_Y07 |  | float32
CALC.N2BC_CV_EFF_Boiler_X08 | 15399 | 锅炉效率曲线(目标)_X08 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y08 | 15400 | 锅炉效率曲线(目标)_Y08 |  | float32
CALC.N2BC_CV_EFF_Boiler_X09 | 15401 | 锅炉效率曲线(目标)_X09 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y09 | 15402 | 锅炉效率曲线(目标)_Y09 |  | float32
CALC.N2BC_CV_EFF_Boiler_X10 | 15403 | 锅炉效率曲线(目标)_X10 |  | float32
CALC.N2BC_CV_EFF_Boiler_Y10 | 15404 | 锅炉效率曲线(目标)_Y10 |  | float32
CALC.N2BC_CV_F_STKGAS_NUM | 15405 | 烟气流量曲线(目标)_Num |  | float32
CALC.N2BC_CV_F_STKGAS_X01 | 15406 | 烟气流量曲线(目标)_X01 |  | float32
CALC.N2BC_CV_F_STKGAS_Y01 | 15407 | 烟气流量曲线(目标)_Y01 |  | float32
CALC.N2BC_CV_F_STKGAS_X02 | 15408 | 烟气流量曲线(目标)_X02 |  | float32
CALC.N2BC_CV_F_STKGAS_Y02 | 15409 | 烟气流量曲线(目标)_Y02 |  | float32
CALC.N2BC_CV_F_STKGAS_X03 | 15410 | 烟气流量曲线(目标)_X03 |  | float32
CALC.N2BC_CV_F_STKGAS_Y03 | 15411 | 烟气流量曲线(目标)_Y03 |  | float32
CALC.N2BC_CV_F_STKGAS_X04 | 15412 | 烟气流量曲线(目标)_X04 |  | float32
CALC.N2BC_CV_F_STKGAS_Y04 | 15413 | 烟气流量曲线(目标)_Y04 |  | float32
CALC.N2BC_CV_F_STKGAS_X05 | 15414 | 烟气流量曲线(目标)_X05 |  | float32
CALC.N2BC_CV_F_STKGAS_Y05 | 15415 | 烟气流量曲线(目标)_Y05 |  | float32
CALC.N2BC_CV_F_STKGAS_X06 | 15416 | 烟气流量曲线(目标)_X06 |  | float32
CALC.N2BC_CV_F_STKGAS_Y06 | 15417 | 烟气流量曲线(目标)_Y06 |  | float32
CALC.N2BC_CV_F_STKGAS_X07 | 15418 | 烟气流量曲线(目标)_X07 |  | float32
CALC.N2BC_CV_F_STKGAS_Y07 | 15419 | 烟气流量曲线(目标)_Y07 |  | float32
CALC.N2BC_CV_F_STKGAS_X08 | 15420 | 烟气流量曲线(目标)_X08 |  | float32
CALC.N2BC_CV_F_STKGAS_Y08 | 15421 | 烟气流量曲线(目标)_Y08 |  | float32
CALC.N2BC_CV_F_STKGAS_X09 | 15422 | 烟气流量曲线(目标)_X09 |  | float32
CALC.N2BC_CV_F_STKGAS_Y09 | 15423 | 烟气流量曲线(目标)_Y09 |  | float32
CALC.N2BC_CV_F_STKGAS_X10 | 15424 | 烟气流量曲线(目标)_X10 |  | float32
CALC.N2BC_CV_F_STKGAS_Y10 | 15425 | 烟气流量曲线(目标)_Y10 |  | float32
CALC.N2BC_COHPSHOutF_StkGasF | 15426 | 高压蒸汽流量随排气流量修正系数 |  | float32
CALC.N2BC_COHPSHOutF_StkGasT | 15427 | 高压蒸汽流量随排气温度修正系数 |  | float32
CALC.N2BC_COHPSHOutF_CNDInT | 15428 | 高压蒸汽流量随给水温度修正系数 |  | float32
CALC.N2BC_COHPSHOutF_StkH2O | 15429 | 高压蒸汽流量随含水率修正系数 |  | float32
CALC.N2BC_COHPSHOutF_HPStmOutT | 15430 | 高压蒸汽流量随高压缸排汽温度修正系数 |  | float32
CALC.N2BC_COHPSHOutF | 15431 | 高压蒸汽流量总修正系数 |  | float32
CALC.N2BC_F_HPSHOut_GC | 15432 | 修正后高压过热蒸汽流量 | t/h | float32
CALC.N2BC_COHPSHOutT_StkGasF | 15433 | 高压蒸汽温度随排气流量修正系数 |  | float32
CALC.N2BC_COHPSHOutT_StkGasT | 15434 | 高压蒸汽温度随排气温度修正系数 |  | float32
CALC.N2BC_COHPSHOutT_CNDInT | 15435 | 高压蒸汽温度随给水温度修正系数 |  | float32
CALC.N2BC_COHPSHOutT_StkH2O | 15436 | 高压蒸汽温度随含水率修正系数 |  | float32
CALC.N2BC_COHPSHOutT_HPStmOutT | 15437 | 高压蒸汽温度随高压缸排汽温度修正系数 |  | float32
CALC.N2BC_COHPSHOutT | 15438 | 高压蒸汽温度总修正系数 |  | float32
CALC.N2BC_T_HPSHOut_GC | 15439 | 修正后高压蒸汽温度 | ℃ | float32
CALC.N2BC_COIPSHOutF_StkGasF | 15440 | 再热蒸汽流量随排气流量修正系数 |  | float32
CALC.N2BC_COIPSHOutF_StkGasT | 15441 | 再热蒸汽流量随排气温度修正系数 |  | float32
CALC.N2BC_COIPSHOutF_CNDInT | 15442 | 再热蒸汽流量随给水温度修正系数 |  | float32
CALC.N2BC_COIPSHOutF_StkH2O | 15443 | 再热蒸汽流量随含水率修正系数 |  | float32
CALC.N2BC_COIPSHOutF_HPStmOutT | 15444 | 再热蒸汽流量随高压缸排汽温度修正系数 |  | float32
CALC.N2BC_COIPSHOutF | 15445 | 再热蒸汽流量总修正系数 |  | float32
CALC.N2BC_F_IPSHOut_GC | 15446 | 修正后再热蒸汽流量 | t/h | float32
CALC.N2BC_COIPSHOutT_StkGasF | 15447 | 再热蒸汽温度随排气流量修正系数 |  | float32
CALC.N2BC_COIPSHOutT_StkGasT | 15448 | 再热蒸汽温度随排气温度修正系数 |  | float32
CALC.N2BC_COIPSHOutT_CNDInT | 15449 | 再热蒸汽温度随给水温度修正系数 |  | float32
CALC.N2BC_COIPSHOutT_StkH2O | 15450 | 再热蒸汽温度随含水率修正系数 |  | float32
CALC.N2BC_COIPSHOutT_HPStmOutT | 15451 | 再热蒸汽温度随高压缸排汽温度修正系数 |  | float32
CALC.N2BC_COIPSHOutT | 15452 | 再热蒸汽温度总修正系数 |  | float32
CALC.N2BC_T_IPSHOut_GC | 15453 | 修正后再热蒸汽温度 | ℃ | float32
CALC.N2BC_COLPSHOutF_StkGasF | 15454 | 低压蒸汽流量随排气流量修正系数 |  | float32
CALC.N2BC_COLPSHOutF_StkGasT | 15455 | 低压蒸汽流量随排气温度修正系数 |  | float32
CALC.N2BC_COLPSHOutF_CNDInT | 15456 | 低压蒸汽流量随给水温度修正系数 |  | float32
CALC.N2BC_COLPSHOutF_StkH2O | 15457 | 低压蒸汽流量随含水率修正系数 |  | float32
CALC.N2BC_COLPSHOutF_HPStmOutT | 15458 | 低压蒸汽流量随高压缸排汽温度修正系数 |  | float32
CALC.N2BC_COLPSHOutF | 15459 | 低压蒸汽流量总修正系数 |  | float32
CALC.N2BC_F_LPSHOut_GC | 15460 | 修正后低压蒸汽流量 | t/h | float32
CALC.N2BC_COLPSHOutF_LPSHOutP | 15461 | 低压蒸汽流量随低压蒸汽压力修正系数 |  | float32
CALC.N2BC_COLPSHOutT_StkGasF | 15462 | 低压蒸汽温度随排气流量修正系数 |  | float32
CALC.N2BC_COLPSHOutT_StkGasT | 15463 | 低压蒸汽温度随排气温度修正系数 |  | float32
CALC.N2BC_COLPSHOutT_CNDInT | 15464 | 低压蒸汽温度随给水温度修正系数 |  | float32
CALC.N2BC_COLPSHOutT_StkH2O | 15465 | 低压蒸汽温度随含水率修正系数 |  | float32
CALC.N2BC_COLPSHOutT_HPStmOutT | 15466 | 低压蒸汽温度随高压缸排汽温度修正系数 |  | float32
CALC.N2BC_COLPSHOutT | 15467 | 低压蒸汽温度总修正系数 |  | float32
CALC.N2BC_T_LPSHOut_GC | 15468 | 修正后低压蒸汽温度 | ℃ | float32
CALC.N2BC_CEFB_StkGasF | 15469 | 余热锅炉效率随排气流量修正系数 |  | float32
CALC.N2BC_CEFB_StkGasT | 15470 | 余热锅炉效率随排气温度修正系数 |  | float32
CALC.N2BC_CEFB_CNDInT | 15471 | 余热锅炉效率随给水温度修正系数 |  | float32
CALC.N2BC_CEFB_StkH2O | 15472 | 余热锅炉效率随含水率修正系数 |  | float32
CALC.N2BC_CEFB_HPStmOutT | 15473 | 余热锅炉效率随高压缸排汽温度修正系数 |  | float32
CALC.N2BC_CEFB_BOILER | 15474 | 余热锅炉效率总修正系数 |  | float32
CALC.N2BC_EFF_BOILER_GC | 15475 | 修正后余热锅炉效率 | % | float32
CALC.N2BC_CEFB_LPSHOutP | 15476 | 余热锅炉效率随低压蒸汽压力修正系数 |  | float32
CALC.N2BC_COGasDiffP_StkGasF | 15477 | 排气压降随排气流量修正系数 |  | float32
CALC.N2BC_COGasDiffP_StkGasT | 15478 | 排气压降随排气温度修正系数 |  | float32
CALC.N2BC_COGasDiffP | 15479 | 排气压降总修正系数 |  | float32
CALC.N2BC_P_GasDiff_GC | 15480 | 修正后排气压降 | kPa | float32
CALC.N2TC_Han_HPStmIn | 15481 | 高压缸入口蒸汽焓值 | kJ/kg | float32
CALC.N2TC_Han_HPStmOut | 15482 | 高压缸出口蒸汽焓值 | kJ/kg | float32
CALC.N2TC_Eff_HP | 15483 | 高压缸效率 | % | float32
CALC.N2TC_Han_IPStmIn | 15484 | 中压缸入口蒸汽焓值 | kJ/kg | float32
CALC.N2TC_Han_IPStmOut | 15485 | 中压缸出口蒸汽焓值 | kJ/kg | float32
CALC.N2TC_Eff_IP | 15486 | 中压缸效率 | % | float32
CALC.N2TC_Han_LPStmIn | 15487 | 低压缸入口蒸汽焓值 | kJ/kg | float32
CALC.N2TC_Han_CNDIn | 15488 | 给水焓值 | kJ/kg | float32
CALC.N2TC_Han_SupplyHeat | 15489 | 采暖蒸汽焓值 | kJ/kg | float32
CALC.N2TC_Han_ShuWater | 15490 | 热网加热器疏水焓 | kJ/kg | float32
CALC.N2TS_Q_SupplyHeat | 15491 | 热负荷功率 | MW | float32
CALC.N2TC_HeatRate | 15492 | 汽轮机热耗率 | kJ/kwh | float32
CALC.N2TC_EFF_Turbine | 15493 | 汽轮机电效率 | % | float32
CALC.N2TC_SteamRate | 15494 | 汽轮机汽耗率 | kg/kWh | float32
CALC.N2TC_RW_SupplyHeat | 15495 | 供热比 | % | float32
CALC.N2TC_RW_HeatToEle | 15496 | 热电比 | GJ/MWh | float32
CALC.N2TC_R_WaterRep | 15497 | 补水率 | % | float32
CALC.N2TC_R_WaterRepHeat | 15498 | 供热补水率 | % | float32
CALC.N2TC_Eff_SupplyHeat | 15499 | 供热热效率 | % | float32
CALC.N2TC_Eff_Fuel | 15500 | 燃料利用系数 | % | float32
CALC.N2TC_W_PEC | 15501 | 厂用电功率 | MW | float32
CALC.N2TC_RW_PEC | 15502 | 厂用电率 | % | float32
CALC.N2TC_R_FuelExpendGE | 15503 | 供电气耗 | Nm3/kWh | float32
CALC.N2TC_R_FuelExpend | 15504 | 发电气耗率 | Nm3/kWh | float32
CALC.N2TC_R_FuelExpendHE | 15505 | 供热气耗 | Nm3/GJ | float32
CALC.N2TC_CoalRate | 15506 | 供电煤耗 | g/kWh | float32
CALC.N2TC_CoalRate_GE | 15507 | 发电煤耗 | g/kWh | float32
CALC.N2TC_CoalRateHeatHE | 15508 | 供热煤耗 | kg/GJ | float32
CALC.N2TC_N_HetLoad | 15509 | 凝汽器热负荷 | GJ/h | float32
CALC.N2TC_N_AdLoad | 15510 | 凝汽器附加热负荷 | GJ/h | float32
CALC.N2TC_DT_CirWater | 15511 | 循环水温升 | ℃ | float32
CALC.N2TC_C_HetTrs | 15512 | 凝汽器传热系数 | W/(m2C) | float32
CALC.N2TC_ConWaterSC | 15513 | 凝结水过冷度 | ℃ | float32
CALC.N2TC_TTD_Con | 15514 | 凝汽器端差 | ℃ | float32
CALC.N2TC_TS_LPex | 15515 | 低压缸排汽压力对应饱和温度 | kPa | float32
CALC.N2TC_P_LPEX_COE | 15516 | 真空度 | % | float32
CALC.N2TC_Eff_LP | 15517 | 低压缸效率 | % | float32
CALC.N2TC_X_LPex | 15518 | 汽轮机排汽干度 |  | float32
CALC.N2TC_Han_LPex | 15519 | 低压缸出口蒸汽焓值 | kJ/kg | float32
CALC.N2TS_T_MS_T | 15520 | 主蒸汽温度(目标) | ℃ | float32
CALC.N2TS_P_MS_T | 15521 | 主蒸汽压力(目标) | MPa | float32
CALC.N2TS_T_HRh_T | 15522 | 再热蒸汽温度(目标) | ℃ | float32
CALC.N2TC_Eff_HP_T | 15523 | 高压缸效率(目标) | % | float32
CALC.N2TC_Eff_IP_T | 15524 | 中压缸效率(目标) | % | float32
CALC.N2TS_P_LPex_T | 15525 | 低排压力(目标) | kPa | float32
CALC.N2TC_HeatRate_T | 15526 | 汽机热耗率(目标) | kJ/kWh | float32
CALC.N2TS_P_LPexAST_T | 15527 | 低压缸排汽压力(目标)(绝对值) |  | float32
CALC.N2TC_CV_T_MS_NUM | 15528 | 主蒸汽温度曲线(目标)_Num |  | float32
CALC.N2TC_CV_T_MS_X01 | 15529 | 主蒸汽温度曲线(目标)_X01 |  | float32
CALC.N2TC_CV_T_MS_Y01 | 15530 | 主蒸汽温度曲线(目标)_Y01 |  | float32
CALC.N2TC_CV_T_MS_X02 | 15531 | 主蒸汽温度曲线(目标)_X02 |  | float32
CALC.N2TC_CV_T_MS_Y02 | 15532 | 主蒸汽温度曲线(目标)_Y02 |  | float32
CALC.N2TC_CV_T_MS_X03 | 15533 | 主蒸汽温度曲线(目标)_X03 |  | float32
CALC.N2TC_CV_T_MS_Y03 | 15534 | 主蒸汽温度曲线(目标)_Y03 |  | float32
CALC.N2TC_CV_T_MS_X04 | 15535 | 主蒸汽温度曲线(目标)_X04 |  | float32
CALC.N2TC_CV_T_MS_Y04 | 15536 | 主蒸汽温度曲线(目标)_Y04 |  | float32
CALC.N2TC_CV_T_MS_X05 | 15537 | 主蒸汽温度曲线(目标)_X05 |  | float32
CALC.N2TC_CV_T_MS_Y05 | 15538 | 主蒸汽温度曲线(目标)_Y05 |  | float32
CALC.N2TC_CV_T_MS_X06 | 15539 | 主蒸汽温度曲线(目标)_X06 |  | float32
CALC.N2TC_CV_T_MS_Y06 | 15540 | 主蒸汽温度曲线(目标)_Y06 |  | float32
CALC.N2TC_CV_T_MS_X07 | 15541 | 主蒸汽温度曲线(目标)_X07 |  | float32
CALC.N2TC_CV_T_MS_Y07 | 15542 | 主蒸汽温度曲线(目标)_Y07 |  | float32
CALC.N2TC_CV_T_MS_X08 | 15543 | 主蒸汽温度曲线(目标)_X08 |  | float32
CALC.N2TC_CV_T_MS_Y08 | 15544 | 主蒸汽温度曲线(目标)_Y08 |  | float32
CALC.N2TC_CV_T_MS_X09 | 15545 | 主蒸汽温度曲线(目标)_X09 |  | float32
CALC.N2TC_CV_T_MS_Y09 | 15546 | 主蒸汽温度曲线(目标)_Y09 |  | float32
CALC.N2TC_CV_T_MS_X10 | 15547 | 主蒸汽温度曲线(目标)_X10 |  | float32
CALC.N2TC_CV_T_MS_Y10 | 15548 | 主蒸汽温度曲线(目标)_Y10 |  | float32
CALC.N2TC_CV_P_MS_NUM | 15549 | 主蒸汽压力曲线(目标)_Num |  | float32
CALC.N2TC_CV_P_MS_X01 | 15550 | 主蒸汽压力曲线(目标)_X01 |  | float32
CALC.N2TC_CV_P_MS_Y01 | 15551 | 主蒸汽压力曲线(目标)_Y01 |  | float32
CALC.N2TC_CV_P_MS_X02 | 15552 | 主蒸汽压力曲线(目标)_X02 |  | float32
CALC.N2TC_CV_P_MS_Y02 | 15553 | 主蒸汽压力曲线(目标)_Y02 |  | float32
CALC.N2TC_CV_P_MS_X03 | 15554 | 主蒸汽压力曲线(目标)_X03 |  | float32
CALC.N2TC_CV_P_MS_Y03 | 15555 | 主蒸汽压力曲线(目标)_Y03 |  | float32
CALC.N2TC_CV_P_MS_X04 | 15556 | 主蒸汽压力曲线(目标)_X04 |  | float32
CALC.N2TC_CV_P_MS_Y04 | 15557 | 主蒸汽压力曲线(目标)_Y04 |  | float32
CALC.N2TC_CV_P_MS_X05 | 15558 | 主蒸汽压力曲线(目标)_X05 |  | float32
CALC.N2TC_CV_P_MS_Y05 | 15559 | 主蒸汽压力曲线(目标)_Y05 |  | float32
CALC.N2TC_CV_P_MS_X06 | 15560 | 主蒸汽压力曲线(目标)_X06 |  | float32
CALC.N2TC_CV_P_MS_Y06 | 15561 | 主蒸汽压力曲线(目标)_Y06 |  | float32
CALC.N2TC_CV_P_MS_X07 | 15562 | 主蒸汽压力曲线(目标)_X07 |  | float32
CALC.N2TC_CV_P_MS_Y07 | 15563 | 主蒸汽压力曲线(目标)_Y07 |  | float32
CALC.N2TC_CV_P_MS_X08 | 15564 | 主蒸汽压力曲线(目标)_X08 |  | float32
CALC.N2TC_CV_P_MS_Y08 | 15565 | 主蒸汽压力曲线(目标)_Y08 |  | float32
CALC.N2TC_CV_P_MS_X09 | 15566 | 主蒸汽压力曲线(目标)_X09 |  | float32
CALC.N2TC_CV_P_MS_Y09 | 15567 | 主蒸汽压力曲线(目标)_Y09 |  | float32
CALC.N2TC_CV_P_MS_X10 | 15568 | 主蒸汽压力曲线(目标)_X10 |  | float32
CALC.N2TC_CV_P_MS_Y10 | 15569 | 主蒸汽压力曲线(目标)_Y10 |  | float32
CALC.N2TC_CV_T_HRH_NUM | 15570 | 再热蒸汽温度曲线(目标)_Num |  | float32
CALC.N2TC_CV_T_HRH_X01 | 15571 | 再热蒸汽温度曲线(目标)_X01 |  | float32
CALC.N2TC_CV_T_HRH_Y01 | 15572 | 再热蒸汽温度曲线(目标)_Y01 |  | float32
CALC.N2TC_CV_T_HRH_X02 | 15573 | 再热蒸汽温度曲线(目标)_X02 |  | float32
CALC.N2TC_CV_T_HRH_Y02 | 15574 | 再热蒸汽温度曲线(目标)_Y02 |  | float32
CALC.N2TC_CV_T_HRH_X03 | 15575 | 再热蒸汽温度曲线(目标)_X03 |  | float32
CALC.N2TC_CV_T_HRH_Y03 | 15576 | 再热蒸汽温度曲线(目标)_Y03 |  | float32
CALC.N2TC_CV_T_HRH_X04 | 15577 | 再热蒸汽温度曲线(目标)_X04 |  | float32
CALC.N2TC_CV_T_HRH_Y04 | 15578 | 再热蒸汽温度曲线(目标)_Y04 |  | float32
CALC.N2TC_CV_T_HRH_X05 | 15579 | 再热蒸汽温度曲线(目标)_X05 |  | float32
CALC.N2TC_CV_T_HRH_Y05 | 15580 | 再热蒸汽温度曲线(目标)_Y05 |  | float32
CALC.N2TC_CV_T_HRH_X06 | 15581 | 再热蒸汽温度曲线(目标)_X06 |  | float32
CALC.N2TC_CV_T_HRH_Y06 | 15582 | 再热蒸汽温度曲线(目标)_Y06 |  | float32
CALC.N2TC_CV_T_HRH_X07 | 15583 | 再热蒸汽温度曲线(目标)_X07 |  | float32
CALC.N2TC_CV_T_HRH_Y07 | 15584 | 再热蒸汽温度曲线(目标)_Y07 |  | float32
CALC.N2TC_CV_T_HRH_X08 | 15585 | 再热蒸汽温度曲线(目标)_X08 |  | float32
CALC.N2TC_CV_T_HRH_Y08 | 15586 | 再热蒸汽温度曲线(目标)_Y08 |  | float32
CALC.N2TC_CV_T_HRH_X09 | 15587 | 再热蒸汽温度曲线(目标)_X09 |  | float32
CALC.N2TC_CV_T_HRH_Y09 | 15588 | 再热蒸汽温度曲线(目标)_Y09 |  | float32
CALC.N2TC_CV_T_HRH_X10 | 15589 | 再热蒸汽温度曲线(目标)_X10 |  | float32
CALC.N2TC_CV_T_HRH_Y10 | 15590 | 再热蒸汽温度曲线(目标)_Y10 |  | float32
CALC.N2TC_CV_EFF_HP_NUM | 15591 | 高压缸效率曲线(目标)_Num |  | float32
CALC.N2TC_CV_EFF_HP_X01 | 15592 | 高压缸效率曲线(目标)_X01 |  | float32
CALC.N2TC_CV_EFF_HP_Y01 | 15593 | 高压缸效率曲线(目标)_Y01 |  | float32
CALC.N2TC_CV_EFF_HP_X02 | 15594 | 高压缸效率曲线(目标)_X02 |  | float32
CALC.N2TC_CV_EFF_HP_Y02 | 15595 | 高压缸效率曲线(目标)_Y02 |  | float32
CALC.N2TC_CV_EFF_HP_X03 | 15596 | 高压缸效率曲线(目标)_X03 |  | float32
CALC.N2TC_CV_EFF_HP_Y03 | 15597 | 高压缸效率曲线(目标)_Y03 |  | float32
CALC.N2TC_CV_EFF_HP_X04 | 15598 | 高压缸效率曲线(目标)_X04 |  | float32
CALC.N2TC_CV_EFF_HP_Y04 | 15599 | 高压缸效率曲线(目标)_Y04 |  | float32
CALC.N2TC_CV_EFF_HP_X05 | 15600 | 高压缸效率曲线(目标)_X05 |  | float32
CALC.N2TC_CV_EFF_HP_Y05 | 15601 | 高压缸效率曲线(目标)_Y05 |  | float32
CALC.N2TC_CV_EFF_HP_X06 | 15602 | 高压缸效率曲线(目标)_X06 |  | float32
CALC.N2TC_CV_EFF_HP_Y06 | 15603 | 高压缸效率曲线(目标)_Y06 |  | float32
CALC.N2TC_CV_EFF_HP_X07 | 15604 | 高压缸效率曲线(目标)_X07 |  | float32
CALC.N2TC_CV_EFF_HP_Y07 | 15605 | 高压缸效率曲线(目标)_Y07 |  | float32
CALC.N2TC_CV_EFF_HP_X08 | 15606 | 高压缸效率曲线(目标)_X08 |  | float32
CALC.N2TC_CV_EFF_HP_Y08 | 15607 | 高压缸效率曲线(目标)_Y08 |  | float32
CALC.N2TC_CV_EFF_HP_X09 | 15608 | 高压缸效率曲线(目标)_X09 |  | float32
CALC.N2TC_CV_EFF_HP_Y09 | 15609 | 高压缸效率曲线(目标)_Y09 |  | float32
CALC.N2TC_CV_EFF_HP_X10 | 15610 | 高压缸效率曲线(目标)_X10 |  | float32
CALC.N2TC_CV_EFF_HP_Y10 | 15611 | 高压缸效率曲线(目标)_Y10 |  | float32
CALC.N2TC_CV_EFF_IP_NUM | 15612 | 中压缸效率曲线(目标)_Num |  | float32
CALC.N2TC_CV_EFF_IP_X01 | 15613 | 中压缸效率曲线(目标)_X01 |  | float32
CALC.N2TC_CV_EFF_IP_Y01 | 15614 | 中压缸效率曲线(目标)_Y01 |  | float32
CALC.N2TC_CV_EFF_IP_X02 | 15615 | 中压缸效率曲线(目标)_X02 |  | float32
CALC.N2TC_CV_EFF_IP_Y02 | 15616 | 中压缸效率曲线(目标)_Y02 |  | float32
CALC.N2TC_CV_EFF_IP_X03 | 15617 | 中压缸效率曲线(目标)_X03 |  | float32
CALC.N2TC_CV_EFF_IP_Y03 | 15618 | 中压缸效率曲线(目标)_Y03 |  | float32
CALC.N2TC_CV_EFF_IP_X04 | 15619 | 中压缸效率曲线(目标)_X04 |  | float32
CALC.N2TC_CV_EFF_IP_Y04 | 15620 | 中压缸效率曲线(目标)_Y04 |  | float32
CALC.N2TC_CV_EFF_IP_X05 | 15621 | 中压缸效率曲线(目标)_X05 |  | float32
CALC.N2TC_CV_EFF_IP_Y05 | 15622 | 中压缸效率曲线(目标)_Y05 |  | float32
CALC.N2TC_CV_EFF_IP_X06 | 15623 | 中压缸效率曲线(目标)_X06 |  | float32
CALC.N2TC_CV_EFF_IP_Y06 | 15624 | 中压缸效率曲线(目标)_Y06 |  | float32
CALC.N2TC_CV_EFF_IP_X07 | 15625 | 中压缸效率曲线(目标)_X07 |  | float32
CALC.N2TC_CV_EFF_IP_Y07 | 15626 | 中压缸效率曲线(目标)_Y07 |  | float32
CALC.N2TC_CV_EFF_IP_X08 | 15627 | 中压缸效率曲线(目标)_X08 |  | float32
CALC.N2TC_CV_EFF_IP_Y08 | 15628 | 中压缸效率曲线(目标)_Y08 |  | float32
CALC.N2TC_CV_EFF_IP_X09 | 15629 | 中压缸效率曲线(目标)_X09 |  | float32
CALC.N2TC_CV_EFF_IP_Y09 | 15630 | 中压缸效率曲线(目标)_Y09 |  | float32
CALC.N2TC_CV_EFF_IP_X10 | 15631 | 中压缸效率曲线(目标)_X10 |  | float32
CALC.N2TC_CV_EFF_IP_Y10 | 15632 | 中压缸效率曲线(目标)_Y10 |  | float32
CALC.N2TC_CV_HEATRATE_NUM | 15633 | 热耗率曲线(目标)_Num |  | float32
CALC.N2TC_CV_HEATRATE_X01 | 15634 | 热耗率曲线(目标)_X01 |  | float32
CALC.N2TC_CV_HEATRATE_Y01 | 15635 | 热耗率曲线(目标)_Y01 |  | float32
CALC.N2TC_CV_HEATRATE_X02 | 15636 | 热耗率曲线(目标)_X02 |  | float32
CALC.N2TC_CV_HEATRATE_Y02 | 15637 | 热耗率曲线(目标)_Y02 |  | float32
CALC.N2TC_CV_HEATRATE_X03 | 15638 | 热耗率曲线(目标)_X03 |  | float32
CALC.N2TC_CV_HEATRATE_Y03 | 15639 | 热耗率曲线(目标)_Y03 |  | float32
CALC.N2TC_CV_HEATRATE_X04 | 15640 | 热耗率曲线(目标)_X04 |  | float32
CALC.N2TC_CV_HEATRATE_Y04 | 15641 | 热耗率曲线(目标)_Y04 |  | float32
CALC.N2TC_CV_HEATRATE_X05 | 15642 | 热耗率曲线(目标)_X05 |  | float32
CALC.N2TC_CV_HEATRATE_Y05 | 15643 | 热耗率曲线(目标)_Y05 |  | float32
CALC.N2TC_CV_HEATRATE_X06 | 15644 | 热耗率曲线(目标)_X06 |  | float32
CALC.N2TC_CV_HEATRATE_Y06 | 15645 | 热耗率曲线(目标)_Y06 |  | float32
CALC.N2TC_CV_P_LPEX_NUM | 15646 | 低排压力曲线(目标)_Num |  | float32
CALC.N2TC_CV_P_LPEX_X01 | 15647 | 低排压力曲线(目标)_X01 |  | float32
CALC.N2TC_CV_P_LPEX_Y01 | 15648 | 低排压力曲线(目标)_Y01 |  | float32
CALC.N2TC_CV_P_LPEX_X02 | 15649 | 低排压力曲线(目标)_X02 |  | float32
CALC.N2TC_CV_P_LPEX_Y02 | 15650 | 低排压力曲线(目标)_Y02 |  | float32
CALC.N2TC_CV_P_LPEX_X03 | 15651 | 低排压力曲线(目标)_X03 |  | float32
CALC.N2TC_CV_P_LPEX_Y03 | 15652 | 低排压力曲线(目标)_Y03 |  | float32
CALC.N2TC_CV_P_LPEX_X04 | 15653 | 低排压力曲线(目标)_X04 |  | float32
CALC.N2TC_CV_P_LPEX_Y04 | 15654 | 低排压力曲线(目标)_Y04 |  | float32
CALC.N2TC_CV_P_LPEX_X05 | 15655 | 低排压力曲线(目标)_X05 |  | float32
CALC.N2TC_CV_P_LPEX_Y05 | 15656 | 低排压力曲线(目标)_Y05 |  | float32
CALC.N2TC_CV_P_LPEX_X06 | 15657 | 低排压力曲线(目标)_X06 |  | float32
CALC.N2TC_CV_P_LPEX_Y06 | 15658 | 低排压力曲线(目标)_Y06 |  | float32
CALC.N2TC_CV_P_LPEX_X07 | 15659 | 低排压力曲线(目标)_X07 |  | float32
CALC.N2TC_CV_P_LPEX_Y07 | 15660 | 低排压力曲线(目标)_Y07 |  | float32
CALC.N2TC_CV_P_LPEX_X08 | 15661 | 低排压力曲线(目标)_X08 |  | float32
CALC.N2TC_CV_P_LPEX_Y08 | 15662 | 低排压力曲线(目标)_Y08 |  | float32
CALC.N2TC_CV_P_LPEX_X09 | 15663 | 低排压力曲线(目标)_X09 |  | float32
CALC.N2TC_CV_P_LPEX_Y09 | 15664 | 低排压力曲线(目标)_Y09 |  | float32
CALC.N2TC_CV_P_LPEX_X10 | 15665 | 低排压力曲线(目标)_X10 |  | float32
CALC.N2TC_CV_P_LPEX_Y10 | 15666 | 低排压力曲线(目标)_Y10 |  | float32
CALC.N2TC_CV_HEATRT_D_NUM | 15667 | 热耗率曲线(未修正)_Num |  | float32
CALC.N2TC_CV_HEATRT_D_X01 | 15668 | 热耗率曲线(未修正)_X01 |  | float32
CALC.N2TC_CV_HEATRT_D_Y01 | 15669 | 热耗率曲线(未修正)_Y01 |  | float32
CALC.N2TC_CV_HEATRT_D_X02 | 15670 | 热耗率曲线(未修正)_X02 |  | float32
CALC.N2TC_CV_HEATRT_D_Y02 | 15671 | 热耗率曲线(未修正)_Y02 |  | float32
CALC.N2TC_CV_HEATRT_D_X03 | 15672 | 热耗率曲线(未修正)_X03 |  | float32
CALC.N2TC_CV_HEATRT_D_Y03 | 15673 | 热耗率曲线(未修正)_Y03 |  | float32
CALC.N2TC_CV_HEATRT_D_X04 | 15674 | 热耗率曲线(未修正)_X04 |  | float32
CALC.N2TC_CV_HEATRT_D_Y04 | 15675 | 热耗率曲线(未修正)_Y04 |  | float32
CALC.N2TC_CV_HEATRT_D_X05 | 15676 | 热耗率曲线(未修正)_X05 |  | float32
CALC.N2TC_CV_HEATRT_D_Y05 | 15677 | 热耗率曲线(未修正)_Y05 |  | float32
CALC.N2TC_CV_HEATRT_D_X06 | 15678 | 热耗率曲线(未修正)_X06 |  | float32
CALC.N2TC_CV_HEATRT_D_Y06 | 15679 | 热耗率曲线(未修正)_Y06 |  | float32
CALC.N2TC_CV_HEATRT_D_X07 | 15680 | 热耗率曲线(未修正)_X07 |  | float32
CALC.N2TC_CV_HEATRT_D_Y07 | 15681 | 热耗率曲线(未修正)_Y07 |  | float32
CALC.N2TC_CV_HEATRT_D_X08 | 15682 | 热耗率曲线(未修正)_X08 |  | float32
CALC.N2TC_CV_HEATRT_D_Y08 | 15683 | 热耗率曲线(未修正)_Y08 |  | float32
CALC.N2TC_CV_HEATRT_D_X09 | 15684 | 热耗率曲线(未修正)_X09 |  | float32
CALC.N2TC_CV_HEATRT_D_Y09 | 15685 | 热耗率曲线(未修正)_Y09 |  | float32
CALC.N2TC_CV_HEATRT_D_X10 | 15686 | 热耗率曲线(未修正)_X10 |  | float32
CALC.N2TC_CV_HEATRT_D_Y10 | 15687 | 热耗率曲线(未修正)_Y10 |  | float32
CALC.N2TC_CPR_P_HPStmIn | 15688 | 高压蒸汽压力对功率的修正系数 |  | float32
CALC.N2TC_CPR_T_HPStmIn | 15689 | 高压蒸汽温度对功率的修正系数 |  | float32
CALC.N2TC_CPR_T_IPStmIn | 15690 | 中压蒸汽温度对功率的修正系数 |  | float32
CALC.N2TC_CPR_T_LPStmIn | 15691 | 低压蒸汽温度对功率的修正系数 |  | float32
CALC.N2TC_CPR_P_Lpex | 15692 | 蒸汽轮机背压对功率的修正系数 |  | float32
CALC.N2TC_CPR_F_LPStmIn | 15693 | 低压蒸汽流量对功率的修正系数 |  | float32
CALC.N2TC_CPR_W_G | 15694 | 汽轮机功率总修正系数 |  | float32
CALC.N2TC_W_G_GC | 15695 | 汽轮机功率(修正) | MW | float32
CALC.N2TC_Han_GRWaterRep | 15696 | 供热补水焓 | kJ/kg | float32
CALC.N2GC_R_CToH | 15697 | 碳氢比 |  | float32
CALC.N2GC_MT_FUEL | 15698 | 燃料分子量 | kg/kmol | float32
CALC.N2GC_Qnetar | 15699 | 燃料低热值(计算)kJ/kg | kJ/kg | float32
CALC.N2GC_MT_GAS | 15700 | 燃气分子量 | kg/kmol | float32
CALC.N2GC_R_P2VsP1 | 15701 | 压气机压比P2/P1 |  | float32
CALC.N2GC_Eff_COMP | 15702 | 压气机内效率 | % | float32
CALC.N2GC_R_FuelToAir | 15703 | 燃料空气比(不考虑冷却) |  | float32
CALC.N2GC_T_GASTInISO | 15704 | 燃机入口温度T3(ISO) | ℃ | float32
CALC.N2GC_R_INLET | 15705 | 实际燃料空气比(考虑冷却) |  | float32
CALC.N2GC_R_T3VsT1 | 15706 | 燃气轮机装置温比T3/T1 |  | float32
CALC.N2GC_W_GAST | 15707 | 燃气透平功率 | MW | float32
CALC.N2GC_W_COMPA | 15708 | 压气机耗功率 | MW | float32
CALC.N2GC_T_GASTIn | 15709 | 燃气轮机进口温度T3 | ℃ | float32
CALC.N2GC_Eff_GAST | 15710 | 燃气轮机内效率 | % | float32
CALC.N2GC_R_FuelExpend | 15711 | 燃机发电气耗率 | Nm3/kWh | float32
CALC.N2GC_GASTHeatRate | 15712 | 燃机热耗率 | kJ/kWh | float32
CALC.N2GC_Eff_GASTUnit | 15713 | 燃机发电效率 | % | float32
CALC.N2GC_W_PEC | 15714 | 厂用电功率 | MW | float32
CALC.N2GC_RW_PEC | 15715 | 厂用电率 | % | float32
CALC.N2GC_R_FuelExpendGE | 15716 | 燃机供电气耗 | Nm3/kWh | float32
CALC.N2GC_CoalRate_GE | 15717 | 燃机发电煤耗 | g/kWh | float32
CALC.N2GC_CoalRate | 15718 | 燃机供电煤耗 | g/kWh | float32
CALC.N2GC_Eff_COMP_T | 15719 | 压气机效率(目标) | ℃ | float32
CALC.N2GC_Eff_GAST_T | 15720 | 燃机效率(目标) | ℃ | float32
CALC.N2GC_T_GASTOut_T | 15721 | 燃机出口温度(目标) | ℃ | float32
CALC.N2GC_CV_Eff_COMP_NUM | 15722 | 压气机效率曲线(目标)_Num |  | float32
CALC.N2GC_CV_Eff_COMP_X01 | 15723 | 压气机效率曲线(目标)_X01 |  | float32
CALC.N2GC_CV_Eff_COMP_Y01 | 15724 | 压气机效率曲线(目标)_Y01 |  | float32
CALC.N2GC_CV_Eff_COMP_X02 | 15725 | 压气机效率曲线(目标)_X02 |  | float32
CALC.N2GC_CV_Eff_COMP_Y02 | 15726 | 压气机效率曲线(目标)_Y02 |  | float32
CALC.N2GC_CV_Eff_COMP_X03 | 15727 | 压气机效率曲线(目标)_X03 |  | float32
CALC.N2GC_CV_Eff_COMP_Y03 | 15728 | 压气机效率曲线(目标)_Y03 |  | float32
CALC.N2GC_CV_Eff_COMP_X04 | 15729 | 压气机效率曲线(目标)_X04 |  | float32
CALC.N2GC_CV_Eff_COMP_Y04 | 15730 | 压气机效率曲线(目标)_Y04 |  | float32
CALC.N2GC_CV_Eff_COMP_X05 | 15731 | 压气机效率曲线(目标)_X05 |  | float32
CALC.N2GC_CV_Eff_COMP_Y05 | 15732 | 压气机效率曲线(目标)_Y05 |  | float32
CALC.N2GC_CV_Eff_COMP_X06 | 15733 | 压气机效率曲线(目标)_X06 |  | float32
CALC.N2GC_CV_Eff_COMP_Y06 | 15734 | 压气机效率曲线(目标)_Y06 |  | float32
CALC.N2GC_CV_Eff_COMP_X07 | 15735 | 压气机效率曲线(目标)_X07 |  | float32
CALC.N2GC_CV_Eff_COMP_Y07 | 15736 | 压气机效率曲线(目标)_Y07 |  | float32
CALC.N2GC_CV_Eff_COMP_X08 | 15737 | 压气机效率曲线(目标)_X08 |  | float32
CALC.N2GC_CV_Eff_COMP_Y08 | 15738 | 压气机效率曲线(目标)_Y08 |  | float32
CALC.N2GC_CV_Eff_COMP_X09 | 15739 | 压气机效率曲线(目标)_X09 |  | float32
CALC.N2GC_CV_Eff_COMP_Y09 | 15740 | 压气机效率曲线(目标)_Y09 |  | float32
CALC.N2GC_CV_Eff_COMP_X10 | 15741 | 压气机效率曲线(目标)_X10 |  | float32
CALC.N2GC_CV_Eff_COMP_Y10 | 15742 | 压气机效率曲线(目标)_Y10 |  | float32
CALC.N2GC_CV_Eff_GAST_NUM | 15743 | 燃机效率曲线(目标)_Num |  | float32
CALC.N2GC_CV_Eff_GAST_X01 | 15744 | 燃机效率曲线(目标)_X01 |  | float32
CALC.N2GC_CV_Eff_GAST_Y01 | 15745 | 燃机效率曲线(目标)_Y01 |  | float32
CALC.N2GC_CV_Eff_GAST_X02 | 15746 | 燃机效率曲线(目标)_X02 |  | float32
CALC.N2GC_CV_Eff_GAST_Y02 | 15747 | 燃机效率曲线(目标)_Y02 |  | float32
CALC.N2GC_CV_Eff_GAST_X03 | 15748 | 燃机效率曲线(目标)_X03 |  | float32
CALC.N2GC_CV_Eff_GAST_Y03 | 15749 | 燃机效率曲线(目标)_Y03 |  | float32
CALC.N2GC_CV_Eff_GAST_X04 | 15750 | 燃机效率曲线(目标)_X04 |  | float32
CALC.N2GC_CV_Eff_GAST_Y04 | 15751 | 燃机效率曲线(目标)_Y04 |  | float32
CALC.N2GC_CV_Eff_GAST_X05 | 15752 | 燃机效率曲线(目标)_X05 |  | float32
CALC.N2GC_CV_Eff_GAST_Y05 | 15753 | 燃机效率曲线(目标)_Y05 |  | float32
CALC.N2GC_CV_Eff_GAST_X06 | 15754 | 燃机效率曲线(目标)_X06 |  | float32
CALC.N2GC_CV_Eff_GAST_Y06 | 15755 | 燃机效率曲线(目标)_Y06 |  | float32
CALC.N2GC_CV_Eff_GAST_X07 | 15756 | 燃机效率曲线(目标)_X07 |  | float32
CALC.N2GC_CV_Eff_GAST_Y07 | 15757 | 燃机效率曲线(目标)_Y07 |  | float32
CALC.N2GC_CV_Eff_GAST_X08 | 15758 | 燃机效率曲线(目标)_X08 |  | float32
CALC.N2GC_CV_Eff_GAST_Y08 | 15759 | 燃机效率曲线(目标)_Y08 |  | float32
CALC.N2GC_CV_Eff_GAST_X09 | 15760 | 燃机效率曲线(目标)_X09 |  | float32
CALC.N2GC_CV_Eff_GAST_Y09 | 15761 | 燃机效率曲线(目标)_Y09 |  | float32
CALC.N2GC_CV_Eff_GAST_X10 | 15762 | 燃机效率曲线(目标)_X10 |  | float32
CALC.N2GC_CV_Eff_GAST_Y10 | 15763 | 燃机效率曲线(目标)_Y10 |  | float32
CALC.N2GC_CV_T_GASTOut_NUM | 15764 | 燃机出口温度曲线(目标)_Num |  | float32
CALC.N2GC_CV_T_GASTOut_X01 | 15765 | 燃机出口温度曲线(目标)_X01 |  | float32
CALC.N2GC_CV_T_GASTOut_Y01 | 15766 | 燃机出口温度曲线(目标)_Y01 |  | float32
CALC.N2GC_CV_T_GASTOut_X02 | 15767 | 燃机出口温度曲线(目标)_X02 |  | float32
CALC.N2GC_CV_T_GASTOut_Y02 | 15768 | 燃机出口温度曲线(目标)_Y02 |  | float32
CALC.N2GC_CV_T_GASTOut_X03 | 15769 | 燃机出口温度曲线(目标)_X03 |  | float32
CALC.N2GC_CV_T_GASTOut_Y03 | 15770 | 燃机出口温度曲线(目标)_Y03 |  | float32
CALC.N2GC_CV_T_GASTOut_X04 | 15771 | 燃机出口温度曲线(目标)_X04 |  | float32
CALC.N2GC_CV_T_GASTOut_Y04 | 15772 | 燃机出口温度曲线(目标)_Y04 |  | float32
CALC.N2GC_CV_T_GASTOut_X05 | 15773 | 燃机出口温度曲线(目标)_X05 |  | float32
CALC.N2GC_CV_T_GASTOut_Y05 | 15774 | 燃机出口温度曲线(目标)_Y05 |  | float32
CALC.N2GC_CV_T_GASTOut_X06 | 15775 | 燃机出口温度曲线(目标)_X06 |  | float32
CALC.N2GC_CV_T_GASTOut_Y06 | 15776 | 燃机出口温度曲线(目标)_Y06 |  | float32
CALC.N2GC_CV_T_GASTOut_X07 | 15777 | 燃机出口温度曲线(目标)_X07 |  | float32
CALC.N2GC_CV_T_GASTOut_Y07 | 15778 | 燃机出口温度曲线(目标)_Y07 |  | float32
CALC.N2GC_CV_T_GASTOut_X08 | 15779 | 燃机出口温度曲线(目标)_X08 |  | float32
CALC.N2GC_CV_T_GASTOut_Y08 | 15780 | 燃机出口温度曲线(目标)_Y08 |  | float32
CALC.N2GC_CV_T_GASTOut_X09 | 15781 | 燃机出口温度曲线(目标)_X09 |  | float32
CALC.N2GC_CV_T_GASTOut_Y09 | 15782 | 燃机出口温度曲线(目标)_Y09 |  | float32
CALC.N2GC_CV_T_GASTOut_X10 | 15783 | 燃机出口温度曲线(目标)_X10 |  | float32
CALC.N2GC_CV_T_GASTOut_Y10 | 15784 | 燃机出口温度曲线(目标)_Y10 |  | float32
CALC.N2PC_R_STToGT | 15785 | 联合循环蒸燃功比 | % | float32
CALC.N2PC_R_STToUnit | 15786 | 联合循环蒸功百分率 | % | float32
CALC.N2PC_HeatRate | 15787 | 联合循环热耗率 | kJ/kWh | float32
CALC.N2PC_Eff_Unit | 15788 | 联合循环电效率 | % | float32
CALC.N2PC_W_PEC | 15789 | 厂用电功率 | MW | float32
CALC.N2PC_RW_PEC | 15790 | 厂用电率 | % | float32
CALC.N2PC_CoalRate_GE | 15791 | 联合循环发电煤耗 | g/kWh | float32
CALC.N2PC_CoalRate | 15792 | 联合循环供电煤耗 | g/kWh | float32
CALC.N2PC_Eff_Fuel | 15793 | 燃料利用系数 | % | float32
CALC.N2PC_RW_HeatToEle | 15794 | 热电比 | GJ/MWh | float32
CALC.N2PC_RW_SupplyHeat | 15795 | 供热比 | % | float32
CALC.N2PC_Eff_SupplyHeat | 15796 | 供热热效率 | % | float32
CALC.N2PC_RW_PECHeat | 15797 | 供热用厂用电率 | kWh/GJ | float32
CALC.N2PC_R_FuelExpendHE | 15798 | 联合循环供热气耗 | Nm3/GJ | float32
CALC.N2PC_R_FuelExpend | 15799 | 联合循环发电气耗率 | Nm3/kWh | float32
CALC.N2PC_R_FuelExpendGE | 15800 | 联合循环供电气耗 | Nm3/kWh | float32
CALC.N2PC_RW_PECEle | 15801 | 发电用厂用电率 | Nm3/GJ | float32
CALC.N2PC_CoalRateHeatHE | 15802 | 联合循环供热煤耗 | % | float32
CALC.N2PS_Qnetar | 15803 | 燃料低热值 | % | float32
CALC.N2PC_CHR_P_atm | 15804 | 大气压力对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_P_atm | 15805 | 大气压力对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CHR_T_atm | 15806 | 大气温度对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_T_atm | 15807 | 大气温度对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CHR_Qnetar | 15808 | 燃料低热值对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_Qnetar | 15809 | 燃料低热值对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CHR_Humidity | 15810 | 相对湿度对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_Humidity | 15811 | 相对湿度对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CHR_P_Lpex | 15812 | 蒸汽轮机背压对联合热耗修正系数 |  | float32
CALC.N2PC_HR_P_Lpex | 15813 | 蒸汽轮机背压对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CHR_R_WaterRep | 15814 | 补给水率对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_R_WaterRep | 15815 | 补给水率对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CHR_Frequency | 15816 | 发电机频率对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_Frequency | 15817 | 发电机频率对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CHR_SupplyHeat | 15818 | 热负荷对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_SupplyHeat | 15819 | 热负荷对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CHR_Runtime | 15820 | 老化对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_Runtime | 15821 | 老化对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_HeatRate_GC | 15822 | 联合循环热耗率(基准工况) | kJ/kWh | float32
CALC.N2PC_CPR_P_atm | 15823 | 大气压力对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_P_atm | 15824 | 大气压力对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_CPR_T_atm | 15825 | 大气温度对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_T_atm | 15826 | 大气温度对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_CPR_Qnetar | 15827 | 燃料低热值对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_Qnetar | 15828 | 燃料低热值对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_CPR_Humidity | 15829 | 相对湿度对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_Humidity | 15830 | 相对湿度对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_CPR_P_Lpex | 15831 | 蒸汽轮机背压对联合功率修正系数 |  | float32
CALC.N2PC_PR_P_Lpex | 15832 | 蒸汽轮机背压对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_CPR_R_WaterRep | 15833 | 补给水率对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_R_WaterRep | 15834 | 补给水率对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_CPR_Frequency | 15835 | 发电机频率对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_Frequency | 15836 | 发电机频率对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_CPR_SupplyHeat | 15837 | 热负荷对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_SupplyHeat | 15838 | 热负荷对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_CPR_Runtime | 15839 | 老化对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_Runtime | 15840 | 老化对联合循环功率的影响 | kJ/kWh | float32
CALC.N2PC_W_G_GC | 15841 | 联合循环发电机功率(基准工况) | MW | float32
CALC.N2PC_W_GT | 15842 | 联合循环发电机理论功率 | MW | float32
CALC.N2PC_CV_HEATRATE_NUM | 15843 | 热耗率曲线(目标)_Num |  | float32
CALC.N2PC_CV_HEATRATE_X01 | 15844 | 热耗率曲线(目标)_X01 |  | float32
CALC.N2PC_CV_HEATRATE_Y01 | 15845 | 热耗率曲线(目标)_Y01 |  | float32
CALC.N2PC_CV_HEATRATE_X02 | 15846 | 热耗率曲线(目标)_X02 |  | float32
CALC.N2PC_CV_HEATRATE_Y02 | 15847 | 热耗率曲线(目标)_Y02 |  | float32
CALC.N2PC_CV_HEATRATE_X03 | 15848 | 热耗率曲线(目标)_X03 |  | float32
CALC.N2PC_CV_HEATRATE_Y03 | 15849 | 热耗率曲线(目标)_Y03 |  | float32
CALC.N2PC_CV_HEATRATE_X04 | 15850 | 热耗率曲线(目标)_X04 |  | float32
CALC.N2PC_CV_HEATRATE_Y04 | 15851 | 热耗率曲线(目标)_Y04 |  | float32
CALC.N2PC_CV_HEATRATE_X05 | 15852 | 热耗率曲线(目标)_X05 |  | float32
CALC.N2PC_CV_HEATRATE_Y05 | 15853 | 热耗率曲线(目标)_Y05 |  | float32
CALC.N2PC_CV_HEATRATE_X06 | 15854 | 热耗率曲线(目标)_X06 |  | float32
CALC.N2PC_CV_HEATRATE_Y06 | 15855 | 热耗率曲线(目标)_Y06 |  | float32
CALC.N2PC_CV_HEATRATE_X07 | 15856 | 热耗率曲线(目标)_X07 |  | float32
CALC.N2PC_CV_HEATRATE_Y07 | 15857 | 热耗率曲线(目标)_Y07 |  | float32
CALC.N2PC_CV_HEATRATE_X08 | 15858 | 热耗率曲线(目标)_X08 |  | float32
CALC.N2PC_CV_HEATRATE_Y08 | 15859 | 热耗率曲线(目标)_Y08 |  | float32
CALC.N2PC_CV_HEATRATE_X09 | 15860 | 热耗率曲线(目标)_X09 |  | float32
CALC.N2PC_CV_HEATRATE_Y09 | 15861 | 热耗率曲线(目标)_Y09 |  | float32
CALC.N2PC_CV_HEATRATE_X10 | 15862 | 热耗率曲线(目标)_X10 |  | float32
CALC.N2PC_CV_HEATRATE_Y10 | 15863 | 热耗率曲线(目标)_Y10 |  | float32
CALC.N2PC_HeatRate_GC_T | 15864 | 联合循环热耗率(基准工况目标) |  | float32
CALC.N2PC_CPH_P_atm | 15865 | 大气压力对热负荷修正系数 |  | float32
CALC.N2PC_PH_P_atm | 15866 | 大气压力对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_CPH_T_atm | 15867 | 大气温度对热负荷修正系数 |  | float32
CALC.N2PC_PH_T_atm | 15868 | 大气温度对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_CPH_Qnetar | 15869 | 燃料低热值对热负荷修正系数 |  | float32
CALC.N2PC_PH_Qnetar | 15870 | 燃料低热值对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_CPH_Humidity | 15871 | 相对湿度对热负荷修正系数 |  | float32
CALC.N2PC_PH_Humidity | 15872 | 相对湿度对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_CPH_P_Lpex | 15873 | 蒸汽轮机背压对热负荷修正系数 |  | float32
CALC.N2PC_PH_P_Lpex | 15874 | 蒸汽轮机背压对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_CPH_R_WaterRep | 15875 | 补给水率对热负荷修正系数 |  | float32
CALC.N2PC_PH_R_WaterRep | 15876 | 补给水率对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_CPH_Frequency | 15877 | 发电机频率对热负荷修正系数 |  | float32
CALC.N2PC_PH_Frequency | 15878 | 发电机频率对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_CPH_SupplyHeat | 15879 | 热负荷对热负荷修正系数 |  | float32
CALC.N2PC_PH_SupplyHeat | 15880 | 热负荷对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_CPH_Runtime | 15881 | 老化对热负荷修正系数 |  | float32
CALC.N2PC_PH_Runtime | 15882 | 老化对热负荷的影响 | kJ/kWh | float32
CALC.N2PC_HeatRate_PS | 15883 | 联合循环供电热耗率 | kJ/kWh | float32
CALC.N2PC_Eff_Unit_PS | 15884 | 联合循环供电效率 | % | float32
CALC.N2TC_HeatRate_PS | 15885 | 汽轮机供电热耗率 | kJ/kWh | float32
CALC.N2TC_EFF_Turbine_PS | 15886 | 汽轮机供电效率 | % | float32
CALC.N2GC_GASTHeatRate_PS | 15887 | 燃机供电热耗率 | kJ/kWh | float32
CALC.N2GC_Eff_GASTUnit_PS | 15888 | 燃机供电效率 | % | float32
CALC.N2BS_A_HPFPA | 15889 | 高压给水泵A电流 | A | float32
CALC.N2BS_A_HPFPB | 15890 | 高压给水泵B电流 | A | float32
CALC.N2BS_A_IPFPA | 15891 | 中压给水泵A电流 | A | float32
CALC.N2BS_A_IPFPB | 15892 | 中压给水泵B电流 | A | float32
N2DCS.20CJA01DP300FX | 15893 | 低压压力设定值（匹配燃机负荷 |  | float32
N2DCS.20CJA01DP200SP | 15894 | 中压压力偏置值 |  | float32
N2DCS.20CJA01DP200FX | 15895 | 中压压力设定值（匹配燃机负荷 |  | float32
N2DCS.20CJA01DP100SP | 15896 | 高压压力偏置值 |  | float32
N2DCS.20CJA01DP100FX | 15897 | 高压压力设定值（匹配燃机负荷 |  | float32
N2DCS.RSTA3001501 | 15898 |  |  | float32
N2DCS.DCSETSFO | 15899 | #3机ETS跳闸首出（打包点的位号) |  | float32
N2DCS.20LBG21GH001TC | 15900 | #3机轴封电加热器出口温度设定值 |  | float32
N2DCS.20LBG21GH001PO | 15901 | #3机轴封电加热器功率 |  | float32
N2DCS.20LCM40CL101I | 15902 | 疏水扩容器液位（计算后） |  | float32
N2DCS.ZSFWKD | 15903 | 高旁阀最小阀位开度 |  | float32
N2DCS.WARMMODE | 15904 | 温态启动次数 |  | float32
N2DCS.TRIPNUM | 15905 | #3跳闸次数 |  | float32
N2DCS.LTPLKD | 15906 | 汽机冷态启动高旁阀最小阀位 |  | float32
N2DCS.HOTMODE | 15907 | 热态启动次数 |  | float32
N2DCS.GTNUM | 15908 | #4启动次数 |  | float32
N2DCS.GEFIRING | 15909 | Ovation Control Builder |  | float32
N2DCS.COLDMODE | 15910 | 冷态启动次数 |  | float32
N2DCS.20MBY10CE901YQ01A | 15911 | #4机实际负荷-ACTIVE POWER |  | float32
N2DCS.20MBY10CE901YQ01_SUM5 | 15912 | #4点火运行时间 |  | float32
N2DCS.20MBY10CE901YQ01_SUM4 | 15913 | #4运行时间 |  | float32
N2DCS.20CJA01DP300_DCS | 15914 | 低压主蒸汽压力设定值 |  | float32
N2DCS.20CJA01DP300SP | 15915 | 低压压力偏置值 |  | float32
N2DCS.20CFE40CF101LS | 15916 | 烟气出口流速 |  | float32
N2DCS.20CFE40CF101_LL | 15917 | 烟气流量 |  | float32
N2DCS.LPLVLPID1_OUT | 15918 | 低压给水调阀三冲量主调输出 |  | float32
N2DCS.LPLVLADD_OUT | 15919 | 低压给水调阀三冲量副调输入 |  | float32
N2DCS.LPDWTC | 15920 | 低压汽包上下壁温差 |  | float32
N2DCS.LPDWC | 15921 | 低压汽包上下壁温差 |  | float32
N2DCS.20HAD70CLB3 | 15922 | Ovation Control Builder |  | float32
N2DCS.20HAD70CLB2 | 15923 | Ovation Control Builder |  | float32
N2DCS.20HAD70CLB1 | 15924 | Ovation Control Builder |  | float32
N2DCS.ROTFLTRBFRBHDL | 15925 | #2旋转滤网前后液位差 |  | float32
N2DCS.20PSA01CL101P | 15926 | #2冷却塔排水池液位(计算后） |  | float32
N2DCS.20MKA30CT | 15927 | #3发电机进风温度（8选后） |  | float32
N2DCS.20MAW20CTL | 15928 | 轴封供汽母管高中压侧温度(2选后 |  | float32
N2DCS.20LCR10CF101_CAL | 15929 | 凝汽器补水流量(计算后) |  | float32
N2DCS.20LCE16CF101I | 15930 | 闭式水箱正常补水流量计算后 |  | float32
N2DCS.20LBG21GH001TO | 15931 | #3机轴封电加热器出口温度 |  | float32
N2DCS.STTRIPFO1 | 15932 | #3机跳闸首出（打包点位号） |  | float32
N2DCS.IPLVLPID1_OUT | 15933 | 中压给水调阀三冲量副调设定 |  | float32
N2DCS.IPLVLADD_OUT | 15934 | 中压给水调阀三冲量主调输出 |  | float32
N2DCS.IPDWTC | 15935 | 中压汽包上下壁温差 |  | float32
N2DCS.IPDWC | 15936 | 中压汽包上下壁温差 |  | float32
N2DCS.HRSGFO1 | 15937 | #3炉跳闸首出(打包点位号 |  | float32
N2DCS.20HAD80CLB3 | 15938 | Ovation Control Builder |  | float32
N2DCS.20HAD80CLB2 | 15939 | Ovation Control Builder |  | float32
N2DCS.20HAD80CLB1 | 15940 | Ovation Control Builder |  | float32
N2DCS.20CFE40CQ104P | 15941 | 烟囱出口CO含量(ppm) |  | float32
N2DCS.20CFE40CQ103P | 15942 | 烟囱出口SO2含量(ppm) |  | float32
N2DCS.20CFE40CQ103_1 | 15943 | 烟囱出口SO2含量1 |  | float32
N2DCS.20CFE40CQ101XP | 15944 | 烟囱出口NOX含量(ppm) |  | float32
N2DCS.20CFE40CQ101X | 15945 | 烟囱出口NOX含量 |  | float32
N2DCS.20CFE40CQ101P | 15946 | 烟囱出口NO含量(ppm) |  | float32
N2DCS.20CFE40CM101_YQSD | 15947 | 烟气湿度 |  | float32
N2DCS.1_1_8_COIL_2_KSERVO_A | 15948 | Ovation Control Builder |  | float32
N2DCS.1_1_8_COIL_1_KSERVO_A | 15949 | Ovation Control Builder |  | float32
N2DCS.ZYGSXBWC | 15950 | 中压缸上下中壁温差 |  | float32
N2DCS.GYGSXBWC | 15951 | 高压缸上下中壁温差 |  | float32
N2DCS.20MAB50FT350 | 15952 | 中压缸上下温差 |  | float32
N2DCS.20MAA50FT350 | 15953 | 高压缸上下温差 |  | float32
N2DCS.HPLVLPID1_OUT | 15954 | 高压变频三冲量主调输出 |  | float32
N2DCS.HPLVLADD_OUT | 15955 | 高压变频三冲量副调设定 |  | float32
N2DCS.HPDWC | 15956 | 高压包上下壁温差 |  | float32
N2DCS.HPDSTCF1 | 15957 | 高压主蒸汽流量滤波后 |  | float32
N2DCS.20LBA20CT007_SP | 15958 | 主蒸汽温度限值 |  | float32
N2DCS.20LAE90AA101_SP1 | 15959 | Ovation Control Builder |  | float32
N2DCS.20HAD90CLB3 | 15960 | Ovation Control Builder |  | float32
N2DCS.20HAD90CLB2 | 15961 | Ovation Control Builder |  | float32
N2DCS.20HAD90CLB1 | 15962 | Ovation Control Builder |  | float32
N2DCS.WJD | 15963 | 主汽温降大 |  | float32
N2DCS.TEST_YNOR | 15964 | Ovation Control Builder |  | float32
N2DCS.TEST_WY | 15965 | Ovation Control Builder |  | float32
N2DCS.TEST_SET | 15966 | Ovation Control Builder |  | float32
N2DCS.TEST_PID | 15967 | Ovation Control Builder |  | float32
N2DCS.TEST_OSV | 15968 | Ovation Control Builder |  | float32
N2DCS.TEST_NSV | 15969 | Ovation Control Builder |  | float32
N2DCS.TEST_N490 | 15970 | Ovation Control Builder |  | float32
N2DCS.TEST_N420 | 15971 | Ovation Control Builder |  | float32
N2DCS.TEST_N410 | 15972 | Ovation Control Builder |  | float32
N2DCS.TEST_KOS | 15973 | Ovation Control Builder |  | float32
N2DCS.TEST_KDN | 15974 | Ovation Control Builder |  | float32
N2DCS.TEST_DNY | 15975 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU060_YRT | 15976 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU060_YRFDT | 15977 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU060_OSFDT | 15978 | Ovation Control Builder |  | float32
N2DCS.20MYA01DU050_YNORT | 15979 | Ovation Control Builder |  | float32
N2DCS.STBPSTOPMODE | 15980 | 旁路停机模式 |  | digital
N2DCS.MONITORRE | 15981 | 光字牌声音报警 |  | digital
N2DCS.GTFIRING | 15982 | #4机在运行（有火焰） |  | digital
N2DCS.GOUPMOD | 15983 | 手动投入高中压旁路冲转模式 |  | digital
N2DCS.GOUP | 15984 | 高中压旁路冲转状态 |  | digital
N2DCS.CANCEL180 | 15985 | Ovation Control Builder |  | digital
N2DCS.GT_CTR_REMOTE | 15986 | #4机允许CCS控制 |  | digital
N2DCS.DCSETSTRIPRSPB | 15987 | ETS跳闸首出复位指令 |  | digital
N2DCS.20MAY01EZ011_XK468 | 15988 | #3机遮断系统已遮断8 |  | digital
N2DCS.20MAP10AA101CPDO | 15989 | 低旁阀全关位置(至DROP8) |  | digital
N2DCS.20MAN20AA101CPDO | 15990 | 中旁阀全关位置(至DROP8) |  | digital
N2DCS.20MAN10AA101CPDO | 15991 | 高旁阀全关位置(至DROP8) |  | digital
N2DCS.20HYY01EY001DSOE | 15992 | #3炉保护跳闸（SOE） |  | digital
N2DCS.GYZZQGRD | 15993 | 高压主蒸汽过热度 |  | float32
N2DCS.20LBB50CT007_SP | 15994 | 热再蒸汽温度限值 |  | float32
N2DCS.20MAC10CT313 | 15995 | 末级蒸汽温度3#(静叶环温度) |  | float32
N2DCS.20LBG21AC001RCT | 15996 | 轴封电加热器允许接受温度设定 |  | digital
N2DCS.20LBG21AC001RC | 15997 | 轴封电加热器在远控 |  | digital
N2DCS.20LBG21AC001PF | 15998 | 轴封电加热器综合故障 |  | digital
N2DCS.20LBG21AA003RC | 15999 | 轴封电加热器出口电动门在远控 |  | digital
N2DCS.20LBG21AA003PF | 16000 | 轴封电加热器出口电动门故障 |  | digital
N2DCS.20LBG21AA003OP | 16001 | 轴封电加热器出口电动门全开位 |  | digital
N2DCS.20LBG21AA003OD | 16002 | 轴封电加热器出口电动门打开指令 |  | digital
N2DCS.20LBG21AA003CP | 16003 | 轴封电加热器出口电动门全关位 |  | digital
N2DCS.20LBG21AA003CD | 16004 | 轴封电加热器出口电动门关闭指令 |  | digital
N2DCS.20LBG21AA002RC | 16005 | 轴封电加热器进口电动门在远控 |  | digital
N2DCS.20LBG21AA002PF | 16006 | 轴封电加热器进口电动门故障 |  | digital
N2DCS.20LBG21AA002OP | 16007 | 轴封电加热器进口电动门全开位 |  | digital
N2DCS.20LBG21AA002OD | 16008 | 轴封电加热器进口电动门打开指令 |  | digital
N2DCS.20LBG21AA002CP | 16009 | 轴封电加热器进口电动门全关位 |  | digital
N2DCS.20LBG21AA002CD | 16010 | 轴封电加热器进口电动门关闭指令 |  | digital
N2DCS.HTQR | 16011 | 手动确认轴封电加热器已投入 |  | digital
N2DCS.DEHALM007 | 16012 | #3机凝汽器真空>20KPa |  | digital
N2DCS.DEHALM006 | 16013 | #3机凝汽器真空测量故障 |  | digital
N2DCS.DEHALM005 | 16014 | #3机润滑油箱液位＞1000mm |  | digital
N2DCS.DEHALM004 | 16015 | #3机润滑油箱液位＜900mm |  | digital
N2DCS.DEHALM003 | 16016 | #3机润滑油箱液位测量故障 |  | digital
N2DCS.DEHALM002 | 16017 | #3机润滑油母管压力＜0.25MPa |  | digital
N2DCS.DEHALM001 | 16018 | #3机润滑油母管压力测量故障 |  | digital
N2DCS.20MAY01DU100_XK96 | 16019 | Ovation Control Builder |  | digital
N2DCS.20LBG21AC001_PUT | 16020 | 轴封电加热器已连锁投入 |  | digital
N2DCS.DEHALM100 | 16021 | #3机Z准则计算故障 |  | digital
N2DCS.DEHALM014 | 16022 | #2 CSI6300测试模式 |  | digital
N2DCS.20LCB11AP001CPDO | 16023 | #1凝结水泵已停止(至DROP9) |  | digital
N2DCS.20LBG21AC001TP | 16024 | 轴封电加热器已停止 |  | digital
N2DCS.20LBG21AC001TD | 16025 | 轴封电加热器停止指令 |  | digital
N2DCS.20LBG21AC001RP | 16026 | 轴封电加热器在运行 |  | digital
N2DCS.20LBG21AC001RD | 16027 | 轴封电加热器启动指令 |  | digital
N2DCS.DEHALM024 | 16028 | ＜47.5HZ且中压缸上下温差＞55℃ |  | digital
N2DCS.DEHALM023 | 16029 | #3机低压排汽支架温度＞70℃ |  | digital
N2DCS.DEHALM022 | 16030 | #3机低压排汽支架温度测量故障 |  | digital
N2DCS.DEHALM021 | 16031 | #3机中压缸排汽蒸汽温度＞323℃ |  | digital
N2DCS.DEHALM020 | 16032 | #3机中压缸排汽蒸汽温度＞305℃ |  | digital
N2DCS.DEHALM019 | 16033 | #3机高压缸排汽口温度＞384℃ |  | digital
N2DCS.DEHALM018 | 16034 | #3机低压缸末级蒸汽温度＞230℃ |  | digital
N2DCS.DEHALM017 | 16035 | #3机低压缸末级蒸汽温度＞180℃ |  | digital
N2DCS.DEHALM016 | 16036 | #3机高压缸排汽口温度大于计算值 |  | digital
N2DCS.DEHALM015 | 16037 | #3机高压缸排汽口温度测量故障 |  | digital
N2DCS.DEHALM013 | 16038 | #3机DEH控制器站间通讯中断 |  | digital
N2DCS.DEHALM012 | 16039 | #3机轴向位移＞0.5mm |  | digital
N2DCS.DEHALM011 | 16040 | #3机轴向位移＜-0.5mm |  | digital
N2DCS.DEHALM010 | 16041 | #3机轴向位移测量故障 |  | digital
N2DCS.DEHALM009 | 16042 | #3机EH油压力＜12MPa |  | digital
N2DCS.DEHALM008 | 16043 | #3机EH油压力测量故障 |  | digital
N2DCS.DEHALM040 | 16044 | #3机推力轴承前左上温度＞90℃ |  | digital
N2DCS.DEHALM039 | 16045 | #3机推力轴承前左上温度测量故障 |  | digital
N2DCS.DEHALM038 | 16046 | #2径向轴承前右下温度＞90℃ |  | digital
N2DCS.DEHALM037 | 16047 | #2径向轴承前右下温度测量故障 |  | digital
N2DCS.DEHALM036 | 16048 | #2径向轴承前左下温度＞90℃ |  | digital
N2DCS.DEHALM035 | 16049 | #2径向轴承前左下温度测量故障 |  | digital
N2DCS.DEHALM034 | 16050 | #2径向轴承前右上温度＞90℃ |  | digital
N2DCS.DEHALM033 | 16051 | #2径向轴承前右上温度测量故障 |  | digital
N2DCS.DEHALM032 | 16052 | #2径向轴承前左上温度＞90℃ |  | digital
N2DCS.DEHALM031 | 16053 | #2径向轴承前左上温度测量故障 |  | digital
N2DCS.DEHALM030 | 16054 | #3机#1轴承后右下温度＞90℃ |  | digital
N2DCS.DEHALM029 | 16055 | #3机#1轴承后右下温度测量故障 |  | digital
N2DCS.DEHALM028 | 16056 | #3机#1轴承前右下温度＞90℃ |  | digital
N2DCS.DEHALM027 | 16057 | #3机#1轴承前右下温度测量故障 |  | digital
N2DCS.DEHALM026 | 16058 | 并网120s后中压缸上下温差>45℃ |  | digital
N2DCS.DEHALM025 | 16059 | #3机中压缸上下温差＞30℃ |  | digital
N2DCS.DEHALM056 | 16060 | #3机#3轴承后右下温度＞90℃ |  | digital
N2DCS.DEHALM055 | 16061 | #3机#3轴承后右下温度测量故障 |  | digital
N2DCS.DEHALM054 | 16062 | #3机#3轴承前右下温度＞90℃ |  | digital
N2DCS.DEHALM053 | 16063 | #3机#3轴承前右下温度测量故障 |  | digital
N2DCS.DEHALM052 | 16064 | #3机#3轴承前左下温度＞90℃ |  | digital
N2DCS.DEHALM051 | 16065 | #3机#3轴承前左下温度测量故障 |  | digital
N2DCS.DEHALM050 | 16066 | #3机#3轴承前右上温度＞90℃ |  | digital
N2DCS.DEHALM049 | 16067 | #3机#3轴承前右上温度测量故障 |  | digital
N2DCS.DEHALM048 | 16068 | #3机#3轴承前左上温度＞90℃ |  | digital
N2DCS.DEHALM047 | 16069 | #3机#3轴承前左上温度测量故障 |  | digital
N2DCS.DEHALM046 | 16070 | #3机推力轴承前右下温度＞90℃ |  | digital
N2DCS.DEHALM045 | 16071 | #3机推力轴承前右下温度测量故障 |  | digital
N2DCS.DEHALM044 | 16072 | #3机推力轴承前左下温度＞90℃ |  | digital
N2DCS.DEHALM043 | 16073 | #3机推力轴承前左下温度测量故障 |  | digital
N2DCS.DEHALM042 | 16074 | #3机推力轴承前右上温度＞90℃ |  | digital
N2DCS.DEHALM041 | 16075 | #3机推力轴承前右上温度测量故障 |  | digital
N2DCS.DEHALM072 | 16076 | #3机#3转速探头故障 |  | digital
N2DCS.DEHALM071 | 16077 | #3机#2转速探头故障 |  | digital
N2DCS.DEHALM070 | 16078 | #3机#1转速探头故障 |  | digital
N2DCS.DEHALM069 | 16079 | #3机紧急跳闸按钮通道3动作 |  | digital
N2DCS.DEHALM068 | 16080 | #3机紧急跳闸按钮通道2动作 |  | digital
N2DCS.DEHALM067 | 16081 | #3机紧急跳闸按钮通道1动作 |  | digital
N2DCS.DEHALM066 | 16082 | #3轴承座振动＞9.3mm/s |  | digital
N2DCS.DEHALM065 | 16083 | #3轴承座振动测量故障 |  | digital
N2DCS.DEHALM064 | 16084 | #2轴承座振动＞9.3mm/s |  | digital
N2DCS.DEHALM063 | 16085 | #2轴承座振动测量故障 |  | digital
N2DCS.DEHALM062 | 16086 | #1轴承座振动＞9.3mm/s |  | digital
N2DCS.DEHALM061 | 16087 | #1轴承座振动测量故障 |  | digital
N2DCS.DEHALM060 | 16088 | #3机#4轴承励端温度＞99℃ |  | digital
N2DCS.DEHALM059 | 16089 | #3机#4轴承励端温度测量故障 |  | digital
N2DCS.DEHALM058 | 16090 | #3机#4轴承机端温度＞99℃ |  | digital
N2DCS.DEHALM057 | 16091 | #3机#4轴承机端温度测量故障 |  | digital
N2DCS.DEHALM088 | 16092 | #4轴承振动＞130um |  | digital
N2DCS.DEHALM087 | 16093 | #4轴承振动＞83um |  | digital
N2DCS.DEHALM086 | 16094 | #4轴承振动测量故障 |  | digital
N2DCS.DEHALM085 | 16095 | #3轴承振动＞130um |  | digital
N2DCS.DEHALM084 | 16096 | #3轴承振动＞83um |  | digital
N2DCS.DEHALM083 | 16097 | #3轴承振动测量故障 |  | digital
N2DCS.DEHALM082 | 16098 | #2轴承振动＞130um |  | digital
N2DCS.DEHALM081 | 16099 | #2轴承振动＞83um |  | digital
N2DCS.DEHALM080 | 16100 | #2轴承振动测量故障 |  | digital
N2DCS.DEHALM079 | 16101 | #1轴承振动＞130um |  | digital
N2DCS.DEHALM078 | 16102 | #1轴承振动＞83um |  | digital
N2DCS.DEHALM077 | 16103 | #1轴承振动测量故障 |  | digital
N2DCS.DEHALM076 | 16104 | #3机负荷＞20且高压缸压比＜1.08 |  | digital
N2DCS.DEHALM075 | 16105 | #3机#3功率变送器故障 |  | digital
N2DCS.DEHALM074 | 16106 | #3机#2功率变送器故障 |  | digital
N2DCS.DEHALM073 | 16107 | #3机#1功率变送器故障 |  | digital
N2DCS.TALM033 | 16108 | #1高压给水泵无启允许 |  | digital
N2DCS.DEHALMUNACK1 | 16109 | #3机DEH光字牌报警手动确认指令 |  | digital
N2DCS.DEHALMUNACK | 16110 | #3机DEH光字牌报警手动确认指令 |  | digital
N2DCS.DEHALMALL1 | 16111 | #3机DEH光字牌报警汇总信号 |  | digital
N2DCS.DEHALMALL | 16112 | #3机DEH光字牌报警总信号 |  | digital
N2DCS.DEHALM099 | 16113 | #3机Z准则计算故障 |  | digital
N2DCS.DEHALM098 | 16114 | #3机X准则计算故障 |  | digital
N2DCS.DEHALM097 | 16115 | #3机再热主汽门前蒸汽温度高 |  | digital
N2DCS.DEHALM096 | 16116 | #3机高压主汽门前蒸汽温度高 |  | digital
N2DCS.DEHALM095 | 16117 | 中压缸排汽蒸汽过热度＜10℃ |  | digital
N2DCS.DEHALM094 | 16118 | 中压缸排汽蒸汽过热度＜20℃ |  | digital
N2DCS.DEHALM093 | 16119 | 高压缸排汽口蒸汽过热度＜10℃ |  | digital
N2DCS.DEHALM092 | 16120 | 高压缸排汽口蒸汽过热度＜20℃ |  | digital
N2DCS.DEHALM091 | 16121 | #5轴承振动＞130um |  | digital
N2DCS.DEHALM090 | 16122 | #5轴承振动＞83um |  | digital
N2DCS.DEHALM089 | 16123 | #5轴承振动测量故障 |  | digital
N2DCS.TALM049 | 16124 | 任一EH油泵无启允许 |  | digital
N2DCS.TALM048 | 16125 | #2真空泵无启允许 |  | digital
N2DCS.TALM047 | 16126 | #1真空泵无启允许 |  | digital
N2DCS.TALM046 | 16127 | #2开式水泵无启允许 |  | digital
N2DCS.TALM045 | 16128 | #1开式水泵无启允许 |  | digital
N2DCS.TALM044 | 16129 | #2闭式水泵无启允许 |  | digital
N2DCS.TALM043 | 16130 | #1闭式水泵无启允许 |  | digital
N2DCS.TALM042 | 16131 | #4循环水泵无启允许 |  | digital
N2DCS.TALM041 | 16132 | #3循环水泵无启允许 |  | digital
N2DCS.TALM040 | 16133 | 低压省煤器#2再循环泵无启允许 |  | digital
N2DCS.TALM039 | 16134 | 低压省煤器#1再循环泵无启允许 |  | digital
N2DCS.TALM038 | 16135 | #2凝结水泵无启允许 |  | digital
N2DCS.TALM037 | 16136 | #1凝结水泵无启允许 |  | digital
N2DCS.TALM036 | 16137 | #2中压给水泵无启允许 |  | digital
N2DCS.TALM035 | 16138 | #1中压给水泵无启允许 |  | digital
N2DCS.TALM034 | 16139 | #2高压给水泵无启允许 |  | digital
N2DCS.XZLWBGSSP | 16140 | #2旋转滤网高速自动停止指令 |  | digital
N2DCS.XZLWBDSST | 16141 | #2旋转滤网低速自动启动指令 |  | digital
N2DCS.XZLWBDSSP | 16142 | #2旋转滤网低速自动停止指令 |  | digital
N2DCS.XZLWAGSST | 16143 | #1旋转滤网高速自动启动指令 |  | digital
N2DCS.XZLWAGSSP | 16144 | #1旋转滤网高速自动停止指令 |  | digital
N2DCS.XZLWADSST | 16145 | #1旋转滤网低速自动启动指令 |  | digital
N2DCS.XZLWADSSP | 16146 | #1旋转滤网低速自动停止指令 |  | digital
N2DCS.4HXBBY | 16147 | 四号循泵备用 |  | digital
N2DCS.3HXBBY | 16148 | 三号循泵备用 |  | digital
N2DCS.2XBBY | 16149 | #4循环水泵在备用状态 |  | digital
N2DCS.1XBBY | 16150 | #3循环水泵在备用状态 |  | digital
N2DCS.20LCB12AP001CPDO | 16151 | #2凝结水泵已停止(至DROP9) |  | digital
N2DCS.TALM053 | 16152 | 高压给水泵变频器在手动模式 |  | digital
N2DCS.TALM052 | 16153 | 低压给水气动调节阀在手动模式 |  | digital
N2DCS.TALM051 | 16154 | 中压给水气动调节阀在手动模式 |  | digital
N2DCS.TALM050 | 16155 | 高压给水气动调节阀在手动模式 |  | digital
N2DCS.BALM030 | 16156 | 汽机侧热再主蒸汽温度突变30℃ |  | digital
N2DCS.BALM029 | 16157 | 汽机侧高压主蒸汽温度突变30℃ |  | digital
N2DCS.20LAF80AA102BHG1 | 16158 | Ovation Control Builder |  | digital
N2DCS.20LAF80AA102BHG | 16159 | Ovation Control Builder |  | digital
N2DCS.20LAF80AA101BHG1 | 16160 | Ovation Control Builder |  | digital
N2DCS.20LAF80AA101BHG | 16161 | Ovation Control Builder |  | digital
N2DCS.20LAB70AA101DVHI | 16162 | 低压给水调节阀指令反馈偏差大 |  | digital
N2DCS.20LAB70AA101_AUTO | 16163 | 低压给水气动调节阀在自动 |  | digital
N2DCS.20HAD70CLBS3 | 16164 | 低压汽包液位3（计算后）高高高 |  | digital
N2DCS.20HAD70CLBS2 | 16165 | 低压汽包液位2（计算后）高高高 |  | digital
N2DCS.20HAD70CLBS1 | 16166 | 低压汽包液位1（计算后）高高高 |  | digital
N2DCS.RH2OUTSTCTSC | 16167 | 热再主蒸汽温度突变 |  | digital
N2DCS.QDLGRWDG | 16168 | 启动炉出口主蒸汽温度高（340） |  | digital
N2DCS.QDLGRWDD | 16169 | 启动炉出口主蒸汽温度低（280） |  | digital
N2DCS.J0LBG22CT301DEVHIG1 | 16170 | 启动锅炉出口主蒸汽温度偏差大 |  | digital
N2DCS.XZLWBGSST | 16171 | #2旋转滤网高速自动启动指令 |  | digital
N2DCS.RHDSTCTSCM | 16172 | 锅炉侧热再主蒸汽温度突升50℃ |  | digital
N2DCS.RHDSTCTSC1 | 16173 | 汽机侧热再主蒸汽温度突升30℃ |  | digital
N2DCS.RHDSTCTSC | 16174 | 锅炉侧热再主蒸汽温度突降50℃ |  | digital
N2DCS.LPDW_AUTO | 16175 | Ovation Control Builder |  | digital
N2DCS.LPDRUMLVLDEVHI | 16176 | 低压给水调阀设定、反馈偏差大 |  | digital
N2DCS.HPDSTCTSCM1 | 16177 | 汽机侧高压主蒸汽温度突升30℃ |  | digital
N2DCS.HPDSTCTSCM | 16178 | 锅炉侧高压主蒸汽温度突升50℃ |  | digital
N2DCS.HPDSTCTSC1 | 16179 | 汽机侧高压主蒸汽温度突降30℃ |  | digital
N2DCS.HPDSTCTSC | 16180 | 锅炉侧高压主蒸汽温度突降50℃ |  | digital
N2DCS.HGF | 16181 | Ovation Control Builder |  | digital
N2DCS.GSD2 | 16182 | Ovation Control Builder |  | digital
N2DCS.GSD1 | 16183 | Ovation Control Builder |  | digital
N2DCS.GSD | 16184 | Ovation Control Builder |  | digital
N2DCS.DFS | 16185 | Ovation Control Builder |  | digital
N2DCS.BALM032 | 16186 | 锅炉侧高压主蒸汽温度突变50℃ |  | digital
N2DCS.BALM031 | 16187 | 锅炉侧热再主蒸汽温度突变50℃ |  | digital
N2DCS.GTHINTERLOCK1 | 16188 | #4机跳闸至DCS（3取2后） |  | digital
N2DCS.DCSTRIPTURB1 | 16189 | 锅炉保护跳闸联跳汽机 |  | digital
N2DCS.20LAB83AA101DVHI | 16190 | 中压给水调节阀指令、反馈偏差大 |  | digital
N2DCS.20HAD80CLBS3 | 16191 | 中压汽包液位3（计算后）高高高 |  | digital
N2DCS.20HAD80CLBS2 | 16192 | 中压汽包液位2（计算后）高高高 |  | digital
N2DCS.20HAD80CLBS1 | 16193 | 中压汽包液位1（计算后）高高高 |  | digital
N2DCS.20MAP10AA101CPDI | 16194 | 低旁阀全关(锅炉主保护) |  | digital
N2DCS.20MAN20AA101CPDI | 16195 | 中旁阀全关(锅炉主保护) |  | digital
N2DCS.20MAN10AA101CPDI | 16196 | 高旁阀全关(锅炉主保护) |  | digital
N2DCS.20LCB12AP001CPDI | 16197 | #2凝结水泵已停止(锅炉主保护) |  | digital
N2DCS.20LCB11AP001CPDI | 16198 | #1凝结水泵已停止(锅炉主保护) |  | digital
N2DCS.20HYY01EY001DSOE_DO | 16199 | #3炉停机SOE(送至DROP1) |  | digital
N2DCS.20CJJ030PCDI | 16200 | OPC动作(锅炉主保护) |  | digital
N2DCS.TEM | 16201 | Ovation Control Builder |  | digital
N2DCS.SDS | 16202 | Ovation Control Builder |  | digital
N2DCS.RHDSTCTSCM1 | 16203 | 汽机侧热再主蒸汽温度突降30℃ |  | digital
N2DCS.HRSGTRIP6 | 16204 | 低压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTRIP5A | 16205 | 低压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTRIP5 | 16206 | 低压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTRIP4A | 16207 | 中压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTRIP4 | 16208 | 中压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTRIP3A | 16209 | 中压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTRIP3 | 16210 | 中压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTRIP2A | 16211 | 高压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTRIP2 | 16212 | 高压汽包液位（计算后）低低低 |  | digital
N2DCS.HRSGTRIP1A | 16213 | 高压汽包液位（计算后）高高高 |  | digital
N2DCS.HRSGTRIP14 | 16214 | 燃机联锁跳余热锅炉 |  | digital
N2DCS.HRSGTRIP13 | 16215 | #3炉手动跳闸指令 |  | digital
N2DCS.HRSGTRIP12 | 16216 | 凝汽器真空低(大于30KPa） |  | digital
N2DCS.HRSGTRIP11 | 16217 | OPC或汽机跳闸30s后任一旁路未开 |  | digital
N2DCS.HRSGTRIP10 | 16218 | 烟囱挡板未在全开位置 |  | digital
N2DCS.HRSGTRIP1 | 16219 | 高压汽包液位（计算后）高高高 |  | digital
N2DCS.20LAE90AA102BHG2 | 16220 | Ovation Control Builder |  | digital
N2DCS.20LAE90AA102BHG1 | 16221 | Ovation Control Builder |  | digital
N2DCS.20LAE90AA102BHG | 16222 | Ovation Control Builder |  | digital
N2DCS.20LAE90AA101BHG2 | 16223 | Ovation Control Builder |  | digital
N2DCS.20LAE90AA101BHG1 | 16224 | Ovation Control Builder |  | digital
N2DCS.20LAE90AA101BHG | 16225 | Ovation Control Builder |  | digital
N2DCS.20HAD90CLBS3 | 16226 | 高压汽包液位3（计算后）高高高 |  | digital
N2DCS.20HAD90CLBS2 | 16227 | 高压汽包液位2（计算后）高高高 |  | digital
N2DCS.20HAD90CLBS1 | 16228 | 高压汽包液位1（计算后）高高高 |  | digital
N2DCS.WJG | 16229 | 主汽温降大 |  | digital
N2DCS.HRSGTRIPRSPB1 | 16230 | #3炉手动跳闸指令 |  | digital
N2DCS.HRSGTRIPPP | 16231 | 余热锅炉保护跳闸指令 |  | digital
N2DCS.HRSGTRIP9 | 16232 | #3机凝结水泵全停 |  | digital
N2DCS.HRSGTRIP8 | 16233 | #3炉中压给水泵全停 |  | digital
N2DCS.HRSGTRIP7 | 16234 | #3炉高压给水泵全停 |  | digital
N2DCS.HRSGTRIP6A | 16235 | 低压汽包液位（计算后）低低低 |  | digital
N2DCS.10MAY10DU100_1TO2 | 16236 | Ovation Control Builder |  | digital
N2DCS.10MAY01DU100_XK96 | 16237 | COMMUNICATION TRIP |  | digital
N2DCS.10MAY01DU100_1TO2 | 16238 | Ovation Control Builder |  | digital
N2DCS.2ROP41GW001_XM10 | 16239 | 机柜电源正常 |  | digital
N2DCS.2ROP41GW001_XM09 | 16240 | 机柜空开正常 |  | digital
N2DCS.20MAD12CY113_XM71 | 16241 | 轴向位移3#OK |  | digital
N2DCS.EALM32 | 16242 | 发电机漏水 |  | digital
N2DCS.KJK2 | 16243 | Ovation Control Builder |  | digital
N2DCS.KJK1 | 16244 | Ovation Control Builder |  | digital
N2DCS.KJK | 16245 | Ovation Control Builder |  | digital
N2DCS.HPBPLVLDEVHI | 16246 | 高给变频器设定反馈偏差大 |  | digital
N2DCS.FGD | 16247 | Ovation Control Builder |  | digital
N2DCS.FAS | 16248 | Ovation Control Builder |  | digital
N2DCS.CZYLMZ | 16249 | 高压过热器出口压力正常(大于6.4 |  | digital
N2DCS.ASD | 16250 | Ovation Control Builder |  | digital
N2DCS.20LAE90AA102PIDDVDI | 16251 | 高压主汽减温水阀设定反馈偏差大 |  | digital
N2DCS.2TPEL3 | 16252 | #3功率变送器故障 |  | digital
N2DCS.2TPEL2 | 16253 | #2功率变送器故障 |  | digital
N2DCS.2TPEL1 | 16254 | #1功率变送器故障 |  | digital
N2DCS.2TNT3 | 16255 | #3转速探头故障 |  | digital
N2DCS.2TNT2 | 16256 | #2转速探头故障 |  | digital
N2DCS.2TNT1 | 16257 | #1转速探头故障 |  | digital
N2DCS.2NTGR | 16258 | 转速控制偏差大 |  | digital
N2DCS.2JWC | 16259 | 暖机完成 |  | digital
N2DCS.2GZDSALM | 16260 | 中压压力手动设定报警 |  | digital
N2DCS.2GOSALM | 16261 | 负荷设定报警 |  | digital
N2DCS.2GNSALM | 16262 | 转速设定报警 |  | digital
N2DCS.2GFDSALM | 16263 | 高压压力手动设定报警 |  | digital
N2DCS.2ANUALL_MAL11 | 16264 | 高调门前疏水阀在手动 |  | digital
N2DCS.20MAY01DU100_XK96Z | 16265 | COMMUNICATION ALARM |  | digital
N2DCS.20MAY01DU100_3TO1 | 16266 | Ovation Control Builder |  | digital
N2DCS.20MAY01DU100_1TO2 | 16267 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101A_XM99 | 16268 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101A_XM98 | 16269 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101A_XM97 | 16270 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101A_DL23 | 16271 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101A_DL13 | 16272 | Ovation Control Builder |  | digital
N2DCS.20LBC40FP101A_DL12 | 16273 | Ovation Control Builder |  | digital
N2DCS.20LBC40CP103_XH01 | 16274 | HP EXH PRS 3>4.23MPa |  | digital
N2DCS.20LBC40CP102_XH01 | 16275 | HP EXH PRS 2>4.23MPa |  | digital
N2DCS.20LBC40CP101_XH01 | 16276 | HP EXH PRS 1>4.23MPa |  | digital
N2DCS.1_1_8_COIL_2_KSERVO_ALM | 16277 | Ovation Control Builder |  | digital
N2DCS.1_1_8_COIL_1_KSERVO_ALM | 16278 | Ovation Control Builder |  | digital
N2DCS.10MAY10DU100_2TO3 | 16279 | Ovation Control Builder |  | digital
N2DCS.10MAY01DU100_2TO3 | 16280 | Ovation Control Builder |  | digital
N2DCS.10LBC40CP103_XH01 | 16281 | HP EXH resP 3>4.23MPa |  | digital
N2DCS.10LBC40CP102_XH01 | 16282 | HP EXH Pres 2>4.23MPa |  | digital
N2DCS.10LBC40CP101_XH01 | 16283 | HP EXH PRES 1>4.23MPa |  | digital
N2DCS.CANCEL201 | 16284 |  |  | digital
N2DCS.CANCEL200 | 16285 |  |  | digital
N2DCS.CANCEL181 | 16286 |  |  | digital
N2DCS.CANCEL160 | 16287 |  |  | digital
N2DCS.20MAY01DU100_3TO1Z | 16288 | Ovation Control Builder |  | digital
N2DCS.10MAY01DU100_3TO1Z | 16289 | Ovation Control Builder |  | digital
N2DCS.10MAY01DU100_3TO1 | 16290 | Ovation Control Builder |  | digital
N2DCS.TEST_NORIE | 16291 | Ovation Control Builder |  | digital
N2DCS.SDAUTO | 16292 | 自动状态 |  | digital
N2DCS.NJWC | 16293 | 暖机完成 |  | digital
N2DCS.20MYA01CS901_ZV84 | 16294 | 汽机转速<1000RPM |  | digital
N2DCS.20MYA01CS901_XH72 | 16295 | 转速小于3030RPM |  | digital
N2DCS.20MYA01CS901_XH17 | 16296 | SPEED>49Hz |  | digital
N2DCS.20MYA01CS901_XH07 | 16297 | ST SPEED >2700rpm |  | digital
N2DCS.20MAY01DU100_2TO3 | 16298 | Ovation Control Builder |  | digital
N2DCS.20MAL11AA051T_OPEN | 16299 | TRIP OPEN DRAIN VLV |  | digital
N2DCS.STTRIPTAGLP1 | 16300 | #3机主保护条件解除信号 |  | digital
N2DCS.STTRIPLP1 | 16301 | #3机主保护条件 |  | digital
N2DCS.HRSGTRIPP | 16302 | #1余热锅炉主保护条件 |  | digital
N2DCS.20LBG21AC001_LP | 16303 | 轴封电加热器 |  | digital
N2DCS.20LBG21AA003_LP | 16304 | 轴封电加热器出口电动门 |  | digital
N2DCS.20LBG21AA002_LP | 16305 | 轴封电加热器进口电动门 |  | digital
N2DCS.CANCEL212 | 16306 |  |  | digital
N2DCS.CANCEL211 | 16307 |  |  | digital
DLCJ.DL001 | 16308 | #2燃机主变高压侧主表正向有功电能(总) | kWh | float32
DLCJ.DL002 | 16309 | #2燃机主变高压侧主表正向有功电能(尖) | kWh | float32
DLCJ.DL003 | 16310 | #2燃机主变高压侧主表正向有功电能(峰) | kWh | float32
DLCJ.DL004 | 16311 | #2燃机主变高压侧主表正向有功电能(平) | kWh | float32
DLCJ.DL005 | 16312 | #2燃机主变高压侧主表正向有功电能(谷) | kWh | float32
DLCJ.DL006 | 16313 | #2燃机主变高压侧主表反向有功电能(总) | kWh | float32
DLCJ.DL007 | 16314 | #2燃机主变高压侧主表反向有功电能(尖) | kWh | float32
DLCJ.DL008 | 16315 | #2燃机主变高压侧主表反向有功电能(峰) | kWh | float32
DLCJ.DL009 | 16316 | #2燃机主变高压侧主表反向有功电能(平) | kWh | float32
DLCJ.DL010 | 16317 | #2燃机主变高压侧主表反向有功电能(谷) | kWh | float32
DLCJ.DL011 | 16318 | #2燃机主变高压侧主表正向无功电能(总) | kWh | float32
DLCJ.DL012 | 16319 | #2燃机主变高压侧主表正向无功电能(尖) | kWh | float32
DLCJ.DL013 | 16320 | #2燃机主变高压侧主表正向无功电能(峰) | kWh | float32
DLCJ.DL014 | 16321 | #2燃机主变高压侧主表正向无功电能(平) | kWh | float32
DLCJ.DL015 | 16322 | #2燃机主变高压侧主表正向无功电能(谷) | kWh | float32
DLCJ.DL016 | 16323 | #2燃机主变高压侧主表反向无功电能(总) | kWh | float32
DLCJ.DL017 | 16324 | #2燃机主变高压侧主表反向无功电能(尖) | kWh | float32
DLCJ.DL018 | 16325 | #2燃机主变高压侧主表反向无功电能(峰) | kWh | float32
DLCJ.DL019 | 16326 | #2燃机主变高压侧主表反向无功电能(平) | kWh | float32
DLCJ.DL020 | 16327 | #2燃机主变高压侧主表反向无功电能(谷) | kWh | float32
DLCJ.DL021 | 16328 | #2燃机主变高压侧副表正向有功电能(总) | kWh | float32
DLCJ.DL022 | 16329 | #2燃机主变高压侧副表正向有功电能(尖) | kWh | float32
DLCJ.DL023 | 16330 | #2燃机主变高压侧副表正向有功电能(峰) | kWh | float32
DLCJ.DL024 | 16331 | #2燃机主变高压侧副表正向有功电能(平) | kWh | float32
DLCJ.DL025 | 16332 | #2燃机主变高压侧副表正向有功电能(谷) | kWh | float32
DLCJ.DL026 | 16333 | #2燃机主变高压侧副表反向有功电能(总) | kWh | float32
DLCJ.DL027 | 16334 | #2燃机主变高压侧副表反向有功电能(尖) | kWh | float32
DLCJ.DL028 | 16335 | #2燃机主变高压侧副表反向有功电能(峰) | kWh | float32
DLCJ.DL029 | 16336 | #2燃机主变高压侧副表反向有功电能(平) | kWh | float32
DLCJ.DL030 | 16337 | #2燃机主变高压侧副表反向有功电能(谷) | kWh | float32
DLCJ.DL031 | 16338 | #2燃机主变高压侧副表正向无功电能(总) | kWh | float32
DLCJ.DL032 | 16339 | #2燃机主变高压侧副表正向无功电能(尖) | kWh | float32
DLCJ.DL033 | 16340 | #2燃机主变高压侧副表正向无功电能(峰) | kWh | float32
DLCJ.DL034 | 16341 | #2燃机主变高压侧副表正向无功电能(平) | kWh | float32
DLCJ.DL035 | 16342 | #2燃机主变高压侧副表正向无功电能(谷) | kWh | float32
DLCJ.DL036 | 16343 | #2燃机主变高压侧副表反向无功电能(总) | kWh | float32
DLCJ.DL037 | 16344 | #2燃机主变高压侧副表反向无功电能(尖) | kWh | float32
DLCJ.DL038 | 16345 | #2燃机主变高压侧副表反向无功电能(峰) | kWh | float32
DLCJ.DL039 | 16346 | #2燃机主变高压侧副表反向无功电能(平) | kWh | float32
DLCJ.DL040 | 16347 | #2燃机主变高压侧副表反向无功电能(谷) | kWh | float32
DLCJ.DL041 | 16348 | #1汽机主变高压测主表正向有功电能(总) | kWh | float32
DLCJ.DL042 | 16349 | #1汽机主变高压测主表正向有功电能(尖) | kWh | float32
DLCJ.DL043 | 16350 | #1汽机主变高压测主表正向有功电能(峰) | kWh | float32
DLCJ.DL044 | 16351 | #1汽机主变高压测主表正向有功电能(平) | kWh | float32
DLCJ.DL045 | 16352 | #1汽机主变高压测主表正向有功电能(谷) | kWh | float32
DLCJ.DL046 | 16353 | #1汽机主变高压测主表反向有功电能(总) | kWh | float32
DLCJ.DL047 | 16354 | #1汽机主变高压测主表反向有功电能(尖) | kWh | float32
DLCJ.DL048 | 16355 | #1汽机主变高压测主表反向有功电能(峰) | kWh | float32
DLCJ.DL049 | 16356 | #1汽机主变高压测主表反向有功电能(平) | kWh | float32
DLCJ.DL050 | 16357 | #1汽机主变高压测主表反向有功电能(谷) | kWh | float32
DLCJ.DL051 | 16358 | #1汽机主变高压测主表正向无功电能(总) | kWh | float32
DLCJ.DL052 | 16359 | #1汽机主变高压测主表正向无功电能(尖) | kWh | float32
DLCJ.DL053 | 16360 | #1汽机主变高压测主表正向无功电能(峰) | kWh | float32
DLCJ.DL054 | 16361 | #1汽机主变高压测主表正向无功电能(平) | kWh | float32
DLCJ.DL055 | 16362 | #1汽机主变高压测主表正向无功电能(谷) | kWh | float32
DLCJ.DL056 | 16363 | #1汽机主变高压测主表反向无功电能(总) | kWh | float32
DLCJ.DL057 | 16364 | #1汽机主变高压测主表反向无功电能(尖) | kWh | float32
DLCJ.DL058 | 16365 | #1汽机主变高压测主表反向无功电能(峰) | kWh | float32
DLCJ.DL059 | 16366 | #1汽机主变高压测主表反向无功电能(平) | kWh | float32
DLCJ.DL060 | 16367 | #1汽机主变高压测主表反向无功电能(谷) | kWh | float32
DLCJ.DL061 | 16368 | #1汽机主变高压侧副表正向有功电能(总) | kWh | float32
DLCJ.DL062 | 16369 | #1汽机主变高压侧副表正向有功电能(尖) | kWh | float32
DLCJ.DL063 | 16370 | #1汽机主变高压侧副表正向有功电能(峰) | kWh | float32
DLCJ.DL064 | 16371 | #1汽机主变高压侧副表正向有功电能(平) | kWh | float32
DLCJ.DL065 | 16372 | #1汽机主变高压侧副表正向有功电能(谷) | kWh | float32
DLCJ.DL066 | 16373 | #1汽机主变高压侧副表反向有功电能(总) | kWh | float32
DLCJ.DL067 | 16374 | #1汽机主变高压侧副表反向有功电能(尖) | kWh | float32
DLCJ.DL068 | 16375 | #1汽机主变高压侧副表反向有功电能(峰) | kWh | float32
DLCJ.DL069 | 16376 | #1汽机主变高压侧副表反向有功电能(平) | kWh | float32
DLCJ.DL070 | 16377 | #1汽机主变高压侧副表反向有功电能(谷) | kWh | float32
DLCJ.DL071 | 16378 | #1汽机主变高压侧副表正向无功电能(总) | kWh | float32
DLCJ.DL072 | 16379 | #1汽机主变高压侧副表正向无功电能(尖) | kWh | float32
DLCJ.DL073 | 16380 | #1汽机主变高压侧副表正向无功电能(峰) | kWh | float32
DLCJ.DL074 | 16381 | #1汽机主变高压侧副表正向无功电能(平) | kWh | float32
DLCJ.DL075 | 16382 | #1汽机主变高压侧副表正向无功电能(谷) | kWh | float32
DLCJ.DL076 | 16383 | #1汽机主变高压侧副表反向无功电能(总) | kWh | float32
DLCJ.DL077 | 16384 | #1汽机主变高压侧副表反向无功电能(尖) | kWh | float32
DLCJ.DL078 | 16385 | #1汽机主变高压侧副表反向无功电能(峰) | kWh | float32
DLCJ.DL079 | 16386 | #1汽机主变高压侧副表反向无功电能(平) | kWh | float32
DLCJ.DL080 | 16387 | #1汽机主变高压侧副表反向无功电能(谷) | kWh | float32
DLCJ.DL081 | 16388 | #4燃机主变高压侧主表正向有功电能(总) | kWh | float32
DLCJ.DL082 | 16389 | #4燃机主变高压侧主表正向有功电能(尖) | kWh | float32
DLCJ.DL083 | 16390 | #4燃机主变高压侧主表正向有功电能(峰) | kWh | float32
DLCJ.DL084 | 16391 | #4燃机主变高压侧主表正向有功电能(平) | kWh | float32
DLCJ.DL085 | 16392 | #4燃机主变高压侧主表正向有功电能(谷) | kWh | float32
DLCJ.DL086 | 16393 | #4燃机主变高压侧主表反向有功电能(总) | kWh | float32
DLCJ.DL087 | 16394 | #4燃机主变高压侧主表反向有功电能(尖) | kWh | float32
DLCJ.DL088 | 16395 | #4燃机主变高压侧主表反向有功电能(峰) | kWh | float32
DLCJ.DL089 | 16396 | #4燃机主变高压侧主表反向有功电能(平) | kWh | float32
DLCJ.DL090 | 16397 | #4燃机主变高压侧主表反向有功电能(谷) | kWh | float32
DLCJ.DL091 | 16398 | #4燃机主变高压侧主表正向无功电能(总) | kWh | float32
DLCJ.DL092 | 16399 | #4燃机主变高压侧主表正向无功电能(尖) | kWh | float32
DLCJ.DL093 | 16400 | #4燃机主变高压侧主表正向无功电能(峰) | kWh | float32
DLCJ.DL094 | 16401 | #4燃机主变高压侧主表正向无功电能(平) | kWh | float32
DLCJ.DL095 | 16402 | #4燃机主变高压侧主表正向无功电能(谷) | kWh | float32
DLCJ.DL096 | 16403 | #4燃机主变高压侧主表反向无功电能(总) | kWh | float32
DLCJ.DL097 | 16404 | #4燃机主变高压侧主表反向无功电能(尖) | kWh | float32
DLCJ.DL098 | 16405 | #4燃机主变高压侧主表反向无功电能(峰) | kWh | float32
DLCJ.DL099 | 16406 | #4燃机主变高压侧主表反向无功电能(平) | kWh | float32
DLCJ.DL100 | 16407 | #4燃机主变高压侧主表反向无功电能(谷) | kWh | float32
DLCJ.DL101 | 16408 | #4燃机主变高压侧副表正向有功电能(总) | kWh | float32
DLCJ.DL102 | 16409 | #4燃机主变高压侧副表正向有功电能(尖) | kWh | float32
DLCJ.DL103 | 16410 | #4燃机主变高压侧副表正向有功电能(峰) | kWh | float32
DLCJ.DL104 | 16411 | #4燃机主变高压侧副表正向有功电能(平) | kWh | float32
DLCJ.DL105 | 16412 | #4燃机主变高压侧副表正向有功电能(谷) | kWh | float32
DLCJ.DL106 | 16413 | #4燃机主变高压侧副表反向有功电能(总) | kWh | float32
DLCJ.DL107 | 16414 | #4燃机主变高压侧副表反向有功电能(尖) | kWh | float32
DLCJ.DL108 | 16415 | #4燃机主变高压侧副表反向有功电能(峰) | kWh | float32
DLCJ.DL109 | 16416 | #4燃机主变高压侧副表反向有功电能(平) | kWh | float32
DLCJ.DL110 | 16417 | #4燃机主变高压侧副表反向有功电能(谷) | kWh | float32
DLCJ.DL111 | 16418 | #4燃机主变高压侧副表正向无功电能(总) | kWh | float32
DLCJ.DL112 | 16419 | #4燃机主变高压侧副表正向无功电能(尖) | kWh | float32
DLCJ.DL113 | 16420 | #4燃机主变高压侧副表正向无功电能(峰) | kWh | float32
DLCJ.DL114 | 16421 | #4燃机主变高压侧副表正向无功电能(平) | kWh | float32
DLCJ.DL115 | 16422 | #4燃机主变高压侧副表正向无功电能(谷) | kWh | float32
DLCJ.DL116 | 16423 | #4燃机主变高压侧副表反向无功电能(总) | kWh | float32
DLCJ.DL117 | 16424 | #4燃机主变高压侧副表反向无功电能(尖) | kWh | float32
DLCJ.DL118 | 16425 | #4燃机主变高压侧副表反向无功电能(峰) | kWh | float32
DLCJ.DL119 | 16426 | #4燃机主变高压侧副表反向无功电能(平) | kWh | float32
DLCJ.DL120 | 16427 | #4燃机主变高压侧副表反向无功电能(谷) | kWh | float32
DLCJ.DL121 | 16428 | #3汽机主变高压侧主表正向有功电能(总) | kWh | float32
DLCJ.DL122 | 16429 | #3汽机主变高压侧主表正向有功电能(尖) | kWh | float32
DLCJ.DL123 | 16430 | #3汽机主变高压侧主表正向有功电能(峰) | kWh | float32
DLCJ.DL124 | 16431 | #3汽机主变高压侧主表正向有功电能(平) | kWh | float32
DLCJ.DL125 | 16432 | #3汽机主变高压侧主表正向有功电能(谷) | kWh | float32
DLCJ.DL126 | 16433 | #3汽机主变高压侧主表反向有功电能(总) | kWh | float32
DLCJ.DL127 | 16434 | #3汽机主变高压侧主表反向有功电能(尖) | kWh | float32
DLCJ.DL128 | 16435 | #3汽机主变高压侧主表反向有功电能(峰) | kWh | float32
DLCJ.DL129 | 16436 | #3汽机主变高压侧主表反向有功电能(平) | kWh | float32
DLCJ.DL130 | 16437 | #3汽机主变高压侧主表反向有功电能(谷) | kWh | float32
DLCJ.DL131 | 16438 | #3汽机主变高压侧主表正向无功电能(总) | kWh | float32
DLCJ.DL132 | 16439 | #3汽机主变高压侧主表正向无功电能(尖) | kWh | float32
DLCJ.DL133 | 16440 | #3汽机主变高压侧主表正向无功电能(峰) | kWh | float32
DLCJ.DL134 | 16441 | #3汽机主变高压侧主表正向无功电能(平) | kWh | float32
DLCJ.DL135 | 16442 | #3汽机主变高压侧主表正向无功电能(谷) | kWh | float32
DLCJ.DL136 | 16443 | #3汽机主变高压侧主表反向无功电能(总) | kWh | float32
DLCJ.DL137 | 16444 | #3汽机主变高压侧主表反向无功电能(尖) | kWh | float32
DLCJ.DL138 | 16445 | #3汽机主变高压侧主表反向无功电能(峰) | kWh | float32
DLCJ.DL139 | 16446 | #3汽机主变高压侧主表反向无功电能(平) | kWh | float32
DLCJ.DL140 | 16447 | #3汽机主变高压侧主表反向无功电能(谷) | kWh | float32
DLCJ.DL141 | 16448 | #3汽机主变高压侧副表正向有功电能(总) | kWh | float32
DLCJ.DL142 | 16449 | #3汽机主变高压侧副表正向有功电能(尖) | kWh | float32
DLCJ.DL143 | 16450 | #3汽机主变高压侧副表正向有功电能(峰) | kWh | float32
DLCJ.DL144 | 16451 | #3汽机主变高压侧副表正向有功电能(平) | kWh | float32
DLCJ.DL145 | 16452 | #3汽机主变高压侧副表正向有功电能(谷) | kWh | float32
DLCJ.DL146 | 16453 | #3汽机主变高压侧副表反向有功电能(总) | kWh | float32
DLCJ.DL147 | 16454 | #3汽机主变高压侧副表反向有功电能(尖) | kWh | float32
DLCJ.DL148 | 16455 | #3汽机主变高压侧副表反向有功电能(峰) | kWh | float32
DLCJ.DL149 | 16456 | #3汽机主变高压侧副表反向有功电能(平) | kWh | float32
DLCJ.DL150 | 16457 | #3汽机主变高压侧副表反向有功电能(谷) | kWh | float32
DLCJ.DL151 | 16458 | #3汽机主变高压侧副表正向无功电能(总) | kWh | float32
DLCJ.DL152 | 16459 | #3汽机主变高压侧副表正向无功电能(尖) | kWh | float32
DLCJ.DL153 | 16460 | #3汽机主变高压侧副表正向无功电能(峰) | kWh | float32
DLCJ.DL154 | 16461 | #3汽机主变高压侧副表正向无功电能(平) | kWh | float32
DLCJ.DL155 | 16462 | #3汽机主变高压侧副表正向无功电能(谷) | kWh | float32
DLCJ.DL156 | 16463 | #3汽机主变高压侧副表反向无功电能(总) | kWh | float32
DLCJ.DL157 | 16464 | #3汽机主变高压侧副表反向无功电能(尖) | kWh | float32
DLCJ.DL158 | 16465 | #3汽机主变高压侧副表反向无功电能(峰) | kWh | float32
DLCJ.DL159 | 16466 | #3汽机主变高压侧副表反向无功电能(平) | kWh | float32
DLCJ.DL160 | 16467 | #3汽机主变高压侧副表反向无功电能(谷) | kWh | float32
DLCJ.DL161 | 16468 | #01高备变高压侧主表正向有功电能(总) | kWh | float32
DLCJ.DL162 | 16469 | #01高备变高压侧主表正向有功电能(尖) | kWh | float32
DLCJ.DL163 | 16470 | #01高备变高压侧主表正向有功电能(峰) | kWh | float32
DLCJ.DL164 | 16471 | #01高备变高压侧主表正向有功电能(平) | kWh | float32
DLCJ.DL165 | 16472 | #01高备变高压侧主表正向有功电能(谷) | kWh | float32
DLCJ.DL166 | 16473 | #01高备变高压侧主表反向有功电能(总) | kWh | float32
DLCJ.DL167 | 16474 | #01高备变高压侧主表反向有功电能(尖) | kWh | float32
DLCJ.DL168 | 16475 | #01高备变高压侧主表反向有功电能(峰) | kWh | float32
DLCJ.DL169 | 16476 | #01高备变高压侧主表反向有功电能(平) | kWh | float32
DLCJ.DL170 | 16477 | #01高备变高压侧主表反向有功电能(谷) | kWh | float32
DLCJ.DL171 | 16478 | #01高备变高压侧主表正向无功电能(总) | kWh | float32
DLCJ.DL172 | 16479 | #01高备变高压侧主表正向无功电能(尖) | kWh | float32
DLCJ.DL173 | 16480 | #01高备变高压侧主表正向无功电能(峰) | kWh | float32
DLCJ.DL174 | 16481 | #01高备变高压侧主表正向无功电能(平) | kWh | float32
DLCJ.DL175 | 16482 | #01高备变高压侧主表正向无功电能(谷) | kWh | float32
DLCJ.DL176 | 16483 | #01高备变高压侧主表反向无功电能(总) | kWh | float32
DLCJ.DL177 | 16484 | #01高备变高压侧主表反向无功电能(尖) | kWh | float32
DLCJ.DL178 | 16485 | #01高备变高压侧主表反向无功电能(峰) | kWh | float32
DLCJ.DL179 | 16486 | #01高备变高压侧主表反向无功电能(平) | kWh | float32
DLCJ.DL180 | 16487 | #01高备变高压侧主表反向无功电能(谷) | kWh | float32
DLCJ.DL181 | 16488 | #01高备变高压侧副表正向有功电能(总) | kWh | float32
DLCJ.DL182 | 16489 | #01高备变高压侧副表正向有功电能(尖) | kWh | float32
DLCJ.DL183 | 16490 | #01高备变高压侧副表正向有功电能(峰) | kWh | float32
DLCJ.DL184 | 16491 | #01高备变高压侧副表正向有功电能(平) | kWh | float32
DLCJ.DL185 | 16492 | #01高备变高压侧副表正向有功电能(谷) | kWh | float32
DLCJ.DL186 | 16493 | #01高备变高压侧副表反向有功电能(总) | kWh | float32
DLCJ.DL187 | 16494 | #01高备变高压侧副表反向有功电能(尖) | kWh | float32
DLCJ.DL188 | 16495 | #01高备变高压侧副表反向有功电能(峰) | kWh | float32
DLCJ.DL189 | 16496 | #01高备变高压侧副表反向有功电能(平) | kWh | float32
DLCJ.DL190 | 16497 | #01高备变高压侧副表反向有功电能(谷) | kWh | float32
DLCJ.DL191 | 16498 | #01高备变高压侧副表正向无功电能(总) | kWh | float32
DLCJ.DL192 | 16499 | #01高备变高压侧副表正向无功电能(尖) | kWh | float32
DLCJ.DL193 | 16500 | #01高备变高压侧副表正向无功电能(峰) | kWh | float32
DLCJ.DL194 | 16501 | #01高备变高压侧副表正向无功电能(平) | kWh | float32
DLCJ.DL195 | 16502 | #01高备变高压侧副表正向无功电能(谷) | kWh | float32
DLCJ.DL196 | 16503 | #01高备变高压侧副表反向无功电能(总) | kWh | float32
DLCJ.DL197 | 16504 | #01高备变高压侧副表反向无功电能(尖) | kWh | float32
DLCJ.DL198 | 16505 | #01高备变高压侧副表反向无功电能(峰) | kWh | float32
DLCJ.DL199 | 16506 | #01高备变高压侧副表反向无功电能(平) | kWh | float32
DLCJ.DL200 | 16507 | #01高备变高压侧副表反向无功电能(谷) | kWh | float32
DLCJ.DL201 | 16508 | 220kV桔布乙线正向有功电能(总) | kWh | float32
DLCJ.DL202 | 16509 | 220kV桔布乙线正向有功电能(尖) | kWh | float32
DLCJ.DL203 | 16510 | 220kV桔布乙线正向有功电能(峰) | kWh | float32
DLCJ.DL204 | 16511 | 220kV桔布乙线正向有功电能(平) | kWh | float32
DLCJ.DL205 | 16512 | 220kV桔布乙线正向有功电能(谷) | kWh | float32
DLCJ.DL206 | 16513 | 220kV桔布乙线反向有功电能(总) | kWh | float32
DLCJ.DL207 | 16514 | 220kV桔布乙线反向有功电能(尖) | kWh | float32
DLCJ.DL208 | 16515 | 220kV桔布乙线反向有功电能(峰) | kWh | float32
DLCJ.DL209 | 16516 | 220kV桔布乙线反向有功电能(平) | kWh | float32
DLCJ.DL210 | 16517 | 220kV桔布乙线反向有功电能(谷) | kWh | float32
DLCJ.DL211 | 16518 | 220kV桔布乙线正向无功电能(总) | kWh | float32
DLCJ.DL212 | 16519 | 220kV桔布乙线正向无功电能(尖) | kWh | float32
DLCJ.DL213 | 16520 | 220kV桔布乙线正向无功电能(峰) | kWh | float32
DLCJ.DL214 | 16521 | 220kV桔布乙线正向无功电能(平) | kWh | float32
DLCJ.DL215 | 16522 | 220kV桔布乙线正向无功电能(谷) | kWh | float32
DLCJ.DL216 | 16523 | 220kV桔布乙线反向无功电能(总) | kWh | float32
DLCJ.DL217 | 16524 | 220kV桔布乙线反向无功电能(尖) | kWh | float32
DLCJ.DL218 | 16525 | 220kV桔布乙线反向无功电能(峰) | kWh | float32
DLCJ.DL219 | 16526 | 220kV桔布乙线反向无功电能(平) | kWh | float32
DLCJ.DL220 | 16527 | 220kV桔布乙线反向无功电能(谷) | kWh | float32
DLCJ.DL221 | 16528 | 220kV桔布甲线正向有功电能(总) | kWh | float32
DLCJ.DL222 | 16529 | 220kV桔布甲线正向有功电能(尖) | kWh | float32
DLCJ.DL223 | 16530 | 220kV桔布甲线正向有功电能(峰) | kWh | float32
DLCJ.DL224 | 16531 | 220kV桔布甲线正向有功电能(平) | kWh | float32
DLCJ.DL225 | 16532 | 220kV桔布甲线正向有功电能(谷) | kWh | float32
DLCJ.DL226 | 16533 | 220kV桔布甲线反向有功电能(总) | kWh | float32
DLCJ.DL227 | 16534 | 220kV桔布甲线反向有功电能(尖) | kWh | float32
DLCJ.DL228 | 16535 | 220kV桔布甲线反向有功电能(峰) | kWh | float32
DLCJ.DL229 | 16536 | 220kV桔布甲线反向有功电能(平) | kWh | float32
DLCJ.DL230 | 16537 | 220kV桔布甲线反向有功电能(谷) | kWh | float32
DLCJ.DL231 | 16538 | 220kV桔布甲线正向无功电能(总) | kWh | float32
DLCJ.DL232 | 16539 | 220kV桔布甲线正向无功电能(尖) | kWh | float32
DLCJ.DL233 | 16540 | 220kV桔布甲线正向无功电能(峰) | kWh | float32
DLCJ.DL234 | 16541 | 220kV桔布甲线正向无功电能(平) | kWh | float32
DLCJ.DL235 | 16542 | 220kV桔布甲线正向无功电能(谷) | kWh | float32
DLCJ.DL236 | 16543 | 220kV桔布甲线反向无功电能(总) | kWh | float32
DLCJ.DL237 | 16544 | 220kV桔布甲线反向无功电能(尖) | kWh | float32
DLCJ.DL238 | 16545 | 220kV桔布甲线反向无功电能(峰) | kWh | float32
DLCJ.DL239 | 16546 | 220kV桔布甲线反向无功电能(平) | kWh | float32
DLCJ.DL240 | 16547 | 220kV桔布甲线反向无功电能(谷) | kWh | float32
DLCJ.DL241 | 16548 | #1汽机发电机机端正向有功电能(总) | kWh | float32
DLCJ.DL242 | 16549 | #1汽机发电机机端正向有功电能(尖) | kWh | float32
DLCJ.DL243 | 16550 | #1汽机发电机机端正向有功电能(峰) | kWh | float32
DLCJ.DL244 | 16551 | #1汽机发电机机端正向有功电能(平) | kWh | float32
DLCJ.DL245 | 16552 | #1汽机发电机机端正向有功电能(谷) | kWh | float32
DLCJ.DL246 | 16553 | #1汽机发电机机端反向有功电能(总) | kWh | float32
DLCJ.DL247 | 16554 | #1汽机发电机机端反向有功电能(尖) | kWh | float32
DLCJ.DL248 | 16555 | #1汽机发电机机端反向有功电能(峰) | kWh | float32
DLCJ.DL249 | 16556 | #1汽机发电机机端反向有功电能(平) | kWh | float32
DLCJ.DL250 | 16557 | #1汽机发电机机端反向有功电能(谷) | kWh | float32
DLCJ.DL251 | 16558 | #1汽机发电机机端正向无功电能(总) | kWh | float32
DLCJ.DL252 | 16559 | #1汽机发电机机端正向无功电能(尖) | kWh | float32
DLCJ.DL253 | 16560 | #1汽机发电机机端正向无功电能(峰) | kWh | float32
DLCJ.DL254 | 16561 | #1汽机发电机机端正向无功电能(平) | kWh | float32
DLCJ.DL255 | 16562 | #1汽机发电机机端正向无功电能(谷) | kWh | float32
DLCJ.DL256 | 16563 | #1汽机发电机机端反向无功电能(总) | kWh | float32
DLCJ.DL257 | 16564 | #1汽机发电机机端反向无功电能(尖) | kWh | float32
DLCJ.DL258 | 16565 | #1汽机发电机机端反向无功电能(峰) | kWh | float32
DLCJ.DL259 | 16566 | #1汽机发电机机端反向无功电能(平) | kWh | float32
DLCJ.DL260 | 16567 | #1汽机发电机机端反向无功电能(谷) | kWh | float32
DLCJ.DL261 | 16568 | #1汽机励磁变高压侧正向有功电能(总) | kWh | float32
DLCJ.DL262 | 16569 | #1汽机励磁变高压侧正向有功电能(尖) | kWh | float32
DLCJ.DL263 | 16570 | #1汽机励磁变高压侧正向有功电能(峰) | kWh | float32
DLCJ.DL264 | 16571 | #1汽机励磁变高压侧正向有功电能(平) | kWh | float32
DLCJ.DL265 | 16572 | #1汽机励磁变高压侧正向有功电能(谷) | kWh | float32
DLCJ.DL266 | 16573 | #1汽机励磁变高压侧反向有功电能(总) | kWh | float32
DLCJ.DL267 | 16574 | #1汽机励磁变高压侧反向有功电能(尖) | kWh | float32
DLCJ.DL268 | 16575 | #1汽机励磁变高压侧反向有功电能(峰) | kWh | float32
DLCJ.DL269 | 16576 | #1汽机励磁变高压侧反向有功电能(平) | kWh | float32
DLCJ.DL270 | 16577 | #1汽机励磁变高压侧反向有功电能(谷) | kWh | float32
DLCJ.DL271 | 16578 | #1汽机励磁变高压侧正向无功电能(总) | kWh | float32
DLCJ.DL272 | 16579 | #1汽机励磁变高压侧正向无功电能(尖) | kWh | float32
DLCJ.DL273 | 16580 | #1汽机励磁变高压侧正向无功电能(峰) | kWh | float32
DLCJ.DL274 | 16581 | #1汽机励磁变高压侧正向无功电能(平) | kWh | float32
DLCJ.DL275 | 16582 | #1汽机励磁变高压侧正向无功电能(谷) | kWh | float32
DLCJ.DL276 | 16583 | #1汽机励磁变高压侧反向无功电能(总) | kWh | float32
DLCJ.DL277 | 16584 | #1汽机励磁变高压侧反向无功电能(尖) | kWh | float32
DLCJ.DL278 | 16585 | #1汽机励磁变高压侧反向无功电能(峰) | kWh | float32
DLCJ.DL279 | 16586 | #1汽机励磁变高压侧反向无功电能(平) | kWh | float32
DLCJ.DL280 | 16587 | #1汽机励磁变高压侧反向无功电能(谷) | kWh | float32
DLCJ.DL281 | 16588 | #2燃机发电机机端正向有功电能(总) | kWh | float32
DLCJ.DL282 | 16589 | #2燃机发电机机端正向有功电能(尖) | kWh | float32
DLCJ.DL283 | 16590 | #2燃机发电机机端正向有功电能(峰) | kWh | float32
DLCJ.DL284 | 16591 | #2燃机发电机机端正向有功电能(平) | kWh | float32
DLCJ.DL285 | 16592 | #2燃机发电机机端正向有功电能(谷) | kWh | float32
DLCJ.DL286 | 16593 | #2燃机发电机机端反向有功电能(总) | kWh | float32
DLCJ.DL287 | 16594 | #2燃机发电机机端反向有功电能(尖) | kWh | float32
DLCJ.DL288 | 16595 | #2燃机发电机机端反向有功电能(峰) | kWh | float32
DLCJ.DL289 | 16596 | #2燃机发电机机端反向有功电能(平) | kWh | float32
DLCJ.DL290 | 16597 | #2燃机发电机机端反向有功电能(谷) | kWh | float32
DLCJ.DL291 | 16598 | #2燃机发电机机端正向无功电能(总) | kWh | float32
DLCJ.DL292 | 16599 | #2燃机发电机机端正向无功电能(尖) | kWh | float32
DLCJ.DL293 | 16600 | #2燃机发电机机端正向无功电能(峰) | kWh | float32
DLCJ.DL294 | 16601 | #2燃机发电机机端正向无功电能(平) | kWh | float32
DLCJ.DL295 | 16602 | #2燃机发电机机端正向无功电能(谷) | kWh | float32
DLCJ.DL296 | 16603 | #2燃机发电机机端反向无功电能(总) | kWh | float32
DLCJ.DL297 | 16604 | #2燃机发电机机端反向无功电能(尖) | kWh | float32
DLCJ.DL298 | 16605 | #2燃机发电机机端反向无功电能(峰) | kWh | float32
DLCJ.DL299 | 16606 | #2燃机发电机机端反向无功电能(平) | kWh | float32
DLCJ.DL300 | 16607 | #2燃机发电机机端反向无功电能(谷) | kWh | float32
DLCJ.DL301 | 16608 | #2燃机励磁变高压侧正向有功电能(总) | kWh | float32
DLCJ.DL302 | 16609 | #2燃机励磁变高压侧正向有功电能(尖) | kWh | float32
DLCJ.DL303 | 16610 | #2燃机励磁变高压侧正向有功电能(峰) | kWh | float32
DLCJ.DL304 | 16611 | #2燃机励磁变高压侧正向有功电能(平) | kWh | float32
DLCJ.DL305 | 16612 | #2燃机励磁变高压侧正向有功电能(谷) | kWh | float32
DLCJ.DL306 | 16613 | #2燃机励磁变高压侧反向有功电能(总) | kWh | float32
DLCJ.DL307 | 16614 | #2燃机励磁变高压侧反向有功电能(尖) | kWh | float32
DLCJ.DL308 | 16615 | #2燃机励磁变高压侧反向有功电能(峰) | kWh | float32
DLCJ.DL309 | 16616 | #2燃机励磁变高压侧反向有功电能(平) | kWh | float32
DLCJ.DL310 | 16617 | #2燃机励磁变高压侧反向有功电能(谷) | kWh | float32
DLCJ.DL311 | 16618 | #2燃机励磁变高压侧正向无功电能(总) | kWh | float32
DLCJ.DL312 | 16619 | #2燃机励磁变高压侧正向无功电能(尖) | kWh | float32
DLCJ.DL313 | 16620 | #2燃机励磁变高压侧正向无功电能(峰) | kWh | float32
DLCJ.DL314 | 16621 | #2燃机励磁变高压侧正向无功电能(平) | kWh | float32
DLCJ.DL315 | 16622 | #2燃机励磁变高压侧正向无功电能(谷) | kWh | float32
DLCJ.DL316 | 16623 | #2燃机励磁变高压侧反向无功电能(总) | kWh | float32
DLCJ.DL317 | 16624 | #2燃机励磁变高压侧反向无功电能(尖) | kWh | float32
DLCJ.DL318 | 16625 | #2燃机励磁变高压侧反向无功电能(峰) | kWh | float32
DLCJ.DL319 | 16626 | #2燃机励磁变高压侧反向无功电能(平) | kWh | float32
DLCJ.DL320 | 16627 | #2燃机励磁变高压侧反向无功电能(谷) | kWh | float32
DLCJ.DL321 | 16628 | #2燃机高厂变高压侧正向有功电能(总) | kWh | float32
DLCJ.DL322 | 16629 | #2燃机高厂变高压侧正向有功电能(尖) | kWh | float32
DLCJ.DL323 | 16630 | #2燃机高厂变高压侧正向有功电能(峰) | kWh | float32
DLCJ.DL324 | 16631 | #2燃机高厂变高压侧正向有功电能(平) | kWh | float32
DLCJ.DL325 | 16632 | #2燃机高厂变高压侧正向有功电能(谷) | kWh | float32
DLCJ.DL326 | 16633 | #2燃机高厂变高压侧反向有功电能(总) | kWh | float32
DLCJ.DL327 | 16634 | #2燃机高厂变高压侧反向有功电能(尖) | kWh | float32
DLCJ.DL328 | 16635 | #2燃机高厂变高压侧反向有功电能(峰) | kWh | float32
DLCJ.DL329 | 16636 | #2燃机高厂变高压侧反向有功电能(平) | kWh | float32
DLCJ.DL330 | 16637 | #2燃机高厂变高压侧反向有功电能(谷) | kWh | float32
DLCJ.DL331 | 16638 | #2燃机高厂变高压侧正向无功电能(总) | kWh | float32
DLCJ.DL332 | 16639 | #2燃机高厂变高压侧正向无功电能(尖) | kWh | float32
DLCJ.DL333 | 16640 | #2燃机高厂变高压侧正向无功电能(峰) | kWh | float32
DLCJ.DL334 | 16641 | #2燃机高厂变高压侧正向无功电能(平) | kWh | float32
DLCJ.DL335 | 16642 | #2燃机高厂变高压侧正向无功电能(谷) | kWh | float32
DLCJ.DL336 | 16643 | #2燃机高厂变高压侧反向无功电能(总) | kWh | float32
DLCJ.DL337 | 16644 | #2燃机高厂变高压侧反向无功电能(尖) | kWh | float32
DLCJ.DL338 | 16645 | #2燃机高厂变高压侧反向无功电能(峰) | kWh | float32
DLCJ.DL339 | 16646 | #2燃机高厂变高压侧反向无功电能(平) | kWh | float32
DLCJ.DL340 | 16647 | #2燃机高厂变高压侧反向无功电能(谷) | kWh | float32
DLCJ.DL341 | 16648 | #3汽机发电机机端正向有功电能(总) | kWh | float32
DLCJ.DL342 | 16649 | #3汽机发电机机端正向有功电能(尖) | kWh | float32
DLCJ.DL343 | 16650 | #3汽机发电机机端正向有功电能(峰) | kWh | float32
DLCJ.DL344 | 16651 | #3汽机发电机机端正向有功电能(平) | kWh | float32
DLCJ.DL345 | 16652 | #3汽机发电机机端正向有功电能(谷) | kWh | float32
DLCJ.DL346 | 16653 | #3汽机发电机机端反向有功电能(总) | kWh | float32
DLCJ.DL347 | 16654 | #3汽机发电机机端反向有功电能(尖) | kWh | float32
DLCJ.DL348 | 16655 | #3汽机发电机机端反向有功电能(峰) | kWh | float32
DLCJ.DL349 | 16656 | #3汽机发电机机端反向有功电能(平) | kWh | float32
DLCJ.DL350 | 16657 | #3汽机发电机机端反向有功电能(谷) | kWh | float32
DLCJ.DL351 | 16658 | #3汽机发电机机端正向无功电能(总) | kWh | float32
DLCJ.DL352 | 16659 | #3汽机发电机机端正向无功电能(尖) | kWh | float32
DLCJ.DL353 | 16660 | #3汽机发电机机端正向无功电能(峰) | kWh | float32
DLCJ.DL354 | 16661 | #3汽机发电机机端正向无功电能(平) | kWh | float32
DLCJ.DL355 | 16662 | #3汽机发电机机端正向无功电能(谷) | kWh | float32
DLCJ.DL356 | 16663 | #3汽机发电机机端反向无功电能(总) | kWh | float32
DLCJ.DL357 | 16664 | #3汽机发电机机端反向无功电能(尖) | kWh | float32
DLCJ.DL358 | 16665 | #3汽机发电机机端反向无功电能(峰) | kWh | float32
DLCJ.DL359 | 16666 | #3汽机发电机机端反向无功电能(平) | kWh | float32
DLCJ.DL360 | 16667 | #3汽机发电机机端反向无功电能(谷) | kWh | float32
DLCJ.DL361 | 16668 | #3汽机励磁变高压侧正向有功电能(总) | kWh | float32
DLCJ.DL362 | 16669 | #3汽机励磁变高压侧正向有功电能(尖) | kWh | float32
DLCJ.DL363 | 16670 | #3汽机励磁变高压侧正向有功电能(峰) | kWh | float32
DLCJ.DL364 | 16671 | #3汽机励磁变高压侧正向有功电能(平) | kWh | float32
DLCJ.DL365 | 16672 | #3汽机励磁变高压侧正向有功电能(谷) | kWh | float32
DLCJ.DL366 | 16673 | #3汽机励磁变高压侧反向有功电能(总) | kWh | float32
DLCJ.DL367 | 16674 | #3汽机励磁变高压侧反向有功电能(尖) | kWh | float32
DLCJ.DL368 | 16675 | #3汽机励磁变高压侧反向有功电能(峰) | kWh | float32
DLCJ.DL369 | 16676 | #3汽机励磁变高压侧反向有功电能(平) | kWh | float32
DLCJ.DL370 | 16677 | #3汽机励磁变高压侧反向有功电能(谷) | kWh | float32
DLCJ.DL371 | 16678 | #3汽机励磁变高压侧正向无功电能(总) | kWh | float32
DLCJ.DL372 | 16679 | #3汽机励磁变高压侧正向无功电能(尖) | kWh | float32
DLCJ.DL373 | 16680 | #3汽机励磁变高压侧正向无功电能(峰) | kWh | float32
DLCJ.DL374 | 16681 | #3汽机励磁变高压侧正向无功电能(平) | kWh | float32
DLCJ.DL375 | 16682 | #3汽机励磁变高压侧正向无功电能(谷) | kWh | float32
DLCJ.DL376 | 16683 | #3汽机励磁变高压侧反向无功电能(总) | kWh | float32
DLCJ.DL377 | 16684 | #3汽机励磁变高压侧反向无功电能(尖) | kWh | float32
DLCJ.DL378 | 16685 | #3汽机励磁变高压侧反向无功电能(峰) | kWh | float32
DLCJ.DL379 | 16686 | #3汽机励磁变高压侧反向无功电能(平) | kWh | float32
DLCJ.DL380 | 16687 | #3汽机励磁变高压侧反向无功电能(谷) | kWh | float32
DLCJ.DL381 | 16688 | #4燃机发电机机端正向有功电能(总) | kWh | float32
DLCJ.DL382 | 16689 | #4燃机发电机机端正向有功电能(尖) | kWh | float32
DLCJ.DL383 | 16690 | #4燃机发电机机端正向有功电能(峰) | kWh | float32
DLCJ.DL384 | 16691 | #4燃机发电机机端正向有功电能(平) | kWh | float32
DLCJ.DL385 | 16692 | #4燃机发电机机端正向有功电能(谷) | kWh | float32
DLCJ.DL386 | 16693 | #4燃机发电机机端反向有功电能(总) | kWh | float32
DLCJ.DL387 | 16694 | #4燃机发电机机端反向有功电能(尖) | kWh | float32
DLCJ.DL388 | 16695 | #4燃机发电机机端反向有功电能(峰) | kWh | float32
DLCJ.DL389 | 16696 | #4燃机发电机机端反向有功电能(平) | kWh | float32
DLCJ.DL390 | 16697 | #4燃机发电机机端反向有功电能(谷) | kWh | float32
DLCJ.DL391 | 16698 | #4燃机发电机机端正向无功电能(总) | kWh | float32
DLCJ.DL392 | 16699 | #4燃机发电机机端正向无功电能(尖) | kWh | float32
DLCJ.DL393 | 16700 | #4燃机发电机机端正向无功电能(峰) | kWh | float32
DLCJ.DL394 | 16701 | #4燃机发电机机端正向无功电能(平) | kWh | float32
DLCJ.DL395 | 16702 | #4燃机发电机机端正向无功电能(谷) | kWh | float32
DLCJ.DL396 | 16703 | #4燃机发电机机端反向无功电能(总) | kWh | float32
DLCJ.DL397 | 16704 | #4燃机发电机机端反向无功电能(尖) | kWh | float32
DLCJ.DL398 | 16705 | #4燃机发电机机端反向无功电能(峰) | kWh | float32
DLCJ.DL399 | 16706 | #4燃机发电机机端反向无功电能(平) | kWh | float32
DLCJ.DL400 | 16707 | #4燃机发电机机端反向无功电能(谷) | kWh | float32
DLCJ.DL401 | 16708 | #4燃机励磁变高压侧正向有功电能(总) | kWh | float32
DLCJ.DL402 | 16709 | #4燃机励磁变高压侧正向有功电能(尖) | kWh | float32
DLCJ.DL403 | 16710 | #4燃机励磁变高压侧正向有功电能(峰) | kWh | float32
DLCJ.DL404 | 16711 | #4燃机励磁变高压侧正向有功电能(平) | kWh | float32
DLCJ.DL405 | 16712 | #4燃机励磁变高压侧正向有功电能(谷) | kWh | float32
DLCJ.DL406 | 16713 | #4燃机励磁变高压侧反向有功电能(总) | kWh | float32
DLCJ.DL407 | 16714 | #4燃机励磁变高压侧反向有功电能(尖) | kWh | float32
DLCJ.DL408 | 16715 | #4燃机励磁变高压侧反向有功电能(峰) | kWh | float32
DLCJ.DL409 | 16716 | #4燃机励磁变高压侧反向有功电能(平) | kWh | float32
DLCJ.DL410 | 16717 | #4燃机励磁变高压侧反向有功电能(谷) | kWh | float32
DLCJ.DL411 | 16718 | #4燃机励磁变高压侧正向无功电能(总) | kWh | float32
DLCJ.DL412 | 16719 | #4燃机励磁变高压侧正向无功电能(尖) | kWh | float32
DLCJ.DL413 | 16720 | #4燃机励磁变高压侧正向无功电能(峰) | kWh | float32
DLCJ.DL414 | 16721 | #4燃机励磁变高压侧正向无功电能(平) | kWh | float32
DLCJ.DL415 | 16722 | #4燃机励磁变高压侧正向无功电能(谷) | kWh | float32
DLCJ.DL416 | 16723 | #4燃机励磁变高压侧反向无功电能(总) | kWh | float32
DLCJ.DL417 | 16724 | #4燃机励磁变高压侧反向无功电能(尖) | kWh | float32
DLCJ.DL418 | 16725 | #4燃机励磁变高压侧反向无功电能(峰) | kWh | float32
DLCJ.DL419 | 16726 | #4燃机励磁变高压侧反向无功电能(平) | kWh | float32
DLCJ.DL420 | 16727 | #4燃机励磁变高压侧反向无功电能(谷) | kWh | float32
DLCJ.DL421 | 16728 | #4燃机高厂变高压侧正向有功电能(总) | kWh | float32
DLCJ.DL422 | 16729 | #4燃机高厂变高压侧正向有功电能(尖) | kWh | float32
DLCJ.DL423 | 16730 | #4燃机高厂变高压侧正向有功电能(峰) | kWh | float32
DLCJ.DL424 | 16731 | #4燃机高厂变高压侧正向有功电能(平) | kWh | float32
DLCJ.DL425 | 16732 | #4燃机高厂变高压侧正向有功电能(谷) | kWh | float32
DLCJ.DL426 | 16733 | #4燃机高厂变高压侧反向有功电能(总) | kWh | float32
DLCJ.DL427 | 16734 | #4燃机高厂变高压侧反向有功电能(尖) | kWh | float32
DLCJ.DL428 | 16735 | #4燃机高厂变高压侧反向有功电能(峰) | kWh | float32
DLCJ.DL429 | 16736 | #4燃机高厂变高压侧反向有功电能(平) | kWh | float32
DLCJ.DL430 | 16737 | #4燃机高厂变高压侧反向有功电能(谷) | kWh | float32
DLCJ.DL431 | 16738 | #4燃机高厂变高压侧正向无功电能(总) | kWh | float32
DLCJ.DL432 | 16739 | #4燃机高厂变高压侧正向无功电能(尖) | kWh | float32
DLCJ.DL433 | 16740 | #4燃机高厂变高压侧正向无功电能(峰) | kWh | float32
DLCJ.DL434 | 16741 | #4燃机高厂变高压侧正向无功电能(平) | kWh | float32
DLCJ.DL435 | 16742 | #4燃机高厂变高压侧正向无功电能(谷) | kWh | float32
DLCJ.DL436 | 16743 | #4燃机高厂变高压侧反向无功电能(总) | kWh | float32
DLCJ.DL437 | 16744 | #4燃机高厂变高压侧反向无功电能(尖) | kWh | float32
DLCJ.DL438 | 16745 | #4燃机高厂变高压侧反向无功电能(峰) | kWh | float32
DLCJ.DL439 | 16746 | #4燃机高厂变高压侧反向无功电能(平) | kWh | float32
DLCJ.DL440 | 16747 | #4燃机高厂变高压侧反向无功电能(谷) | kWh | float32
DLCJ.YC001 | 16748 | #2燃机主变高压侧主表A相电压 | V | float32
DLCJ.YC002 | 16749 | #2燃机主变高压侧主表B相电压 | V | float32
DLCJ.YC003 | 16750 | #2燃机主变高压侧主表C相电压 | V | float32
DLCJ.YC004 | 16751 | #2燃机主变高压侧主表A相电流 | A | float32
DLCJ.YC005 | 16752 | #2燃机主变高压侧主表B相电流 | A | float32
DLCJ.YC006 | 16753 | #2燃机主变高压侧主表C相电流 | A | float32
DLCJ.YC007 | 16754 | #2燃机主变高压侧主表总有功功率 | kW | float32
DLCJ.YC008 | 16755 | #2燃机主变高压侧主表A相有功功率 | kW | float32
DLCJ.YC009 | 16756 | #2燃机主变高压侧主表B相有功功率 | kW | float32
DLCJ.YC010 | 16757 | #2燃机主变高压侧主表C相有功功率 | kW | float32
DLCJ.YC011 | 16758 | #2燃机主变高压侧主表总无功功率 | kvar | float32
DLCJ.YC012 | 16759 | #2燃机主变高压侧主表A相无功功率 | kvar | float32
DLCJ.YC013 | 16760 | #2燃机主变高压侧主表B相无功功率 | kvar | float32
DLCJ.YC014 | 16761 | #2燃机主变高压侧主表C相无功功率 | kvar | float32
DLCJ.YC015 | 16762 | #2燃机主变高压侧主表总功率因数 |  | float32
DLCJ.YC016 | 16763 | #2燃机主变高压侧主表A相功率因数 |  | float32
DLCJ.YC017 | 16764 | #2燃机主变高压侧主表B相功率因数 |  | float32
DLCJ.YC018 | 16765 | #2燃机主变高压侧主表C相功率因数 |  | float32
DLCJ.YC019 | 16766 | #2燃机主变高压侧副表A相电压 | V | float32
DLCJ.YC020 | 16767 | #2燃机主变高压侧副表B相电压 | V | float32
DLCJ.YC021 | 16768 | #2燃机主变高压侧副表C相电压 | V | float32
DLCJ.YC022 | 16769 | #2燃机主变高压侧副表A相电流 | A | float32
DLCJ.YC023 | 16770 | #2燃机主变高压侧副表B相电流 | A | float32
DLCJ.YC024 | 16771 | #2燃机主变高压侧副表C相电流 | A | float32
DLCJ.YC025 | 16772 | #2燃机主变高压侧副表总有功功率 | kW | float32
DLCJ.YC026 | 16773 | #2燃机主变高压侧副表A相有功功率 | kW | float32
DLCJ.YC027 | 16774 | #2燃机主变高压侧副表B相有功功率 | kW | float32
DLCJ.YC028 | 16775 | #2燃机主变高压侧副表C相有功功率 | kW | float32
DLCJ.YC029 | 16776 | #2燃机主变高压侧副表总无功功率 | kvar | float32
DLCJ.YC030 | 16777 | #2燃机主变高压侧副表A相无功功率 | kvar | float32
DLCJ.YC031 | 16778 | #2燃机主变高压侧副表B相无功功率 | kvar | float32
DLCJ.YC032 | 16779 | #2燃机主变高压侧副表C相无功功率 | kvar | float32
DLCJ.YC033 | 16780 | #2燃机主变高压侧副表总功率因数 |  | float32
DLCJ.YC034 | 16781 | #2燃机主变高压侧副表A相功率因数 |  | float32
DLCJ.YC035 | 16782 | #2燃机主变高压侧副表B相功率因数 |  | float32
DLCJ.YC036 | 16783 | #2燃机主变高压侧副表C相功率因数 |  | float32
DLCJ.YC037 | 16784 | #1汽机主变高压测主表A相电压 | V | float32
DLCJ.YC038 | 16785 | #1汽机主变高压测主表B相电压 | V | float32
DLCJ.YC039 | 16786 | #1汽机主变高压测主表C相电压 | V | float32
DLCJ.YC040 | 16787 | #1汽机主变高压测主表A相电流 | A | float32
DLCJ.YC041 | 16788 | #1汽机主变高压测主表B相电流 | A | float32
DLCJ.YC042 | 16789 | #1汽机主变高压测主表C相电流 | A | float32
DLCJ.YC043 | 16790 | #1汽机主变高压测主表总有功功率 | kW | float32
DLCJ.YC044 | 16791 | #1汽机主变高压测主表A相有功功率 | kW | float32
DLCJ.YC045 | 16792 | #1汽机主变高压测主表B相有功功率 | kW | float32
DLCJ.YC046 | 16793 | #1汽机主变高压测主表C相有功功率 | kW | float32
DLCJ.YC047 | 16794 | #1汽机主变高压测主表总无功功率 | kvar | float32
DLCJ.YC048 | 16795 | #1汽机主变高压测主表A相无功功率 | kvar | float32
DLCJ.YC049 | 16796 | #1汽机主变高压测主表B相无功功率 | kvar | float32
DLCJ.YC050 | 16797 | #1汽机主变高压测主表C相无功功率 | kvar | float32
DLCJ.YC051 | 16798 | #1汽机主变高压测主表总功率因数 |  | float32
DLCJ.YC052 | 16799 | #1汽机主变高压测主表A相功率因数 |  | float32
DLCJ.YC053 | 16800 | #1汽机主变高压测主表B相功率因数 |  | float32
DLCJ.YC054 | 16801 | #1汽机主变高压测主表C相功率因数 |  | float32
DLCJ.YC055 | 16802 | #1汽机主变高压侧副表A相电压 | V | float32
DLCJ.YC056 | 16803 | #1汽机主变高压侧副表B相电压 | V | float32
DLCJ.YC057 | 16804 | #1汽机主变高压侧副表C相电压 | V | float32
DLCJ.YC058 | 16805 | #1汽机主变高压侧副表A相电流 | A | float32
DLCJ.YC059 | 16806 | #1汽机主变高压侧副表B相电流 | A | float32
DLCJ.YC060 | 16807 | #1汽机主变高压侧副表C相电流 | A | float32
DLCJ.YC061 | 16808 | #1汽机主变高压侧副表总有功功率 | kW | float32
DLCJ.YC062 | 16809 | #1汽机主变高压侧副表A相有功功率 | kW | float32
DLCJ.YC063 | 16810 | #1汽机主变高压侧副表B相有功功率 | kW | float32
DLCJ.YC064 | 16811 | #1汽机主变高压侧副表C相有功功率 | kW | float32
DLCJ.YC065 | 16812 | #1汽机主变高压侧副表总无功功率 | kvar | float32
DLCJ.YC066 | 16813 | #1汽机主变高压侧副表A相无功功率 | kvar | float32
DLCJ.YC067 | 16814 | #1汽机主变高压侧副表B相无功功率 | kvar | float32
DLCJ.YC068 | 16815 | #1汽机主变高压侧副表C相无功功率 | kvar | float32
DLCJ.YC069 | 16816 | #1汽机主变高压侧副表总功率因数 |  | float32
DLCJ.YC070 | 16817 | #1汽机主变高压侧副表A相功率因数 |  | float32
DLCJ.YC071 | 16818 | #1汽机主变高压侧副表B相功率因数 |  | float32
DLCJ.YC072 | 16819 | #1汽机主变高压侧副表C相功率因数 |  | float32
DLCJ.YC073 | 16820 | #4燃机主变高压侧主表A相电压 | V | float32
DLCJ.YC074 | 16821 | #4燃机主变高压侧主表B相电压 | V | float32
DLCJ.YC075 | 16822 | #4燃机主变高压侧主表C相电压 | V | float32
DLCJ.YC076 | 16823 | #4燃机主变高压侧主表A相电流 | A | float32
DLCJ.YC077 | 16824 | #4燃机主变高压侧主表B相电流 | A | float32
DLCJ.YC078 | 16825 | #4燃机主变高压侧主表C相电流 | A | float32
DLCJ.YC079 | 16826 | #4燃机主变高压侧主表总有功功率 | kW | float32
DLCJ.YC080 | 16827 | #4燃机主变高压侧主表A相有功功率 | kW | float32
DLCJ.YC081 | 16828 | #4燃机主变高压侧主表B相有功功率 | kW | float32
DLCJ.YC082 | 16829 | #4燃机主变高压侧主表C相有功功率 | kW | float32
DLCJ.YC083 | 16830 | #4燃机主变高压侧主表总无功功率 | kvar | float32
DLCJ.YC084 | 16831 | #4燃机主变高压侧主表A相无功功率 | kvar | float32
DLCJ.YC085 | 16832 | #4燃机主变高压侧主表B相无功功率 | kvar | float32
DLCJ.YC086 | 16833 | #4燃机主变高压侧主表C相无功功率 | kvar | float32
DLCJ.YC087 | 16834 | #4燃机主变高压侧主表总功率因数 |  | float32
DLCJ.YC088 | 16835 | #4燃机主变高压侧主表A相功率因数 |  | float32
DLCJ.YC089 | 16836 | #4燃机主变高压侧主表B相功率因数 |  | float32
DLCJ.YC090 | 16837 | #4燃机主变高压侧主表C相功率因数 |  | float32
DLCJ.YC091 | 16838 | #4燃机主变高压侧副表A相电压 | V | float32
DLCJ.YC092 | 16839 | #4燃机主变高压侧副表B相电压 | V | float32
DLCJ.YC093 | 16840 | #4燃机主变高压侧副表C相电压 | V | float32
DLCJ.YC094 | 16841 | #4燃机主变高压侧副表A相电流 | A | float32
DLCJ.YC095 | 16842 | #4燃机主变高压侧副表B相电流 | A | float32
DLCJ.YC096 | 16843 | #4燃机主变高压侧副表C相电流 | A | float32
DLCJ.YC097 | 16844 | #4燃机主变高压侧副表总有功功率 | kW | float32
DLCJ.YC098 | 16845 | #4燃机主变高压侧副表A相有功功率 | kW | float32
DLCJ.YC099 | 16846 | #4燃机主变高压侧副表B相有功功率 | kW | float32
DLCJ.YC100 | 16847 | #4燃机主变高压侧副表C相有功功率 | kW | float32
DLCJ.YC101 | 16848 | #4燃机主变高压侧副表总无功功率 | kvar | float32
DLCJ.YC102 | 16849 | #4燃机主变高压侧副表A相无功功率 | kvar | float32
DLCJ.YC103 | 16850 | #4燃机主变高压侧副表B相无功功率 | kvar | float32
DLCJ.YC104 | 16851 | #4燃机主变高压侧副表C相无功功率 | kvar | float32
DLCJ.YC105 | 16852 | #4燃机主变高压侧副表总功率因数 |  | float32
DLCJ.YC106 | 16853 | #4燃机主变高压侧副表A相功率因数 |  | float32
DLCJ.YC107 | 16854 | #4燃机主变高压侧副表B相功率因数 |  | float32
DLCJ.YC108 | 16855 | #4燃机主变高压侧副表C相功率因数 |  | float32
DLCJ.YC109 | 16856 | #3汽机主变高压侧主表A相电压 | V | float32
DLCJ.YC110 | 16857 | #3汽机主变高压侧主表B相电压 | V | float32
DLCJ.YC111 | 16858 | #3汽机主变高压侧主表C相电压 | V | float32
DLCJ.YC112 | 16859 | #3汽机主变高压侧主表A相电流 | A | float32
DLCJ.YC113 | 16860 | #3汽机主变高压侧主表B相电流 | A | float32
DLCJ.YC114 | 16861 | #3汽机主变高压侧主表C相电流 | A | float32
DLCJ.YC115 | 16862 | #3汽机主变高压侧主表总有功功率 | kW | float32
DLCJ.YC116 | 16863 | #3汽机主变高压侧主表A相有功功率 | kW | float32
DLCJ.YC117 | 16864 | #3汽机主变高压侧主表B相有功功率 | kW | float32
DLCJ.YC118 | 16865 | #3汽机主变高压侧主表C相有功功率 | kW | float32
DLCJ.YC119 | 16866 | #3汽机主变高压侧主表总无功功率 | kvar | float32
DLCJ.YC120 | 16867 | #3汽机主变高压侧主表A相无功功率 | kvar | float32
DLCJ.YC121 | 16868 | #3汽机主变高压侧主表B相无功功率 | kvar | float32
DLCJ.YC122 | 16869 | #3汽机主变高压侧主表C相无功功率 | kvar | float32
DLCJ.YC123 | 16870 | #3汽机主变高压侧主表总功率因数 |  | float32
DLCJ.YC124 | 16871 | #3汽机主变高压侧主表A相功率因数 |  | float32
DLCJ.YC125 | 16872 | #3汽机主变高压侧主表B相功率因数 |  | float32
DLCJ.YC126 | 16873 | #3汽机主变高压侧主表C相功率因数 |  | float32
DLCJ.YC127 | 16874 | #3汽机主变高压侧副表A相电压 | V | float32
DLCJ.YC128 | 16875 | #3汽机主变高压侧副表B相电压 | V | float32
DLCJ.YC129 | 16876 | #3汽机主变高压侧副表C相电压 | V | float32
DLCJ.YC130 | 16877 | #3汽机主变高压侧副表A相电流 | A | float32
DLCJ.YC131 | 16878 | #3汽机主变高压侧副表B相电流 | A | float32
DLCJ.YC132 | 16879 | #3汽机主变高压侧副表C相电流 | A | float32
DLCJ.YC133 | 16880 | #3汽机主变高压侧副表总有功功率 | kW | float32
DLCJ.YC134 | 16881 | #3汽机主变高压侧副表A相有功功率 | kW | float32
DLCJ.YC135 | 16882 | #3汽机主变高压侧副表B相有功功率 | kW | float32
DLCJ.YC136 | 16883 | #3汽机主变高压侧副表C相有功功率 | kW | float32
DLCJ.YC137 | 16884 | #3汽机主变高压侧副表总无功功率 | kvar | float32
DLCJ.YC138 | 16885 | #3汽机主变高压侧副表A相无功功率 | kvar | float32
DLCJ.YC139 | 16886 | #3汽机主变高压侧副表B相无功功率 | kvar | float32
DLCJ.YC140 | 16887 | #3汽机主变高压侧副表C相无功功率 | kvar | float32
DLCJ.YC141 | 16888 | #3汽机主变高压侧副表总功率因数 |  | float32
DLCJ.YC142 | 16889 | #3汽机主变高压侧副表A相功率因数 |  | float32
DLCJ.YC143 | 16890 | #3汽机主变高压侧副表B相功率因数 |  | float32
DLCJ.YC144 | 16891 | #3汽机主变高压侧副表C相功率因数 |  | float32
DLCJ.YC145 | 16892 | #01高备变高压侧主表A相电压 | V | float32
DLCJ.YC146 | 16893 | #01高备变高压侧主表B相电压 | V | float32
DLCJ.YC147 | 16894 | #01高备变高压侧主表C相电压 | V | float32
DLCJ.YC148 | 16895 | #01高备变高压侧主表A相电流 | A | float32
DLCJ.YC149 | 16896 | #01高备变高压侧主表B相电流 | A | float32
DLCJ.YC150 | 16897 | #01高备变高压侧主表C相电流 | A | float32
DLCJ.YC151 | 16898 | #01高备变高压侧主表总有功功率 | kW | float32
DLCJ.YC152 | 16899 | #01高备变高压侧主表A相有功功率 | kW | float32
DLCJ.YC153 | 16900 | #01高备变高压侧主表B相有功功率 | kW | float32
DLCJ.YC154 | 16901 | #01高备变高压侧主表C相有功功率 | kW | float32
DLCJ.YC155 | 16902 | #01高备变高压侧主表总无功功率 | kvar | float32
DLCJ.YC156 | 16903 | #01高备变高压侧主表A相无功功率 | kvar | float32
DLCJ.YC157 | 16904 | #01高备变高压侧主表B相无功功率 | kvar | float32
DLCJ.YC158 | 16905 | #01高备变高压侧主表C相无功功率 | kvar | float32
DLCJ.YC159 | 16906 | #01高备变高压侧主表总功率因数 |  | float32
DLCJ.YC160 | 16907 | #01高备变高压侧主表A相功率因数 |  | float32
DLCJ.YC161 | 16908 | #01高备变高压侧主表B相功率因数 |  | float32
DLCJ.YC162 | 16909 | #01高备变高压侧主表C相功率因数 |  | float32
DLCJ.YC163 | 16910 | #01高备变高压侧副表A相电压 | V | float32
DLCJ.YC164 | 16911 | #01高备变高压侧副表B相电压 | V | float32
DLCJ.YC165 | 16912 | #01高备变高压侧副表C相电压 | V | float32
DLCJ.YC166 | 16913 | #01高备变高压侧副表A相电流 | A | float32
DLCJ.YC167 | 16914 | #01高备变高压侧副表B相电流 | A | float32
DLCJ.YC168 | 16915 | #01高备变高压侧副表C相电流 | A | float32
DLCJ.YC169 | 16916 | #01高备变高压侧副表总有功功率 | kW | float32
DLCJ.YC170 | 16917 | #01高备变高压侧副表A相有功功率 | kW | float32
DLCJ.YC171 | 16918 | #01高备变高压侧副表B相有功功率 | kW | float32
DLCJ.YC172 | 16919 | #01高备变高压侧副表C相有功功率 | kW | float32
DLCJ.YC173 | 16920 | #01高备变高压侧副表总无功功率 | kvar | float32
DLCJ.YC174 | 16921 | #01高备变高压侧副表A相无功功率 | kvar | float32
DLCJ.YC175 | 16922 | #01高备变高压侧副表B相无功功率 | kvar | float32
DLCJ.YC176 | 16923 | #01高备变高压侧副表C相无功功率 | kvar | float32
DLCJ.YC177 | 16924 | #01高备变高压侧副表总功率因数 |  | float32
DLCJ.YC178 | 16925 | #01高备变高压侧副表A相功率因数 |  | float32
DLCJ.YC179 | 16926 | #01高备变高压侧副表B相功率因数 |  | float32
DLCJ.YC180 | 16927 | #01高备变高压侧副表C相功率因数 |  | float32
DLCJ.YC181 | 16928 | 220kV桔布乙线A相电压 | V | float32
DLCJ.YC182 | 16929 | 220kV桔布乙线B相电压 | V | float32
DLCJ.YC183 | 16930 | 220kV桔布乙线C相电压 | V | float32
DLCJ.YC184 | 16931 | 220kV桔布乙线A相电流 | A | float32
DLCJ.YC185 | 16932 | 220kV桔布乙线B相电流 | A | float32
DLCJ.YC186 | 16933 | 220kV桔布乙线C相电流 | A | float32
DLCJ.YC187 | 16934 | 220kV桔布乙线总有功功率 | kW | float32
DLCJ.YC188 | 16935 | 220kV桔布乙线A相有功功率 | kW | float32
DLCJ.YC189 | 16936 | 220kV桔布乙线B相有功功率 | kW | float32
DLCJ.YC190 | 16937 | 220kV桔布乙线C相有功功率 | kW | float32
DLCJ.YC191 | 16938 | 220kV桔布乙线总无功功率 | kvar | float32
DLCJ.YC192 | 16939 | 220kV桔布乙线A相无功功率 | kvar | float32
DLCJ.YC193 | 16940 | 220kV桔布乙线B相无功功率 | kvar | float32
DLCJ.YC194 | 16941 | 220kV桔布乙线C相无功功率 | kvar | float32
DLCJ.YC195 | 16942 | 220kV桔布乙线总功率因数 |  | float32
DLCJ.YC196 | 16943 | 220kV桔布乙线A相功率因数 |  | float32
DLCJ.YC197 | 16944 | 220kV桔布乙线B相功率因数 |  | float32
DLCJ.YC198 | 16945 | 220kV桔布乙线C相功率因数 |  | float32
DLCJ.YC199 | 16946 | 220kV桔布甲线A相电压 | V | float32
DLCJ.YC200 | 16947 | 220kV桔布甲线B相电压 | V | float32
DLCJ.YC201 | 16948 | 220kV桔布甲线C相电压 | V | float32
DLCJ.YC202 | 16949 | 220kV桔布甲线A相电流 | A | float32
DLCJ.YC203 | 16950 | 220kV桔布甲线B相电流 | A | float32
DLCJ.YC204 | 16951 | 220kV桔布甲线C相电流 | A | float32
DLCJ.YC205 | 16952 | 220kV桔布甲线总有功功率 | kW | float32
DLCJ.YC206 | 16953 | 220kV桔布甲线A相有功功率 | kW | float32
DLCJ.YC207 | 16954 | 220kV桔布甲线B相有功功率 | kW | float32
DLCJ.YC208 | 16955 | 220kV桔布甲线C相有功功率 | kW | float32
DLCJ.YC209 | 16956 | 220kV桔布甲线总无功功率 | kvar | float32
DLCJ.YC210 | 16957 | 220kV桔布甲线A相无功功率 | kvar | float32
DLCJ.YC211 | 16958 | 220kV桔布甲线B相无功功率 | kvar | float32
DLCJ.YC212 | 16959 | 220kV桔布甲线C相无功功率 | kvar | float32
DLCJ.YC213 | 16960 | 220kV桔布甲线总功率因数 |  | float32
DLCJ.YC214 | 16961 | 220kV桔布甲线A相功率因数 |  | float32
DLCJ.YC215 | 16962 | 220kV桔布甲线B相功率因数 |  | float32
DLCJ.YC216 | 16963 | 220kV桔布甲线C相功率因数 |  | float32
DLCJ.YC217 | 16964 | #1汽机发电机机端A相电压 | V | float32
DLCJ.YC218 | 16965 | #1汽机发电机机端B相电压 | V | float32
DLCJ.YC219 | 16966 | #1汽机发电机机端C相电压 | V | float32
DLCJ.YC220 | 16967 | #1汽机发电机机端A相电流 | A | float32
DLCJ.YC221 | 16968 | #1汽机发电机机端B相电流 | A | float32
DLCJ.YC222 | 16969 | #1汽机发电机机端C相电流 | A | float32
DLCJ.YC223 | 16970 | #1汽机发电机机端总有功功率 | kW | float32
DLCJ.YC224 | 16971 | #1汽机发电机机端A相有功功率 | kW | float32
DLCJ.YC225 | 16972 | #1汽机发电机机端B相有功功率 | kW | float32
DLCJ.YC226 | 16973 | #1汽机发电机机端C相有功功率 | kW | float32
DLCJ.YC227 | 16974 | #1汽机发电机机端总无功功率 | kvar | float32
DLCJ.YC228 | 16975 | #1汽机发电机机端A相无功功率 | kvar | float32
DLCJ.YC229 | 16976 | #1汽机发电机机端B相无功功率 | kvar | float32
DLCJ.YC230 | 16977 | #1汽机发电机机端C相无功功率 | kvar | float32
DLCJ.YC231 | 16978 | #1汽机发电机机端总功率因数 |  | float32
DLCJ.YC232 | 16979 | #1汽机发电机机端A相功率因数 |  | float32
DLCJ.YC233 | 16980 | #1汽机发电机机端B相功率因数 |  | float32
DLCJ.YC234 | 16981 | #1汽机发电机机端C相功率因数 |  | float32
DLCJ.YC235 | 16982 | #1汽机励磁变高压侧A相电压 | V | float32
DLCJ.YC236 | 16983 | #1汽机励磁变高压侧B相电压 | V | float32
DLCJ.YC237 | 16984 | #1汽机励磁变高压侧C相电压 | V | float32
DLCJ.YC238 | 16985 | #1汽机励磁变高压侧A相电流 | A | float32
DLCJ.YC239 | 16986 | #1汽机励磁变高压侧B相电流 | A | float32
DLCJ.YC240 | 16987 | #1汽机励磁变高压侧C相电流 | A | float32
DLCJ.YC241 | 16988 | #1汽机励磁变高压侧总有功功率 | kW | float32
DLCJ.YC242 | 16989 | #1汽机励磁变高压侧A相有功功率 | kW | float32
DLCJ.YC243 | 16990 | #1汽机励磁变高压侧B相有功功率 | kW | float32
DLCJ.YC244 | 16991 | #1汽机励磁变高压侧C相有功功率 | kW | float32
DLCJ.YC245 | 16992 | #1汽机励磁变高压侧总无功功率 | kvar | float32
DLCJ.YC246 | 16993 | #1汽机励磁变高压侧A相无功功率 | kvar | float32
DLCJ.YC247 | 16994 | #1汽机励磁变高压侧B相无功功率 | kvar | float32
DLCJ.YC248 | 16995 | #1汽机励磁变高压侧C相无功功率 | kvar | float32
DLCJ.YC249 | 16996 | #1汽机励磁变高压侧总功率因数 |  | float32
DLCJ.YC250 | 16997 | #1汽机励磁变高压侧A相功率因数 |  | float32
DLCJ.YC251 | 16998 | #1汽机励磁变高压侧B相功率因数 |  | float32
DLCJ.YC252 | 16999 | #1汽机励磁变高压侧C相功率因数 |  | float32
DLCJ.YC253 | 17000 | #2燃机发电机机端A相电压 | V | float32
DLCJ.YC254 | 17001 | #2燃机发电机机端B相电压 | V | float32
DLCJ.YC255 | 17002 | #2燃机发电机机端C相电压 | V | float32
DLCJ.YC256 | 17003 | #2燃机发电机机端A相电流 | A | float32
DLCJ.YC257 | 17004 | #2燃机发电机机端B相电流 | A | float32
DLCJ.YC258 | 17005 | #2燃机发电机机端C相电流 | A | float32
DLCJ.YC259 | 17006 | #2燃机发电机机端总有功功率 | kW | float32
DLCJ.YC260 | 17007 | #2燃机发电机机端A相有功功率 | kW | float32
DLCJ.YC261 | 17008 | #2燃机发电机机端B相有功功率 | kW | float32
DLCJ.YC262 | 17009 | #2燃机发电机机端C相有功功率 | kW | float32
DLCJ.YC263 | 17010 | #2燃机发电机机端总无功功率 | kvar | float32
DLCJ.YC264 | 17011 | #2燃机发电机机端A相无功功率 | kvar | float32
DLCJ.YC265 | 17012 | #2燃机发电机机端B相无功功率 | kvar | float32
DLCJ.YC266 | 17013 | #2燃机发电机机端C相无功功率 | kvar | float32
DLCJ.YC267 | 17014 | #2燃机发电机机端总功率因数 |  | float32
DLCJ.YC268 | 17015 | #2燃机发电机机端A相功率因数 |  | float32
DLCJ.YC269 | 17016 | #2燃机发电机机端B相功率因数 |  | float32
DLCJ.YC270 | 17017 | #2燃机发电机机端C相功率因数 |  | float32
DLCJ.YC271 | 17018 | #2燃机励磁变高压侧A相电压 | V | float32
DLCJ.YC272 | 17019 | #2燃机励磁变高压侧B相电压 | V | float32
DLCJ.YC273 | 17020 | #2燃机励磁变高压侧C相电压 | V | float32
DLCJ.YC274 | 17021 | #2燃机励磁变高压侧A相电流 | A | float32
DLCJ.YC275 | 17022 | #2燃机励磁变高压侧B相电流 | A | float32
DLCJ.YC276 | 17023 | #2燃机励磁变高压侧C相电流 | A | float32
DLCJ.YC277 | 17024 | #2燃机励磁变高压侧总有功功率 | kW | float32
DLCJ.YC278 | 17025 | #2燃机励磁变高压侧A相有功功率 | kW | float32
DLCJ.YC279 | 17026 | #2燃机励磁变高压侧B相有功功率 | kW | float32
DLCJ.YC280 | 17027 | #2燃机励磁变高压侧C相有功功率 | kW | float32
DLCJ.YC281 | 17028 | #2燃机励磁变高压侧总无功功率 | kvar | float32
DLCJ.YC282 | 17029 | #2燃机励磁变高压侧A相无功功率 | kvar | float32
DLCJ.YC283 | 17030 | #2燃机励磁变高压侧B相无功功率 | kvar | float32
DLCJ.YC284 | 17031 | #2燃机励磁变高压侧C相无功功率 | kvar | float32
DLCJ.YC285 | 17032 | #2燃机励磁变高压侧总功率因数 |  | float32
DLCJ.YC286 | 17033 | #2燃机励磁变高压侧A相功率因数 |  | float32
DLCJ.YC287 | 17034 | #2燃机励磁变高压侧B相功率因数 |  | float32
DLCJ.YC288 | 17035 | #2燃机励磁变高压侧C相功率因数 |  | float32
DLCJ.YC289 | 17036 | #2燃机高厂变高压侧A相电压 | V | float32
DLCJ.YC290 | 17037 | #2燃机高厂变高压侧B相电压 | V | float32
DLCJ.YC291 | 17038 | #2燃机高厂变高压侧C相电压 | V | float32
DLCJ.YC292 | 17039 | #2燃机高厂变高压侧A相电流 | A | float32
DLCJ.YC293 | 17040 | #2燃机高厂变高压侧B相电流 | A | float32
DLCJ.YC294 | 17041 | #2燃机高厂变高压侧C相电流 | A | float32
DLCJ.YC295 | 17042 | #2燃机高厂变高压侧总有功功率 | kW | float32
DLCJ.YC296 | 17043 | #2燃机高厂变高压侧A相有功功率 | kW | float32
DLCJ.YC297 | 17044 | #2燃机高厂变高压侧B相有功功率 | kW | float32
DLCJ.YC298 | 17045 | #2燃机高厂变高压侧C相有功功率 | kW | float32
DLCJ.YC299 | 17046 | #2燃机高厂变高压侧总无功功率 | kvar | float32
DLCJ.YC300 | 17047 | #2燃机高厂变高压侧A相无功功率 | kvar | float32
DLCJ.YC301 | 17048 | #2燃机高厂变高压侧B相无功功率 | kvar | float32
DLCJ.YC302 | 17049 | #2燃机高厂变高压侧C相无功功率 | kvar | float32
DLCJ.YC303 | 17050 | #2燃机高厂变高压侧总功率因数 |  | float32
DLCJ.YC304 | 17051 | #2燃机高厂变高压侧A相功率因数 |  | float32
DLCJ.YC305 | 17052 | #2燃机高厂变高压侧B相功率因数 |  | float32
DLCJ.YC306 | 17053 | #2燃机高厂变高压侧C相功率因数 |  | float32
DLCJ.YC307 | 17054 | #3汽机发电机机端A相电压 | V | float32
DLCJ.YC308 | 17055 | #3汽机发电机机端B相电压 | V | float32
DLCJ.YC309 | 17056 | #3汽机发电机机端C相电压 | V | float32
DLCJ.YC310 | 17057 | #3汽机发电机机端A相电流 | A | float32
DLCJ.YC311 | 17058 | #3汽机发电机机端B相电流 | A | float32
DLCJ.YC312 | 17059 | #3汽机发电机机端C相电流 | A | float32
DLCJ.YC313 | 17060 | #3汽机发电机机端总有功功率 | kW | float32
DLCJ.YC314 | 17061 | #3汽机发电机机端A相有功功率 | kW | float32
DLCJ.YC315 | 17062 | #3汽机发电机机端B相有功功率 | kW | float32
DLCJ.YC316 | 17063 | #3汽机发电机机端C相有功功率 | kW | float32
DLCJ.YC317 | 17064 | #3汽机发电机机端总无功功率 | kvar | float32
DLCJ.YC318 | 17065 | #3汽机发电机机端A相无功功率 | kvar | float32
DLCJ.YC319 | 17066 | #3汽机发电机机端B相无功功率 | kvar | float32
DLCJ.YC320 | 17067 | #3汽机发电机机端C相无功功率 | kvar | float32
DLCJ.YC321 | 17068 | #3汽机发电机机端总功率因数 |  | float32
DLCJ.YC322 | 17069 | #3汽机发电机机端A相功率因数 |  | float32
DLCJ.YC323 | 17070 | #3汽机发电机机端B相功率因数 |  | float32
DLCJ.YC324 | 17071 | #3汽机发电机机端C相功率因数 |  | float32
DLCJ.YC325 | 17072 | #3汽机励磁变高压侧A相电压 | V | float32
DLCJ.YC326 | 17073 | #3汽机励磁变高压侧B相电压 | V | float32
DLCJ.YC327 | 17074 | #3汽机励磁变高压侧C相电压 | V | float32
DLCJ.YC328 | 17075 | #3汽机励磁变高压侧A相电流 | A | float32
DLCJ.YC329 | 17076 | #3汽机励磁变高压侧B相电流 | A | float32
DLCJ.YC330 | 17077 | #3汽机励磁变高压侧C相电流 | A | float32
DLCJ.YC331 | 17078 | #3汽机励磁变高压侧总有功功率 | kW | float32
DLCJ.YC332 | 17079 | #3汽机励磁变高压侧A相有功功率 | kW | float32
DLCJ.YC333 | 17080 | #3汽机励磁变高压侧B相有功功率 | kW | float32
DLCJ.YC334 | 17081 | #3汽机励磁变高压侧C相有功功率 | kW | float32
DLCJ.YC335 | 17082 | #3汽机励磁变高压侧总无功功率 | kvar | float32
DLCJ.YC336 | 17083 | #3汽机励磁变高压侧A相无功功率 | kvar | float32
DLCJ.YC337 | 17084 | #3汽机励磁变高压侧B相无功功率 | kvar | float32
DLCJ.YC338 | 17085 | #3汽机励磁变高压侧C相无功功率 | kvar | float32
DLCJ.YC339 | 17086 | #3汽机励磁变高压侧总功率因数 |  | float32
DLCJ.YC340 | 17087 | #3汽机励磁变高压侧A相功率因数 |  | float32
DLCJ.YC341 | 17088 | #3汽机励磁变高压侧B相功率因数 |  | float32
DLCJ.YC342 | 17089 | #3汽机励磁变高压侧C相功率因数 |  | float32
DLCJ.YC343 | 17090 | #4燃机发电机机端A相电压 | V | float32
DLCJ.YC344 | 17091 | #4燃机发电机机端B相电压 | V | float32
DLCJ.YC345 | 17092 | #4燃机发电机机端C相电压 | V | float32
DLCJ.YC346 | 17093 | #4燃机发电机机端A相电流 | A | float32
DLCJ.YC347 | 17094 | #4燃机发电机机端B相电流 | A | float32
DLCJ.YC348 | 17095 | #4燃机发电机机端C相电流 | A | float32
DLCJ.YC349 | 17096 | #4燃机发电机机端总有功功率 | kW | float32
DLCJ.YC350 | 17097 | #4燃机发电机机端A相有功功率 | kW | float32
DLCJ.YC351 | 17098 | #4燃机发电机机端B相有功功率 | kW | float32
DLCJ.YC352 | 17099 | #4燃机发电机机端C相有功功率 | kW | float32
DLCJ.YC353 | 17100 | #4燃机发电机机端总无功功率 | kvar | float32
DLCJ.YC354 | 17101 | #4燃机发电机机端A相无功功率 | kvar | float32
DLCJ.YC355 | 17102 | #4燃机发电机机端B相无功功率 | kvar | float32
DLCJ.YC356 | 17103 | #4燃机发电机机端C相无功功率 | kvar | float32
DLCJ.YC357 | 17104 | #4燃机发电机机端总功率因数 |  | float32
DLCJ.YC358 | 17105 | #4燃机发电机机端A相功率因数 |  | float32
DLCJ.YC359 | 17106 | #4燃机发电机机端B相功率因数 |  | float32
DLCJ.YC360 | 17107 | #4燃机发电机机端C相功率因数 |  | float32
DLCJ.YC361 | 17108 | #4燃机励磁变高压侧A相电压 | V | float32
DLCJ.YC362 | 17109 | #4燃机励磁变高压侧B相电压 | V | float32
DLCJ.YC363 | 17110 | #4燃机励磁变高压侧C相电压 | V | float32
DLCJ.YC364 | 17111 | #4燃机励磁变高压侧A相电流 | A | float32
DLCJ.YC365 | 17112 | #4燃机励磁变高压侧B相电流 | A | float32
DLCJ.YC366 | 17113 | #4燃机励磁变高压侧C相电流 | A | float32
DLCJ.YC367 | 17114 | #4燃机励磁变高压侧总有功功率 | kW | float32
DLCJ.YC368 | 17115 | #4燃机励磁变高压侧A相有功功率 | kW | float32
DLCJ.YC369 | 17116 | #4燃机励磁变高压侧B相有功功率 | kW | float32
DLCJ.YC370 | 17117 | #4燃机励磁变高压侧C相有功功率 | kW | float32
DLCJ.YC371 | 17118 | #4燃机励磁变高压侧总无功功率 | kvar | float32
DLCJ.YC372 | 17119 | #4燃机励磁变高压侧A相无功功率 | kvar | float32
DLCJ.YC373 | 17120 | #4燃机励磁变高压侧B相无功功率 | kvar | float32
DLCJ.YC374 | 17121 | #4燃机励磁变高压侧C相无功功率 | kvar | float32
DLCJ.YC375 | 17122 | #4燃机励磁变高压侧总功率因数 |  | float32
DLCJ.YC376 | 17123 | #4燃机励磁变高压侧A相功率因数 |  | float32
DLCJ.YC377 | 17124 | #4燃机励磁变高压侧B相功率因数 |  | float32
DLCJ.YC378 | 17125 | #4燃机励磁变高压侧C相功率因数 |  | float32
DLCJ.YC379 | 17126 | #4燃机高厂变高压侧A相电压 | V | float32
DLCJ.YC380 | 17127 | #4燃机高厂变高压侧B相电压 | V | float32
DLCJ.YC381 | 17128 | #4燃机高厂变高压侧C相电压 | V | float32
DLCJ.YC382 | 17129 | #4燃机高厂变高压侧A相电流 | A | float32
DLCJ.YC383 | 17130 | #4燃机高厂变高压侧B相电流 | A | float32
DLCJ.YC384 | 17131 | #4燃机高厂变高压侧C相电流 | A | float32
DLCJ.YC385 | 17132 | #4燃机高厂变高压侧总有功功率 | kW | float32
DLCJ.YC386 | 17133 | #4燃机高厂变高压侧A相有功功率 | kW | float32
DLCJ.YC387 | 17134 | #4燃机高厂变高压侧B相有功功率 | kW | float32
DLCJ.YC388 | 17135 | #4燃机高厂变高压侧C相有功功率 | kW | float32
DLCJ.YC389 | 17136 | #4燃机高厂变高压侧总无功功率 | kvar | float32
DLCJ.YC390 | 17137 | #4燃机高厂变高压侧A相无功功率 | kvar | float32
DLCJ.YC391 | 17138 | #4燃机高厂变高压侧B相无功功率 | kvar | float32
DLCJ.YC392 | 17139 | #4燃机高厂变高压侧C相无功功率 | kvar | float32
DLCJ.YC393 | 17140 | #4燃机高厂变高压侧总功率因数 |  | float32
DLCJ.YC394 | 17141 | #4燃机高厂变高压侧A相功率因数 |  | float32
DLCJ.YC395 | 17142 | #4燃机高厂变高压侧B相功率因数 |  | float32
DLCJ.YC396 | 17143 | #4燃机高厂变高压侧C相功率因数 |  | float32
N1DCS.10AGCLOADMAX | 17144 | 第一套机组总负荷上限值 | % | float32
N1DCS.10AGCLOADMIN | 17145 | 第一套机组总负荷下限值 | % | float32
N1DCS.10AGCLOADP2 | 17146 | 第一套机组实际总负荷 | % | float32
N1DCS.10AGCLOADSP | 17147 | AGC总负荷指令 | MW | float32
N1DCS.10AGCLOADTP | 17148 | AGC目标定值返回值 | % | float32
N1DCS.10AGCLOADVR | 17149 | 第一套机组总负荷响应速率 | % | float32
N1DCS.10CJA01DE002XQ01 | 17150 | EXTERNAL LOAD REFERENCE - RAMP |  | float32
N1DCS.10CJA01DE003XQ01 | 17151 | EXTERNAL LOAD REFERENCE |  | float32
N1DCS.10CJA01DP100 | 17152 | 高压主蒸汽压力设定值 |  | float32
N1DCS.10CJA01DP200 | 17153 | 再热主蒸汽压力设定值 |  | float32
N1DCS.10LBA10CP101 | 17154 | 高压主蒸汽压力1 | MPa | float32
N1DCS.10LBA10CP102 | 17155 | 高压主蒸汽压力2 | MPa | float32
N1DCS.10LBA10CP103 | 17156 | 高压主蒸汽压力3 | MPa | float32
N1DCS.10LBA10CPX3 | 17157 | 高压主蒸汽压力（3选后） |  | float32
N1DCS.10LBA10CT301 | 17158 | 高压主蒸汽温度 | ℃ | float32
N1DCS.10LBA10CT302 | 17159 | 高压主汽母管疏水气动门1前温度 | ℃ | float32
N1DCS.10LBA10CT303 | 17160 | 高压主汽母管疏水气动门2前温度 | ℃ | float32
N1DCS.10LBA10CT304 | 17161 | 高压主汽母管疏水气动门2后温度 | ℃ | float32
N1DCS.10LBA10CT305 | 17162 | 高压主汽母管疏水气动门1后温度 | ℃ | float32
N1DCS.10LBA20CP101 | 17163 | 低压主蒸汽母管压力1 | MPa | float32
N1DCS.10LBA20CP102 | 17164 | 低压主蒸汽母管压力2 | MPa | float32
N1DCS.10LBA20CPX2 | 17165 | 低压主蒸汽母管压力（2选后） |  | float32
N1DCS.10LBA20CT301 | 17166 | 低压主汽母管温度 | ℃ | float32
N1DCS.10LBA20CT302 | 17167 | 低压主汽母管疏水门前壁温 | ℃ | float32
N1DCS.10LBA20CT303 | 17168 | 低压主汽母管疏水门后壁温 | ℃ | float32
N1DCS.10LBA20CT304 | 17169 | 低压主汽门前疏水门前壁温 | ℃ | float32
N1DCS.10LBA20CT305 | 17170 | 低压主汽门前疏水门后壁温 | ℃ | float32
N1DCS.10LBB10CP101 | 17171 | 高温再热蒸汽压力1 | MPa | float32
N1DCS.10LBB10CP102 | 17172 | 高温再热蒸汽压力2 | MPa | float32
N1DCS.10LBB10CPX2 | 17173 | 高温再热蒸汽压力（2选后） |  | float32
N1DCS.10LBB10CT301 | 17174 | 高温再热蒸汽温度 | ℃ | float32
N1DCS.10LBB10CT302 | 17175 | 中旁阀前疏水气动门前温度 | ℃ | float32
N1DCS.10LBB10CT303 | 17176 | 中旁阀前疏水气动门后温度 | ℃ | float32
N1DCS.10LBB10CT304 | 17177 | 高温再热蒸汽母管疏水门前温度 | ℃ | float32
N1DCS.10LBB10CT305 | 17178 | 高温再热蒸汽母管疏水门后温度 | ℃ | float32
N1DCS.10LBC10CP104 | 17179 | 高压缸排汽压力 | MPa | float32
N1DCS.10LBC10CP105 | 17180 | 冷再母管蒸汽压力 | MPa | float32
N1DCS.10LBC10CT303 | 17181 | 高压缸排汽管垂直管壁温 | ℃ | float32
N1DCS.10LBC10CT304 | 17182 | 冷再母管蒸汽温度 | ℃ | float32
N1DCS.10LBC10CT306 | 17183 | 高压缸排汽管下壁温 | ℃ | float32
N1DCS.10LBC10CT307 | 17184 | 高排逆止门后疏水门后管温度 | ℃ | float32
N1DCS.10LBC10CT308 | 17185 | 冷再冷段疏水门后管温度 | ℃ | float32
N1DCS.10LBH10CT301 | 17186 | 高排通风阀前疏水门后管温度 | ℃ | float32
N1DCS.10LEDAO01 | 17187 | 炉侧主汽温度 | % | float32
N1DCS.10LEDAO02 | 17188 | #1机转速 | % | float32
N1DCS.10LEDAO03 | 17189 | 无功功率 | % | float32
N1DCS.10LEDAO04 | 17190 | 机组负荷 | % | float32
N1DCS.10LEDAO05 | 17191 | 炉侧主汽压力 | % | float32
N1DCS.10MAL11CT301 | 17192 | 高压主汽门后疏水门前管壁温 | ℃ | float32
N1DCS.10MAL11CT302 | 17193 | 高压主汽门后疏水门后管壁温 | ℃ | float32
N1DCS.10MAL23CT301 | 17194 | 中压主汽门滤网疏水门后温度 |  | float32
N1DCS.10MAL26CT301 | 17195 | 中压调门疏水门后温度 |  | float32
N1DCS.10MAL65CT305 | 17196 | 高排逆止门前疏水门后管温度 | ℃ | float32
N1DCS.10MAN10AA101C | 17197 | 高旁阀阀位控制指令 | % | float32
N1DCS.10MAN10AA101P | 17198 | 高旁阀阀位反馈 | % | float32
N1DCS.10MAN10AA101SP | 17199 | 高旁压力设定偏置值 |  | float32
N1DCS.10MAN10AA102C | 17200 | 高旁减温水调节阀阀位控制指令 | % | float32
N1DCS.10MAN10AA102P | 17201 | 高旁减温水调节阀阀位反馈 | % | float32
N1DCS.10MAN10CP101 | 17202 | 高旁阀后蒸汽压力1 | MPa | float32
N1DCS.10MAN10CP102 | 17203 | 高旁阀后蒸汽压力2 | MPa | float32
N1DCS.10MAN10CP103 | 17204 | 高旁减温水压力 | MPa | float32
N1DCS.10MAN10CPX2 | 17205 | 高旁阀后蒸汽压力（2选后） |  | float32
N1DCS.10MAN10CT301 | 17206 | 高旁阀后蒸汽温度1 | ℃ | float32
N1DCS.10MAN10CT302 | 17207 | 高旁阀后蒸汽温度2 | ℃ | float32
N1DCS.10MAN10CTX2 | 17208 | 高旁阀后蒸汽温度（2选后） |  | float32
N1DCS.10MAN10GH001PT | 17209 | 高旁阀油站油压 | MPa | float32
N1DCS.10MAN20AA101C | 17210 | 中旁阀阀位控制指令 | % | float32
N1DCS.10MAN20AA101P | 17211 | 中旁阀阀位反馈 | % | float32
N1DCS.10MAN20AA101SP | 17212 | 中旁压力设定偏置值 |  | float32
N1DCS.10MAN20AA101SP1 | 17213 | Ovation Control Builder |  | float32
N1DCS.10MAN20CP101 | 17214 | 中旁阀后蒸汽压力1 | MPa | float32
N1DCS.10MAN20CP102 | 17215 | 中旁阀后蒸汽压力2 | MPa | float32
N1DCS.10MAN20CPX2 | 17216 | 中旁阀后蒸汽压力（2选后） |  | float32
N1DCS.10MAN20CT301 | 17217 | 中旁阀后蒸汽温度1 | ℃ | float32
N1DCS.10MAN20CT302 | 17218 | 中旁阀后蒸汽温度2 | ℃ | float32
N1DCS.10MAN20CTX2 | 17219 | 中旁阀后蒸汽温度（2选后） |  | float32
N1DCS.10MAN20GH001PT | 17220 | 中旁阀油站油压 | MPa | float32
N1DCS.10MAP10AA101C | 17221 | 低旁阀阀位控制指令 | % | float32
N1DCS.10MAP10AA101P | 17222 | 低旁阀阀位反馈 | % | float32
N1DCS.10MAP10AA101SP | 17223 | 低旁压力设定偏置值 |  | float32
N1DCS.10MAP10AA101SP1 | 17224 | Ovation Control Builder |  | float32
N1DCS.10MAP10CP101 | 17225 | 低旁阀后蒸汽压力1 | MPa | float32
N1DCS.10MAP10CP102 | 17226 | 低旁阀后蒸汽压力2 | MPa | float32
N1DCS.10MAP10CPX2 | 17227 | 低旁阀后蒸汽压力（2选后） |  | float32
N1DCS.10MAP10CT301 | 17228 | 低旁阀前疏水门前温度 | ℃ | float32
N1DCS.10MAP10CT302 | 17229 | 低旁阀前疏水门后温度 | ℃ | float32
N1DCS.10MAP10CT303 | 17230 | 低旁阀后蒸汽温度1 | ℃ | float32
N1DCS.10MAP10CT304 | 17231 | 低旁阀后蒸汽温度2 | ℃ | float32
N1DCS.10MAP10CTX2 | 17232 | 低旁阀后蒸汽温度（2选后） |  | float32
N1DCS.10MBY10CE901YQ01 | 17233 | #2机实际负荷-ACTIVE POWER | MW | float32
N1DCS.10MBY10CS901YQ01 | 17234 | #2机实际转速 | Hz | float32
N1DCS.10MBY10DE010YQ01 | 17235 | #2机负荷设定值 | MW | float32
N1DCS.10MBY10DE010YQ02 | 17236 | #2机负荷设定参考 |  | float32
N1DCS.10MBY10DS010YQ01 | 17237 | #2机频率偏差 |  | float32
N1DCS.10MBY10DT040YQ01 | 17238 | IGV实际开度 |  | float32
N1DCS.10MBY10DU050YQ01 | 17239 | #2调频前修正指令 | MW | float32
N1DCS.10MBY10DU062 | 17240 | #2机燃烧负荷设定 |  | float32
N1DCS.10MBY10FT010YQ01 | 17241 | #2机透平排气温度TETC（计算值） | C | float32
N1DCS.10MBY10FT010YQ02 | 17242 | 燃机压气机进口温度 | C | float32
N1DCS.10MKA02CE901 | 17243 | #1发电机实际功率 | MW | float32
N1DCS.10MKA10FA103 | 17244 | #1机频率偏差 |  | float32
N1DCS.10MYA01CS118 | 17245 | #1机实际转速 |  | float32
N1DCS.10MYA01CS901C | 17246 | #1机实际转速 | rpm | float32
N1DCS.D1P1B1L1C9 | 17247 | TC温度补偿点 | C | float32
N1DCS.D1P1B2L8C9 | 17248 | TC温度补偿点 | C | float32
N1DCS.D1P1B3L1C9 | 17249 | TC温度补偿点 | C | float32
N1DCS.D1P1B4L8C9 | 17250 | TC温度补偿点 | C | float32
N1DCS.GTLOAD | 17251 | #2机实际负荷-ACTIVE POWER |  | float32
N1DCS.HIGBYPSPRSSET | 17252 | 高旁压力设定值 |  | float32
N1DCS.HIGBYPSPRSSET_TOUT | 17253 | 高旁压力设定值跟踪值 |  | float32
N1DCS.HPDSHTEMSP | 17254 | 高旁温度设定值 |  | float32
N1DCS.INTBYPSPRSSET | 17255 | 中旁压力设定值 |  | float32
N1DCS.INTBYPSPRSSET_TOUT | 17256 | 中旁压力设定跟踪值值 |  | float32
N1DCS.LOWBYPSPRSSET | 17257 | 低旁压力设定值 |  | float32
N1DCS.LOWBYPSPRSSET_TOUT | 17258 | 低旁设定值跟踪 |  | float32
N1DCS.STLOAD | 17259 | #1机实际负荷 |  | float32
N1DCS.TOTALMW | 17260 | 第一套机组实际总负荷 |  | float32
N1DCS.10CJA01DP100FX | 17261 | 高压压力设定值（匹配燃机负荷 |  | float32
N1DCS.10CJA01DP100SP | 17262 | 高压压力偏置值 |  | float32
N1DCS.10CJA01DP200FX | 17263 | 中压压力设定值（匹配燃机负荷 |  | float32
N1DCS.10CJA01DP200SP | 17264 | 中压压力偏置值 |  | float32
N1DCS.10CJA01DP300FX | 17265 | 低压压力设定值（匹配燃机负荷 |  | float32
N1DCS.10CJA01DP300SP | 17266 | 低压压力偏置值 |  | float32
N1DCS.10CJA01DP300_DCS | 17267 | 低压主蒸汽压力设定值 |  | float32
N1DCS.10MBY10CE901YQ01_SUM | 17268 | #2机当月启动时间 |  | float32
N1DCS.10MBY10CE901YQ01_SUM2 | 17269 | #2机年启动时间 |  | float32
N1DCS.10MBY10CE901YQ01_SUM3 | 17270 | #2机单次启动时间 |  | float32
N1DCS.10MBY10CE901YQ01_SUM4 | 17271 | #2机运行时间 |  | float32
N1DCS.10MBY10CE901YQ01_SUM5 | 17272 | #2机点火运行时间 |  | float32
N1DCS.10MBY10CE901YQ01A | 17273 | #2机实际负荷-ACTIVE POWER |  | float32
N1DCS.10MKA01CE903_PEL_SUM | 17274 | #1机月启动时间 |  | float32
N1DCS.10MKA01CE903_PEL_SUM2 | 17275 | #1机年启动时间 |  | float32
N1DCS.10MKA01CE903_PEL_SUM3 | 17276 | #1机单次启动时间 |  | float32
N1DCS.ACTLOADDMD1 | 17277 | 第一套机组总负荷设定值 |  | float32
N1DCS.ACTLOADDMDT | 17278 | 第一套机组总负荷设定值跟踪值 |  | float32
N1DCS.COLDMODE | 17279 | 冷态启动次数 |  | float32
N1DCS.CPRESSINTEM | 17280 | 燃机压气机进口温度 |  | float32
N1DCS.DCS_HPFLOW1 | 17281 | 高压主蒸汽流量（计算后） |  | float32
N1DCS.DCS_IPFLOW1 | 17282 | 中压主蒸汽流量（计算后） |  | float32
N1DCS.DCS_IP_BP_D_PRESS1 | 17283 | 中旁阀后蒸汽压力（2选后） |  | float32
N1DCS.DCS_IP_BP_POS1 | 17284 | 中旁阀阀位反馈 |  | float32
N1DCS.DCS_IP_BP_U_PRESS1 | 17285 | 高温再热蒸汽压力（2选后） |  | float32
N1DCS.DCSETSFO | 17286 | #1机ETS跳闸首出（打包点的位号) |  | float32
N1DCS.GEFIRING | 17287 | Ovation Control Builder |  | float32
N1DCS.GEN_NUM | 17288 | #1机月启动次数 |  | float32
N1DCS.GEN_NUM2 | 17289 | #1机年启动次数 |  | float32
N1DCS.GT_NUM | 17290 | #2机月启动次数 |  | float32
N1DCS.GT_NUM2 | 17291 | #2机年启动次数 |  | float32
N1DCS.GTALRFB | 17292 | #2机负荷设定参考 |  | float32
N1DCS.GTFIRE | 17293 | Ovation Control Builder |  | float32
N1DCS.GTFRQ | 17294 | #2机频率偏差 |  | float32
N1DCS.GTGENLOAD1 | 17295 | #2发电机有功功率 |  | float32
N1DCS.GTLOADDMD1 | 17296 | #2机负荷设定值 |  | float32
N1DCS.GTLOADMAX | 17297 | #2机负荷设定上限值 |  | float32
N1DCS.GTLOADMAX1 | 17298 | #2机负荷设定上限值 |  | float32
N1DCS.GTLOADMIN | 17299 | #2机负荷设定下限值 |  | float32
N1DCS.GTLOADMIN1 | 17300 | #2机负荷设定下限值 |  | float32
N1DCS.GTLOADP1 | 17301 | #2机负荷百分比 |  | float32
N1DCS.GTLOADSET | 17302 | #2机实际负荷设定值 |  | float32
N1DCS.GTLOADSP1 | 17303 | Ovation Control Builder |  | float32
N1DCS.GTNUM | 17304 | #2机启动次数 |  | float32
N1DCS.GTSPEED1 | 17305 | #2机实际转速 |  | float32
N1DCS.GTTETC | 17306 | #2机透平排气温度TETC（计算值） |  | float32
N1DCS.HIGBYPS | 17307 | Ovation Control Builder |  | float32
N1DCS.HOTMODE | 17308 | 热态启动次数 |  | float32
N1DCS.HPBT_SPO | 17309 | Ovation Control Builder |  | float32
N1DCS.HPBTBIAS | 17310 | 高旁出口温度偏置值 |  | float32
N1DCS.IGVPOS | 17311 | IGV阀位反馈 |  | float32
N1DCS.KDELTAF | 17312 | #2机调频修正前指令 |  | float32
N1DCS.LOADMAX1 | 17313 | 第一套机组总负荷设定上限值 |  | float32
N1DCS.LOADMIN1 | 17314 | 第一套机组总负荷设定下限值 |  | float32
N1DCS.LOADRATE_DCS | 17315 | 第一套机组总负荷变化率 |  | float32
N1DCS.LOADSP1 | 17316 | Ovation Control Builder |  | float32
N1DCS.LTPLKD | 17317 | 汽机冷态启动高旁阀最小阀位 |  | float32
N1DCS.RB_TPFO | 17318 | 燃机RB首出 |  | float32
N1DCS.STTRIPFO | 17319 | 汽机跳闸首出(对应打包点的位号) |  | float32
N1DCS.TOTALSTMFLW | 17320 | #1机组过热器出口蒸汽总流量 |  | float32
N1DCS.TRIPNUM | 17321 | #1跳闸次数 |  | float32
N1DCS.TURBLOAD | 17322 | #1发电机有功功率 |  | float32
N1DCS.TURBSPEED | 17323 | #1机实际转速 |  | float32
N1DCS.WARMMODE | 17324 | 温态启动次数 |  | float32
N1DCS.ZSFWKD | 17325 | 高旁阀最小阀位开度 |  | float32
N1DCS.10CJA06DU001 | 17326 | 遥控目标负荷设定1 |  | float32
N1DCS.10LBD20AC001C | 17327 | 冷再供热减温减压阀阀位控制指令 | % | float32
N1DCS.10LBD20AC001P | 17328 | 冷再供热减温减压调阀阀位反馈 | % | float32
N1DCS.10LBD20AC001SP | 17329 | 冷再供热减温减压调阀压力设定值 |  | float32
N1DCS.10LBD20CP101 | 17330 | 冷再供热蒸汽压力 | MPa | float32
N1DCS.10LBD20CP103 | 17331 | 冷再供热减温减压器后蒸汽压力 | MPa | float32
N1DCS.10LBD20CT301 | 17332 | 冷再供热蒸汽温度 | ℃ | float32
N1DCS.10LBD20CT302 | 17333 | 冷再供热气动疏水门后温度 | ℃ | float32
N1DCS.10LBD20CT303 | 17334 | 冷再供热减温减压器后蒸汽温度 | ℃ | float32
N1DCS.10LBD40AC001C | 17335 | 热再供热减温减压阀阀位控制指令 | % | float32
N1DCS.10LBD40AC001P | 17336 | 热再供热减温减压调阀阀位反馈 | % | float32
N1DCS.10LBD40AC001SP | 17337 | 热再供热减温减压器压力设定值 |  | float32
N1DCS.10LBD40CP101 | 17338 | 热再供热蒸汽压力 | MPa | float32
N1DCS.10LBD40CP105 | 17339 | 热再供热减温减压器后蒸汽压力 | MPa | float32
N1DCS.10LBD40CT301 | 17340 | 热再供热蒸汽温度 | ℃ | float32
N1DCS.10LBD40CT302 | 17341 | 热再供热气动疏水门后温度 | ℃ | float32
N1DCS.10LBD40CT303 | 17342 | 热再供热减温减压器后蒸汽温度 | ℃ | float32
N1DCS.10LBD60CF101 | 17343 | #1机组抽汽供热母管蒸汽流量 | kPa | float32
N1DCS.10LBD60CP101 | 17344 | 第1套机组抽汽供热母管蒸汽压力 | MPa | float32
N1DCS.10LBD60CT301 | 17345 | 第1套机组抽汽供热母管蒸汽温度 | ℃ | float32
N1DCS.10LBD80CT301 | 17346 | 冷再抽汽至预留中压管疏水门后温 | ℃ | float32
N1DCS.10LBG11AC001C | 17347 | 高排至辅汽母管减压器控制指令 | % | float32
N1DCS.10LBG11AC001P | 17348 | 高排至辅汽母管减压器阀位反馈 | % | float32
N1DCS.10LBG11AC001SP | 17349 | 高排至辅汽母管减压器压力设定值 |  | float32
N1DCS.10LCE11AA101C | 17350 | 凝结水至辅汽减温水调阀控制指令 | % | float32
N1DCS.10LCE11AA101P | 17351 | 凝结水至辅汽减温水调阀阀位指令 | % | float32
N1DCS.10LCE11AA101SP | 17352 | 凝结水至辅汽减温水调阀温度设定 |  | float32
N1DCS.10LCE12AA101C | 17353 | 低旁减温水调阀阀位控制指令 | % | float32
N1DCS.10LCE12AA101P | 17354 | 低旁减温水调阀阀位反馈 | % | float32
N1DCS.10LCE12AA101SP | 17355 | 低旁减温水调阀温度设定值 |  | float32
N1DCS.10LCE12CP101 | 17356 | 低旁减温水压力 | MPa | float32
N1DCS.10LCE13AA101C | 17357 | 凝结水至热再减温水调阀控制指令 | % | float32
N1DCS.10LCE13AA101P | 17358 | 凝结水至热再减温水调阀阀位指令 | % | float32
N1DCS.10LCE13AA101SP | 17359 | 凝结水至热再减温水调阀温度设定 |  | float32
N1DCS.10LCE15AA101C | 17360 | 中旁减温水调阀阀位控制指令 | % | float32
N1DCS.10LCE15AA101P | 17361 | 中旁减温水调阀阀位反馈 | % | float32
N1DCS.10LCE15AA101SP | 17362 | 中旁减温水调阀温度设定值 |  | float32
N1DCS.10LCE15CP101 | 17363 | 中旁减温水压力 | MPa | float32
N1DCS.10LCE17AA101C | 17364 | 凝结水至冷再减温水调阀控制指令 | % | float32
N1DCS.10LCE17AA101P | 17365 | 凝结水至冷再减温水调阀阀位指令 | % | float32
N1DCS.10LCE17AA101SP | 17366 | 凝结水至冷再减温水调阀温度设定 |  | float32
N1DCS.10LCE18AA152C | 17367 | 凝结水至轴封减温水调阀控制指令 | % | float32
N1DCS.10LCE18AA152P | 17368 | 凝结水至轴封减温水调阀阀位反馈 | % | float32
N1DCS.10LCE18AA152SP | 17369 | 凝结水至轴封减温水调阀温度设定 |  | float32
N1DCS.10LCE19AA101C | 17370 | 凝汽器水幕喷水调节阀控制指令 | % | float32
N1DCS.10LCE19AA101P | 17371 | 凝汽器水幕喷水调节阀阀位反馈 | % | float32
N1DCS.10LCE19AA101SP | 17372 | 凝汽器水幕喷水调节阀温度设定 |  | float32
N1DCS.10LCE20AA101C | 17373 | 疏水扩容器喷水调节阀控制指令 | % | float32
N1DCS.10LCE20AA101P | 17374 | 疏水扩容器喷水调节阀阀位反馈 | % | float32
N1DCS.10LCE20AA101SP | 17375 | 疏水扩容器喷水调节阀温度设定 |  | float32
N1DCS.10LCM40CL101 | 17376 | 疏水扩容器液位 | mm | float32
N1DCS.10LCM40CT301 | 17377 | 疏水扩容器温度 | ℃ | float32
N1DCS.10MAC10CP104 | 17378 | 中压排汽压力 | MPa | float32
N1DCS.10MAL22CT301 | 17379 | 高压缸气动疏水门1后温度 | ℃ | float32
N1DCS.10MAL22CT303 | 17380 | 高压缸气动疏水门2后温度 | ℃ | float32
N1DCS.10MAL22CT304 | 17381 | 高压缸气动疏水门3后温度 | ℃ | float32
N1DCS.10MAL35CT301 | 17382 | 中压缸气动疏水门1后温度 | ℃ | float32
N1DCS.10MAL36CT301 | 17383 | 中压缸气动疏水门2后温度 | ℃ | float32
N1DCS.10MAL50CT301 | 17384 | 低压缸气动疏水门后温度 | ℃ | float32
N1DCS.10MAW10AA151C | 17385 | 辅汽至高中压轴封调阀控制指令 | % | float32
N1DCS.10MAW10AA151P | 17386 | 辅汽至高中压轴封调阀阀位反馈 | % | float32
N1DCS.10MAW10AA151SP | 17387 | 辅汽至高中压轴封调阀压力设定值 |  | float32
N1DCS.10MAW13AA151C | 17388 | 辅汽至低压轴封调阀控制指令 | % | float32
N1DCS.10MAW13AA151P | 17389 | 辅汽至低压轴封调阀阀位反馈 | % | float32
N1DCS.10MAW13AA151SP | 17390 | 辅汽至低压轴封调阀压力设定值 |  | float32
N1DCS.10MAW20CP101 | 17391 | 高中压轴封供汽母管压力1 | KPa | float32
N1DCS.10MAW20CP102 | 17392 | 高中压轴封供汽母管压力2 | KPa | float32
N1DCS.10MAW20CT301 | 17393 | 高中压轴封供汽母管高压侧温度 | ℃ | float32
N1DCS.10MAW20CT303 | 17394 | 高中压轴封供汽母管中压侧温度 | ℃ | float32
N1DCS.10MAW24CP101 | 17395 | 低压轴封供汽母管压力1 | KPa | float32
N1DCS.10MAW24CP102 | 17396 | 低压轴封供汽母管压力2 | KPa | float32
N1DCS.10MAW24CT301 | 17397 | 低压轴封供汽母管温度1 | ℃ | float32
N1DCS.10MAW24CT302 | 17398 | 低压轴封供汽母管温度2 | ℃ | float32
N1DCS.10MAW50AA151C | 17399 | 轴封供汽溢流气动调节阀控制指令 | % | float32
N1DCS.10MAW50AA151P | 17400 | 轴封供汽溢流气动调节阀阀位反馈 | % | float32
N1DCS.10MAW50AA151SP | 17401 | 轴封供汽溢流调节阀压力设定值 |  | float32
N1DCS.10MAW65CT301 | 17402 | 高压缸轴封漏汽温度 | ℃ | float32
N1DCS.10MAW80CP101 | 17403 | 轴封冷却器蒸汽进口压力 | KPa | float32
N1DCS.10MBY10DU061 | 17404 | #2机燃烧负荷设定2 |  | float32
N1DCS.10MKA10FA102 | 17405 | 协调控制负荷设定3 |  | float32
N1DCS.10MYA01DG010C | 17406 | 负荷参考 |  | float32
N1DCS.AUXSTMSYS_SEQSTSTEP | 17407 | 辅汽系统启顺控步号 |  | float32
N1DCS.AUXSTMSYS_SEQSTTIME1 | 17408 | 辅汽系统启顺控第1步剩余时间 |  | float32
N1DCS.AUXSTMSYS_SEQSTTIME2 | 17409 | 辅汽系统启顺控第2步剩余时间 |  | float32
N1DCS.AUXSTMSYS_SEQSTTIME3 | 17410 | 辅汽系统启顺控第3步剩余时间 |  | float32
N1DCS.D2P1B1L3C9 | 17411 | TC温度补偿点 | C | float32
N1DCS.D2P1B2L6C9 | 17412 | TC温度补偿点 | C | float32
N1DCS.D2P1B3L3C9 | 17413 | TC温度补偿点 | C | float32
N1DCS.GLDSTMSYS_SEQSPSTEP | 17414 | 轴封系统停顺控步号 |  | float32
N1DCS.GLDSTMSYS_SEQSPTIME1 | 17415 | 轴封系统停顺控第1步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSPTIME2 | 17416 | 轴封系统停顺控第2步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSPTIME3 | 17417 | 轴封系统停顺控第3步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSPTIME4 | 17418 | 轴封系统停顺控第4步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSPTIME5 | 17419 | 轴封系统停顺控第5步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSTSTEP | 17420 | 轴封系统启顺控步号 |  | float32
N1DCS.GLDSTMSYS_SEQSTTIME1 | 17421 | 轴封系统启顺控第1步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSTTIME2 | 17422 | 轴封系统启顺控第2步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSTTIME3 | 17423 | 轴封系统启顺控第3步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSTTIME4 | 17424 | 轴封系统启顺控第4步剩余时间 |  | float32
N1DCS.GLDSTMSYS_SEQSTTIME5 | 17425 | 轴封系统启顺控第5步剩余时间 |  | float32
N1DCS.HGLDHDRPRS | 17426 | 高中压轴封供汽母管压力(2选后） |  | float32
N1DCS.HGLDHDRTEM | 17427 | 高中压轴封供汽母管温度(2选后） |  | float32
N1DCS.IPBTBIAS | 17428 | 中旁出口温度偏置值 |  | float32
N1DCS.J0LBG10CPX2 | 17429 | 辅汽母管压力 |  | float32
N1DCS.J0LBG10CTX2 | 17430 | 辅汽母管温度 |  | float32
N1DCS.LOWGLDSPLPRS | 17431 | 低压轴封供汽母管压力(2选后） |  | float32
N1DCS.LOWGLDSPLTEM | 17432 | 低压轴封供汽母管温度(2选后） |  | float32
N1DCS.LPBTBIAS | 17433 | 低旁出口温度偏置值 |  | float32
N1DCS.10LCM40CL101I | 17434 | 疏水扩容器液位（计算后） |  | float32
N1DCS.10MAA50CT | 17435 | 高压缸金属温度(50%)(2选后) |  | float32
N1DCS.10MAB50CT | 17436 | 中压缸金属温度(50%)(2选后) |  | float32
N1DCS.10MAY01EP144 | 17437 | 高压转子温度(3选后) |  | float32
N1DCS.10MAY01EP145 | 17438 | 中压转子温度(3选后) |  | float32
N1DCS.IPBT_SPO | 17439 | Ovation Control Builder |  | float32
N1DCS.LPBT_SP | 17440 | Ovation Control Builder |  | float32
N1DCS.10LBG21GH001PO | 17441 | #1机轴封电加热器功率 |  | float32
N1DCS.10LBG21GH001TC | 17442 | #1机轴封电加热器出口温度设定值 |  | float32
N1DCS.10LBG21GH001TO | 17443 | #1机轴封电加热器出口温度 |  | float32
N1DCS.10LCA11CP101 | 17444 | #1凝结水泵进口滤网差压 | KPa | float32
N1DCS.10LCA11CT301 | 17445 | #1凝结水泵进口温度 | ℃ | float32
N1DCS.10LCA11CY101 | 17446 | #1凝结水泵轴承振动（X方向） |  | float32
N1DCS.10LCA11CY102 | 17447 | #1凝结水泵轴承振动（Y方向） |  | float32
N1DCS.10LCA20CF101 | 17448 | 凝结水泵出口母管流量 | t/h | float32
N1DCS.10LCA20CF101_CAL | 17449 | 凝结水泵出口母管流量（计算后) |  | float32
N1DCS.10LCA20CF102 | 17450 | 凝结水泵供余热锅炉流量 | t/h | float32
N1DCS.10LCA20CP101 | 17451 | 凝结水泵出口母管压力 | MPa | float32
N1DCS.10LCA20CP102 | 17452 | #1机除铁过滤器出口母管压力 | MPa | float32
N1DCS.10LCA20CP103 | 17453 | #1机轴封冷却器出口压力（水侧） | MPa | float32
N1DCS.10LCA20CT301 | 17454 | 凝结水泵出口母管温度 | ℃ | float32
N1DCS.10LCA20CT302 | 17455 | #1机轴封冷却器出口温度（水侧） | ℃ | float32
N1DCS.10LCA30AA101C | 17456 | 凝结水再循环气动调节阀控制指令 | % | float32
N1DCS.10LCA30AA101P | 17457 | 凝结水再循环气动调节阀阀位反馈 | % | float32
N1DCS.10LCA30AA101SP | 17458 | 凝结水再循环气动调节阀设定值 |  | float32
N1DCS.10LCB11AP001I | 17459 | #1凝结水泵电机电流 | A | float32
N1DCS.10LCB11CT301 | 17460 | #1凝结水泵电机线圈温度1 | ℃ | float32
N1DCS.10LCB11CT302 | 17461 | #1凝结水泵电机线圈温度2 | ℃ | float32
N1DCS.10LCB11CT303 | 17462 | #1凝结水泵电机线圈温度3 | ℃ | float32
N1DCS.10LCB11CT304 | 17463 | #1凝结水泵电机线圈温度4 | ℃ | float32
N1DCS.10LCB11CT305 | 17464 | #1凝结水泵电机线圈温度5 | ℃ | float32
N1DCS.10LCB11CT306 | 17465 | #1凝结水泵电机线圈温度6 | ℃ | float32
N1DCS.10LCB11CT307 | 17466 | #1凝结水泵电机下轴承温度 | ℃ | float32
N1DCS.10LCB11CT308 | 17467 | #1凝结水泵电机上轴承温度 | ℃ | float32
N1DCS.10LCB11CT309 | 17468 | #1凝结水泵轴承温度 | ℃ | float32
N1DCS.10LCB11GH001C | 17469 | #1凝结水泵永磁调速器控制指令 | % | float32
N1DCS.10LCB11GH001FT | 17470 | #1凝结水泵冷却水流量 |  | float32
N1DCS.10LCB11GH001P | 17471 | #1凝结水泵永磁控制器阀位反馈 | % | float32
N1DCS.10LCB11GH001S | 17472 | #1凝结水泵转速 |  | float32
N1DCS.10LCB11GH001SP | 17473 | #1凝结水泵永磁调速器压力设定值 |  | float32
N1DCS.10LCB11GH001T1 | 17474 | #1凝结水泵输出端轴承温度 |  | float32
N1DCS.10LCB11GH001T2 | 17475 | #1凝结水泵轴承油箱温度 |  | float32
N1DCS.10LCB11GH001T3 | 17476 | #1凝结水泵冷却水回水温度 |  | float32
N1DCS.10LCE16AA101C | 17477 | 闭式水箱补水电动调节阀控制指令 | % | float32
N1DCS.10LCE16AA101P | 17478 | 闭式水箱补水电动调节阀阀位反馈 | % | float32
N1DCS.10LCE16CF101 | 17479 | 闭式水箱正常补水流量 | t/h | float32
N1DCS.10LCR10AA101C | 17480 | 凝汽器正常补水调节阀控制指令 | % | float32
N1DCS.10LCR10AA101P | 17481 | 凝汽器正常补水调节阀阀位反馈 | % | float32
N1DCS.10LCR10AA101SP | 17482 | 凝汽器正常补水调节阀液位设定值 |  | float32
N1DCS.10LCR10AA102C | 17483 | 凝汽器启动补水调节阀控制指令 | % | float32
N1DCS.10LCR10AA102P | 17484 | 凝汽器启动补水调节阀阀位反馈 | % | float32
N1DCS.10LCR10AA102SP | 17485 | 凝汽器启动补水调节阀液位设定值 |  | float32
N1DCS.10LCR10CF101 | 17486 | 凝汽器补水流量 | t/h | float32
N1DCS.10LCR10CP101 | 17487 | 凝结水补水压力 | MPa | float32
N1DCS.10LDB10CP101 | 17488 | #1机凝结水除铁过滤器进出口差压 | MPa | float32
N1DCS.10LDK10CP101 | 17489 | #1机凝结水除铁过滤器进口压力 | MPa | float32
N1DCS.10MAC01CP101 | 17490 | 低压缸喷水过滤器差压 | KPa | float32
N1DCS.10MAG10CL101 | 17491 | 凝汽器热井液位1 | mm | float32
N1DCS.10MAG10CL102 | 17492 | 凝汽器热井液位2 | mm | float32
N1DCS.10MAG10CL103 | 17493 | 凝汽器热井液位3 | mm | float32
N1DCS.10PAB11AA001P | 17494 | 凝汽器循环水进水#1电动门门位反 | % | float32
N1DCS.10PAB11CP101 | 17495 | 凝汽器循环水管#1进水压力 |  | float32
N1DCS.10PAB11CT301 | 17496 | 凝汽器循环水管#1进水温度 | ℃ | float32
N1DCS.10PAB21CP101 | 17497 | 凝汽器循环水管#1出水压力 | MPa | float32
N1DCS.10PAB21CT301 | 17498 | 凝汽器循环水管#1出水温度 | ℃ | float32
N1DCS.10PAB40CL101 | 17499 | 凝泵坑液位 | mm | float32
N1DCS.10PAH11CP101 | 17500 | #1收球网进出口差压 | KPa | float32
N1DCS.10PCB10CP101 | 17501 | 开式水电动过滤器进出口差压 | kPa | float32
N1DCS.10PCB11AP001I | 17502 | #1开式冷却水泵电机电流 | A | float32
N1DCS.10PCB11CP101 | 17503 | 开式冷却水泵出口母管压力 | Mpa | float32
N1DCS.10PCB11CT301 | 17504 | #1开式水泵电机定子线圈温度1 | ℃ | float32
N1DCS.10PCB11CT302 | 17505 | #1开式水泵电机定子线圈温度2 | ℃ | float32
N1DCS.10PCB11CT303 | 17506 | #1开式水泵电机定子线圈温度3 | ℃ | float32
N1DCS.10PCB11CT304 | 17507 | #1开式水泵电机定子线圈温度4 | ℃ | float32
N1DCS.10PCB11CT305 | 17508 | #1开式水泵电机定子线圈温度5 | ℃ | float32
N1DCS.10PCB11CT306 | 17509 | #1开式水泵电机定子线圈温度6 | ℃ | float32
N1DCS.10PCB11CT307 | 17510 | #1开式水泵电机驱动端轴承温度 | ℃ | float32
N1DCS.10PCB11CT308 | 17511 | #1开式水泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10PCB11CT309 | 17512 | #1开式水泵驱动端轴承温度 | ℃ | float32
N1DCS.10PCB11CT310 | 17513 | #1开式水泵非驱动端轴承温度 | ℃ | float32
N1DCS.10PCB21CT301 | 17514 | #1热交换器开式冷却水进口温度 | ℃ | float32
N1DCS.10PCB31AA001P | 17515 | #1热交换器开式水出口门门位反馈 | % | float32
N1DCS.10PCB31CT302 | 17516 | #1热交换器开式冷却水出口温度 | ℃ | float32
N1DCS.10PGA10CL101SP | 17517 | 闭式水箱补水电动调阀液位设定值 |  | float32
N1DCS.10PGA11AP001I | 17518 | #1闭式水泵电机电流 | A | float32
N1DCS.10PGA11CP101 | 17519 | #1闭式水泵进口滤网差压 | kPa | float32
N1DCS.10PGA11CT301 | 17520 | #1闭式水泵电机定子线圈温度1 | ℃ | float32
N1DCS.10PGA11CT302 | 17521 | #1闭式水泵电机定子线圈温度2 | ℃ | float32
N1DCS.10PGA11CT303 | 17522 | #1闭式水泵电机定子线圈温度3 | ℃ | float32
N1DCS.10PGA11CT304 | 17523 | #1闭式水泵电机定子线圈温度4 | ℃ | float32
N1DCS.10PGA11CT305 | 17524 | #1闭式水泵电机定子线圈温度5 | ℃ | float32
N1DCS.10PGA11CT306 | 17525 | #1闭式水泵电机定子线圈温度6 | ℃ | float32
N1DCS.10PGA11CT307 | 17526 | #1闭式水泵电机驱动端轴承温度 | ℃ | float32
N1DCS.10PGA11CT308 | 17527 | #1闭式水泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10PGA11CT311 | 17528 | #1闭式水泵驱动端轴承温度 | ℃ | float32
N1DCS.10PGA11CT312 | 17529 | #1闭式水泵非驱动端轴承温度 | ℃ | float32
N1DCS.10PGA21CT302 | 17530 | #1热交换器闭式冷却水出水温度 | ℃ | float32
N1DCS.CIRWTR_SEQSTSTEP | 17531 | 开式水系统启顺控步号 |  | float32
N1DCS.CIRWTR_SEQSTTIME1 | 17532 | 开式水系统启顺控第1步剩余时间 |  | float32
N1DCS.CIRWTR_SEQSTTIME2 | 17533 | 开式水系统启顺控第2步剩余时间 |  | float32
N1DCS.CIRWTR_SEQSTTIME3 | 17534 | 开式水系统启顺控第3步剩余时间 |  | float32
N1DCS.CLCLGPMPA_SEQSPSTEP | 17535 | #1闭式水泵停顺控步号 |  | float32
N1DCS.CLCLGPMPA_SEQSPTIME1 | 17536 | #1闭式水泵停顺控第1步剩余时间 |  | float32
N1DCS.CLCLGPMPA_SEQSPTIME2 | 17537 | #1闭式水泵停顺控第2步剩余时间 |  | float32
N1DCS.CLCLGPMPA_SEQSPTIME3 | 17538 | #1闭式水泵停顺控第3步剩余时间 |  | float32
N1DCS.CLCLGPMPA_SEQSTSTEP | 17539 | #1闭式水泵启顺控步号 |  | float32
N1DCS.CLCLGPMPA_SEQSTTIME1 | 17540 | #1闭式水泵启顺控第1步剩余时间 |  | float32
N1DCS.CLCLGPMPA_SEQSTTIME2 | 17541 | #1闭式水泵启顺控第2步剩余时间 |  | float32
N1DCS.CLCLGPMPA_SEQSTTIME3 | 17542 | #1闭式水泵启顺控第3步剩余时间 |  | float32
N1DCS.CLCLGPMPA_SEQSTTIME4 | 17543 | #1闭式水泵启顺控第4步剩余时间 |  | float32
N1DCS.CLCLGPMPA_SEQSTTIME5 | 17544 | #1闭式水泵启顺控第5步剩余时间 |  | float32
N1DCS.CLCLGPMPA_TPFO | 17545 | #1闭式水泵跳闸首出(打包点位号 |  | float32
N1DCS.CLCLGWTR_SEQSTSTEP | 17546 | 闭式水系统启顺控步号 |  | float32
N1DCS.CLCLGWTR_SEQSTTIME1 | 17547 | 闭式水系统启顺控第1步剩余时间 |  | float32
N1DCS.CLCLGWTR_SEQSTTIME2 | 17548 | 闭式水系统启顺控第2步剩余时间 |  | float32
N1DCS.CLCLGWTR_SEQSTTIME3 | 17549 | 闭式水系统启顺控第3步剩余时间 |  | float32
N1DCS.CLCLGWTR_SEQSTTIME4 | 17550 | 闭式水系统启顺控第4步剩余时间 |  | float32
N1DCS.CLCLGWTR_SEQSTTIME5 | 17551 | 闭式水系统启顺控第5步剩余时间 |  | float32
N1DCS.CLCLGWTR_SEQSTTIME6 | 17552 | 闭式水系统启顺控第6步剩余时间 |  | float32
N1DCS.CLCLGWTR_SEQSTTIME7 | 17553 | 闭式水系统启顺控第7步剩余时间 |  | float32
N1DCS.CNDHWLVL | 17554 | 凝汽器热井液位（3选后） |  | float32
N1DCS.CNDPA_SEQSPTIME1 | 17555 | #1凝结水泵停顺控第1步剩余时间 |  | float32
N1DCS.CNDPA_SEQSPTIME2 | 17556 | #1凝结水泵停顺控第2步剩余时间 |  | float32
N1DCS.CNDPA_SEQSPTIME3 | 17557 | #1凝结水泵停顺控第3步剩余时间 |  | float32
N1DCS.CNDPA_SEQSTTIME1 | 17558 | #1凝结水泵启顺控第1步剩余时间 |  | float32
N1DCS.CNDPA_SEQSTTIME2 | 17559 | #1凝结水泵启顺控第2步剩余时间 |  | float32
N1DCS.CNDPA_SEQSTTIME3 | 17560 | #1凝结水泵启顺控第3步剩余时间 |  | float32
N1DCS.CNDPAPA_SEQSPSTEP | 17561 | #1凝结水泵停顺控步号 |  | float32
N1DCS.CNDPAPA_SEQSTSTEP | 17562 | #1凝结水泵启顺控步号 |  | float32
N1DCS.CNDPMPA_TPFO | 17563 | #1凝结水泵跳闸首出(打包点位号 |  | float32
N1DCS.CNDWTRSYS_SEQSTREYSTEP | 17564 | 凝结水系统准备顺控步号 |  | float32
N1DCS.CNDWTRSYS_SEQSTREYTIME1 | 17565 | 凝结水系统准备顺控1步剩余时间 |  | float32
N1DCS.CNDWTRSYS_SEQSTREYTIME2 | 17566 | 凝结水系统准备顺控2步剩余时间 |  | float32
N1DCS.CNDWTRSYS_SEQSTREYTIME3 | 17567 | 凝结水系统准备顺控3步剩余时间 |  | float32
N1DCS.CNDWTRSYS_SEQSTREYTIME4 | 17568 | 凝结水系统准备顺控4步剩余时间 |  | float32
N1DCS.CNDWTRSYS_SEQSTREYTIME5 | 17569 | 凝结水系统准备顺控5步剩余时间 |  | float32
N1DCS.CNDWTRSYS_SEQSTSTEP | 17570 | 凝结水系统启顺控步号 |  | float32
N1DCS.CNDWTRSYS_SEQSTTIME1 | 17571 | 凝结水系统启顺控第1步剩余时间 |  | float32
N1DCS.CNDWTRSYS_SEQSTTIME2 | 17572 | 凝结水系统启顺控第2步剩余时间 |  | float32
N1DCS.CNDWTRSYS_SEQSTTIME3 | 17573 | 凝结水系统启顺控第3步剩余时间 |  | float32
N1DCS.CNDWTRSYS_SEQSTTIME4 | 17574 | 凝结水系统启顺控第4步剩余时间 |  | float32
N1DCS.CNSRLVL | 17575 | 凝汽器热井液位（3选后） |  | float32
N1DCS.OPNCIRPMPA_SEQSPSTEP | 17576 | #1开式水泵停顺控步号 |  | float32
N1DCS.OPNCIRPMPA_SEQSPTIME1 | 17577 | #1开式水泵停顺控第1步剩余时间 |  | float32
N1DCS.OPNCIRPMPA_SEQSPTIME2 | 17578 | #1开式水泵停顺控第2步剩余时间 |  | float32
N1DCS.OPNCIRPMPA_SEQSTSTEP | 17579 | #1开式水泵启顺控步号 |  | float32
N1DCS.OPNCIRPMPA_SEQSTTIME1 | 17580 | #1开式水泵启顺控第1步剩余时间 |  | float32
N1DCS.OPNCIRPMPA_SEQSTTIME2 | 17581 | #1开式水泵启顺控第2步剩余时间 |  | float32
N1DCS.OPNCIRPMPA_SEQSTTIME3 | 17582 | #1开式水泵启顺控第3步剩余时间 |  | float32
N1DCS.OPNCIRPMPA_TPFO | 17583 | #1开式水泵跳闸首出(打包点位号 |  | float32
N1DCS.OPNCIRWTR_SEQSTSTEP | 17584 | 开式水系统启顺控步号 |  | float32
N1DCS.OPNCIRWTR_SEQSTTIME1 | 17585 | 开式水系统启顺控第1步剩余时间 |  | float32
N1DCS.OPNCIRWTR_SEQSTTIME2 | 17586 | 开式水系统启顺控第2步剩余时间 |  | float32
N1DCS.OPNCIRWTR_SEQSTTIME3 | 17587 | 开式水系统启顺控第3步剩余时间 |  | float32
N1DCS.OPNCIRWTR_SEQSTTIME4 | 17588 | 开式水系统启顺控第4步剩余时间 |  | float32
N1DCS.RBBRBALLA_SEQSPSTEP | 17589 | 凝汽器#1胶球收球顺控步号 |  | float32
N1DCS.RBBRBALLA_SEQSPTIME1 | 17590 | #1胶球收球顺控第1步剩余时间 |  | float32
N1DCS.RBBRBALLA_SEQSPTIME2 | 17591 | #1胶球收球顺控第2步剩余时间 |  | float32
N1DCS.RBBRBALLA_SEQSPTIME3 | 17592 | #1胶球收球顺控第3步剩余时间 |  | float32
N1DCS.RBBRBALLA_SEQSPTIME4 | 17593 | #1胶球收球顺控第4步剩余时间 |  | float32
N1DCS.RBBRBALLA_SEQSTSTEP | 17594 | 凝汽器#1胶球投球顺控步号 |  | float32
N1DCS.RBBRBALLA_SEQSTTIME1 | 17595 | #1胶球投球顺控第1步剩余时间 |  | float32
N1DCS.RBBRBALLA_SEQSTTIME2 | 17596 | #1胶球投球顺控第2步剩余时间 |  | float32
N1DCS.RBBRBALLA_SEQSTTIME3 | 17597 | #1胶球投球顺控第3步剩余时间 |  | float32
N1DCS.RBBRBALLA_SEQSTTIME4 | 17598 | #1胶球投球顺控第4步剩余时间 |  | float32
N1DCS.10LCA20CF101_SUM | 17599 | 凝结水泵出口母管流量累计值 |  | float32
N1DCS.10LCA20CF102I | 17600 | 凝结水泵供余热锅炉流量(计算后) |  | float32
N1DCS.10LCR10CF101_CAL | 17601 | 凝汽器补水流量(计算后) |  | float32
N1DCS.10LCR10CF101_SUM | 17602 | 凝汽器补水流量累计值 |  | float32
N1DCS.10MAW20CTL | 17603 | 轴封供汽母管高中压侧温度(2选后 |  | float32
N1DCS.10PCB10GH501RUN_SV | 17604 | 开式水电动过滤器清洗时间 |  | float32
N1DCS.10PCB10GH501SET_SV | 17605 | 开式水电动过滤器定时时间 |  | float32
N1DCS.JQSQAT | 17606 | #1胶球系统收球时间 |  | float32
N1DCS.JQSQAT1 | 17607 | #1胶球系统投球时间 |  | float32
N1DCS.10LCA12CP101 | 17608 | #2凝结水泵进口滤网差压 | KPa | float32
N1DCS.10LCA12CT301 | 17609 | #2凝结水泵进口温度 | ℃ | float32
N1DCS.10LCA12CY101 | 17610 | #2凝结水泵轴承振动(X方向) |  | float32
N1DCS.10LCA12CY102 | 17611 | #2凝结水泵轴承振动(Y方向) |  | float32
N1DCS.10LCB12AP002I | 17612 | #2凝结水泵电机电流 | A | float32
N1DCS.10LCB12CT301 | 17613 | #2凝结水泵电机定子线圈温度1 | ℃ | float32
N1DCS.10LCB12CT302 | 17614 | #2凝结水泵电机定子线圈温度2 | ℃ | float32
N1DCS.10LCB12CT303 | 17615 | #2凝结水泵电机定子线圈温度3 | ℃ | float32
N1DCS.10LCB12CT304 | 17616 | #2凝结水泵电机定子线圈温度4 | ℃ | float32
N1DCS.10LCB12CT305 | 17617 | #2凝结水泵电机定子线圈温度5 | ℃ | float32
N1DCS.10LCB12CT306 | 17618 | #2凝结水泵电机定子线圈温度6 | ℃ | float32
N1DCS.10LCB12CT307 | 17619 | #2凝结水泵电机下轴承温度 | ℃ | float32
N1DCS.10LCB12CT308 | 17620 | #2凝结水泵电机上轴承温度 | ℃ | float32
N1DCS.10LCB12CT309 | 17621 | #2凝结水泵轴承温度 | ℃ | float32
N1DCS.10LCB12GH001C | 17622 | #2凝结水泵永磁调速器控制指令 | % | float32
N1DCS.10LCB12GH001FT | 17623 | #2凝结水泵冷却水流量 |  | float32
N1DCS.10LCB12GH001FT2 | 17624 | #2凝结水泵轴承油流量 |  | float32
N1DCS.10LCB12GH001LT | 17625 | #2凝结水泵水箱液位 |  | float32
N1DCS.10LCB12GH001P | 17626 | #2凝结水泵永磁控制器阀位反馈 | % | float32
N1DCS.10LCB12GH001S | 17627 | #2凝结水泵转速 |  | float32
N1DCS.10LCB12GH001T1 | 17628 | #2凝结水泵输出端轴承温度 |  | float32
N1DCS.10LCB12GH001T2 | 17629 | #2凝结水泵轴承油箱温度 |  | float32
N1DCS.10LCB12GH001T3 | 17630 | #2凝结水泵冷却水回水温度 |  | float32
N1DCS.10PAB12AA001P | 17631 | 凝汽器循环水进水#2电动门门位反 | % | float32
N1DCS.10PAB12CP101 | 17632 | 凝汽器循环水管#2进水压力 |  | float32
N1DCS.10PAB12CT301 | 17633 | 凝汽器循环水管#2进水温度 | ℃ | float32
N1DCS.10PAB22CP101 | 17634 | 凝汽器循环水管#2出水压力 | MPa | float32
N1DCS.10PAB22CT301 | 17635 | 凝汽器循环水管#2出水温度 | ℃ | float32
N1DCS.10PAH12CP101 | 17636 | #2收球网进出口差压 | KPa | float32
N1DCS.10PCB11AP002I | 17637 | #2开式冷却水泵电机电流 | A | float32
N1DCS.10PCB11CT311 | 17638 | #2开式水泵电机定子线圈温度1 | ℃ | float32
N1DCS.10PCB11CT312 | 17639 | #2开式水泵电机定子线圈温度2 | ℃ | float32
N1DCS.10PCB11CT313 | 17640 | #2开式水泵电机定子线圈温度3 | ℃ | float32
N1DCS.10PCB11CT314 | 17641 | #2开式水泵电机定子线圈温度4 | ℃ | float32
N1DCS.10PCB11CT315 | 17642 | #2开式水泵电机定子线圈温度5 | ℃ | float32
N1DCS.10PCB11CT316 | 17643 | #2开式水泵电机定子线圈温度6 | ℃ | float32
N1DCS.10PCB11CT317 | 17644 | #2开式水泵电机驱动端轴承温度 | ℃ | float32
N1DCS.10PCB11CT318 | 17645 | #2开式水泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10PCB11CT319 | 17646 | #2开式水泵驱动端轴承温度 | ℃ | float32
N1DCS.10PCB11CT320 | 17647 | #2开式水泵非驱动端轴承温度 | ℃ | float32
N1DCS.10PCB22CT301 | 17648 | #2热交换器开式冷却水进口温度 | ℃ | float32
N1DCS.10PCB32AA001P | 17649 | #2热交换器开式水出口门门位反馈 | % | float32
N1DCS.10PCB32CT302 | 17650 | #2热交换器开式冷却水出口温度 | ℃ | float32
N1DCS.10PGA10CL101 | 17651 | 闭式水箱液位 | mm | float32
N1DCS.10PGA12AP001I | 17652 | #2闭式水泵电机电流 | A | float32
N1DCS.10PGA12CP101 | 17653 | #2闭式水泵进口滤网差压 | kPa | float32
N1DCS.10PGA12CT301 | 17654 | #2闭式水泵电机定子线圈温度1 | ℃ | float32
N1DCS.10PGA12CT302 | 17655 | #2闭式水泵电机定子线圈温度2 | ℃ | float32
N1DCS.10PGA12CT303 | 17656 | #2闭式水泵电机定子线圈温度3 | ℃ | float32
N1DCS.10PGA12CT304 | 17657 | #2闭式水泵电机定子线圈温度4 | ℃ | float32
N1DCS.10PGA12CT305 | 17658 | #2闭式水泵电机定子线圈温度5 | ℃ | float32
N1DCS.10PGA12CT306 | 17659 | #2闭式水泵电机定子线圈温度6 | ℃ | float32
N1DCS.10PGA12CT307 | 17660 | #2闭式水泵电机驱动端轴承温度 | ℃ | float32
N1DCS.10PGA12CT308 | 17661 | #2闭式水泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10PGA12CT311 | 17662 | #2闭式水泵驱动端轴承温度 | ℃ | float32
N1DCS.10PGA12CT312 | 17663 | #2闭式水泵非驱动端轴承温度 | ℃ | float32
N1DCS.10PGA20CP101 | 17664 | 闭式水泵出口母管压力 | Mpa | float32
N1DCS.10PGA20CP102 | 17665 | 热交热器闭式冷却水出口母管压力 | Mpa | float32
N1DCS.10PGA20CT301 | 17666 | 热交换器闭式冷却水进口母管温度 | ℃ | float32
N1DCS.10PGA22CT302 | 17667 | #2热交换器闭式冷却水出水温度 | ℃ | float32
N1DCS.10PGA26AA101C | 17668 | #2发电机定冷水进水调阀控制指令 | % | float32
N1DCS.10PGA26AA101P | 17669 | #2发电机定冷水进水调阀阀位反馈 | % | float32
N1DCS.10PGA26AA101SP | 17670 | #2发电机定冷水进水调阀温度设定 |  | float32
N1DCS.10PGA26AA101TEMP | 17671 | 临时温度测点 |  | float32
N1DCS.10PGA26AA102C | 17672 | #2发电机氢冷器进水调阀控制指令 | % | float32
N1DCS.10PGA26AA102P | 17673 | #2发电机氢冷器进水调阀阀位反馈 | % | float32
N1DCS.10PGA26AA102SP | 17674 | #2发电机氢冷器进水调阀温度设定 |  | float32
N1DCS.10PGA26AA103C | 17675 | #2机滑油冷却器进水调阀控制指令 | % | float32
N1DCS.10PGA26AA103P | 17676 | #2机滑油冷却器进水调阀阀位反馈 | % | float32
N1DCS.10PGA26AA103SP | 17677 | #2机滑油冷却器进水调阀温度设定 |  | float32
N1DCS.10PGA32AA101C | 17678 | #1机EH油冷却器进水调阀控制指令 | % | float32
N1DCS.10PGA32AA101P | 17679 | #1机EH油冷却器进水调阀反馈反馈 | % | float32
N1DCS.10PGA32AA101SP | 17680 | #1机EH油冷却器进水调阀温度设定 |  | float32
N1DCS.10PGA32AA101TEMP | 17681 | 临时温度测点 |  | float32
N1DCS.10PGA33AA101C | 17682 | #1机滑油冷却器进水调阀控制指令 | % | float32
N1DCS.10PGA33AA101P | 17683 | #1机滑油冷却器进水调阀阀位反馈 | % | float32
N1DCS.10PGA33AA101SP | 17684 | #1机滑油冷却器进水调阀温度设定 |  | float32
N1DCS.10PGA34AA101C | 17685 | #1发电机空冷器进水调阀控制指令 | % | float32
N1DCS.10PGA34AA101P | 17686 | #1发电机空冷器进水调阀阀位反馈 | % | float32
N1DCS.10PGA34AA101SP | 17687 | #1发电机空冷器进水调阀温度设定 |  | float32
N1DCS.CLCLGPMPB_SEQSPSTEP | 17688 | #2闭式水泵停顺控步号 |  | float32
N1DCS.CLCLGPMPB_SEQSPTIME1 | 17689 | #2闭式水泵停顺控第1步剩余时间 |  | float32
N1DCS.CLCLGPMPB_SEQSPTIME2 | 17690 | #2闭式水泵停顺控第2步剩余时间 |  | float32
N1DCS.CLCLGPMPB_SEQSTSTEP | 17691 | #2闭式水泵启顺控步号 |  | float32
N1DCS.CLCLGPMPB_SEQSTTIME1 | 17692 | #2闭式水泵启顺控第1步剩余时间 |  | float32
N1DCS.CLCLGPMPB_SEQSTTIME2 | 17693 | #2闭式水泵启顺控第2步剩余时间 |  | float32
N1DCS.CLCLGPMPB_SEQSTTIME3 | 17694 | #2闭式水泵启顺控第3步剩余时间 |  | float32
N1DCS.CLCLGPMPB_TPFO | 17695 | #2闭式水泵跳闸首出(打包点位号 |  | float32
N1DCS.CNDPAPB_SEQSPSTEP | 17696 | #2凝结水泵停顺控步号 |  | float32
N1DCS.CNDPAPB_SEQSTSTEP | 17697 | #2凝结水泵启顺控步号 |  | float32
N1DCS.CNDPB_SEQSPTIME1 | 17698 | #2凝结水泵停顺控第1步剩余时间 |  | float32
N1DCS.CNDPB_SEQSPTIME2 | 17699 | #2凝结水泵停顺控第2步剩余时间 |  | float32
N1DCS.CNDPB_SEQSPTIME3 | 17700 | #2凝结水泵停顺控第3步剩余时间 |  | float32
N1DCS.CNDPB_SEQSTTIME1 | 17701 | #2凝结水泵启顺控第1步剩余时间 |  | float32
N1DCS.CNDPB_SEQSTTIME2 | 17702 | #2凝结水泵启顺控第2步剩余时间 |  | float32
N1DCS.CNDPB_SEQSTTIME3 | 17703 | #2凝结水泵启顺控第3步剩余时间 |  | float32
N1DCS.CNDPB_SEQSTTIME4 | 17704 | #2凝结水泵启顺控第4步剩余时间 |  | float32
N1DCS.CNDPMPB_TPFO | 17705 | #2凝结水泵跳闸首出(打包点位号 |  | float32
N1DCS.OPNCIRPMPB_SEQSPSTEP | 17706 | #2开式水泵停顺控步号 |  | float32
N1DCS.OPNCIRPMPB_SEQSPTIME1 | 17707 | #2开式水泵停顺控第1步剩余时间 |  | float32
N1DCS.OPNCIRPMPB_SEQSPTIME2 | 17708 | #2开式水泵停顺控第2步剩余时间 |  | float32
N1DCS.OPNCIRPMPB_SEQSTSTEP | 17709 | #2开式水泵启顺控步号 |  | float32
N1DCS.OPNCIRPMPB_SEQSTTIME1 | 17710 | #2开式水泵启顺控第1步剩余时间 |  | float32
N1DCS.OPNCIRPMPB_SEQSTTIME2 | 17711 | #2开式水泵启顺控第2步剩余时间 |  | float32
N1DCS.OPNCIRPMPB_SEQSTTIME3 | 17712 | #2开式水泵启顺控第3步剩余时间 |  | float32
N1DCS.OPNCIRPMPB_TPFO | 17713 | #2开式水泵跳闸首出(打包点位号 |  | float32
N1DCS.RBBRBALLB_SEQSPSTEP | 17714 | 凝汽器#2胶球收球顺控步号 |  | float32
N1DCS.RBBRBALLB_SEQSPTIME1 | 17715 | #2胶球收球顺控第1步剩余时间 |  | float32
N1DCS.RBBRBALLB_SEQSPTIME2 | 17716 | #2胶球收球顺控第2步剩余时间 |  | float32
N1DCS.RBBRBALLB_SEQSPTIME3 | 17717 | #2胶球收球顺控第3步剩余时间 |  | float32
N1DCS.RBBRBALLB_SEQSPTIME4 | 17718 | #2胶球收球顺控第4步剩余时间 |  | float32
N1DCS.RBBRBALLB_SEQSTSTEP | 17719 | 凝汽器#2胶球投球顺控步号 |  | float32
N1DCS.RBBRBALLB_SEQSTTIME1 | 17720 | #2胶球投球顺控第1步剩余时间 |  | float32
N1DCS.RBBRBALLB_SEQSTTIME2 | 17721 | #2胶球投球顺控第2步剩余时间 |  | float32
N1DCS.RBBRBALLB_SEQSTTIME3 | 17722 | #2胶球投球顺控第3步剩余时间 |  | float32
N1DCS.RBBRBALLB_SEQSTTIME4 | 17723 | #2胶球投球顺控第4步剩余时间 |  | float32
N1DCS.10LCB12GH001LTMM | 17724 | #2凝结水泵冷却水箱液位(计算后) |  | float32
N1DCS.10LCB12GH001SP | 17725 | #2凝结水泵永磁调速器压力设定值 |  | float32
N1DCS.10MKA30CT | 17726 | #1发电机进风温度（8选后） |  | float32
N1DCS.10PGA33AA101SPO | 17727 | #1机滑油冷却器进水调阀温度设定 |  | float32
N1DCS.HXCTQ_SEQSPSTEP | 17728 | 除铁过滤器停顺控 |  | float32
N1DCS.HXCTQ_SEQSPTIME1 | 17729 | 除铁过滤器停顺控第1步剩余时间 |  | float32
N1DCS.HXCTQ_SEQSPTIME2 | 17730 | 除铁过滤器停顺控第2步剩余时间 |  | float32
N1DCS.HXCTQ_SEQSPTIME3 | 17731 | 除铁过滤器停顺控第3步剩余时间 |  | float32
N1DCS.HXCTQ_SEQSTSTEP | 17732 | 除铁过滤器启顺控 |  | float32
N1DCS.HXCTQ_SEQSTTIME1 | 17733 | 除铁过滤器启顺控第1步剩余时间 |  | float32
N1DCS.HXCTQ_SEQSTTIME2 | 17734 | 除铁过滤器启顺控第2步剩余时间 |  | float32
N1DCS.HXCTQ_SEQSTTIME3 | 17735 | 除铁过滤器启顺控第3步剩余时间 |  | float32
N1DCS.HXCTQ_SEQSTTIME4 | 17736 | 除铁过滤器启顺控第4步剩余时间 |  | float32
N1DCS.HXCTQ_SEQSTTIME5 | 17737 | 除铁过滤器启顺控第5步剩余时间 |  | float32
N1DCS.HXCTQ_SP1 | 17738 | Ovation Control Builder |  | float32
N1DCS.HXCTQ_SP2 | 17739 | Ovation Control Builder |  | float32
N1DCS.HXCTQCY | 17740 | 凝结水出口母管与除铁器进口压差 |  | float32
N1DCS.JQSQBT | 17741 | #2胶球系统收球时间 |  | float32
N1DCS.JQSQBT1 | 17742 | #2胶球系统投球时间 |  | float32
N1DCS.10MAG01GH001C | 17743 | 凝汽器电导率 |  | float32
N1DCS.10MAG10CP104 | 17744 | 凝汽器真空4 | KPa | float32
N1DCS.10MAG10CP105 | 17745 | 凝汽器真空5 | KPa | float32
N1DCS.10MAG10CT301 | 17746 | 凝汽器温度 | ℃ | float32
N1DCS.10MAJ21AP001I | 17747 | #1真空泵电机电流 | A | float32
N1DCS.10MAJ21CL501 | 17748 | #1真空泵汽水分离器 | mm | float32
N1DCS.10MAJ21CP101 | 17749 | #1真空泵进口手动门前绝对压力 | KPa | float32
N1DCS.10MAJ21CP102 | 17750 | #1真空泵进口蝶阀前后差压 | KPa | float32
N1DCS.10MAJ21CT301 | 17751 | #1真空泵电机定子线圈温度1 | ℃ | float32
N1DCS.10MAJ21CT302 | 17752 | #1真空泵电机定子线圈温度2 | ℃ | float32
N1DCS.10MAJ21CT303 | 17753 | #1真空泵电机定子线圈温度3 | ℃ | float32
N1DCS.10MAJ21CT304 | 17754 | #1真空泵电机定子线圈温度4 | ℃ | float32
N1DCS.10MAJ21CT305 | 17755 | #1真空泵电机定子线圈温度5 | ℃ | float32
N1DCS.10MAJ21CT306 | 17756 | #1真空泵电机定子线圈温度6 | ℃ | float32
N1DCS.10MAJ21CT307 | 17757 | #1真空泵电机前轴承温度 | ℃ | float32
N1DCS.10MAJ21CT308 | 17758 | #1真空泵电机后轴承温度 | ℃ | float32
N1DCS.10MAJ21CT311 | 17759 | #1真空泵前轴承温度 |  | float32
N1DCS.10MAJ21CT312 | 17760 | #1真空泵后轴承温度 |  | float32
N1DCS.10MAJ23AA101C | 17761 | 蒸汽喷射装置压力调节阀控制指令 | % | float32
N1DCS.10MAJ23AA101P | 17762 | 蒸汽喷射装置压力调节阀阀位指令 | % | float32
N1DCS.10MAJ23AA101SP | 17763 | 蒸汽喷射装置压力调节阀压力设定 |  | float32
N1DCS.10MAJ23CF101 | 17764 | 蒸汽喷射装置压力调节阀后流量 | kg/h | float32
N1DCS.10MAJ23CP101 | 17765 | 蒸汽喷射装置压力调节阀前压力 | MPa | float32
N1DCS.10MAJ23CP102 | 17766 | 蒸汽喷射装置换热器汽侧出口压力 | KPa | float32
N1DCS.10MAJ23CP103 | 17767 | 蒸汽喷射装置压力调节阀后压力 |  | float32
N1DCS.10MAJ23CT301 | 17768 | 蒸汽喷射装置进口辅汽温度 | ℃ | float32
N1DCS.10MAJ23CT302 | 17769 | 蒸汽喷射装置进气温度 | ℃ | float32
N1DCS.10MAJ23CT303 | 17770 | 蒸汽喷射装置换热器供水温度 | ℃ | float32
N1DCS.10MAJ23CT304 | 17771 | 蒸汽喷射装置换热器回水温度 | ℃ | float32
N1DCS.10MAJ23CT305 | 17772 | 蒸汽喷射装置换热器汽侧出口温度 | ℃ | float32
N1DCS.10MAV21AP021I | 17773 | #1润滑油泵电机电流 | A | float32
N1DCS.10MAV31AP001I | 17774 | #1顶轴油泵电机电流 | A | float32
N1DCS.10MAV31CP101 | 17775 | #1顶轴油泵出口压力 | MPa | float32
N1DCS.10MAV82AN001I | 17776 | #1润滑油风机电流 | A | float32
N1DCS.10MAX01AP001I | 17777 | #1EH油泵电机电流 | A | float32
N1DCS.10MAX01AP011I | 17778 | #1EH油循环泵电机电流 | A | float32
N1DCS.10PAB11AA002CT | 17779 | #1循环水泵出口液控蝶阀油箱油温 | ℃ | float32
N1DCS.10PAB11AA002P1 | 17780 | #1循环水泵出口液控阀蓄能器压力 | MPa | float32
N1DCS.10PAB11AA002P2 | 17781 | #1循环水泵出口液控蝶阀A口油压 | MPa | float32
N1DCS.10PAB11AA002P3 | 17782 | #1循环水泵出口液控蝶阀B口油压 | MPa | float32
N1DCS.10PAB11CL102 | 17783 | #1旋转滤网前水位 | m | float32
N1DCS.10PAB11CL103 | 17784 | #1旋转滤网后水位 | m | float32
N1DCS.10PAB43CP101 | 17785 | #1循环水泵冷却水进口母管压力 | MPa | float32
N1DCS.10PAC11AP001I | 17786 | #1循环水泵电机电流 |  | float32
N1DCS.10PAC11CP101 | 17787 | #1循环水泵出口压力 |  | float32
N1DCS.10PAC11CS101 | 17788 | #1循环水泵转速 |  | float32
N1DCS.10PAC11CT301 | 17789 | #1循环水泵电机“U”绕组温度1 | ℃ | float32
N1DCS.10PAC11CT302 | 17790 | #1循环水泵电机“U”绕组温度2 | ℃ | float32
N1DCS.10PAC11CT303 | 17791 | #1循环水泵电机“V”绕组温度1 | ℃ | float32
N1DCS.10PAC11CT304 | 17792 | #1循环水泵电机“V”绕组温度2 | ℃ | float32
N1DCS.10PAC11CT305 | 17793 | #1循环水泵电机“W”绕组温度1 | ℃ | float32
N1DCS.10PAC11CT306 | 17794 | #1循环水泵电机“W”绕组温度2 | ℃ | float32
N1DCS.10PAC11CT307 | 17795 | #1循环水泵电机导轴瓦温度1 | ℃ | float32
N1DCS.10PAC11CT308 | 17796 | #1循环水泵电机导轴瓦温度2 | ℃ | float32
N1DCS.10PAC11CT309 | 17797 | #1循环水泵电机推力瓦温度1 | ℃ | float32
N1DCS.10PAC11CT310 | 17798 | #1循环水泵电机推力瓦温度2 | ℃ | float32
N1DCS.10PAC11CT311 | 17799 | #1循环水泵电机下轴承温度 | ℃ | float32
N1DCS.10PAC11CY101 | 17800 | #1循环水泵垂直方向振动 |  | float32
N1DCS.10PAC11CY102 | 17801 | #1循环水泵水平方向振动 |  | float32
N1DCS.10PAC12AP001I | 17802 | #2循环水泵电机电流 |  | float32
N1DCS.CIRPMPA_TPFO | 17803 | #1循环水泵跳闸首出(打包点位号) |  | float32
N1DCS.CIRWTRPMPA_SEQSPSTEP | 17804 | #1循环水泵停顺控步号 |  | float32
N1DCS.CIRWTRPMPA_SEQSPTIME1 | 17805 | #1循环水泵停顺控第1步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSPTIME2 | 17806 | #1循环水泵停顺控第2步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSPTIME3 | 17807 | #1循环水泵停顺控第3步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSPTIME4 | 17808 | #1循环水泵停顺控第4步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSTSTEP | 17809 | #1循环水泵启顺控步号 |  | float32
N1DCS.CIRWTRPMPA_SEQSTTIME1 | 17810 | #1循环水泵启顺控第1步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSTTIME2 | 17811 | #1循环水泵启顺控第2步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSTTIME3 | 17812 | #1循环水泵启顺控第3步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSTTIME4 | 17813 | #1循环水泵启顺控第4步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSTTIME5 | 17814 | #1循环水泵启顺控第5步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSTTIME6 | 17815 | #1循环水泵启顺控第6步剩余时间 |  | float32
N1DCS.CIRWTRPMPA_SEQSTTIME7 | 17816 | #1循环水泵启顺控第7步剩余时间 |  | float32
N1DCS.CIRWTRSYS_SEQSTSTEP | 17817 | 循环水系统启顺控步号 |  | float32
N1DCS.CIRWTRSYS_SEQSTTIME1 | 17818 | 循环水系统启顺控第1步剩余时间 |  | float32
N1DCS.CIRWTRSYS_SEQSTTIME2 | 17819 | 循环水系统启顺控第2步剩余时间 |  | float32
N1DCS.CIRWTRSYS_SEQSTTIME3 | 17820 | 循环水系统启顺控第3步剩余时间 |  | float32
N1DCS.CIRWTRSYS_SEQSTTIME4 | 17821 | 循环水系统启顺控第4步剩余时间 |  | float32
N1DCS.CNSRVACM | 17822 | 凝汽器真空（2选后） |  | float32
N1DCS.EHOILSYS_SEQSPSTEP | 17823 | EH油系统停顺控步号 |  | float32
N1DCS.EHOILSYS_SEQSPTIME1 | 17824 | EH油系统停顺控第1步剩余时间 |  | float32
N1DCS.EHOILSYS_SEQSPTIME2 | 17825 | EH油系统停顺控第2步剩余时间 |  | float32
N1DCS.EHOILSYS_SEQSTSTEP | 17826 | EH油系统启顺控步号 |  | float32
N1DCS.EHOILSYS_SEQSTTIME1 | 17827 | EH油系统启顺控第1步剩余时间 |  | float32
N1DCS.EHOILSYS_SEQSTTIME2 | 17828 | EH油系统启顺控第2步剩余时间 |  | float32
N1DCS.EHOILSYS_SEQSTTIME3 | 17829 | EH油系统启顺控第3步剩余时间 |  | float32
N1DCS.LUBOILBOXTEM | 17830 | #1机润滑油箱温度 |  | float32
N1DCS.ROTFLTRA_SEQSTSTEP | 17831 | #1旋转滤网冲洗顺控 |  | float32
N1DCS.ROTFLTRA_SEQSTTIME1 | 17832 | #1旋转滤网冲洗顺控第1步剩余时? |  | float32
N1DCS.ROTFLTRA_SEQSTTIME2 | 17833 | #1旋转滤网冲洗顺控第2步剩余时? |  | float32
N1DCS.ROTFLTRA_SEQSTTIME3 | 17834 | #1旋转滤网冲洗顺控第3步剩余时? |  | float32
N1DCS.ROTFLTRAFRBHDL | 17835 | #1旋转滤网前后液位差 |  | float32
N1DCS.TURBOILSYS_SEQSTSTEP | 17836 | #1机润滑油系统启顺控步号 |  | float32
N1DCS.TURBOILSYS_SEQSTTIME1 | 17837 | #1机滑油系统启顺控1步剩余时间 |  | float32
N1DCS.TURBOILSYS_SEQSTTIME2 | 17838 | #1机滑油系统启顺控2步剩余时间 |  | float32
N1DCS.TURBOILSYS_SEQSTTIME3 | 17839 | #1机滑油系统启顺控3步剩余时间 |  | float32
N1DCS.TURBOILSYS_SEQSTTIME4 | 17840 | #1机滑油系统启顺控4步剩余时间 |  | float32
N1DCS.TURBOILSYS_SEQSTTIME5 | 17841 | #1机滑油系统启顺控5步剩余时间 |  | float32
N1DCS.VACMPMPA_SEQSPSTEP | 17842 | #1真空泵停顺控步号 |  | float32
N1DCS.VACMPMPA_SEQSPTIME1 | 17843 | #1真空泵停顺控第1步剩余时间 |  | float32
N1DCS.VACMPMPA_SEQSPTIME2 | 17844 | #1真空泵停顺控第2步剩余时间 |  | float32
N1DCS.VACMPMPA_SEQSTSTEP | 17845 | #1真空泵启顺控步号 |  | float32
N1DCS.VACMPMPA_SEQSTTIME1 | 17846 | #1真空泵启顺控第1步剩余时间 |  | float32
N1DCS.VACMPMPA_SEQSTTIME2 | 17847 | #1真空泵启顺控第2步剩余时间 |  | float32
N1DCS.VACMPMPA_SEQSTTIME3 | 17848 | #1真空泵启顺控第3步剩余时间 |  | float32
N1DCS.VACMPMPA_TPFO | 17849 | #1真空泵跳闸首出(打包点位号) |  | float32
N1DCS.VACMSYS_SEQSPSTEP | 17850 | 抽真空系统停顺控步号 |  | float32
N1DCS.VACMSYS_SEQSPTIME1 | 17851 | 抽真空系统停顺控第1步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSPTIME2 | 17852 | 抽真空系统停顺控第2步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSPTIME3 | 17853 | 抽真空系统停顺控第3步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSPTIME4 | 17854 | 抽真空系统停顺控第4步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSPTIME5 | 17855 | 抽真空系统停顺控第5步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSTSTEP | 17856 | 抽真空系统启顺控步号 |  | float32
N1DCS.VACMSYS_SEQSTTIME1 | 17857 | 抽真空系统启顺控第1步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSTTIME2 | 17858 | 抽真空系统启顺控第2步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSTTIME3 | 17859 | 抽真空系统启顺控第3步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSTTIME4 | 17860 | 抽真空系统启顺控第4步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSTTIME5 | 17861 | 抽真空系统启顺控第5步剩余时间 |  | float32
N1DCS.VACMSYS_SEQSTTIME6 | 17862 | 抽真空系统启顺控第6步剩余时间 |  | float32
N1DCS.RHYCKMGYLBD | 17863 | Ovation Control Builder |  | float32
N1DCS.ZQPSSYS_SEQSPSTEP | 17864 | 蒸汽喷射装置停顺控步号 |  | float32
N1DCS.ZQPSSYS_SEQSPTIME1 | 17865 | 蒸汽喷射装置停顺控1步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSPTIME2 | 17866 | 蒸汽喷射装置停顺控2步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSPTIME3 | 17867 | 蒸汽喷射装置停顺控3步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSPTIME4 | 17868 | 蒸汽喷射装置停顺控4步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSPTIME5 | 17869 | 蒸汽喷射装置停顺控5步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSTSTEP | 17870 | 蒸汽喷射装置启顺控步号 |  | float32
N1DCS.ZQPSSYS_SEQSTTIME1 | 17871 | 蒸汽喷射装置启顺控1步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSTTIME2 | 17872 | 蒸汽喷射装置启顺控2步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSTTIME3 | 17873 | 蒸汽喷射装置启顺控3步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSTTIME4 | 17874 | 蒸汽喷射装置启顺控4步剩余时间 |  | float32
N1DCS.ZQPSSYS_SEQSTTIME5 | 17875 | 蒸汽喷射装置启顺控5步剩余时间 |  | float32
N1DCS.10MAJ22AP001I | 17876 | #2真空泵电机电流 | A | float32
N1DCS.10MAJ22CL501 | 17877 | #2真空泵汽水分离器 |  | float32
N1DCS.10MAJ22CP101 | 17878 | #2真空泵进口手动门前绝对压力 | KPa | float32
N1DCS.10MAJ22CP102 | 17879 | #2真空泵进口蝶阀前后差压 | KPa | float32
N1DCS.10MAJ22CT301 | 17880 | #2真空泵电机定子线圈温度1 | ℃ | float32
N1DCS.10MAJ22CT302 | 17881 | #2真空泵电机定子线圈温度2 | ℃ | float32
N1DCS.10MAJ22CT303 | 17882 | #2真空泵电机定子线圈温度3 | ℃ | float32
N1DCS.10MAJ22CT304 | 17883 | #2真空泵电机定子线圈温度4 | ℃ | float32
N1DCS.10MAJ22CT305 | 17884 | #2真空泵电机定子线圈温度5 | ℃ | float32
N1DCS.10MAJ22CT306 | 17885 | #2真空泵电机定子线圈温度6 | ℃ | float32
N1DCS.10MAJ22CT307 | 17886 | #2真空泵电机前轴承温度 | ℃ | float32
N1DCS.10MAJ22CT308 | 17887 | #2真空泵电机后轴承温度 | ℃ | float32
N1DCS.10MAJ22CT311 | 17888 | #2真空泵前轴承温度 | ℃ | float32
N1DCS.10MAJ22CT312 | 17889 | #2真空泵后轴承温度 |  | float32
N1DCS.10MAV10CT301 | 17890 | #1机润滑油箱温度 | ℃ | float32
N1DCS.10MAV21AP022I | 17891 | #2润滑油泵电机电流 | A | float32
N1DCS.10MAV24AP001I | 17892 | 应急滑油泵电机电流 | A | float32
N1DCS.10MAV32AP001I | 17893 | #2顶轴油泵电机电流 | A | float32
N1DCS.10MAV32CP101 | 17894 | #2顶轴油泵出口压力 | MPa | float32
N1DCS.10MAV35CP101 | 17895 | 顶轴油母管压力 | MPa | float32
N1DCS.10MAV35CT301 | 17896 | 顶轴油母管温度 | ℃ | float32
N1DCS.10MAV42CT301 | 17897 | #1机润滑油温控阀后温度 | ℃ | float32
N1DCS.10MAV82AN002I | 17898 | #1机#2润滑油风机电流 | A | float32
N1DCS.10MAV82CP101 | 17899 | #1机润滑油风机进口压力 | KPa | float32
N1DCS.10MAX01AP002I | 17900 | #2EH油泵电机电流 | A | float32
N1DCS.10MAX01AP012I | 17901 | #2EH油循环泵电机电流 | A | float32
N1DCS.10MAX01CL101 | 17902 | #1机EH油箱液位 | mm | float32
N1DCS.10MAX01CT301 | 17903 | #1机EH油箱油温 | ℃ | float32
N1DCS.10MKA10CT301 | 17904 | #1发电机定子线圈温度1(5号槽) | ℃ | float32
N1DCS.10MKA10CT302 | 17905 | #1发电机定子线圈温度2(5号槽) | ℃ | float32
N1DCS.10MKA10CT303 | 17906 | #1发电机定子线圈温度1(6号槽) | ℃ | float32
N1DCS.10MKA10CT304 | 17907 | #1发电机定子线圈温度2(6号槽) | ℃ | float32
N1DCS.10MKA10CT305 | 17908 | #1发电机定子线圈温度1(14号槽) | ℃ | float32
N1DCS.10MKA10CT306 | 17909 | #1发电机定子线圈温度2(14号槽) | ℃ | float32
N1DCS.10MKA10CT307 | 17910 | #1发电机定子线圈温度1(15号槽) | ℃ | float32
N1DCS.10MKA10CT308 | 17911 | #1发电机定子线圈温度2(15号槽) | ℃ | float32
N1DCS.10MKA10CT309 | 17912 | #1发电机定子线圈温度1(23号槽) | ℃ | float32
N1DCS.10MKA10CT310 | 17913 | #1发电机定子线圈温度2(23号槽) | ℃ | float32
N1DCS.10MKA10CT311 | 17914 | #1发电机定子线圈温度1(24号槽) | ℃ | float32
N1DCS.10MKA10CT312 | 17915 | #1发电机定子线圈温度2(24号槽) | ℃ | float32
N1DCS.10MKA10CT313 | 17916 | #1发电机定子线圈温度1(32号槽) | ℃ | float32
N1DCS.10MKA10CT314 | 17917 | #1发电机定子线圈温度2(32号槽) | ℃ | float32
N1DCS.10MKA10CT315 | 17918 | #1发电机定子线圈温度1(33号槽) | ℃ | float32
N1DCS.10MKA10CT316 | 17919 | #1发电机定子线圈温度2(33号槽) | ℃ | float32
N1DCS.10MKA10CT317 | 17920 | #1发电机定子线圈温度1(41号槽) | ℃ | float32
N1DCS.10MKA10CT318 | 17921 | #1发电机定子线圈温度2(41号槽) | ℃ | float32
N1DCS.10MKA10CT319 | 17922 | #1发电机定子线圈温度1(42号槽) | ℃ | float32
N1DCS.10MKA10CT320 | 17923 | #1发电机定子线圈温度2(42号槽) | ℃ | float32
N1DCS.10MKA10CT321 | 17924 | #1发电机定子线圈温度1(50号槽) | ℃ | float32
N1DCS.10MKA10CT322 | 17925 | #1发电机定子线圈温度2(50号槽) | ℃ | float32
N1DCS.10MKA10CT323 | 17926 | #1发电机定子线圈温度1(51号槽) | ℃ | float32
N1DCS.10MKA10CT324 | 17927 | #1发电机定子线圈温度2(51号槽) | ℃ | float32
N1DCS.10MKA20CT301 | 17928 | #1发电机定子轭部温度1(2~3号槽) | ℃ | float32
N1DCS.10MKA20CT302 | 17929 | #1发电机定子轭部温度2(2~3号槽) | ℃ | float32
N1DCS.10MKA20CT303 | 17930 | #1发电机定子齿部温度1(2~3号槽) | ℃ | float32
N1DCS.10MKA20CT304 | 17931 | #1发电机定子齿部温度2(2~3号槽) | ℃ | float32
N1DCS.10MKA20CT305 | 17932 | #1发电机定子轭部温度1(26~27槽) | ℃ | float32
N1DCS.10MKA20CT306 | 17933 | #1发电机定子轭部温度2(26~27槽) | ℃ | float32
N1DCS.10MKA20CT307 | 17934 | #1发电机定子齿部温度1(26~27槽) | ℃ | float32
N1DCS.10MKA20CT308 | 17935 | #1发电机定子齿部温度2(26~27槽) | ℃ | float32
N1DCS.10MKA20CT309 | 17936 | #1发电机定子轭部温度1(44~45槽) | ℃ | float32
N1DCS.10MKA20CT310 | 17937 | #1发电机定子轭部温度2(44~45槽) | ℃ | float32
N1DCS.10MKA20CT311 | 17938 | #1发电机定子齿部温度1(44~45槽) | ℃ | float32
N1DCS.10MKA20CT312 | 17939 | #1发电机定子齿部温度2(44~45槽) | ℃ | float32
N1DCS.10MKA20CT313 | 17940 | #1发电机定子轭部温度3(2~3号槽) | ℃ | float32
N1DCS.10MKA20CT314 | 17941 | #1发电机定子轭部温度4(2~3号槽) | ℃ | float32
N1DCS.10MKA20CT315 | 17942 | #1发电机定子齿部温度3(2~3号槽) | ℃ | float32
N1DCS.10MKA20CT316 | 17943 | #1发电机定子齿部温度4(2~3号槽) | ℃ | float32
N1DCS.10MKA20CT317 | 17944 | #1发电机定子轭部温度3(26~27槽) | ℃ | float32
N1DCS.10MKA20CT318 | 17945 | #1发电机定子轭部温度4(26~27槽) | ℃ | float32
N1DCS.10MKA20CT319 | 17946 | #1发电机定子齿部温度3(26~27槽) | ℃ | float32
N1DCS.10MKA20CT320 | 17947 | #1发电机定子齿部温度4(26~27槽) | ℃ | float32
N1DCS.10MKA20CT321 | 17948 | #1发电机定子轭部温度3(44~45槽) | ℃ | float32
N1DCS.10MKA20CT322 | 17949 | #1发电机定子轭部温度4(44~45槽) | ℃ | float32
N1DCS.10MKA20CT323 | 17950 | #1发电机定子齿部温度3(44~45槽) | ℃ | float32
N1DCS.10MKA20CT324 | 17951 | #1发电机定子齿部温度4(44~45槽) | ℃ | float32
N1DCS.10MKA30CT301 | 17952 | #1发电机励端进风温度1 | ℃ | float32
N1DCS.10MKA30CT302 | 17953 | #1发电机励端进风温度2 | ℃ | float32
N1DCS.10MKA30CT303 | 17954 | #1发电机中部出风温度1 | ℃ | float32
N1DCS.10MKA30CT304 | 17955 | #1发电机中部出风温度2 | ℃ | float32
N1DCS.10MKA30CT305 | 17956 | #1发电机中部出风温度3 | ℃ | float32
N1DCS.10MKA30CT306 | 17957 | #1发电机中部出风温度4 | ℃ | float32
N1DCS.10MKA30CT307 | 17958 | #1发电机中部出风温度5 | ℃ | float32
N1DCS.10MKA30CT308 | 17959 | #1发电机中部出风温度6 | ℃ | float32
N1DCS.10MKA30CT309 | 17960 | #1发电机汽端进风温度1 | ℃ | float32
N1DCS.10MKA30CT310 | 17961 | #1发电机汽端进风温度2 | ℃ | float32
N1DCS.10MKA30CT311 | 17962 | #1发电机励端进风温度3 | ℃ | float32
N1DCS.10MKA30CT312 | 17963 | #1发电机励端进风温度4 | ℃ | float32
N1DCS.10MKA30CT313 | 17964 | #1发电机汽端进风温度3 | ℃ | float32
N1DCS.10MKA30CT314 | 17965 | #1发电机汽端进风温度4 | ℃ | float32
N1DCS.10PAB10CP101 | 17966 | 第一套机组循环水泵出口母管压力 |  | float32
N1DCS.10PAB12AA002CT | 17967 | #2循环水泵出口液控蝶阀油箱油温 | ℃ | float32
N1DCS.10PAB12AA002P1 | 17968 | #2循环水泵出口液控阀蓄能器压力 | MPa | float32
N1DCS.10PAB12AA002P2 | 17969 | #2循环水泵出口液控蝶阀A口油压 | MPa | float32
N1DCS.10PAB12AA002P3 | 17970 | #2循环水泵出口液控蝶阀B口油压 | MPa | float32
N1DCS.10PAB12CL104 | 17971 | #2旋转滤网前水位 | m | float32
N1DCS.10PAB12CL105 | 17972 | #2旋转滤网后水位 | m | float32
N1DCS.10PAB53CP101 | 17973 | #2循环水泵冷却水进口母管压力 | MPa | float32
N1DCS.10PAC12CP101 | 17974 | #2循环水泵出口压力 |  | float32
N1DCS.10PAC12CS101 | 17975 | #2循环水泵转速 |  | float32
N1DCS.10PAC12CT301 | 17976 | #2循环水泵电机“U”绕组温度1 | ℃ | float32
N1DCS.10PAC12CT302 | 17977 | #2循环水泵电机“U”绕组温度2 | ℃ | float32
N1DCS.10PAC12CT303 | 17978 | #2循环水泵电机“V”绕组温度1 | ℃ | float32
N1DCS.10PAC12CT304 | 17979 | #2循环水泵电机“V”绕组温度2 | ℃ | float32
N1DCS.10PAC12CT305 | 17980 | #2循环水泵电机“W”绕组温度1 | ℃ | float32
N1DCS.10PAC12CT306 | 17981 | #2循环水泵电机“W”绕组温度2 | ℃ | float32
N1DCS.10PAC12CT307 | 17982 | #2循环水泵电机导轴瓦温度1 | ℃ | float32
N1DCS.10PAC12CT308 | 17983 | #2循环水泵电机导轴瓦温度2 | ℃ | float32
N1DCS.10PAC12CT309 | 17984 | #2循环水泵电机推力瓦温度1 | ℃ | float32
N1DCS.10PAC12CT310 | 17985 | #2循环水泵电机推力瓦温度2 | ℃ | float32
N1DCS.10PAC12CT311 | 17986 | #2循环水泵电机下轴承温度 | ℃ | float32
N1DCS.10PAC12CY101 | 17987 | #2循环水泵垂直方向振动 |  | float32
N1DCS.10PAC12CY102 | 17988 | #2循环水泵水平方向振动 |  | float32
N1DCS.10PAR01AA002C | 17989 | #1冷却塔进水流量调节阀控制指令 | % | float32
N1DCS.10PAR01AA002P | 17990 | #1冷却塔进水流量调节阀阀位反馈 | % | float32
N1DCS.10PAR01AA002SP | 17991 | #1冷却塔进水流量调节阀流量设定 |  | float32
N1DCS.10PAR01CF101 | 17992 | #1冷却塔进口流量 | Kpa | float32
N1DCS.10PSA01CF101 | 17993 | #1冷却塔排水池出口流量 | m3/h | float32
N1DCS.10PSA01CL101 | 17994 | #1冷却塔排水池液位 | m | float32
N1DCS.CIRPMPB_TPFO | 17995 | #2循环水泵跳闸首出(打包点位号) |  | float32
N1DCS.CIRWTRPMPB_SEQSPSTEP | 17996 | #2循环水泵停顺控步号 |  | float32
N1DCS.CIRWTRPMPB_SEQSPTIME1 | 17997 | #2循环水泵停顺控第1步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSPTIME2 | 17998 | #2循环水泵停顺控第2步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSPTIME3 | 17999 | #2循环水泵停顺控第3步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSPTIME4 | 18000 | #2循环水泵停顺控第4步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSTSTEP | 18001 | #2循环水泵启顺控步号 |  | float32
N1DCS.CIRWTRPMPB_SEQSTTIME1 | 18002 | #2循环水泵启顺控第1步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSTTIME2 | 18003 | #2循环水泵启顺控第2步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSTTIME3 | 18004 | #2循环水泵启顺控第3步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSTTIME4 | 18005 | #2循环水泵启顺控第4步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSTTIME5 | 18006 | #2循环水泵启顺控第5步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSTTIME6 | 18007 | #2循环水泵启顺控第6步剩余时间 |  | float32
N1DCS.CIRWTRPMPB_SEQSTTIME7 | 18008 | #2循环水泵启顺控第7步剩余时间 |  | float32
N1DCS.CLEANOILBOXLVL | 18009 | 第一套机组净油箱液位（2选后） |  | float32
N1DCS.EHOILSPLPRS | 18010 | #1机EH油泵供油压力 |  | float32
N1DCS.J0MAV30CL101 | 18011 | 第一套机组净油箱液位1 | mm | float32
N1DCS.J0MAV30CL102 | 18012 | 第一套机组净油箱液位2 | mm | float32
N1DCS.J0MAV30CL111 | 18013 | 第一套机组污油箱液位1 | mm | float32
N1DCS.J0MAV30CL112 | 18014 | 第一套机组污油箱液位2 | mm | float32
N1DCS.LQTBSLL | 18015 | #1冷却塔进口流量（计算后） |  | float32
N1DCS.LQTPSLL | 18016 | #1冷却塔排水池出口流量(计算后) | t/h | float32
N1DCS.ROTFLTRB_SEQSTSTEP | 18017 | #2旋转滤网冲洗顺控 |  | float32
N1DCS.ROTFLTRB_SEQSTTIME1 | 18018 | #2旋转滤网冲洗顺控第1步剩余时? |  | float32
N1DCS.ROTFLTRB_SEQSTTIME2 | 18019 | #2旋转滤网冲洗顺控第2步剩余时? |  | float32
N1DCS.ROTFLTRB_SEQSTTIME3 | 18020 | #2旋转滤网冲洗顺控第3步剩余时? |  | float32
N1DCS.SPINFLTRBFRBHDL | 18021 | #2旋转滤网前后液位差 |  | float32
N1DCS.VACMPMPB_SEQSPSTEP | 18022 | #2真空泵停顺控步号 |  | float32
N1DCS.VACMPMPB_SEQSPTIME1 | 18023 | #2真空泵停顺控第1步剩余时间 |  | float32
N1DCS.VACMPMPB_SEQSPTIME2 | 18024 | #2真空泵停顺控第2步剩余时间 |  | float32
N1DCS.VACMPMPB_SEQSTSTEP | 18025 | #2真空泵启顺控步号 |  | float32
N1DCS.VACMPMPB_SEQSTTIME1 | 18026 | #2真空泵启顺控第1步剩余时间 |  | float32
N1DCS.VACMPMPB_SEQSTTIME2 | 18027 | #2真空泵启顺控第2步剩余时间 |  | float32
N1DCS.VACMPMPB_SEQSTTIME3 | 18028 | #2真空泵启顺控第3步剩余时间 |  | float32
N1DCS.VACMPMPB_TPFO | 18029 | #2真空泵跳闸首出(打包点位号) |  | float32
N1DCS.10PSA01CL101P | 18030 | #1冷却塔排水池液位(计算后） |  | float32
N1DCS.ROTFLTRBFRBHDL | 18031 | #2旋转滤网前后液位差 |  | float32
N1DCS.10HAD70CL001 | 18032 | 低压汽包左电接点液位 |  | float32
N1DCS.10HAD70CL002 | 18033 | 低压汽包右电接点液位 |  | float32
N1DCS.10HAD70CL101 | 18034 | 低压汽包液位1 | mmH2O | float32
N1DCS.10HAD70CL102 | 18035 | 低压汽包液位2 | mmH2O | float32
N1DCS.10HAD70CL103 | 18036 | 低压汽包液位3 | mmH2O | float32
N1DCS.10HAD70CP101 | 18037 | 低压汽包压力1 | MPa | float32
N1DCS.10HAD70CP102 | 18038 | 低压汽包压力2 | MPa | float32
N1DCS.10HAD70CP103 | 18039 | 低压汽包压力3 | MPa | float32
N1DCS.10HAD70CT301 | 18040 | 低压汽包上壁温1 | ℃ | float32
N1DCS.10HAD70CT302 | 18041 | 低压汽包上壁温2 | ℃ | float32
N1DCS.10HAD70CT303 | 18042 | 低压汽包上壁温3 | ℃ | float32
N1DCS.10HAD70CT304 | 18043 | 低压汽包下壁温1 | ℃ | float32
N1DCS.10HAD70CT305 | 18044 | 低压汽包下壁温2 | ℃ | float32
N1DCS.10HAD70CT306 | 18045 | 低压汽包下壁温3 | ℃ | float32
N1DCS.10HAD74AA401P | 18046 | 低压蒸发器排污至定排门门位开度 |  | float32
N1DCS.10HAD75AA101C | 18047 | 低压汽包连排电动调节门阀位指令 | % | float32
N1DCS.10HAD75AA101P | 18048 | 低压汽包连排电动调节门阀位反馈 |  | float32
N1DCS.10HAD76AA001P | 18049 | 低压汽包启动放水电动门门位反馈 |  | float32
N1DCS.10HAD76AA002P | 18050 | 低压汽包启动放水调节阀阀位反馈 |  | float32
N1DCS.10HAJ81CT301 | 18051 | 一级再热器减温器后温度1 | ℃ | float32
N1DCS.10HAJ81CT302 | 18052 | 一级再热器减温器后温度2 | ℃ | float32
N1DCS.10HAJ81CT303 | 18053 | 一级再热器减温器后温度3 | ℃ | float32
N1DCS.10HAJ81CT304 | 18054 | 一级再热器减温器前温度 | ℃ | float32
N1DCS.10HNA70CP101 | 18055 | HRSG进口烟气压力 | KPa | float32
N1DCS.10HNA80CP103 | 18056 | 低压省煤器出口烟气压力 | KPa | float32
N1DCS.10HNA80CT303 | 18057 | 一级再热器进口烟气温度1 | ℃ | float32
N1DCS.10HNA80CT304 | 18058 | 一级再热器进口烟气温度2 | ℃ | float32
N1DCS.10LAA70AA501P | 18059 | #1炉除氧头放空电动门 |  | float32
N1DCS.10LAA70CP101 | 18060 | 除氧头压力 | MPa | float32
N1DCS.10LAB70AA101C | 18061 | 低压给水调节阀阀位控制指令 | % | float32
N1DCS.10LAB70AA101P | 18062 | 低压给水调节阀阀位反馈 |  | float32
N1DCS.10LAB70CF101 | 18063 | 低压汽包给水流量1 | KPa | float32
N1DCS.10LAB70CF102 | 18064 | 低压汽包给水流量2 | KPa | float32
N1DCS.10LAB70CF103 | 18065 | 低压汽包给水流量3 | KPa | float32
N1DCS.10LAB70CP101 | 18066 | 低压省煤器出口压力 | MPa | float32
N1DCS.10LAB70CT301 | 18067 | 低压省煤器出口温度1 | ℃ | float32
N1DCS.10LAB70CT302 | 18068 | 低压省煤器出口温度2 | ℃ | float32
N1DCS.10LAB70CT303 | 18069 | 低压省煤器出口温度3 | ℃ | float32
N1DCS.10LAF80AA101_SPO | 18070 | Ovation Control Builder |  | float32
N1DCS.10LAF80AA101C | 18071 | 一级再热器减温水调节阀控制指令 | % | float32
N1DCS.10LAF80AA101P | 18072 | 一级再热器减温水调节阀阀位反馈 |  | float32
N1DCS.10LAF80AA102_SPO | 18073 | Ovation Control Builder |  | float32
N1DCS.10LAF80AA102C | 18074 | 二级再热器减温水调节阀控制指令 | % | float32
N1DCS.10LAF80AA102P | 18075 | 二级再热器减温水调节阀阀位反馈 |  | float32
N1DCS.10LAF80CF101 | 18076 | 再热器减温水流量 | KPa | float32
N1DCS.10LBA70AA502P | 18077 | 低压过热器启动排汽门阀位反馈 |  | float32
N1DCS.10LBA70CF101 | 18078 | 低压主蒸汽蒸汽流量1 | KPa | float32
N1DCS.10LBA70CF102 | 18079 | 低压主蒸汽蒸汽流量2 | KPa | float32
N1DCS.10LBA70CF103 | 18080 | 低压主蒸汽蒸汽流量3 | KPa | float32
N1DCS.10LBA70CP101 | 18081 | 低压主蒸汽压力1 | MPa | float32
N1DCS.10LBA70CP102 | 18082 | 低压主蒸汽压力2 | MPa | float32
N1DCS.10LBA70CP103 | 18083 | 低压主蒸汽压力3 | MPa | float32
N1DCS.10LBA70CT301 | 18084 | 低压主蒸汽温度1 | ℃ | float32
N1DCS.10LBA70CT302 | 18085 | 低压主蒸汽温度2 | ℃ | float32
N1DCS.10LBA70CT303 | 18086 | 低压主蒸汽温度3 | ℃ | float32
N1DCS.10LBB80AA502P | 18087 | 热再主蒸汽启动排汽门阀位反馈 |  | float32
N1DCS.10LBB80CP101 | 18088 | 热再主蒸汽压力1 | MPa | float32
N1DCS.10LBB80CP102 | 18089 | 热再主蒸汽压力2 | MPa | float32
N1DCS.10LBB80CP103 | 18090 | 热再主蒸汽压力3 | MPa | float32
N1DCS.10LBB80CT301 | 18091 | 热再主蒸汽温度1 | ℃ | float32
N1DCS.10LBB80CT302 | 18092 | 热再主蒸汽温度2 | ℃ | float32
N1DCS.10LBB80CT303 | 18093 | 热再主蒸汽温度3 | ℃ | float32
N1DCS.10LBC80CP101 | 18094 | 高排至冷再进口蒸汽压力 | MPa | float32
N1DCS.10LBC80CP102 | 18095 | 一级再热器进口压力 | MPa | float32
N1DCS.10LBC80CT301 | 18096 | 高排至冷再进口蒸汽温度 | ℃ | float32
N1DCS.10LBC80CT302 | 18097 | 一级再热器进口蒸汽温度 | ℃ | float32
N1DCS.10LBG70AA101_SPO | 18098 | Ovation Control Builder |  | float32
N1DCS.10LBG70AA101C | 18099 | 辅汽至#1炉除氧头调节阀控制指令 | % | float32
N1DCS.10LBG70AA101P | 18100 | 辅汽至#1炉除氧头调节阀阀位反馈 |  | float32
N1DCS.10LBG70CP101 | 18101 | 辅汽至#1炉除氧头进口压力 | MPa | float32
N1DCS.10LBG70CT301 | 18102 | 辅汽至#1炉除氧头进口温度 | ℃ | float32
N1DCS.10LCA70CP101 | 18103 | 低压省煤器给水压力（混合前） | MPa | float32
N1DCS.10LCA70CP102 | 18104 | 低压省煤器进口压力（混合后） | MPa | float32
N1DCS.10LCA70CT301 | 18105 | 低压省煤器给水温度（混合前） | ℃ | float32
N1DCS.10LCA70CT302 | 18106 | 低压省煤器进口温度（混合后） | ℃ | float32
N1DCS.10LCC71AA101_SPO | 18107 | Ovation Control Builder |  | float32
N1DCS.10LCC71AA101C | 18108 | 低省再循环泵出口调阀控制指令 | % | float32
N1DCS.10LCC71AA101P | 18109 | 低省再循环泵出口调阀阀位反馈 |  | float32
N1DCS.10LCC72AP001I | 18110 | 低压省煤器#1再循环泵电流 |  | float32
N1DCS.10LCC72CP101 | 18111 | 低压省煤器#1再循环泵出口压力 | MPa | float32
N1DCS.10LCC72CT301 | 18112 | #1再循环泵电机驱动端轴承温度 | ℃ | float32
N1DCS.10LCC72CT302 | 18113 | #1再循环泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10LCC72CT303 | 18114 | #1再循环泵电机“W”绕组温度1 | ℃ | float32
N1DCS.10LCC72CT304 | 18115 | #1再循环泵电机“W”绕组温度2 | ℃ | float32
N1DCS.10LCC72CT305 | 18116 | #1再循环泵电机“V”绕组温度1 | ℃ | float32
N1DCS.10LCC72CT306 | 18117 | #1再循环泵电机“V”绕组温度2 | ℃ | float32
N1DCS.10LCC72CT307 | 18118 | #1再循环泵电机“U”绕组温度1 | ℃ | float32
N1DCS.10LCC72CT308 | 18119 | #1再循环泵电机“U”绕组温度2 | ℃ | float32
N1DCS.10LCC72DP101 | 18120 | #1再循环泵进口过滤器前后差压 | KPa | float32
N1DCS.10LCC73AP001I | 18121 | 低压省煤器#2再循环泵电流 |  | float32
N1DCS.10LCC73CP101 | 18122 | 低压省煤器#2再循环泵出口压力 | MPa | float32
N1DCS.10LCC73CT301 | 18123 | #2再循环泵电机驱动端轴承温度 | ℃ | float32
N1DCS.10LCC73CT302 | 18124 | #2再循环泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10LCC73CT303 | 18125 | #2再循环泵电机“W”绕组温度1 | ℃ | float32
N1DCS.10LCC73CT304 | 18126 | #2再循环泵电机“W”绕组温度2 | ℃ | float32
N1DCS.10LCC73CT305 | 18127 | #2再循环泵电机“V”绕组温度1 | ℃ | float32
N1DCS.10LCC73CT306 | 18128 | #2再循环泵电机“V”绕组温度2 | ℃ | float32
N1DCS.10LCC73CT307 | 18129 | #2再循环泵电机“U”绕组温度1 | ℃ | float32
N1DCS.10LCC73CT308 | 18130 | #2再循环泵电机“U”绕组温度2 | ℃ | float32
N1DCS.10LCC73DP101 | 18131 | #2再循环泵进口过滤器前后差压 | KPa | float32
N1DCS.10LCQ74AA101_SPO | 18132 | Ovation Control Builder |  | float32
N1DCS.10LCQ74AA101C | 18133 | 连排至定排气动调节阀控制指令 | % | float32
N1DCS.10LCQ74AA101P | 18134 | 连排至定排气动调节阀阀位反馈 |  | float32
N1DCS.D7P1B1L3C9 | 18135 | TC温度补偿点 | C | float32
N1DCS.D7P1B2L6C9 | 18136 | TC温度补偿点 | C | float32
N1DCS.LPDRUMCP | 18137 | 低压汽包压力（3选后） |  | float32
N1DCS.LPDRUMCTD | 18138 | 低压汽包下壁温（3选后） |  | float32
N1DCS.LPDRUMCTU | 18139 | 低压汽包上壁温（3选后） |  | float32
N1DCS.LPDRUMLVL | 18140 | 低压汽包液位(3选后) |  | float32
N1DCS.LPDRUMLVL_A | 18141 | 低压汽包液位1(计算后) |  | float32
N1DCS.LPDRUMLVL_B | 18142 | 低压汽包液位2(计算后) |  | float32
N1DCS.LPDRUMLVL_C | 18143 | 低压汽包液位3(计算后) |  | float32
N1DCS.LPDRUMLVL_DIF | 18144 | 低压汽包液位(计算后) |  | float32
N1DCS.LPDRUMLVL_SP | 18145 | 低压汽包液位最终设定值 |  | float32
N1DCS.LPDRUMLVL_SP1 | 18146 | 低压汽包液位设定值 |  | float32
N1DCS.LPDSTCF | 18147 | 低压主蒸汽蒸汽流量（3选后） |  | float32
N1DCS.LPDSTCF_A | 18148 | 低压主蒸汽蒸汽流量1（计算后） |  | float32
N1DCS.LPDSTCF_B | 18149 | 低压主蒸汽蒸汽流量2（计算后） |  | float32
N1DCS.LPDSTCF_C | 18150 | 低压主蒸汽蒸汽流量3（计算后） |  | float32
N1DCS.LPDSTCP | 18151 | 低压主蒸汽压力（3选后） |  | float32
N1DCS.LPDSTCT | 18152 | 低压主蒸汽温度（3选后） |  | float32
N1DCS.LPDWTCF | 18153 | 低压汽包给水流量（3选后） |  | float32
N1DCS.LPDWTCF_A | 18154 | 低压汽包给水流量1（计算后） |  | float32
N1DCS.LPDWTCF_B | 18155 | 低压汽包给水流量2（计算后） |  | float32
N1DCS.LPDWTCF_C | 18156 | 低压汽包给水流量3（计算后） |  | float32
N1DCS.LPDWTCT | 18157 | 低压省煤器出口温度（计算后） |  | float32
N1DCS.LPECON_SEQSTSTEP | 18158 | 再循环泵功能组启顺控步号 |  | float32
N1DCS.LPECON_SEQSTTIME1 | 18159 | 再循环泵启顺控第1步剩余时间 |  | float32
N1DCS.LPECON_SEQSTTIME2 | 18160 | 再循环泵启顺控第2步剩余时间 |  | float32
N1DCS.LPECON_SEQSTTIME3 | 18161 | 再循环泵启顺控第3步剩余时间 |  | float32
N1DCS.LPECONPA_SEQSPSTEP | 18162 | #1再循环泵停顺控步号 |  | float32
N1DCS.LPECONPA_SEQSPTIME1 | 18163 | #1再循环泵停顺控第1步剩余时间 |  | float32
N1DCS.LPECONPA_SEQSPTIME2 | 18164 | #1再循环泵停顺控第2步剩余时间 |  | float32
N1DCS.LPECONPA_SEQSTSTEP | 18165 | #1再循环泵启顺控步号 |  | float32
N1DCS.LPECONPA_SEQSTTIME1 | 18166 | #1再循环泵启顺控第1步剩余时间 |  | float32
N1DCS.LPECONPA_SEQSTTIME2 | 18167 | #1再循环泵启顺控第2步剩余时间 |  | float32
N1DCS.LPECONPA_SEQSTTIME3 | 18168 | #1再循环泵启顺控第3步剩余时间 |  | float32
N1DCS.LPECONPA_TPFO | 18169 | #1再循环泵跳闸首出(打包点位号) |  | float32
N1DCS.LPECONPB_SEQSPSTEP | 18170 | #2再循环泵停顺控步号 |  | float32
N1DCS.LPECONPB_SEQSPTIME1 | 18171 | #2再循环泵停顺控第1步剩余时间 |  | float32
N1DCS.LPECONPB_SEQSPTIME2 | 18172 | #2再循环泵停顺控第2步剩余时间 |  | float32
N1DCS.LPECONPB_SEQSTSTEP | 18173 | #2再循环泵启顺控步号 |  | float32
N1DCS.LPECONPB_SEQSTTIME1 | 18174 | #2再循环泵启顺控第1步剩余时间 |  | float32
N1DCS.LPECONPB_SEQSTTIME2 | 18175 | #2再循环泵启顺控第2步剩余时间 |  | float32
N1DCS.LPECONPB_SEQSTTIME3 | 18176 | #2再循环泵启顺控第3步剩余时间 |  | float32
N1DCS.LPECONPB_TPFO | 18177 | #2再循环泵跳闸首出(打包点位号) |  | float32
N1DCS.LPFW_BIASO | 18178 | 低压给水调阀液位设定偏置值 |  | float32
N1DCS.LPFW_SEQSTSTEP | 18179 | 低压汽包上水顺控步号 |  | float32
N1DCS.LPFW_SEQSTTIME1 | 18180 | 低压汽包上水顺控第1步剩余时间 |  | float32
N1DCS.LPFW_SEQSTTIME2 | 18181 | 低压汽包上水顺控第2步剩余时间 |  | float32
N1DCS.LPFW_SEQSTTIME3 | 18182 | 低压汽包上水顺控第3步剩余时间 |  | float32
N1DCS.LPFW_SEQSTTIME4 | 18183 | 低压汽包上水顺控第4步剩余时间 |  | float32
N1DCS.LPFW_SEQSTTIME5 | 18184 | 低压汽包上水顺控第5步剩余时间 |  | float32
N1DCS.LPMS_SEQSTSTEP | 18185 | 低压主汽升温升压顺控步号 |  | float32
N1DCS.LPMS_SEQSTTIME1 | 18186 | 低压主汽升温升压顺控1步剩时间 |  | float32
N1DCS.LPMS_SEQSTTIME2 | 18187 | 低压主汽升温升压顺控2步剩时间 |  | float32
N1DCS.LPMS_SEQSTTIME3 | 18188 | 低压主汽升温升压顺控3步剩时间 |  | float32
N1DCS.LPMS_SEQSTTIME4 | 18189 | 低压主汽升温升压顺控4步剩时间 |  | float32
N1DCS.LPMS_SEQSTTIME5 | 18190 | 低压主汽升温升压顺控5步剩时间 |  | float32
N1DCS.LPMS_SEQSTTIME6 | 18191 | 低压主汽升温升压顺控6步剩时间 |  | float32
N1DCS.LPMS_SEQSTTIME7 | 18192 | 低压主汽升温升压顺控7步剩时间 |  | float32
N1DCS.RH2INSTCT | 18193 | 一级再热器减温器后温度（3选后) |  | float32
N1DCS.RH2OUTSTCP | 18194 | 热再主蒸汽压力(3选后） |  | float32
N1DCS.RH2OUTSTCT | 18195 | 热再主蒸汽温度(3选后） |  | float32
N1DCS.10HAD70CLB1 | 18196 | Ovation Control Builder |  | float32
N1DCS.10HAD70CLB2 | 18197 | Ovation Control Builder |  | float32
N1DCS.10HAD70CLB3 | 18198 | Ovation Control Builder |  | float32
N1DCS.10LAF80AA101_BIAS | 18199 | 一级再热器减温水调阀温度偏置值 |  | float32
N1DCS.10LAF80AA101_SP1 | 18200 | 一级再热器减温调阀最终温度设定 |  | float32
N1DCS.10LAF80AA101_SPB | 18201 | 一级再热器减温水调阀温度设定值 |  | float32
N1DCS.10LAF80AA102_BIAS | 18202 | 二级再热器减温水调阀温度偏置值 |  | float32
N1DCS.10LAF80AA102_SP1 | 18203 | 二级再热器减温调阀最终温度设定 |  | float32
N1DCS.10LAF80AA102_SPB | 18204 | 二级再热器减温水调阀温度设定值 |  | float32
N1DCS.10LAF80CF101I | 18205 | 再热器减温水流量（计算后） |  | float32
N1DCS.DYCGXS | 18206 | 低压汽包吹管系数 |  | float32
N1DCS.GYCGXS | 18207 | 高压汽包吹管系数 |  | float32
N1DCS.LPDRUMLVL_TRKN | 18208 | Ovation Control Builder |  | float32
N1DCS.LPDWC | 18209 | 低压汽包上下壁温差 |  | float32
N1DCS.LPDWTCF_SUM | 18210 | 低压汽包给水累计流量 |  | float32
N1DCS.LPLVLADD_OUT | 18211 | 低压给水调阀三冲量副调输入 |  | float32
N1DCS.LPLVLPID1_OUT | 18212 | 低压给水调阀三冲量主调输出 |  | float32
N1DCS.ZYCGXS | 18213 | 中压汽包吹管系数 |  | float32
N1DCS.10CFE40CF101 | 18214 | 烟囱出口烟气流速差压 | Nm3/h | float32
N1DCS.10CFE40CM101 | 18215 | 烟囱出口湿氧 | % | float32
N1DCS.10CFE40CP101 | 18216 | 烟囱出口烟气压力 | KPa | float32
N1DCS.10CFE40CQ101 | 18217 | 烟囱出口NO含量 | mg/m3 | float32
N1DCS.10CFE40CQ102 | 18218 | 烟囱出口干氧 | % | float32
N1DCS.10CFE40CQ103 | 18219 | 烟囱出口SO2含量 | mg/m3 | float32
N1DCS.10CFE40CQ104 | 18220 | 烟囱出口CO含量 | mg/m3 | float32
N1DCS.10CFE40CQ106 | 18221 | 烟囱出口粉尘含量 | % | float32
N1DCS.10CFE40CT101 | 18222 | 烟囱出口烟气温度 | ℃ | float32
N1DCS.10HAD80CL001 | 18223 | 中压汽包左电接点液位 |  | float32
N1DCS.10HAD80CL002 | 18224 | 中压汽包右电接点液位 |  | float32
N1DCS.10HAD80CL101 | 18225 | 中压汽包液位1 | KPa | float32
N1DCS.10HAD80CL102 | 18226 | 中压汽包液位2 | KPa | float32
N1DCS.10HAD80CL103 | 18227 | 中压汽包液位3 | KPa | float32
N1DCS.10HAD80CP101 | 18228 | 中压汽包压力1 | MPa | float32
N1DCS.10HAD80CP102 | 18229 | 中压汽包压力2 | MPa | float32
N1DCS.10HAD80CP103 | 18230 | 中压汽包压力3 | MPa | float32
N1DCS.10HAD80CT301 | 18231 | 中压汽包上壁温1 | ℃ | float32
N1DCS.10HAD80CT302 | 18232 | 中压汽包上壁温2 | ℃ | float32
N1DCS.10HAD80CT303 | 18233 | 中压汽包上壁温3 | ℃ | float32
N1DCS.10HAD80CT304 | 18234 | 中压汽包下壁温1 | ℃ | float32
N1DCS.10HAD80CT305 | 18235 | 中压汽包下壁温2 | ℃ | float32
N1DCS.10HAD80CT306 | 18236 | 中压汽包下壁温3 | ℃ | float32
N1DCS.10HAD84AA401P | 18237 | 中压蒸发器排污至定排门门位开度 |  | float32
N1DCS.10HAD85AA101C | 18238 | 中压汽包连排电动调节门阀位指令 | % | float32
N1DCS.10HAD85AA101P | 18239 | 中压汽包连排电动调节门阀位反馈 |  | float32
N1DCS.10HAD86AA001P | 18240 | 中压汽包启动放水电动门门位反馈 |  | float32
N1DCS.10HAD86AA002P | 18241 | 中压汽包启动放水调节阀阀位反馈 |  | float32
N1DCS.10HNA80CT307 | 18242 | 中压过热器进口烟气温度1 | ℃ | float32
N1DCS.10HNA80CT308 | 18243 | 中压过热器进口烟气温度2 | ℃ | float32
N1DCS.10HNA80CT311 | 18244 | 低压省煤器进口烟气温度1 | ℃ | float32
N1DCS.10HNA80CT312 | 18245 | 低压省煤器进口烟气温度2 | ℃ | float32
N1DCS.10HNA80CT313 | 18246 | 低压省煤器出口烟气温度1 | ℃ | float32
N1DCS.10HNA80CT314 | 18247 | 低压省煤器出口烟气温度2 | ℃ | float32
N1DCS.10HNE70CP101 | 18248 | 烟囱出口烟气压力 | KPa | float32
N1DCS.10LAB72CP101 | 18249 | #1中压给水泵进口压力 | MPa | float32
N1DCS.10LAB72DP101 | 18250 | #1中压给水泵进口过滤器差压 | KPa | float32
N1DCS.10LAB74CP101 | 18251 | #1高压给水泵进口压力 | MPa | float32
N1DCS.10LAB74DP101 | 18252 | #1高压给水泵进口过滤器差压 | KPa | float32
N1DCS.10LAB80CF101 | 18253 | 中压给水省煤器进口流量1 | KPa | float32
N1DCS.10LAB80CF102 | 18254 | 中压给水省煤器进口流量2 | KPa | float32
N1DCS.10LAB80CF103 | 18255 | 中压给水省煤器进口流量3 | KPa | float32
N1DCS.10LAB80CT301 | 18256 | 中压给水省煤器进口温度1 | ℃ | float32
N1DCS.10LAB80CT302 | 18257 | 中压给水省煤器进口温度2 | ℃ | float32
N1DCS.10LAB80CT303 | 18258 | 中压给水省煤器进口温度3 | ℃ | float32
N1DCS.10LAB81AP001I | 18259 | #1中压给水泵电流 |  | float32
N1DCS.10LAB81CP102 | 18260 | #1中压给水泵出口压力 | MPa | float32
N1DCS.10LAB81CT301 | 18261 | #1中给泵非驱动端径向轴承温度 | ℃ | float32
N1DCS.10LAB81CT302 | 18262 | #1中压给水泵驱动端径向轴承温度 | ℃ | float32
N1DCS.10LAB81CT303 | 18263 | #1中给泵电机驱动端径向轴承温度 | ℃ | float32
N1DCS.10LAB81CT304 | 18264 | #1中给泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10LAB81CT305 | 18265 | #1中压给水泵电机“W”绕组温度1 | ℃ | float32
N1DCS.10LAB81CT306 | 18266 | #1中压给水泵电机“W”绕组温度2 | ℃ | float32
N1DCS.10LAB81CT307 | 18267 | #1中压给水泵电机“V”绕组温度1 | ℃ | float32
N1DCS.10LAB81CT308 | 18268 | #1中压给水泵电机“V”绕组温度2 | ℃ | float32
N1DCS.10LAB81CT309 | 18269 | #1中压给水泵电机“U”绕组温度1 | ℃ | float32
N1DCS.10LAB81CT310 | 18270 | #1中压给水泵电机“U”绕组温度2 | ℃ | float32
N1DCS.10LAB81CT311 | 18271 | #1中给泵轴承冷却水回水温度1 | ℃ | float32
N1DCS.10LAB81CT312 | 18272 | #1中给泵轴承冷却水回水温度2 | ℃ | float32
N1DCS.10LAB81CT313 | 18273 | #1中给泵机密封冷却水回水温度1 | ℃ | float32
N1DCS.10LAB81CT314 | 18274 | #1中给泵机密封冷却水回水温度2 | ℃ | float32
N1DCS.10LAB81CT315 | 18275 | #1中给泵机密封冷却水回水温度3 | ℃ | float32
N1DCS.10LAB81CT316 | 18276 | #1中给泵机密封冷却水回水温度4 | ℃ | float32
N1DCS.10LAB81CY101 | 18277 | #1中给泵非驱动端轴承座振动(X向 | mm/s | float32
N1DCS.10LAB81CY102 | 18278 | #1中给泵非驱动端轴承座振动(Y向 | mm/s | float32
N1DCS.10LAB81CY103 | 18279 | #1中给泵驱动端轴承座振动（X向 | mm/s | float32
N1DCS.10LAB81CY104 | 18280 | #1中给泵驱动端轴承座振动（Y向 | mm/s | float32
N1DCS.10LAB83AA101_DM | 18281 | 中压给水调节阀指令（中间） |  | float32
N1DCS.10LAB83AA101_DMTK | 18282 | 中压给水调节阀指令（中间） |  | float32
N1DCS.10LAB83AA101C | 18283 | 中压给水调节阀控制指令 | % | float32
N1DCS.10LAB83AA101P | 18284 | 中压给水调节阀开度反馈 |  | float32
N1DCS.10LAB83CP101 | 18285 | 中压省煤器出口压力 | MPa | float32
N1DCS.10LAB83CT301 | 18286 | 中压省煤器出口温度 | ℃ | float32
N1DCS.10LAB91AP001I | 18287 | #1高压给水泵电流 |  | float32
N1DCS.10LAB91CP102 | 18288 | #1高压给水泵出口压力 | MPa | float32
N1DCS.10LAB91CS101 | 18289 | #1高压给水泵转速 | rpm | float32
N1DCS.10LAB91CT301 | 18290 | #1高给泵进水端径向轴承轴瓦温度 | ℃ | float32
N1DCS.10LAB91CT302 | 18291 | #1高给泵出水端径向轴承轴瓦温度 | ℃ | float32
N1DCS.10LAB91CT303 | 18292 | #1高给泵电机驱动端径向轴承温度 | ℃ | float32
N1DCS.10LAB91CT304 | 18293 | #1高给泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10LAB91CT305 | 18294 | #1高压给水泵电机“W”绕组温度1 | ℃ | float32
N1DCS.10LAB91CT306 | 18295 | #1高压给水泵电机“W”绕组温度2 | ℃ | float32
N1DCS.10LAB91CT307 | 18296 | #1高压给水泵电机“V”绕组温度1 | ℃ | float32
N1DCS.10LAB91CT308 | 18297 | #1高压给水泵电机“V”绕组温度2 | ℃ | float32
N1DCS.10LAB91CT309 | 18298 | #1高压给水泵电机“U”绕组温度1 | ℃ | float32
N1DCS.10LAB91CT310 | 18299 | #1高压给水泵电机“U”绕组温度2 | ℃ | float32
N1DCS.10LAB91CT311 | 18300 | #1高给泵机密封冷却水回水温度1 | ℃ | float32
N1DCS.10LAB91CT312 | 18301 | #1高给泵机密封冷却水回水温度2 | ℃ | float32
N1DCS.10LAB91CT313 | 18302 | #1高给泵机密封冷却水回水温度3 | ℃ | float32
N1DCS.10LAB91CT314 | 18303 | #1高给泵机密封冷却水回水温度4 | ℃ | float32
N1DCS.10LAB91CY101 | 18304 | #1高给泵非驱动端轴承座振动(X向 | mm/s | float32
N1DCS.10LAB91CY102 | 18305 | #1高给泵非驱动端轴承座振动(Y向 | um | float32
N1DCS.10LAB91CY103 | 18306 | #1高给泵驱动端轴承座振动(X向 | um | float32
N1DCS.10LAB91CY104 | 18307 | #1高给泵驱动端轴承座振动(Y向 | um | float32
N1DCS.10LBA80AA502P | 18308 | 中压主蒸汽启动排汽门门位反馈 |  | float32
N1DCS.10LBA80CF101 | 18309 | 中压主蒸汽流量1 | KPa | float32
N1DCS.10LBA80CF102 | 18310 | 中压主蒸汽流量2 | KPa | float32
N1DCS.10LBA80CF103 | 18311 | 中压主蒸汽流量3 | KPa | float32
N1DCS.10LBA80CP101 | 18312 | 中压主蒸汽压力1 | MPa | float32
N1DCS.10LBA80CP102 | 18313 | 中压主蒸汽压力2 | MPa | float32
N1DCS.10LBA80CP103 | 18314 | 中压主蒸汽压力3 | MPa | float32
N1DCS.10LBA80CT301 | 18315 | 中压主蒸汽温度1 | ℃ | float32
N1DCS.10LBA80CT302 | 18316 | 中压主蒸汽温度2 | ℃ | float32
N1DCS.10LBA80CT303 | 18317 | 中压主蒸汽温度3 | ℃ | float32
N1DCS.10LCQ70CL101 | 18318 | 连排扩容器液位 | mm | float32
N1DCS.10LCQ70CP101 | 18319 | 连排扩容器压力 | MPa | float32
N1DCS.10LCQ75CL101 | 18320 | 定排扩容器液位 | mm | float32
N1DCS.10LCQ75CP101 | 18321 | 定排扩容器压力 | MPa | float32
N1DCS.10LCQ75CT301 | 18322 | 定排扩容器温度 | ℃ | float32
N1DCS.10XAV91CP101 | 18323 | #1高压给水泵稀油站供油母管压力 |  | float32
N1DCS.10XAV91CT301 | 18324 | #1高压给水泵稀油站油箱温度 | ℃ | float32
N1DCS.10XAV91CT302 | 18325 | #1高压给水泵稀油站供油母管温度 | ℃ | float32
N1DCS.10XAV91CT303 | 18326 | #1高压给水泵稀油站回油温度 | ℃ | float32
N1DCS.D8P1B1L3C9 | 18327 | TC温度补偿点 | C | float32
N1DCS.D8P1B2L6C9 | 18328 | TC温度补偿点 | C | float32
N1DCS.D8P1B3L3C9 | 18329 | TC温度补偿点 | C | float32
N1DCS.HPFWPA_SEQSPSTEP | 18330 | #1高压给水泵停顺控步号 |  | float32
N1DCS.HPFWPA_SEQSPTIME1 | 18331 | #1高给泵停顺控第1步剩余时间 |  | float32
N1DCS.HPFWPA_SEQSPTIME2 | 18332 | #1高给泵停顺控第2步剩余时间 |  | float32
N1DCS.HPFWPA_SEQSTSTEP | 18333 | #1高压给水泵启顺控步号 |  | float32
N1DCS.HPFWPA_SEQSTTIME1 | 18334 | #1高给泵启顺控第1步剩余时间 |  | float32
N1DCS.HPFWPA_SEQSTTIME2 | 18335 | #1高给泵启顺控第2步剩余时间 |  | float32
N1DCS.HPFWPA_SEQSTTIME3 | 18336 | #1高给泵启顺控第3步剩余时间 |  | float32
N1DCS.HPFWPA_SEQSTTIME4 | 18337 | #1高给泵启顺控第4步剩余时间 |  | float32
N1DCS.HPFWPA_TPFO | 18338 | #1高给泵跳闸首出(打包点位号 |  | float32
N1DCS.IPDRUMCP | 18339 | 中压汽包压力（3选后） |  | float32
N1DCS.IPDRUMCTD | 18340 | 中压汽包下外壁温（3选后） |  | float32
N1DCS.IPDRUMCTU | 18341 | 中压汽包上外壁温（3选后） |  | float32
N1DCS.IPDRUMLVL | 18342 | 中压汽包液位（3选后） |  | float32
N1DCS.IPDRUMLVL_A | 18343 | 中压汽包液位1（计算后） |  | float32
N1DCS.IPDRUMLVL_B | 18344 | 中压汽包液位2（计算后） |  | float32
N1DCS.IPDRUMLVL_C | 18345 | 中压汽包液位3（计算后） |  | float32
N1DCS.IPDRUMLVL_DIF | 18346 | 中压汽包液位（3选后） |  | float32
N1DCS.IPDRUMLVLBIAS | 18347 | 中压汽包液位偏置值 |  | float32
N1DCS.IPDRUMLVLSP | 18348 | 中压汽包液位最终设定值 |  | float32
N1DCS.IPDRUMLVLSP1 | 18349 | 中压汽包液位设定值 |  | float32
N1DCS.IPDSTCF | 18350 | 中压主蒸汽流量（3选后） |  | float32
N1DCS.IPDSTCF_A | 18351 | 中压主蒸汽流量1（计算后） |  | float32
N1DCS.IPDSTCF_B | 18352 | 中压主蒸汽流量2（计算后） |  | float32
N1DCS.IPDSTCF_C | 18353 | 中压主蒸汽流量3（计算后） |  | float32
N1DCS.IPDSTCP | 18354 | 中压主蒸汽压力（3选后） |  | float32
N1DCS.IPDSTCT | 18355 | 中压主蒸汽温度（3选后） |  | float32
N1DCS.IPDWTCF | 18356 | 中压汽包给水流量（3选后） |  | float32
N1DCS.IPDWTCF_A | 18357 | 中压汽包给水流量1（计算后） |  | float32
N1DCS.IPDWTCF_B | 18358 | 中压汽包给水流量2（计算后） |  | float32
N1DCS.IPDWTCF_C | 18359 | 中压汽包给水流量3（计算后） |  | float32
N1DCS.IPDWTCT | 18360 | 中压给水省煤器进口温度（3选后) |  | float32
N1DCS.IPFW_SEQSTSTEP | 18361 | 中压汽包上水顺控步号 |  | float32
N1DCS.IPFW_SEQSTTIME1 | 18362 | 中压汽包上水顺控第1步剩余时间 |  | float32
N1DCS.IPFW_SEQSTTIME2 | 18363 | 中压汽包上水顺控第2步剩余时间 |  | float32
N1DCS.IPFW_SEQSTTIME3 | 18364 | 中压汽包上水顺控第3步剩余时间 |  | float32
N1DCS.IPFW_SEQSTTIME4 | 18365 | 中压汽包上水顺控第4步剩余时间 |  | float32
N1DCS.IPFW_SEQSTTIME5 | 18366 | 中压汽包上水顺控第5步剩余时间 |  | float32
N1DCS.IPFW_SEQSTTIME6 | 18367 | 中压汽包上水顺控第6步剩余时间 |  | float32
N1DCS.IPFWPA_SEQSPSTEP | 18368 | #1中压给水泵停顺控步号 |  | float32
N1DCS.IPFWPA_SEQSPTIME1 | 18369 | #1中给泵停顺控第1步剩余时间 |  | float32
N1DCS.IPFWPA_SEQSPTIME2 | 18370 | #1中给泵停顺控第2步剩余时间 |  | float32
N1DCS.IPFWPA_SEQSTSTEP | 18371 | #1中压给水泵启顺控步号 |  | float32
N1DCS.IPFWPA_SEQSTTIME1 | 18372 | #1中给泵启顺控第1步剩余时间 |  | float32
N1DCS.IPFWPA_SEQSTTIME2 | 18373 | #1中给泵启顺控第2步剩余时间 |  | float32
N1DCS.IPFWPA_SEQSTTIME3 | 18374 | #1中给泵启顺控第3步剩余时间 |  | float32
N1DCS.IPFWPA_TPFO | 18375 | #1中给泵跳闸首出(打包点位号 |  | float32
N1DCS.IPMS_SEQSTSTEP | 18376 | 中压主蒸汽升温升压顺控步号 |  | float32
N1DCS.IPMS_SEQSTTIME1 | 18377 | 中压主汽升温升压顺控1步剩时间 |  | float32
N1DCS.IPMS_SEQSTTIME2 | 18378 | 中压主汽升温升压顺控2步剩时间 |  | float32
N1DCS.IPMS_SEQSTTIME3 | 18379 | 中压主汽升温升压顺控3步剩时间 |  | float32
N1DCS.IPMS_SEQSTTIME4 | 18380 | 中压主汽升温升压顺控4步剩时间 |  | float32
N1DCS.IPMS_SEQSTTIME5 | 18381 | 中压主汽升温升压顺控5步剩时间 |  | float32
N1DCS.IPMS_SEQSTTIME6 | 18382 | 中压主汽升温升压顺控6步剩时间 |  | float32
N1DCS.IPMS_SEQSTTIME7 | 18383 | 中压主汽升温升压顺控7步剩时间 |  | float32
N1DCS.10CFE40CF101_LL | 18384 | 烟气流量 | m3/h | float32
N1DCS.10CFE40CF101LS | 18385 | 烟气出口流速 | m/s | float32
N1DCS.10CFE40CM101_YQSD | 18386 | 烟气湿度 |  | float32
N1DCS.10CFE40CQ101I | 18387 | 烟囱出口NOX折算值 |  | float32
N1DCS.10CFE40CQ101P | 18388 | 烟囱出口NO含量(ppm) |  | float32
N1DCS.10CFE40CQ101X | 18389 | 烟囱出口NOX含量 |  | float32
N1DCS.10CFE40CQ101XP | 18390 | 烟囱出口NOX含量(ppm) |  | float32
N1DCS.10CFE40CQ103_1 | 18391 | 烟囱出口SO2含量1 |  | float32
N1DCS.10CFE40CQ103I | 18392 | 烟囱出口SO2折算值 |  | float32
N1DCS.10CFE40CQ103P | 18393 | 烟囱出口SO2含量(ppm) |  | float32
N1DCS.10CFE40CQ104P | 18394 | 烟囱出口CO含量(ppm) |  | float32
N1DCS.10CFE40CQ106I | 18395 | 烟囱出口粉尘折算值 |  | float32
N1DCS.10CFE40CQ106P | 18396 | Ovation Control Builder |  | float32
N1DCS.10HAD80CLB1 | 18397 | Ovation Control Builder |  | float32
N1DCS.10HAD80CLB2 | 18398 | Ovation Control Builder |  | float32
N1DCS.10HAD80CLB3 | 18399 | Ovation Control Builder |  | float32
N1DCS.HPFWPA_SEQBPSTSTEP | 18400 | #1高压给水泵变频启顺控步号 |  | float32
N1DCS.HPFWPA_SEQBPSTTIME1 | 18401 | #1高给泵变频启顺控1步剩余时间 |  | float32
N1DCS.HPFWPA_SEQBPSTTIME2 | 18402 | #1高给泵变频启顺控2步剩余时间 |  | float32
N1DCS.HPFWPA_SEQBPSTTIME3 | 18403 | #1高给泵变频启顺控3步剩余时间 |  | float32
N1DCS.HPFWPA_SEQBPSTTIME4 | 18404 | #1高给泵变频启顺控4步剩余时间 |  | float32
N1DCS.HRSGFO1 | 18405 | #1炉跳闸首出(打包点位号 |  | float32
N1DCS.IPDWC | 18406 | 中压汽包上下壁温差 |  | float32
N1DCS.IPDWTCF_SUM | 18407 | 中压汽包给水累计流量 |  | float32
N1DCS.IPLVLADD_OUT | 18408 | 中压给水调阀三冲量主调输出 |  | float32
N1DCS.IPLVLPID1_OUT | 18409 | 中压给水调阀三冲量副调设定 |  | float32
N1DCS.IPMS_SEQSTTIME8 | 18410 | 中压主汽升温升压顺控8步剩时间 |  | float32
N1DCS.STTRIPFO1 | 18411 | #1机跳闸首出（打包点位号） |  | float32
N1DCS.10HAD90CL001 | 18412 | 高压汽包左电接点液位 |  | float32
N1DCS.10HAD90CL002 | 18413 | 高压汽包右电接点液位 |  | float32
N1DCS.10HAD90CL101 | 18414 | 高压汽包液位1 | mm | float32
N1DCS.10HAD90CL102 | 18415 | 高压汽包液位2 | mm | float32
N1DCS.10HAD90CL103 | 18416 | 高压汽包液位3 | mm | float32
N1DCS.10HAD90CP101 | 18417 | 高压汽包压力1 | MPa | float32
N1DCS.10HAD90CP102 | 18418 | 高压汽包压力2 | MPa | float32
N1DCS.10HAD90CP103 | 18419 | 高压汽包压力3 | MPa | float32
N1DCS.10HAD90CT301 | 18420 | 高压汽包上内壁温1 | ℃ | float32
N1DCS.10HAD90CT302 | 18421 | 高压汽包上内壁温2 | ℃ | float32
N1DCS.10HAD90CT303 | 18422 | 高压汽包上内壁温3 | ℃ | float32
N1DCS.10HAD90CT304 | 18423 | 高压汽包上外壁温1 | ℃ | float32
N1DCS.10HAD90CT305 | 18424 | 高压汽包上外壁温2 | ℃ | float32
N1DCS.10HAD90CT306 | 18425 | 高压汽包上外壁温3 | ℃ | float32
N1DCS.10HAD90CT307 | 18426 | 高压汽包下外壁温1 | ℃ | float32
N1DCS.10HAD90CT308 | 18427 | 高压汽包下外壁温2 | ℃ | float32
N1DCS.10HAD90CT309 | 18428 | 高压汽包下外壁温3 | ℃ | float32
N1DCS.10HAD91AA405P | 18429 | 高压蒸发器排污至定排门阀位反馈 |  | float32
N1DCS.10HAD95AA101C | 18430 | 高压汽包连排气动调节阀控制指令 | % | float32
N1DCS.10HAD95AA101P | 18431 | 高压汽包连排气动调节阀阀位反馈 |  | float32
N1DCS.10HAD96AA001P | 18432 | 高压汽包启动放水电动门阀位反馈 |  | float32
N1DCS.10HAD96AA002P | 18433 | 高压汽包启动放水调门阀位反馈 |  | float32
N1DCS.10HAH90CT301 | 18434 | 高压三级过热器进口温度1 | ℃ | float32
N1DCS.10HAH90CT302 | 18435 | 高压三级过热器进口温度2 | ℃ | float32
N1DCS.10HAH90CT303 | 18436 | 高压三级过热器进口温度3 | ℃ | float32
N1DCS.10HAH90CT304 | 18437 | 高压二级过热器出口温度 | ℃ | float32
N1DCS.10HNA80CP101 | 18438 | 高压三级过热器进口烟气压力1 | KPa | float32
N1DCS.10HNA80CP102 | 18439 | 高压三级过热器进口烟气压力2 | KPa | float32
N1DCS.10HNA80CT301 | 18440 | 高压三级过热器进口烟气温度1 | ℃ | float32
N1DCS.10HNA80CT302 | 18441 | 高压三级过热器进口烟气温度2 | ℃ | float32
N1DCS.10HNA80CT305 | 18442 | 高压蒸发器进口烟气温度1 | ℃ | float32
N1DCS.10HNA80CT306 | 18443 | 高压蒸发器进口烟气温度2 | ℃ | float32
N1DCS.10HNA80CT309 | 18444 | 高压二级省煤器进口烟气温度1 | ℃ | float32
N1DCS.10HNA80CT310 | 18445 | 高压二级省煤器进口烟气温度2 | ℃ | float32
N1DCS.10LAB73CP101 | 18446 | #2中压给水泵进口压力 | MPa | float32
N1DCS.10LAB73DP101 | 18447 | #2中压给水泵进口过滤器差压 | KPa | float32
N1DCS.10LAB75CP101 | 18448 | #2高压给水泵进口压力 | MPa | float32
N1DCS.10LAB75DP101 | 18449 | #2高压给水泵进口过滤器差压 | KPa | float32
N1DCS.10LAB82AP001I | 18450 | #2中压给水泵电流 |  | float32
N1DCS.10LAB82CP102 | 18451 | #2中压给水泵出口压力 | MPa | float32
N1DCS.10LAB82CT301 | 18452 | #2中给泵非驱动端径向轴承温度 | ℃ | float32
N1DCS.10LAB82CT302 | 18453 | #2中压给水泵驱动端径向轴承温度 | ℃ | float32
N1DCS.10LAB82CT303 | 18454 | #2中给泵电机驱动端径向轴承温度 | ℃ | float32
N1DCS.10LAB82CT304 | 18455 | #2中给泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10LAB82CT305 | 18456 | #2中压给水泵电机“W”绕组温度1 | ℃ | float32
N1DCS.10LAB82CT306 | 18457 | #2中压给水泵电机“W”绕组温度2 | ℃ | float32
N1DCS.10LAB82CT307 | 18458 | #2中压给水泵电机“V”绕组温度1 | ℃ | float32
N1DCS.10LAB82CT308 | 18459 | #2中压给水泵电机“V”绕组温度2 | ℃ | float32
N1DCS.10LAB82CT309 | 18460 | #2中压给水泵电机“U”绕组温度1 | ℃ | float32
N1DCS.10LAB82CT310 | 18461 | #2中压给水泵电机“U”绕组温度2 | ℃ | float32
N1DCS.10LAB82CT311 | 18462 | #2中给泵轴承冷却水回水温度1 | ℃ | float32
N1DCS.10LAB82CT312 | 18463 | #2中给泵轴承冷却水回水温度2 | ℃ | float32
N1DCS.10LAB82CT313 | 18464 | #2中给泵机密封冷却水回水温度1 | ℃ | float32
N1DCS.10LAB82CT314 | 18465 | #2中给泵机密封冷却水回水温度2 | ℃ | float32
N1DCS.10LAB82CT315 | 18466 | #2中给泵机密封冷却水回水温度3 | ℃ | float32
N1DCS.10LAB82CT316 | 18467 | #2中给泵机密封冷却水回水温度4 | ℃ | float32
N1DCS.10LAB82CY101 | 18468 | #2中给泵非驱动端轴承座振动(X向 | mm/s | float32
N1DCS.10LAB82CY102 | 18469 | #2中给泵非驱动端轴承座振动(Y向 | mm/s | float32
N1DCS.10LAB82CY103 | 18470 | #2中给泵驱动端轴承座振动（X向 | mm/s | float32
N1DCS.10LAB82CY104 | 18471 | #2中给泵驱动端轴承座振动（Y向 | mm/s | float32
N1DCS.10LAB90AA101C | 18472 | 高压给水气动调节阀控制指令 | % | float32
N1DCS.10LAB90AA101P | 18473 | 高压给水气动调节阀阀位反馈 |  | float32
N1DCS.10LAB90CF101 | 18474 | 高压给水流量1 | KPa | float32
N1DCS.10LAB90CF102 | 18475 | 高压给水流量2 | KPa | float32
N1DCS.10LAB90CF103 | 18476 | 高压给水流量3 | KPa | float32
N1DCS.10LAB90CP101 | 18477 | 高压给水调节阀前压力 | MPa | float32
N1DCS.10LAB90CP102 | 18478 | 高压给水调节阀后压力 | MPa | float32
N1DCS.10LAB90CT301 | 18479 | 高压给水温度1 | ℃ | float32
N1DCS.10LAB90CT302 | 18480 | 高压给水温度2 | ℃ | float32
N1DCS.10LAB90CT303 | 18481 | 高压给水温度3 | ℃ | float32
N1DCS.10LAB92AP001I | 18482 | #2高压给水泵电流 |  | float32
N1DCS.10LAB92CP102 | 18483 | #2高压给水泵出口压力 | MPa | float32
N1DCS.10LAB92CS101 | 18484 | #2高压给水泵转速 | rpm | float32
N1DCS.10LAB92CT301 | 18485 | #2高给泵进水端径向轴承轴瓦温度 | ℃ | float32
N1DCS.10LAB92CT302 | 18486 | #2高给泵出水端径向轴承轴瓦温度 | ℃ | float32
N1DCS.10LAB92CT303 | 18487 | #2高给泵电机驱动端径向轴承温度 | ℃ | float32
N1DCS.10LAB92CT304 | 18488 | #2高给泵电机非驱动端轴承温度 | ℃ | float32
N1DCS.10LAB92CT305 | 18489 | #2高压给水泵电机“W”绕组温度1 | ℃ | float32
N1DCS.10LAB92CT306 | 18490 | #2高压给水泵电机“W”绕组温度2 | ℃ | float32
N1DCS.10LAB92CT307 | 18491 | #2高压给水泵电机“V”绕组温度1 | ℃ | float32
N1DCS.10LAB92CT308 | 18492 | #2高压给水泵电机“V”绕组温度2 | ℃ | float32
N1DCS.10LAB92CT309 | 18493 | #2高压给水泵电机“U”绕组温度1 | ℃ | float32
N1DCS.10LAB92CT310 | 18494 | #2高压给水泵电机“U”绕组温度2 | ℃ | float32
N1DCS.10LAB92CT311 | 18495 | #2高给泵机密封冷却水回水温度1 | ℃ | float32
N1DCS.10LAB92CT312 | 18496 | #2高给泵机密封冷却水回水温度2 | ℃ | float32
N1DCS.10LAB92CT313 | 18497 | #2高给泵机密封冷却水回水温度3 | ℃ | float32
N1DCS.10LAB92CT314 | 18498 | #2高给泵机密封冷却水回水温度4 | ℃ | float32
N1DCS.10LAB92CY101 | 18499 | #2高给泵非驱动端轴承座振动(X向 | um | float32
N1DCS.10LAB92CY102 | 18500 | #2高给泵非驱动端轴承座振动(Y向 | um | float32
N1DCS.10LAB92CY103 | 18501 | #2高给泵驱动端轴承座振动(X向 | um | float32
N1DCS.10LAB92CY104 | 18502 | #2高给泵驱动端轴承座振动(Y向 | um | float32
N1DCS.10LAB93CP101 | 18503 | 高压省煤器出口压力 | MPa | float32
N1DCS.10LAB93CT301 | 18504 | 高压省煤器出口温度 | ℃ | float32
N1DCS.10LAC91GX0001_BIAS | 18505 | 高压给水泵变频器压力偏置值 |  | float32
N1DCS.10LAC91GX0001_LVL | 18506 | 高压给水泵变频器液位设定值 |  | float32
N1DCS.10LAC91GX0001_LVLT | 18507 | Ovation Control Builder |  | float32
N1DCS.10LAC91GX0001_PID | 18508 | 高压给水泵变频器PID输出 |  | float32
N1DCS.10LAC91GX0001_PIDT | 18509 | Ovation Control Builder |  | float32
N1DCS.10LAC91GX0001_SP | 18510 | Ovation Control Builder |  | float32
N1DCS.10LAC91GX0001_SP1 | 18511 | 高压给水泵变频器压力设定值 |  | float32
N1DCS.10LAC91GX0001C | 18512 | 高压给水泵变频器频率指令 | HZ | float32
N1DCS.10LAC91GX0001F | 18513 | 高压给水泵变频器频率反馈 | % | float32
N1DCS.10LAC91GX0001I | 18514 | 高压给水泵变频器电流反馈 |  | float32
N1DCS.10LAE90AA101_SPO | 18515 | 高压二级过热器减温调阀温度设定 |  | float32
N1DCS.10LAE90AA101C | 18516 | 高压二级过热器减温调阀控制指令 | % | float32
N1DCS.10LAE90AA101P | 18517 | 高压二级过热器减温调阀阀位反馈 |  | float32
N1DCS.10LAE90AA102_BIAS | 18518 | 高压主蒸汽减温水调节阀温度偏置 |  | float32
N1DCS.10LAE90AA102_SPO | 18519 | 高压主蒸汽减温水调节阀温度设定 |  | float32
N1DCS.10LAE90AA102C | 18520 | 高压主蒸汽减温水调节阀控制指令 | % | float32
N1DCS.10LAE90AA102P | 18521 | 高压主蒸汽减温水调节阀阀位反馈 |  | float32
N1DCS.10LAE90CF101 | 18522 | 高压过热器减温水流量 | KPa | float32
N1DCS.10LAE91AA101_BIAS | 18523 | 高压省煤器旁路调节阀温度偏置值 |  | float32
N1DCS.10LAE91AA101_SP | 18524 | Ovation Control Builder |  | float32
N1DCS.10LAE91AA101_SV | 18525 | Ovation Control Builder |  | float32
N1DCS.10LAE91AA101C | 18526 | 高压省煤器旁路调节阀控制指令 | % | float32
N1DCS.10LAE91AA101P | 18527 | 高压省煤器旁路调节阀阀位反馈 |  | float32
N1DCS.10LBA90AA502P | 18528 | 高压主蒸汽启动排汽门阀位反馈 |  | float32
N1DCS.10LBA90CF101 | 18529 | 高压主蒸汽流量1 | KPa | float32
N1DCS.10LBA90CF102 | 18530 | 高压主蒸汽流量2 | KPa | float32
N1DCS.10LBA90CF103 | 18531 | 高压主蒸汽流量3 | KPa | float32
N1DCS.10LBA90CP101 | 18532 | 高压主蒸汽压力1 | MPa | float32
N1DCS.10LBA90CP102 | 18533 | 高压主蒸汽压力2 | MPa | float32
N1DCS.10LBA90CP103 | 18534 | 高压主蒸汽压力3 | MPa | float32
N1DCS.10LBA90CT301 | 18535 | 高压主蒸汽温度1 | ℃ | float32
N1DCS.10LBA90CT302 | 18536 | 高压主蒸汽温度2 | ℃ | float32
N1DCS.10LBA90CT303 | 18537 | 高压主蒸汽温度3 | ℃ | float32
N1DCS.10XAV92CP101 | 18538 | #2高压给水泵稀油站供油母管压力 |  | float32
N1DCS.10XAV92CT301 | 18539 | #2高压给水泵稀油站油箱温度 | ℃ | float32
N1DCS.10XAV92CT302 | 18540 | #2高压给水泵稀油站供油母管温度 | ℃ | float32
N1DCS.10XAV92CT303 | 18541 | #2高压给水泵稀油站回油温度 | ℃ | float32
N1DCS.D9P1B1L3C9 | 18542 | TC温度补偿点 | C | float32
N1DCS.D9P1B2L6C9 | 18543 | TC温度补偿点 | C | float32
N1DCS.D9P1B2L7C9 | 18544 | TC温度补偿点 | C | float32
N1DCS.D9P1B3L2C9 | 18545 | TC温度补偿点 | C | float32
N1DCS.D9P1B3L3C9 | 18546 | TC温度补偿点 | C | float32
N1DCS.GYSJGRQJKWD | 18547 | 高压三级过热器进口温度（3选后) |  | float32
N1DCS.HPDRUMCP | 18548 | 高压汽包压力(3选后) |  | float32
N1DCS.HPDRUMCTD | 18549 | 高压汽包下外壁温(3选后) |  | float32
N1DCS.HPDRUMCTU | 18550 | 高压汽包上外壁温(3选后) |  | float32
N1DCS.HPDRUMCTU2 | 18551 | 高压汽包上内壁温(3选后) |  | float32
N1DCS.HPDRUMLVL | 18552 | 高压汽包液位(3选后) | mm | float32
N1DCS.HPDRUMLVL_A | 18553 | 高压汽包液位(计算后） |  | float32
N1DCS.HPDRUMLVL_B | 18554 | 高压汽包液位(计算后） |  | float32
N1DCS.HPDRUMLVL_C | 18555 | 高压汽包液位(计算后） |  | float32
N1DCS.HPDRUMLVL_DIF | 18556 | 高压汽包液位(3选后) |  | float32
N1DCS.HPDRUMLVLPIDOUT | 18557 | Ovation Control Builder |  | float32
N1DCS.HPDRUMLVLPIDTOUT | 18558 | Ovation Control Builder |  | float32
N1DCS.HPDRUMLVLSP | 18559 | 高压汽包液位偏置值-250mm |  | float32
N1DCS.HPDRUMLVLSP1 | 18560 | 高压汽包液位基本设定值 |  | float32
N1DCS.HPDRUMLVLSP2 | 18561 | 高压汽包液位最终设定值 |  | float32
N1DCS.HPDSTCF | 18562 | 高压主蒸汽流量（3选后） |  | float32
N1DCS.HPDSTCF_A | 18563 | 高压主蒸汽流量1（计算后） |  | float32
N1DCS.HPDSTCF_B | 18564 | 高压主蒸汽流量2（计算后） |  | float32
N1DCS.HPDSTCF_C | 18565 | 高压主蒸汽流量3（计算后） |  | float32
N1DCS.HPDSTCP | 18566 | 高压主蒸汽压力（3选后） |  | float32
N1DCS.HPDSTCT | 18567 | 高压主蒸汽温度（3选后） |  | float32
N1DCS.HPDWTCF | 18568 | 高压汽包给水流量(3选后) | t/h | float32
N1DCS.HPDWTCF_A | 18569 | 高压汽包给水流量1(计算后) |  | float32
N1DCS.HPDWTCF_B | 18570 | 高压汽包给水流量2(计算后) |  | float32
N1DCS.HPDWTCF_C | 18571 | 高压汽包给水流量3(计算后) |  | float32
N1DCS.HPDWTCT | 18572 | 高压汽包给水温度(3选后) |  | float32
N1DCS.HPFW_SEQSTSTEP | 18573 | 高压汽包上水顺控步号 |  | float32
N1DCS.HPFW_SEQSTTIME1 | 18574 | 高压汽包上水顺控第1步剩余时间 |  | float32
N1DCS.HPFW_SEQSTTIME2 | 18575 | 高压汽包上水顺控第2步剩余时间 |  | float32
N1DCS.HPFW_SEQSTTIME3 | 18576 | 高压汽包上水顺控第3步剩余时间 |  | float32
N1DCS.HPFW_SEQSTTIME4 | 18577 | 高压汽包上水顺控第4步剩余时间 |  | float32
N1DCS.HPFW_SEQSTTIME5 | 18578 | 高压汽包上水顺控第5步剩余时间 |  | float32
N1DCS.HPFW_SEQSTTIME6 | 18579 | 高压汽包上水顺控第6步剩余时间 |  | float32
N1DCS.HPFWPB_SEQSPSTEP | 18580 | #2高压给水泵停顺控步号 |  | float32
N1DCS.HPFWPB_SEQSPTIME1 | 18581 | #2高给泵停顺控第1步剩余时间 |  | float32
N1DCS.HPFWPB_SEQSPTIME2 | 18582 | #2高给泵停顺控第2步剩余时间 |  | float32
N1DCS.HPFWPB_SEQSTSTEP | 18583 | #2高压给水泵启顺控步号 |  | float32
N1DCS.HPFWPB_SEQSTTIME1 | 18584 | #2高给泵启顺控第1步剩余时间 |  | float32
N1DCS.HPFWPB_SEQSTTIME2 | 18585 | #2高给泵启顺控第2步剩余时间 |  | float32
N1DCS.HPFWPB_SEQSTTIME3 | 18586 | #2高给泵启顺控第3步剩余时间 |  | float32
N1DCS.HPFWPB_SEQSTTIME4 | 18587 | #2高给泵启顺控第4步剩余时间 |  | float32
N1DCS.HPFWPB_TPFO | 18588 | #2高给泵跳闸首出(打包点位号 |  | float32
N1DCS.HPMS_SEQSTSTEP | 18589 | 高压主蒸汽升温升压顺控步号 |  | float32
N1DCS.HPMS_SEQSTTIME1 | 18590 | 高压主汽升温升压顺控1步剩时间 |  | float32
N1DCS.HPMS_SEQSTTIME2 | 18591 | 高压主汽升温升压顺控2步剩时间 |  | float32
N1DCS.HPMS_SEQSTTIME3 | 18592 | 高压主汽升温升压顺控3步剩时间 |  | float32
N1DCS.HPMS_SEQSTTIME4 | 18593 | 高压主汽升温升压顺控4步剩时间 |  | float32
N1DCS.IPFWPB_SEQSPSTEP | 18594 | #2中压给水泵停顺控步号 |  | float32
N1DCS.IPFWPB_SEQSPTIME1 | 18595 | #2中给泵停顺控第1步剩余时间 |  | float32
N1DCS.IPFWPB_SEQSPTIME2 | 18596 | #2中给泵停顺控第2步剩余时间 |  | float32
N1DCS.IPFWPB_SEQSTSTEP | 18597 | #2中压给水泵启顺控步号 |  | float32
N1DCS.IPFWPB_SEQSTTIME1 | 18598 | #2中给泵启顺控第1步剩余时间 |  | float32
N1DCS.IPFWPB_SEQSTTIME2 | 18599 | #2中给泵启顺控第2步剩余时间 |  | float32
N1DCS.IPFWPB_SEQSTTIME3 | 18600 | #2中给泵启顺控第3步剩余时间 |  | float32
N1DCS.IPFWPB_TPFO | 18601 | #2中给泵跳闸首出(打包点位号 |  | float32
N1DCS.10HAD90CLB1 | 18602 | Ovation Control Builder |  | float32
N1DCS.10HAD90CLB2 | 18603 | Ovation Control Builder |  | float32
N1DCS.10HAD90CLB3 | 18604 | Ovation Control Builder |  | float32
N1DCS.10LAB93CT301A | 18605 | 高压省煤器出口水饱和温度 |  | float32
N1DCS.10LAC91GX0001_1BIAS | 18606 | 高压给水泵变频器压力偏置值 |  | float32
N1DCS.10LAC91GX0001_2BIAS | 18607 | 高压给水泵变频器液位偏置值 | mm | float32
N1DCS.10LAC91GX0001_SP2 | 18608 | Ovation Control Builder |  | float32
N1DCS.10LAC91GX0001I_BIAS | 18609 | Ovation Control Builder |  | float32
N1DCS.10LAC91GX0001I_SP | 18610 | Ovation Control Builder |  | float32
N1DCS.10LAE90AA101_BIAS | 18611 | Ovation Control Builder |  | float32
N1DCS.10LAE90AA101_SPO1 | 18612 | 高压二级过热器减温水调阀设定 |  | float32
N1DCS.10LAE90AA102_SP1 | 18613 | 高压二级过热器减温水调阀设定 |  | float32
N1DCS.10LAE90CF101I | 18614 | 高压过热器减温水流量（计算后） |  | float32
N1DCS.GHJK | 18615 | Ovation Control Builder |  | float32
N1DCS.GYBPSD | 18616 | Ovation Control Builder |  | float32
N1DCS.HPDRUMCT | 18617 | 高压给水泵变频器设定 |  | float32
N1DCS.HPDRUMLVLPIDOUT1 | 18618 | Ovation Control Builder |  | float32
N1DCS.HPDSTCF1 | 18619 | 高压主蒸汽流量（滤波后） |  | float32
N1DCS.HPDSTCT1 | 18620 | 高压主蒸汽温度 |  | float32
N1DCS.HPDWC | 18621 | 高压汽包上下壁温差 |  | float32
N1DCS.HPDWTCF_SUM | 18622 | 高压汽包给水累计流量 |  | float32
N1DCS.HPFWPB_SEQBPSTSTEP | 18623 | #2高给泵变频启顺控步号 |  | float32
N1DCS.HPFWPB_SEQBPSTTIME1 | 18624 | #2高给泵变频启顺控1步剩余时间 |  | float32
N1DCS.HPFWPB_SEQBPSTTIME2 | 18625 | #2高给泵变频启顺控2步剩余时间 |  | float32
N1DCS.HPFWPB_SEQBPSTTIME3 | 18626 | #2高给泵变频启顺控3步剩余时间 |  | float32
N1DCS.HPFWPB_SEQBPSTTIME4 | 18627 | #2高给泵变频启顺控4步剩余时间 |  | float32
N1DCS.HPLVLADD_OUT | 18628 | 高给泵变频三冲量副调设定 |  | float32
N1DCS.HPLVLPID1_OUT | 18629 | 高给泵变频三冲量主调输出 |  | float32
N1DCS.HPMS_SEQSTTIME5 | 18630 | 高压主汽升温升压顺控5步剩时间 |  | float32
N1DCS.HRSGFO | 18631 | HRSG跳闸首出（打包点位号 |  | float32
N1DCS.SCLSWSD | 18632 | Ovation Control Builder |  | float32
N1DCS.WJD | 18633 | 高压主蒸汽温降大 |  | float32
N1DCS.10BBA00CE001 | 18634 | 6KV IA段母线AC线电压 |  | float32
N1DCS.10BBA00CE101 | 18635 | 6KV IA段工作分支AC线电压 |  | float32
N1DCS.10BBA00GS001I | 18636 | 6KV IA段工作电源进线开关电流 |  | float32
N1DCS.10BBB00CE203 | 18637 | 6KV IA段备用分支AC线电压 |  | float32
N1DCS.10BBB00GS002I | 18638 | 6KV IA段备用电源进线开关电流 |  | float32
N1DCS.10BBB13GS001I | 18639 | #1SFC隔离变馈线开关电流 |  | float32
N1DCS.10BFA00CE201 | 18640 | 380V机组工作PC IA段AC线电压 |  | float32
N1DCS.10BFA00GS001I | 18641 | 380V机组工作段分段开关电流 |  | float32
N1DCS.10BFA00GS201I | 18642 | 380V工作PC IA至保安段开关电流 |  | float32
N1DCS.10BFT10GS101I | 18643 | 工作IA变6kV侧开关电流 |  | float32
N1DCS.10BFT10GS102I | 18644 | 工作IA变380V侧开关电流 |  | float32
N1DCS.10BJA00GS201I | 18645 | 工作PC IA段至#1机MCC A开关电流 |  | float32
N1DCS.10BJB00GS201I | 18646 | 工作PC IA段至#1机MCC B开关电流 |  | float32
N1DCS.10BJC00GS201I | 18647 | 工作PC IA段至#1炉MCC段开关电流 |  | float32
N1DCS.10BJD00GS201I | 18648 | 工作PC IA段至#2机MCC A开关电流 |  | float32
N1DCS.10BJE00GS201I | 18649 | 工作PC IA段至#2机MCC B开关电流 |  | float32
N1DCS.10BNA00GS201I | 18650 | 保安段至#2机EMCC段电源开关电流 |  | float32
N1DCS.12BAT01CE101 | 18651 | #1主变高压侧电流 | A | float32
N1DCS.12BAT01CE201 | 18652 | #1主变油温1 | ℃ | float32
N1DCS.12BAT01CE202 | 18653 | #1主变油温2 | ℃ | float32
N1DCS.12BAT01CE203 | 18654 | #1主变绕组温度 | ℃ | float32
N1DCS.12BAT01CE301 | 18655 | #1主变有功功率 | MW | float32
N1DCS.12BAT01CE302 | 18656 | #1主变无功功率 | MVAR | float32
N1DCS.12BAT01CE501 | 18657 | #1主变主表有功电度 | kWh | float32
N1DCS.12BAT01CE502 | 18658 | #1主变主表无功电度 | kWh | float32
N1DCS.12BAT01CE503 | 18659 | #1主变副表有功电度 | kWh | float32
N1DCS.12BAT01CE504 | 18660 | #1主变副表无功电度 | kWh | float32
N1DCS.12MKA01CE101 | 18661 | #1发电机A相电流 | A | float32
N1DCS.12MKA01CE102 | 18662 | #1发电机B相电流 | A | float32
N1DCS.12MKA01CE103 | 18663 | #1发电机C相电流 | A | float32
N1DCS.12MKA01CE201 | 18664 | #1发电机定子电压(A-C） | kV | float32
N1DCS.12MKA01CE202 | 18665 | #1发电机定子电压(A-B） | kV | float32
N1DCS.12MKA01CE203 | 18666 | #1发电机定子电压(B-C） | kV | float32
N1DCS.12MKA01CE204 | 18667 | #1发电机零序电压 | V | float32
N1DCS.12MKA01CE304 | 18668 | #1发电机有功功率 | MW | float32
N1DCS.12MKA01CE305 | 18669 | #1发电机无功功率 | MVAR | float32
N1DCS.12MKA01CE401 | 18670 | #1发电机频率 | Hz | float32
N1DCS.12MKA01CE402 | 18671 | #1发电机功率因数 |  | float32
N1DCS.12MKA01CE501 | 18672 | #1发电机有功电度 | kWh | float32
N1DCS.12MKA01CE502 | 18673 | #1发电机无功电度 | kWh | float32
N1DCS.12MKC01CE001 | 18674 | #1机励磁电压 |  | float32
N1DCS.12MKC01CE002 | 18675 | #1机励磁电流 |  | float32
N1DCS.12MKC01CE102 | 18676 | #1励磁变高压侧电流 |  | float32
N1DCS.12MKC01CE301 | 18677 | #1励磁变有功功率 |  | float32
N1DCS.12MKC01CE302 | 18678 | #1励磁变无功功率 |  | float32
N1DCS.12MKC01CE501 | 18679 | #1机励磁变有功电度 |  | float32
N1DCS.12MKC01CE502 | 18680 | #1机励磁变无功电度 |  | float32
N1DCS.12BAT01CE501CI | 18681 | #1主变主表有功电度 |  | float32
N1DCS.12BAT01CE502CI | 18682 | #1主变主表无功电度 |  | float32
N1DCS.12BAT01CE503CI | 18683 | #1主变副表有功电度 |  | float32
N1DCS.12BAT01CE504CI | 18684 | #1主变副表无功电度 |  | float32
N1DCS.12MKA01CE402_CAL | 18685 | #1发电机功率因数 |  | float32
N1DCS.12MKA01CE501_CI | 18686 | #1发电机有功电度（脉冲数） |  | float32
N1DCS.12MKA01CE501CI | 18687 | #1发电机有功电度 |  | float32
N1DCS.12MKA01CE502_CI | 18688 | #1发电机无功电度（脉冲数） |  | float32
N1DCS.12MKA01CE502CI | 18689 | #1发电机无功电度 |  | float32
N1DCS.12MKC01CE301CI | 18690 | #1励磁变有功功率 |  | float32
N1DCS.12MKC01CE302CI | 18691 | #1励磁变无功功率 |  | float32
N1DCS.12MKC01CE501CI | 18692 | #1励磁变有功电度 |  | float32
N1DCS.12MKC01CE502CI | 18693 | #1励磁变无功电度 |  | float32
N1DCS.QJBW_SEQSTSTEP | 18694 | #1机并网顺控步号 |  | float32
N1DCS.QJBW_SEQSTTIME1 | 18695 | #1机并网顺控第1步剩余时间 |  | float32
N1DCS.QJBW_SEQSTTIME2 | 18696 | #1机并网顺控第2步剩余时间 |  | float32
N1DCS.QJBW_SEQSTTIME3 | 18697 | #1机并网顺控第3步剩余时间 |  | float32
N1DCS.QJBW_SEQSTTIME4 | 18698 | #1机并网顺控第4步剩余时间 |  | float32
N1DCS.QJBW_SEQSTTIME5 | 18699 | #1机并网顺控第5步剩余时间 |  | float32
N1DCS.QJBW_SEQSTTIME6 | 18700 | #1机并网顺控第6步剩余时间 |  | float32
N1DCS.10BBA00CE203 | 18701 | 6KV IA段备用分支AC线电压 |  | float32
N1DCS.10BBA00GS002I | 18702 | 6KV IA段备用电源进线开关电流 |  | float32
N1DCS.10BBB00CE001 | 18703 | 6KV IB段母线AC线电压 |  | float32
N1DCS.10BBB00CE101 | 18704 | 6kV IB段工作分支AC线电压 |  | float32
N1DCS.10BBB00GS001I | 18705 | 6KV IB段工作进线开关电流 |  | float32
N1DCS.10BBT01CE101 | 18706 | #1高厂变油面温度1 | ℃ | float32
N1DCS.10BBT01CE102 | 18707 | #1高厂变油面温度2 | ℃ | float32
N1DCS.10BBT01CE103 | 18708 | #1高厂变绕组温度 | ℃ | float32
N1DCS.10BBT01CE301 | 18709 | #1高厂变有功功率 | MW | float32
N1DCS.10BBT01CE302 | 18710 | #1高厂变高压侧电流 | A | float32
N1DCS.10BBT01CE501 | 18711 | #1高厂变有功电度 | kWh | float32
N1DCS.10BBT01CE502 | 18712 | #1高厂变无功电度 | kWh | float32
N1DCS.10BFB00CE201 | 18713 | 380V工作PC IB段母线AC线电压 |  | float32
N1DCS.10BFB00GS201I | 18714 | 380V工作PC IB至保安段开关电流 |  | float32
N1DCS.10BFT20GS101I | 18715 | 工作IB变6kV侧开关电流 |  | float32
N1DCS.10BFT20GS102I | 18716 | 工作IB变380V侧开关电流 |  | float32
N1DCS.10BJA00GS202I | 18717 | 工作PC IB段至#1机MCC A开关电流 |  | float32
N1DCS.10BJB00GS202I | 18718 | 工作PC IB段至#1机MCC B开关电流 |  | float32
N1DCS.10BJC00GS202I | 18719 | 工作PC IB段至#1炉MCC段开关电流 |  | float32
N1DCS.10BJD00GS202I | 18720 | 工作PC IB段至#2机MCC A开关电流 |  | float32
N1DCS.10BJE00GS202I | 18721 | 工作PC IB段至#2机MCC B开关电流 |  | float32
N1DCS.10BMA00CE201 | 18722 | 380V保安段母线AC线电压 |  | float32
N1DCS.10BMA00GS001I | 18723 | 保安段柴油发电机K11开关电流 |  | float32
N1DCS.10BMA00GS002I | 18724 | 保安段工作电源进线K12开关电流 |  | float32
N1DCS.10BMA00GS003I | 18725 | 保安段工作电源进线K13开关电流 |  | float32
N1DCS.10BNA00GS202I | 18726 | 工作PC IB段至#2机EMCC开关电流 |  | float32
N1DCS.10BRU03CE101 | 18727 | #1机组UPS系统进线电流 |  | float32
N1DCS.10BRU03CE201 | 18728 | #1机组UPS系统母线电压 |  | float32
N1DCS.10BRU03CE401 | 18729 | #1机组UPS系统母线频率 |  | float32
N1DCS.10BTB01CE101 | 18730 | #1机组110V直流电池组1输出电流 |  | float32
N1DCS.10BTB01CE102 | 18731 | #1机组110V直流电池组1输出电压 |  | float32
N1DCS.10BTB02CE101 | 18732 | #1机组110V直流电池组2输出电流 |  | float32
N1DCS.10BTB02CE102 | 18733 | #1机组110V直流电池组2输出电压 |  | float32
N1DCS.10BTL01CE101 | 18734 | #1机组220V直流系统整流输出电流 |  | float32
N1DCS.10BTL01CE102 | 18735 | #1机组220V直流系统整流输出电压 |  | float32
N1DCS.10BTM01CE101 | 18736 | #1机组110V直流A段整流输出电流 |  | float32
N1DCS.10BTM01CE102 | 18737 | #1机组110V直流A段整流输出电压 |  | float32
N1DCS.10BTM01CE201 | 18738 | #1机组110V直流A段直流母线电压 |  | float32
N1DCS.10BTM02CE101 | 18739 | #1机组110V直流B段整流输出电流 |  | float32
N1DCS.10BTM02CE102 | 18740 | #1机组110V直流B段整流输出电压 |  | float32
N1DCS.10BTM02CE201 | 18741 | #1机组110V直流B段直流母线电压 |  | float32
N1DCS.10BUA02CE101 | 18742 | #1机组220V直流系统电池输出电流 |  | float32
N1DCS.10BUA02CE102 | 18743 | #1机组220V直流系统电池输出电压 |  | float32
N1DCS.10BUA02CE201 | 18744 | #1机组220V直流B段直流母线电压 |  | float32
N1DCS.10MJA01CE102 | 18745 | #1机组柴油发电机B相电流 |  | float32
N1DCS.10MJA01CE203 | 18746 | #1机组柴油发电机AC相线电压 |  | float32
N1DCS.10MJA01CE501 | 18747 | #1机组柴油发电机有功功率 |  | float32
N1DCS.11BAT01CE101 | 18748 | #2主变高压侧电流 | A | float32
N1DCS.11BAT01CE102 | 18749 | #2主变高压侧电压(A-C） | V | float32
N1DCS.11BAT01CE103 | 18750 | #2主变220kV侧系统频率 | Hz | float32
N1DCS.11BAT01CE201 | 18751 | #2主变油温1 | ℃ | float32
N1DCS.11BAT01CE202 | 18752 | #2主变油温2 | ℃ | float32
N1DCS.11BAT01CE203 | 18753 | #2主变绕组温度 | ℃ | float32
N1DCS.11BAT01CE301 | 18754 | #2主变有功功率 | MW | float32
N1DCS.11BAT01CE302 | 18755 | #2主变无功功率 | MVAR | float32
N1DCS.11BAT01CE501 | 18756 | #2主变主表有功电度 | kWh | float32
N1DCS.11BAT01CE502 | 18757 | #2主变主表无功电度 | kWh | float32
N1DCS.11BAT01CE503 | 18758 | #2主变副表有功电度 | kWh | float32
N1DCS.11BAT01CE504 | 18759 | #2主变副表无功电度 | kWh | float32
N1DCS.11MKA01CE501 | 18760 | #2发电机有功电度 | kWh | float32
N1DCS.11MKA01CE502 | 18761 | #2发电机无功电度 | kWh | float32
N1DCS.11MKC01CE501 | 18762 | #2发电机励磁变有功电度 | kWh | float32
N1DCS.11MKC01CE502 | 18763 | #2发电机励磁变无功电度 | kWh | float32
N1DCS.10BBT01CE501CI | 18764 | #1高厂变有功电度 |  | float32
N1DCS.10BBT01CE502CI | 18765 | #1高厂变无功电度 |  | float32
N1DCS.11BAT01CE501CI | 18766 | #2主变主表有功电度 |  | float32
N1DCS.11BAT01CE502CI | 18767 | #2主变主表无功电度 |  | float32
N1DCS.11BAT01CE503CI | 18768 | #2主变副表有功电度 |  | float32
N1DCS.11BAT01CE504CI | 18769 | #2主变副表无功电度 |  | float32
N1DCS.11MKA01CE501CI | 18770 | #2发电机有功电度 |  | float32
N1DCS.11MKA01CE502CI | 18771 | #2发电机无功电度 |  | float32
N1DCS.11MKC01CE501CI | 18772 | #2发电机励磁变有功电度 |  | float32
N1DCS.11MKC01CE502CI | 18773 | #2发电机励磁变无功电度 |  | float32
N1DCS.APSSPBP1_SEQSTEP | 18774 | 降负荷断点步号 |  | float32
N1DCS.APSSPBP1_SEQTIME1 | 18775 | 降负荷断点第1步剩余时间 |  | float32
N1DCS.APSSPBP1_SEQTIME2 | 18776 | 降负荷断点第2步剩余时间 |  | float32
N1DCS.APSSPBP1_SEQTIME3 | 18777 | 降负荷断点第3步剩余时间 |  | float32
N1DCS.APSSPBP1_SEQTIME4 | 18778 | 降负荷断点第4步剩余时间 |  | float32
N1DCS.APSSPBP1_SEQTIME5 | 18779 | 降负荷断点第5步剩余时间 |  | float32
N1DCS.APSSPBP1_SEQTIME6 | 18780 | 降负荷断点第6步剩余时间 |  | float32
N1DCS.APSSPBP1_SEQTIME7 | 18781 | 降负荷断点第7步剩余时间 |  | float32
N1DCS.APSSPBP1_SEQTIME8 | 18782 | 降负荷断点第8步剩余时间 |  | float32
N1DCS.APSSPBP2_SEQSTEP | 18783 | #2机打闸断点步号 |  | float32
N1DCS.APSSPBP2_SEQTIME1 | 18784 | #2机打闸断点第1步剩余时间 |  | float32
N1DCS.APSSPBP2_SEQTIME2 | 18785 | #2机打闸断点第2步剩余时间 |  | float32
N1DCS.APSSPBP2_SEQTIME3 | 18786 | #2机打闸断点第3步剩余时间 |  | float32
N1DCS.APSSPBP2_SEQTIME4 | 18787 | #2机打闸断点第4步剩余时间 |  | float32
N1DCS.APSSPBP2_SEQTIME5 | 18788 | #2机打闸断点第5步剩余时间 |  | float32
N1DCS.APSSPBP2_SEQTIME6 | 18789 | #2机打闸断点第6步剩余时间 |  | float32
N1DCS.APSSPBP2_SEQTIME7 | 18790 | #2机打闸断点第7步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQSTEP | 18791 | 余热锅炉停止断点步号 |  | float32
N1DCS.APSSPBP3_SEQTIME1 | 18792 | 余热锅炉停止断点第1步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME2 | 18793 | 余热锅炉停止断点第2步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME3 | 18794 | 余热锅炉停止断点第3步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME4 | 18795 | 余热锅炉停止断点第4步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME5 | 18796 | 余热锅炉停止断点第5步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME6 | 18797 | 余热锅炉停止断点第6步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME7 | 18798 | 余热锅炉停止断点第7步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME8 | 18799 | 余热锅炉停止断点第8步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQSTEP | 18800 | 机组停运断点步号 |  | float32
N1DCS.APSSPBP4_SEQTIME1 | 18801 | 机组停运断点第1步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME2 | 18802 | 机组停运断点第2步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME3 | 18803 | 机组停运断点第3步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME4 | 18804 | 机组停运断点第4步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME5 | 18805 | 机组停运断点第5步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME6 | 18806 | 机组停运断点第6步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME7 | 18807 | 机组停运断点第7步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME8 | 18808 | 机组停运断点第8步剩余时间 |  | float32
N1DCS.APSSTBP1_SEQSTEP | 18809 | 系统准备断点步号 |  | float32
N1DCS.APSSTBP1_SEQTIME1 | 18810 | 系统准备断点第1步剩余时间 |  | float32
N1DCS.APSSTBP1_SEQTIME2 | 18811 | 系统准备断点第2步剩余时间 |  | float32
N1DCS.APSSTBP1_SEQTIME3 | 18812 | 系统准备断点第3步剩余时间 |  | float32
N1DCS.APSSTBP1_SEQTIME4 | 18813 | 系统准备断点第4步剩余时间 |  | float32
N1DCS.APSSTBP1_SEQTIME5 | 18814 | 系统准备断点第5步剩余时间 |  | float32
N1DCS.APSSTBP1_SEQTIME6 | 18815 | 系统准备断点第6步剩余时间 |  | float32
N1DCS.APSSTBP2_SEQSTEP | 18816 | 机组上水断点步号 |  | float32
N1DCS.APSSTBP2_SEQTIME1 | 18817 | 机组上水断点第1步剩余时间 |  | float32
N1DCS.APSSTBP2_SEQTIME2 | 18818 | 机组上水断点第2步剩余时间 |  | float32
N1DCS.APSSTBP2_SEQTIME3 | 18819 | 机组上水断点第3步剩余时间 |  | float32
N1DCS.APSSTBP2_SEQTIME4 | 18820 | 机组上水断点第4步剩余时间 |  | float32
N1DCS.APSSTBP2_SEQTIME5 | 18821 | 机组上水断点第5步剩余时间 |  | float32
N1DCS.APSSTBP2_SEQTIME6 | 18822 | 机组上水断点第6步剩余时间 |  | float32
N1DCS.APSSTBP2_SEQTIME7 | 18823 | 机组上水断点第7步剩余时间 |  | float32
N1DCS.APSSTBP3_SEQSTEP | 18824 | #2机点火断点步号 |  | float32
N1DCS.APSSTBP3_SEQTIME1 | 18825 | #2机点火断点第1步剩余时间 |  | float32
N1DCS.APSSTBP3_SEQTIME2 | 18826 | #2机点火断点第2步剩余时间 |  | float32
N1DCS.APSSTBP3_SEQTIME3 | 18827 | #2机点火断点第3步剩余时间 |  | float32
N1DCS.APSSTBP3_SEQTIME4 | 18828 | #2机点火断点第4步剩余时间 |  | float32
N1DCS.APSSTBP3_SEQTIME5 | 18829 | #2机点火断点第5步剩余时间 |  | float32
N1DCS.APSSTBP3_SEQTIME6 | 18830 | #2机点火断点第6步剩余时间 |  | float32
N1DCS.APSSTBP3_SEQTIME7 | 18831 | #2机点火断点第7步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQSTEP | 18832 | #1机并网断点步号 |  | float32
N1DCS.APSSTBP4_SEQTIME1 | 18833 | #1机并网断点第1步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME2 | 18834 | #1机并网断点第2步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME3 | 18835 | #1机并网断点第3步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME4 | 18836 | #1机并网断点第4步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME5 | 18837 | #1机并网断点第5步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME6 | 18838 | #1机并网断点第6步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME7 | 18839 | #1机并网断点第7步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME8 | 18840 | #1机并网断点第8步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQSTEP | 18841 | 升负荷断点步号 |  | float32
N1DCS.APSSTBP5_SEQTIME1 | 18842 | 升负荷断点第1步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME2 | 18843 | 升负荷断点第2步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME3 | 18844 | 升负荷断点第3步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME4 | 18845 | 升负荷断点第4步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME5 | 18846 | 升负荷断点第5步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME6 | 18847 | 升负荷断点第6步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME7 | 18848 | 升负荷断点第7步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME8 | 18849 | 升负荷断点第8步剩余时间 |  | float32
N1DCS.TURBWARMTIME | 18850 | 暖机时间 |  | float32
N1DCS.10AO1005GT | 18851 | Ovation Control Builder |  | float32
N1DCS.10LBA10CP | 18852 | 高压主蒸汽压力 |  | float32
N1DCS.10LBA30CP | 18853 | Ovation Control Builder |  | float32
N1DCS.10LBA30CT301 | 18854 | Ovation Control Builder |  | float32
N1DCS.10LBA70CF | 18855 | 低压主蒸汽流量 |  | float32
N1DCS.10LBA80CF | 18856 | 中压主蒸汽流量 |  | float32
N1DCS.10LBA90CF | 18857 | 高压主蒸汽流量 |  | float32
N1DCS.10TCSAI04 | 18858 | Ovation Control Builder |  | float32
N1DCS.AGCLOADDMD | 18859 | Ovation Control Builder |  | float32
N1DCS.APSSPBP1_SEQTIME10 | 18860 | 降负荷断点第10步剩余时间 |  | float32
N1DCS.APSSPBP1_SEQTIME9 | 18861 | 降负荷断点第9步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME10 | 18862 | 余热锅炉停止断点第10步剩余时间 |  | float32
N1DCS.APSSPBP3_SEQTIME9 | 18863 | 余热锅炉停止断点第9步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME10 | 18864 | 机组停运断点第10步剩余时间 |  | float32
N1DCS.APSSPBP4_SEQTIME9 | 18865 | 机组停运断点第9步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME10 | 18866 | #1机并网断点第10步剩余时间 |  | float32
N1DCS.APSSTBP4_SEQTIME9 | 18867 | #1机并网断点第9步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME10 | 18868 | 升负荷断点第10步剩余时间 |  | float32
N1DCS.APSSTBP5_SEQTIME9 | 18869 | 升负荷断点第9步剩余时间 |  | float32
N1DCS.GTFREQ | 18870 | #2机频率偏差 |  | float32
N1DCS.GTRATE | 18871 | #2机负荷变化率 |  | float32
N1DCS.HPCVPOS | 18872 | 高压调阀开度 |  | float32
N1DCS.HPSVPOS | 18873 | 高压主汽门开度 |  | float32
N1DCS.IPCVPOS | 18874 | 中压调阀开度 |  | float32
N1DCS.LOADRATE | 18875 | 第一套机组总负荷变化率 |  | float32
N1DCS.LOADSP | 18876 | Ovation Control Builder |  | float32
N1DCS.LPCVPOS | 18877 | 低压调阀开度 |  | float32
N1DCS.TUERB_SPEED | 18878 | Ovation Control Builder |  | float32
N1DCS.WKWH_TODAY_0 | 18879 | Ovation Control Builder |  | float32
N1DCS.WKWH_TODAY_1 | 18880 | Ovation Control Builder |  | float32
N1DCS.WKWH_TODAY_2 | 18881 | Ovation Control Builder |  | float32
N1DCS.WKWH_TODAY_3 | 18882 | Ovation Control Builder |  | float32
N1DCS.10LBG11CT301 | 18883 | #1机高排至辅汽母管减温器后温度 | ℃ | float32
N1DCS.10QUA01CQ101 | 18884 | #1炉凝结水泵出口电导CC | us/cm | float32
N1DCS.10QUA01CQ102 | 18885 | #1炉凝结水泵出口溶氧O2 | ppm | float32
N1DCS.10QUA02CQ101 | 18886 | #1炉凝结水加药点后电导率SC | us/cm | float32
N1DCS.10QUA03CQ101 | 18887 | #1炉中压省煤器入口电导率SC | us/cm | float32
N1DCS.10QUA03CQ102 | 18888 | #1炉中压省煤器入口电导CC | us/cm | float32
N1DCS.10QUA03CQ103 | 18889 | #1炉中压省煤器入口PH |  | float32
N1DCS.10QUA03CQ104 | 18890 | #1炉中压省煤器入口溶氧O2 | ppm | float32
N1DCS.10QUA04CQ101 | 18891 | #1炉高压省煤器入口电导率SC | us/cm | float32
N1DCS.10QUA04CQ102 | 18892 | #1炉高压省煤器入口电导CC | us/cm | float32
N1DCS.10QUA04CQ103 | 18893 | #1炉高压省煤器入口PH |  | float32
N1DCS.10QUA04CQ104 | 18894 | #1炉高压省煤器入口溶氧O2 | ppm | float32
N1DCS.10QUA05CQ101 | 18895 | #1炉低压汽包炉水电导CC | us/cm | float32
N1DCS.10QUA05CQ102 | 18896 | #1炉低压汽包炉水PH |  | float32
N1DCS.10QUA05CQ103 | 18897 | #1炉低压汽包炉水溶氧O2 | ppm | float32
N1DCS.10QUA06CQ101 | 18898 | #1炉中压汽包炉水电导率SC | us/cm | float32
N1DCS.10QUA06CQ102 | 18899 | #1炉中压汽包炉水PH |  | float32
N1DCS.10QUA06CQ103 | 18900 | #1炉中压汽包炉水PO4 | mg/L | float32
N1DCS.10QUA06CQ104 | 18901 | #1炉中压汽包炉水SiO2 | μg/L | float32
N1DCS.10QUA07CQ101 | 18902 | #1炉高压汽包炉水电导率SC | us/cm | float32
N1DCS.10QUA07CQ102 | 18903 | #1炉高压汽包炉水PH |  | float32
N1DCS.10QUA07CQ103 | 18904 | #1炉高压汽包炉水PO4 | mg/L | float32
N1DCS.10QUA07CQ104 | 18905 | #1炉高压汽包炉水SiO2 | μg/L | float32
N1DCS.10QUA08CQ101 | 18906 | #1炉低压饱和蒸汽电导CC | us/cm | float32
N1DCS.10QUA09CQ101 | 18907 | #1炉中压饱和蒸汽电导CC | us/cm | float32
N1DCS.10QUA10CQ101 | 18908 | #1炉高压饱和蒸汽电导CC | us/cm | float32
N1DCS.10QUA11CQ101 | 18909 | #1炉低压过热蒸汽电导CC | us/cm | float32
N1DCS.10QUA12CQ101 | 18910 | #1炉中压过热蒸汽电导CC | us/cm | float32
N1DCS.10QUA13CQ101 | 18911 | #1炉高压过热蒸汽电导CC | us/cm | float32
N1DCS.10QUA13CQ102 | 18912 | #1炉高压过热蒸汽Na | ppb | float32
N1DCS.10QUA14CQ101 | 18913 | #1炉再热蒸汽电导CC | us/cm | float32
N1DCS.10QUA15CQ101 | 18914 | #1炉闭式冷却水出口母管电导率SC | us/cm | float32
N1DCS.10QUA15CQ102 | 18915 | #1炉闭式冷却水出口母管PH |  | float32
N1DCS.10QUA16CQ101 | 18916 | #2机发电机内冷水电导率SC | us/cm | float32
N1DCS.10QUA16CQ102 | 18917 | #2机发电机内冷水PH |  | float32
N1DCS.20LBG11CT301 | 18918 | #3机高排至辅汽母管减温器后温度 | ℃ | float32
N1DCS.20QUA01CQ101 | 18919 | #3炉凝结水泵出口电导CC | us/cm | float32
N1DCS.20QUA01CQ102 | 18920 | #3炉凝结水泵出口溶氧O2 | us/cm | float32
N1DCS.20QUA02CQ101 | 18921 | #3炉凝结水加药点后电导率SC | ppb | float32
N1DCS.20QUA03CQ101 | 18922 | #3炉中压省煤器入口电导率SC | us/cm | float32
N1DCS.20QUA03CQ102 | 18923 | #3炉中压省煤器入口电导CC | us/cm | float32
N1DCS.20QUA03CQ103 | 18924 | #3炉中压省煤器入口PH | % | float32
N1DCS.20QUA03CQ104 | 18925 | #3炉中压省煤器入口溶氧O2 | % | float32
N1DCS.20QUA04CQ101 | 18926 | #3炉高压省煤器入口电导率SC | us/cm | float32
N1DCS.20QUA04CQ102 | 18927 | #3炉高压省煤器入口电导CC | ppm | float32
N1DCS.20QUA04CQ103 | 18928 | #3炉高压省煤器入口PH | us/cm | float32
N1DCS.20QUA04CQ104 | 18929 | #3炉高压省煤器入口溶氧O2 | us/cm | float32
N1DCS.20QUA05CQ101 | 18930 | #3炉低压汽包炉水电导CC | us/cm | float32
N1DCS.20QUA05CQ102 | 18931 | #3炉低压汽包炉水PH |  | float32
N1DCS.20QUA05CQ103 | 18932 | #3炉低压汽包炉水溶氧O2 | ppm | float32
N1DCS.20QUA06CQ101 | 18933 | #3炉中压汽包炉水电导率SC | us/cm | float32
N1DCS.20QUA06CQ102 | 18934 | #3炉中压汽包炉水PH | us/cm | float32
N1DCS.20QUA06CQ103 | 18935 | #3炉中压汽包炉水PO4 |  | float32
N1DCS.20QUA06CQ104 | 18936 | #3炉中压汽包炉水SiO2 | ppm | float32
N1DCS.20QUA07CQ101 | 18937 | #3炉高压汽包炉水电导率SC | us/cm | float32
N1DCS.20QUA07CQ102 | 18938 | #3炉高压汽包炉水PH |  | float32
N1DCS.20QUA07CQ103 | 18939 | #3炉高压汽包炉水PO4 | ppm | float32
N1DCS.20QUA07CQ104 | 18940 | #3炉高压汽包炉水SiO2 | us/cm | float32
N1DCS.20QUA08CQ101 | 18941 | #3炉低压饱和蒸汽电导CC |  | float32
N1DCS.20QUA09CQ101 | 18942 | #3炉中压饱和蒸汽电导CC | mg/L | float32
N1DCS.20QUA10CQ101 | 18943 | #3炉高压饱和蒸汽电导CC | μg/L | float32
N1DCS.20QUA11CQ101 | 18944 | #3炉低压过热蒸汽电导CC | us/cm | float32
N1DCS.20QUA12CQ101 | 18945 | #3炉中压过热蒸汽电导CC |  | float32
N1DCS.20QUA13CQ101 | 18946 | #3炉高压过热蒸汽电导CC | mg/L | float32
N1DCS.20QUA13CQ102 | 18947 | #3炉高压过热蒸汽Na | μg/L | float32
N1DCS.20QUA14CQ101 | 18948 | #3炉再热蒸汽电导CC | us/cm | float32
N1DCS.20QUA15CQ101 | 18949 | #3炉闭式冷却水出口母管电导率SC | us/cm | float32
N1DCS.20QUA15CQ102 | 18950 | #3炉闭式冷却水出口母管PH | us/cm | float32
N1DCS.20QUA16CQ101 | 18951 | #4机发电机内冷水电导率SC | us/cm | float32
N1DCS.20QUA16CQ102 | 18952 | #4机发电机内冷水PH |  | float32
N1DCS.D31P1B1L6C9 | 18953 | TC温度补偿点 | C | float32
N1DCS.J0LBD20CF101 | 18954 | 供热计量站母管流量 | t/h | float32
N1DCS.J0LBD20CF101AO | 18955 | 供热计量站母管流量 | % | float32
N1DCS.J0LBD20CF102 | 18956 | 供热计量站旁路母管流量 | t/h | float32
N1DCS.J0LBD20CF102AO | 18957 | 供热计量站旁路母管流量 | % | float32
N1DCS.J0LBD20CP101 | 18958 | 供热计量站母管压力 | MPa | float32
N1DCS.J0LBD20CP101AO | 18959 | 供热计量站母管压力 | % | float32
N1DCS.J0LBD20CT303 | 18960 | 供热计量站母管蒸汽温度 | ℃ | float32
N1DCS.J0LBD20CT303AO | 18961 | 供热计量站母管蒸汽温度 | % | float32
N1DCS.J0LBG10CP101 | 18962 | #1机侧辅汽母管压力 | MPa | float32
N1DCS.J0LBG10CP102 | 18963 | #3机侧辅汽母管压力 | MPa | float32
N1DCS.J0LBG10CT301 | 18964 | #1机侧辅汽母管温度 | ℃ | float32
N1DCS.J0LBG10CT302 | 18965 | #3机侧辅汽母管温度 | ℃ | float32
N1DCS.J0LBG22CP101 | 18966 | 启动锅炉供辅汽母管压力 | MPa | float32
N1DCS.J0LBG22CT301 | 18967 | 启动锅炉供辅汽温度 | ℃ | float32
N1DCS.J0QCA21CL101 | 18968 | #1氨溶液箱液位 | m | float32
N1DCS.J0QCA21CQ101 | 18969 | #1氨溶液箱电导率 | us/cm | float32
N1DCS.J0QCA22CL101 | 18970 | #2氨溶液箱液位 | m | float32
N1DCS.J0QCA22CQ101 | 18971 | #2氨溶液箱电导率 | us/cm | float32
N1DCS.J0QCA31AP001C | 18972 | #1中压给水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA31AP001P | 18973 | #1中压给水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCA32AP001C | 18974 | #2中压给水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA32AP001P | 18975 | #2中压给水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCA33AP001C | 18976 | #3中压给水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA33AP001P | 18977 | #3中压给水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCA34AP001C | 18978 | #1高压给水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA34AP001P | 18979 | #1高压给水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCA35AP001C | 18980 | #2高压给水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA35AP001P | 18981 | #2高压给水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCA36AP001C | 18982 | #3高压给水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA36AP001P | 18983 | #3高压给水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCA37AP001C | 18984 | #1凝结水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA37AP001P | 18985 | #1凝结水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCA38AP001C | 18986 | #2凝结水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA38AP001P | 18987 | #2凝结水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCA39AP001C | 18988 | #3凝结水加氨泵变频器频率指令 | % | float32
N1DCS.J0QCA39AP001P | 18989 | #3凝结水加氨泵变频器频率反馈 | % | float32
N1DCS.J0QCB21CL101 | 18990 | #1联氨溶液箱液位 | mm | float32
N1DCS.J0QCB22CL101 | 18991 | #2联氨溶液箱液位 | mm | float32
N1DCS.J0QCB31AP001C | 18992 | #1联氨加药泵变频器频率指令 | % | float32
N1DCS.J0QCB31AP001P | 18993 | #1联氨加药泵变频器频率反馈 | % | float32
N1DCS.J0QCB32AP001C | 18994 | #2联氨加药泵变频器频率指令 | % | float32
N1DCS.J0QCB32AP001P | 18995 | #2联氨加药泵变频器频率反馈 | % | float32
N1DCS.J0QCB33AP001C | 18996 | #3联氨加药泵变频器频率指令 | % | float32
N1DCS.J0QCB33AP001P | 18997 | #3联氨加药泵变频器频率反馈 | % | float32
N1DCS.J0QCB34AP001C | 18998 | #4联氨加药泵变频器频率指令 | % | float32
N1DCS.J0QCB34AP001P | 18999 | #4联氨加药泵变频器频率反馈 | % | float32
N1DCS.J0QCB35AP001C | 19000 | #5联氨加药泵变频器频率指令 | % | float32
N1DCS.J0QCB35AP001P | 19001 | #5联氨加药泵变频器频率反馈 | % | float32
N1DCS.J0QCB36AP001C | 19002 | #6联氨加药泵变频器频率指令 | % | float32
N1DCS.J0QCB36AP001P | 19003 | #6联氨加药泵变频器频率反馈 | % | float32
N1DCS.J0QCC21CL101 | 19004 | #1磷酸盐溶液箱液位 | mm | float32
N1DCS.J0QCC22CL101 | 19005 | #2磷酸盐溶液箱液位 | mm | float32
N1DCS.J0QCC31AP001C | 19006 | #1磷酸盐加药泵变频器频率指令 | % | float32
N1DCS.J0QCC31AP001P | 19007 | #1磷酸盐加药泵变频器频率反馈 | % | float32
N1DCS.J0QCC32AP001C | 19008 | #2磷酸盐加药泵变频器频率指令 | % | float32
N1DCS.J0QCC32AP001P | 19009 | #2磷酸盐加药泵变频器频率反馈 | % | float32
N1DCS.J0QCC33AP001C | 19010 | #3磷酸盐加药泵变频器频率指令 | % | float32
N1DCS.J0QCC33AP001P | 19011 | #3磷酸盐加药泵变频器频率反馈 | % | float32
N1DCS.J0QCC34AP001C | 19012 | #4磷酸盐加药泵变频器频率指令 | % | float32
N1DCS.J0QCC34AP001P | 19013 | #4磷酸盐加药泵变频器频率反馈 | % | float32
N1DCS.J0QCC35AP001C | 19014 | #5磷酸盐加药泵变频器频率指令 | % | float32
N1DCS.J0QCC35AP001P | 19015 | #5磷酸盐加药泵变频器频率反馈 | % | float32
N1DCS.J0QCC36AP001C | 19016 | #6磷酸盐加药泵变频器频率指令 | % | float32
N1DCS.J0QCC36AP001P | 19017 | #6磷酸盐加药泵变频器频率反馈 | % | float32
N1DCS.10MYA01CS901CA | 19018 | #2机实际转速 |  | float32
N1DCS.J0QCA21AA001HLFB | 19019 | #1氨溶液箱自动停止加氨设定值 |  | float32
N1DCS.J0QCA21AA001LLFB | 19020 | #1氨溶液箱自动加氨设定值 |  | float32
N1DCS.J0QCA21AA002HLFB | 19021 | #1氨溶液箱自动停止加水设定值 |  | float32
N1DCS.J0QCA21AA002LLFB | 19022 | #1氨溶液箱自动加水设定值 |  | float32
N1DCS.J0QCA21CQ101SH | 19023 | #1氨溶液箱电导率高值设定 |  | float32
N1DCS.J0QCA21CQ101SL | 19024 | #1氨溶液箱电导率低值设定 |  | float32
N1DCS.J0QCA22AA001HLFB | 19025 | #2氨溶液箱自动停止加氨设定值 |  | float32
N1DCS.J0QCA22AA001LLFB | 19026 | #2氨溶液箱自动加氨设定值 |  | float32
N1DCS.J0QCA22AA002HLFB | 19027 | #2氨溶液箱自动停止加水设定值 |  | float32
N1DCS.J0QCA22AA002LLFB | 19028 | #2氨溶液箱自动加水设定值 |  | float32
N1DCS.J0QCA22CQ101SH | 19029 | #2氨溶液箱电导率高值设定 |  | float32
N1DCS.J0QCA22CQ101SL | 19030 | #2氨溶液电导率低限设定 |  | float32
N1DCS.J0QCA31AP001SP | 19031 | #1中压给水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCA32AP001SP | 19032 | #2中压给水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCA33AP001SP | 19033 | #3中压给水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCA34AP001SP | 19034 | #1高压给水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCA35AP001SP | 19035 | #2高压给水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCA36AP001SP | 19036 | #3高压给水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCA37AP001SP | 19037 | #1凝结水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCA38AP001SP | 19038 | #2凝结水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCA39AP001SP | 19039 | #3凝结水加氨泵变频器频率设定 |  | float32
N1DCS.J0QCB31AP001SP | 19040 | #1联氨加药泵变频器频率设定 |  | float32
N1DCS.J0QCB32AP001SP | 19041 | #2联氨加药泵变频器频率设定 |  | float32
N1DCS.J0QCB33AP001SP | 19042 | #3联氨加药泵变频器频率设定 |  | float32
N1DCS.J0QCB34AP001SP | 19043 | #4联氨加药泵变频器频率设定 |  | float32
N1DCS.J0QCB35AP001SP | 19044 | #5联氨加药泵变频器频率设定 |  | float32
N1DCS.J0QCB36AP001SP | 19045 | #6联氨加药泵变频器频率设定 |  | float32
N1DCS.J0QCC31AP001SP | 19046 | #1磷酸盐加药泵变频器频率设定 |  | float32
N1DCS.J0QCC32AP001SP | 19047 | #2磷酸盐加药泵变频器频率设定 |  | float32
N1DCS.J0QCC33AP001SP | 19048 | #3磷酸盐加药泵变频器频率设定 |  | float32
N1DCS.J0QCC34AP001SP | 19049 | #4磷酸盐加药泵变频器频率设定 |  | float32
N1DCS.J0QCC35AP001SP | 19050 | #5磷酸盐加药泵变频器频率设定 |  | float32
N1DCS.J0QCC36AP001SP | 19051 | #6磷酸盐加药泵变频器频率设定 |  | float32
N1DCS.QDGL30001 | 19052 | 启动锅炉给水温度 |  | float32
N1DCS.QDGL30003 | 19053 | 启动锅炉省煤器出口水温 |  | float32
N1DCS.QDGL30005 | 19054 | 启动锅炉饱和蒸汽出口温度 |  | float32
N1DCS.QDGL30007 | 19055 | 启动锅炉排污扩容器温度 |  | float32
N1DCS.QDGL30009 | 19056 | 启动锅炉炉膛温度1 |  | float32
N1DCS.QDGL30011 | 19057 | 启动锅炉炉膛温度2 |  | float32
N1DCS.QDGL30013 | 19058 | 启动锅炉炉膛温度3 |  | float32
N1DCS.QDGL30015 | 19059 | 启动锅炉过热蒸汽温度 |  | float32
N1DCS.QDGL30017 | 19060 | 启动锅炉排烟温度 |  | float32
N1DCS.QDGL30019 | 19061 | 启动锅炉过热蒸汽压力1 |  | float32
N1DCS.QDGL30021 | 19062 | 启动锅炉过热蒸汽压力2 |  | float32
N1DCS.QDGL30023 | 19063 | 启动锅炉过热蒸汽压力3 |  | float32
N1DCS.QDGL30025 | 19064 | 启动锅炉锅炉本体液位 |  | float32
N1DCS.QDGL30027 | 19065 | 启动锅炉过热蒸汽流量计 |  | float32
N1DCS.QDGL30029 | 19066 | 启动锅炉天然气供气流量 |  | float32
N1DCS.QDGL30031 | 19067 | 启动锅炉给水电动调节阀阀位反馈 |  | float32
N1DCS.QDGL30033 | 19068 | 启动锅炉减温水电动调阀阀位反馈 |  | float32
N1DCS.QDGL30035 | 19069 | 启动炉燃烧器负荷反馈(风门开度) |  | float32
N1DCS.QDGL40001 | 19070 | 启动锅炉给水电动调节阀阀位指令 |  | float32
N1DCS.QDGL40001SP | 19071 | 启动锅炉给水电动调节阀阀位指令 |  | float32
N1DCS.QDGL40003 | 19072 | 启动锅炉减温水电动调阀阀位指令 |  | float32
N1DCS.QDGL40003SP | 19073 | 启动锅炉减温水电动调阀阀位指令 |  | float32
N1DCS.QDGL40005 | 19074 | 启动炉燃烧器负荷设定(压力） |  | float32
N1DCS.QDGL40005SP | 19075 | 启动炉燃烧器负荷设定(压力） |  | float32
N1DCS.10SAC01AH101Q | 19076 | #1机MCC间空调1湿度 | % | float32
N1DCS.10SAC01AH101T | 19077 | #1机MCC间空调1温度 | ℃ | float32
N1DCS.10SAC01AH102Q | 19078 | #1机6KV配电间空调2湿度 | % | float32
N1DCS.10SAC01AH102T | 19079 | #1机6KV配电间空调2温度 | ℃ | float32
N1DCS.10SAC01AH103Q | 19080 | #1机6KV配电间空调3湿度 | % | float32
N1DCS.10SAC01AH103T | 19081 | #1机6KV配电间空调3温度 | ℃ | float32
N1DCS.10SAC01AH201Q | 19082 | #1励磁小室空调4湿度 | % | float32
N1DCS.10SAC01AH201T | 19083 | #1励磁小室空调4温度 | ℃ | float32
N1DCS.10SAC01AH202Q | 19084 | #1励磁小室空调5湿度 | % | float32
N1DCS.10SAC01AH202T | 19085 | #1励磁小室空调5温度 | ℃ | float32
N1DCS.10SAC01AH203Q | 19086 | #2机电子间空调6湿度 | % | float32
N1DCS.10SAC01AH203T | 19087 | #2机电子间空调6温度 | ℃ | float32
N1DCS.10SAC01AH204Q | 19088 | #2机电子间空调7湿度 | % | float32
N1DCS.10SAC01AH204T | 19089 | #2机电子间空调7温度 | ℃ | float32
N1DCS.10SAC01AH205Q | 19090 | #2机配电间空调8湿度 | % | float32
N1DCS.10SAC01AH205T | 19091 | #2机配电间空调8温度 | ℃ | float32
N1DCS.10SAC01AH206Q | 19092 | #1励磁及变频室空调9湿度 | % | float32
N1DCS.10SAC01AH206T | 19093 | #1励磁及变频室空调9温度 | ℃ | float32
N1DCS.10SAC01AH207Q | 19094 | #1励磁及变频室空调10湿度 | % | float32
N1DCS.10SAC01AH207T | 19095 | #1励磁及变频室空调10温度 | ℃ | float32
N1DCS.20PAB10CP101AI | 19096 | 第二套机组循环水泵出口母管压力 |  | float32
N1DCS.20PAB11CL111AI | 19097 | 第二套机组旋转滤网前后液位差 |  | float32
N1DCS.CPRESSAIR | 19098 | 空压机运行个数 |  | float32
N1DCS.CPRESSAIR_SEQSPSTEP | 19099 | 空压机系统停顺控步号 |  | float32
N1DCS.CPRESSAIR_SEQSPTIME1 | 19100 | 空压机系统停顺控第1步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSPTIME2 | 19101 | 空压机系统停顺控第2步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSPTIME3 | 19102 | 空压机系统停顺控第3步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSPTIME4 | 19103 | 空压机系统停顺控第4步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSPTIME5 | 19104 | 空压机系统停顺控第5步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSTSTEP | 19105 | 空压机系统启顺控步号 |  | float32
N1DCS.CPRESSAIR_SEQSTTIME1 | 19106 | 空压机系统启顺控第1步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSTTIME2 | 19107 | 空压机系统启顺控第2步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSTTIME3 | 19108 | 空压机系统启顺控第3步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSTTIME4 | 19109 | 空压机系统启顺控第4步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSTTIME5 | 19110 | 空压机系统启顺控第5步剩余时间 |  | float32
N1DCS.CPRESSAIR_SEQSTTIME6 | 19111 | 空压机系统启顺控第6步剩余时间 |  | float32
N1DCS.J0LBG10CP102_AO | 19112 | #3机侧辅汽母管压力（至第二套) |  | float32
N1DCS.J0LBG10CT302_AO | 19113 | #3机侧辅汽母管温度（至第二套) |  | float32
N1DCS.J0LBG22CP101_AO | 19114 | 启动锅炉供辅汽压力(至第二套) |  | float32
N1DCS.J0LBG22CT301_AO | 19115 | 启动锅炉供辅汽温度（至第二套) |  | float32
N1DCS.J0PAA10CP101 | 19116 | 旋转过滤器冲洗水母管压力 | MPa | float32
N1DCS.J0PAA11CP101 | 19117 | #1全自动滤水器差压 | kPa | float32
N1DCS.J0PAA12CP101 | 19118 | #2全自动滤水器差压 | kPa | float32
N1DCS.J0QEB50CP101 | 19119 | 杂用压缩空气储罐出口母管压力 | MPa | float32
N1DCS.J0QFA11AN001I | 19120 | #1空压机排气压力 | A | float32
N1DCS.J0QFA12AN001I | 19121 | #2空压机排气压力 | A | float32
N1DCS.J0QFA20CP101 | 19122 | 空压机出口母管压力 | MPa | float32
N1DCS.J0QFA40CP101 | 19123 | 压缩空气干燥器出口母管压力 | MPa | float32
N1DCS.J0QFB50CP101 | 19124 | 仪用压缩空气储罐出口母管压力 | MPa | float32
N1DCS.J0SAC02AH101Q | 19125 | 集控楼电子设备间空调21湿度 | % | float32
N1DCS.J0SAC02AH101T | 19126 | 集控楼电子设备间空调21温度 | ℃ | float32
N1DCS.J0SAC02AH103Q | 19127 | 集控楼配电室空调23湿度 | % | float32
N1DCS.J0SAC02AH103T | 19128 | 集控楼配电室空调23温度 | ℃ | float32
N1DCS.J0SAC02AH301Q | 19129 | 集控楼集控室空调25湿度 | % | float32
N1DCS.J0SAC02AH301T | 19130 | 集控楼集控室空调25温度 | ℃ | float32
N1DCS.J0SAC02AH303Q | 19131 | 集控楼继电器室空调27湿度 | % | float32
N1DCS.J0SAC02AH303T | 19132 | 集控楼继电器室空调27温度 | ℃ | float32
N1DCS.J0SAC02AH305Q | 19133 | 集控楼蓄电池室空调29湿度 | % | float32
N1DCS.J0SAC02AH305T | 19134 | 集控楼蓄电池室空调29温度 | ℃ | float32
N1DCS.J0SAQ01AH101Q | 19135 | 联合车间电子设备间空调30湿度 | % | float32
N1DCS.J0SAQ01AH101T | 19136 | 联合车间电子设备间空调30温度 | ℃ | float32
N1DCS.J0SAQ01AH103Q | 19137 | 联合车间配电室空调32湿度 | % | float32
N1DCS.J0SAQ01AH103T | 19138 | 联合车间配电室空调32温度 | ℃ | float32
N1DCS.J0SAQ01AH301Q | 19139 | 联合车间继电器室空调34湿度 | % | float32
N1DCS.J0SAQ01AH301T | 19140 | 联合车间继电器室空调34温度 | ℃ | float32
N1DCS.J0SAQ01AH303Q | 19141 | 联合车间蓄电池室空调36湿度 | % | float32
N1DCS.J0SAQ01AH303T | 19142 | 联合车间蓄电池室空调36温度 | ℃ | float32
N1DCS.J0SAQ01AH304Q | 19143 | 联合车间公用段配电间空调37湿度 | % | float32
N1DCS.J0SAQ01AH304T | 19144 | 联合车间公用段配电间空调37运行 | ℃ | float32
N1DCS.20PAB10CP101_AI | 19145 | #3机循环水泵出口母管压力 |  | float32
N1DCS.20PAB11CL111_AI | 19146 | #3机旋转滤网前后水位差 |  | float32
N1DCS.10SAC01AH210Q | 19147 | #4机电子间空调11湿度 | % | float32
N1DCS.10SAC01AH210T | 19148 | #4机电子间空调11温度 | ℃ | float32
N1DCS.10SAC01AH211Q | 19149 | #4机电子间空调12湿度 | % | float32
N1DCS.10SAC01AH211T | 19150 | #4机电子间空调12温度 | ℃ | float32
N1DCS.20SAC01AH104Q | 19151 | #3机MCC间空调13湿度 | % | float32
N1DCS.20SAC01AH104T | 19152 | #3机MCC间空调13温度 | ℃ | float32
N1DCS.20SAC01AH105Q | 19153 | #3机6KV配电间空调14湿度 | % | float32
N1DCS.20SAC01AH105T | 19154 | #3机6KV配电间空调14温度 | ℃ | float32
N1DCS.20SAC01AH106Q | 19155 | #3机6KV配电间空调15湿度 | % | float32
N1DCS.20SAC01AH106T | 19156 | #3机6KV配电间空调15温度 | ℃ | float32
N1DCS.20SAC01AH208Q | 19157 | #3励磁小室空调机组16湿度 | % | float32
N1DCS.20SAC01AH208T | 19158 | #3励磁小室空调机组16温度 | ℃ | float32
N1DCS.20SAC01AH209Q | 19159 | #3励磁小室空调机组17湿度 | % | float32
N1DCS.20SAC01AH209T | 19160 | #3励磁小室空调机组17温度 | ℃ | float32
N1DCS.20SAC01AH212Q | 19161 | #4机配电间空调18湿度 | % | float32
N1DCS.20SAC01AH212T | 19162 | #4机配电间空调18温度 | ℃ | float32
N1DCS.20SAC01AH213Q | 19163 | #3励磁及变频室空调19湿度 | % | float32
N1DCS.20SAC01AH213T | 19164 | #3励磁及变频室空调19温度 | ℃ | float32
N1DCS.20SAC01AH214Q | 19165 | #3励磁及变频室空调20湿度 | % | float32
N1DCS.20SAC01AH214T | 19166 | #3励磁及变频室空调20温度 | ℃ | float32
N1DCS.J0QFA13AN001I | 19167 | #3空压机排气压力 | A | float32
N1DCS.J0QFA14AN001I | 19168 | #4空压机排气压力 | A | float32
N1DCS.J0SAC02AH102Q | 19169 | 集控楼电子设备间空调22湿度 | % | float32
N1DCS.J0SAC02AH102T | 19170 | 集控楼电子设备间空调22在运行 | ℃ | float32
N1DCS.J0SAC02AH104Q | 19171 | 集控楼配电室空调24故障 | % | float32
N1DCS.J0SAC02AH104T | 19172 | 集控楼配电室空调24在运行 | ℃ | float32
N1DCS.J0SAC02AH302Q | 19173 | 集控楼集控室空调26故障 | % | float32
N1DCS.J0SAC02AH302T | 19174 | 集控楼集控室空调26在运行 | ℃ | float32
N1DCS.J0SAC02AH304Q | 19175 | 集控楼继电器室空调28故障 | % | float32
N1DCS.J0SAC02AH304T | 19176 | 集控楼继电器室空调28在运行 | ℃ | float32
N1DCS.J0SAQ01AH102Q | 19177 | 联合车间电子设备间空调31故障 | % | float32
N1DCS.J0SAQ01AH102T | 19178 | 联合车间电子设备间空调31在运行 | ℃ | float32
N1DCS.J0SAQ01AH104Q | 19179 | 联合车间配电室空调33故障 | % | float32
N1DCS.J0SAQ01AH104T | 19180 | 联合车间配电室空调33在运行 | ℃ | float32
N1DCS.J0SAQ01AH302Q | 19181 | 联合车间继电器室空调35故障 | % | float32
N1DCS.J0SAQ01AH302T | 19182 | 联合车间继电器室空调35在运行 | ℃ | float32
N1DCS.J0SAQ01AH305Q | 19183 | 联合车间公用段配电间空调38故障 | % | float32
N1DCS.J0SAQ01AH305T | 19184 | 联合车间公用段配电间空调38运行 | ℃ | float32
N1DCS.BKTJ1 | 19185 | #1流量计当日标况体积累计量 |  | float32
N1DCS.BKTJ2 | 19186 | #2流量计当日标况体积累计量 |  | float32
N1DCS.KRQT1 | 19187 | 燃气泄漏探头1浓度 |  | float32
N1DCS.KRQT10 | 19188 | 燃气泄漏探头10浓度 |  | float32
N1DCS.KRQT11 | 19189 | 燃气泄漏探头11浓度 |  | float32
N1DCS.KRQT12 | 19190 | 燃气泄漏探头12浓度 |  | float32
N1DCS.KRQT13 | 19191 | 燃气泄漏探头13浓度 |  | float32
N1DCS.KRQT14 | 19192 | 燃气泄漏探头14浓度 |  | float32
N1DCS.KRQT15 | 19193 | 燃气泄漏探头15浓度 |  | float32
N1DCS.KRQT16 | 19194 | 燃气泄漏探头16浓度 |  | float32
N1DCS.KRQT2 | 19195 | 燃气泄漏探头2浓度 |  | float32
N1DCS.KRQT3 | 19196 | 燃气泄漏探头3浓度 |  | float32
N1DCS.KRQT4 | 19197 | 燃气泄漏探头4浓度 |  | float32
N1DCS.KRQT5 | 19198 | 燃气泄漏探头5浓度 |  | float32
N1DCS.KRQT6 | 19199 | 燃气泄漏探头6浓度 |  | float32
N1DCS.KRQT7 | 19200 | 燃气泄漏探头7浓度 |  | float32
N1DCS.KRQT8 | 19201 | 燃气泄漏探头8浓度 |  | float32
N1DCS.KRQT9 | 19202 | 燃气泄漏探头9浓度 |  | float32
N1DCS.KYJ007 | 19203 | #1空压机排气压力（通讯） |  | float32
N1DCS.KYJ064 | 19204 | #1空压机电流 |  | float32
N1DCS.KYJ066 | 19205 | #1空压机运行状态 |  | float32
N1DCS.KYJ113 | 19206 | #2空压机排气压力（通讯） |  | float32
N1DCS.KYJ114 | 19207 | #2空压机电流 |  | float32
N1DCS.KYJ1PRS | 19208 | #1空压机排气压力（2选后） |  | float32
N1DCS.KYJ254 | 19209 | #2空压机运行状态 |  | float32
N1DCS.KYJ261 | 19210 | #3空压机排气压力（通讯） |  | float32
N1DCS.KYJ262 | 19211 | #3空压机电流 |  | float32
N1DCS.KYJ264 | 19212 | #3空压机运行状态 |  | float32
N1DCS.KYJ2PRS | 19213 | #2空压机排气压力（2选后） |  | float32
N1DCS.KYJ3003 | 19214 | #4空压机排气压力（通讯） |  | float32
N1DCS.KYJ3004 | 19215 | #3空压机电流 |  | float32
N1DCS.KYJ3064 | 19216 | #4空压机运行状态 |  | float32
N1DCS.KYJ3PRS | 19217 | #3空压机排气压力（2选后） |  | float32
N1DCS.KYJ4PRS | 19218 | #3空压机排气压力（3选后） |  | float32
N1DCS.RSTA30001 | 19219 | 调压站仪用空气罐压力 |  | float32
N1DCS.RSTA30002 | 19220 | 调压站火警阀后天然气压力 |  | float32
N1DCS.RSTA30003 | 19221 | 调压站火警阀后天然气温度 |  | float32
N1DCS.RSTA30004 | 19222 | #1热水加热器水侧进口调节阀反馈 |  | float32
N1DCS.RSTA30005 | 19223 | #2热水加热器水侧进口调节阀反馈 |  | float32
N1DCS.RSTA30006 | 19224 | 热水加热器水侧进口母管压力 |  | float32
N1DCS.RSTA30007 | 19225 | 热水加热器水侧进口母管温度 |  | float32
N1DCS.RSTA30008 | 19226 | #1热水加热器气侧出口温度 |  | float32
N1DCS.RSTA30009 | 19227 | #2热水加热器气侧出口温度 |  | float32
N1DCS.RSTA30010 | 19228 | #4机调压出口天然气压力 |  | float32
N1DCS.RSTA30011 | 19229 | 备用调压出口天然气压力 |  | float32
N1DCS.RSTA30012 | 19230 | 调压站出口至#4机天然气压力 |  | float32
N1DCS.RSTA30013 | 19231 | 调压站出口至#4机天然气温度 |  | float32
N1DCS.RSTA30014 | 19232 | #2机调压出口天然气压力 |  | float32
N1DCS.RSTA30015 | 19233 | 调压站出口至#2机天然气压力 |  | float32
N1DCS.RSTA30016 | 19234 | 调压站出口至#2机天然气温度 |  | float32
N1DCS.RSTA30017 | 19235 | 启动锅炉调压模块出口天然气压力 |  | float32
N1DCS.RSTA30018 | 19236 | 启动锅炉调压模块出口天然气温度 |  | float32
N1DCS.RSTA30019 | 19237 | 热水锅炉#1调压出口天然气压力 |  | float32
N1DCS.RSTA30020 | 19238 | 热水锅炉#2调压出口天然气压力 |  | float32
N1DCS.RSTA30021 | 19239 | 调压站电加热器出口天然气温度 |  | float32
N1DCS.RSTA30022 | 19240 | #1热水加热器水侧进口调节阀控制 |  | float32
N1DCS.RSTA30023 | 19241 | #2热水加热器水侧进口调节阀控制 |  | float32
N1DCS.RSTA30024 | 19242 | #1热水加热器水侧进口阀阀位指令 |  | float32
N1DCS.RSTA30025 | 19243 | #2热水加热器水侧进口阀阀位指令 |  | float32
N1DCS.RSTA30026 | 19244 | #1热水加热器水侧进口阀设定值 |  | float32
N1DCS.RSTA30027 | 19245 | #2热水加热器水侧进口调设定值 |  | float32
N1DCS.RSTA30028 | 19246 | 调压站备用通道 |  | float32
N1DCS.RSTA30029 | 19247 | 调压站备用通道 |  | float32
N1DCS.RSTA30030 | 19248 | 调压站备用通道 |  | float32
N1DCS.RSTA30031 | 19249 | 调压站备用通道 |  | float32
N1DCS.RSTA30032 | 19250 | 调压站备用通道 |  | float32
N1DCS.RSTA30033 | 19251 | #1流量计热值Hs（高位） |  | float32
N1DCS.RSTA30034 | 19252 | #1流量计算机压力 |  | float32
N1DCS.RSTA30035 | 19253 | #1流量计算机温度 |  | float32
N1DCS.RSTA30036 | 19254 | #1流量计相对密度rd |  | float32
N1DCS.RSTA30037 | 19255 | #1流量计热值Hs（低位） |  | float32
N1DCS.RSTA30038 | 19256 | #1流量计氮气摩尔百分数N2 |  | float32
N1DCS.RSTA30039 | 19257 | #1流量计二氧化炭摩尔百分数CO2 |  | float32
N1DCS.RSTA30040 | 19258 | #1流量计甲烷摩尔百分数C1 |  | float32
N1DCS.RSTA30041 | 19259 | #1流量计乙烷摩尔百分数C2 |  | float32
N1DCS.RSTA30042 | 19260 | #1流量计丙烷摩尔百分数C3 |  | float32
N1DCS.RSTA30043 | 19261 | #1流量计异丁烷摩尔百分数iC4 |  | float32
N1DCS.RSTA30044 | 19262 | #1流量计正丁烷摩尔百分数nC4 |  | float32
N1DCS.RSTA30045 | 19263 | #1流量计异戊烷摩尔百分数iC5 |  | float32
N1DCS.RSTA30046 | 19264 | #1流量计正戊烷摩尔百分数nC5 |  | float32
N1DCS.RSTA30047 | 19265 | #1流量计己烷摩尔百分数nC6 |  | float32
N1DCS.RSTA30048 | 19266 | #1流量计庚烷摩尔百分数nC7 |  | float32
N1DCS.RSTA30049 | 19267 | #1流量计辛烷摩尔百分数nC8 |  | float32
N1DCS.RSTA30050 | 19268 | #1流量计壬烷摩尔百分数nC9 |  | float32
N1DCS.RSTA30051 | 19269 | #1流量计新戊烷摩尔百分数neoC5 |  | float32
N1DCS.RSTA30052 | 19270 | #1超声波流量计平均声速 |  | float32
N1DCS.RSTA30053 | 19271 | #1超声波流量计平均流速 |  | float32
N1DCS.RSTA30054 | 19272 | 调压站备用通道 |  | float32
N1DCS.RSTA30055 | 19273 | 调压站备用通道 |  | float32
N1DCS.RSTA30056 | 19274 | 调压站#1热水锅炉出水温度 |  | float32
N1DCS.RSTA30057 | 19275 | 调压站#1热水锅炉回水温度 |  | float32
N1DCS.RSTA30058 | 19276 | 调压站#2热水锅炉出水温度 |  | float32
N1DCS.RSTA30059 | 19277 | 调压站#2热水锅炉回水温度 |  | float32
N1DCS.RSTA30060 | 19278 | 调压站#3热水锅炉出水温度 |  | float32
N1DCS.RSTA30061 | 19279 | 调压站#3热水锅炉回水温度 |  | float32
N1DCS.RSTA30062 | 19280 | 调压站备用通道 |  | float32
N1DCS.RSTA30063 | 19281 | 调压站备用通道 |  | float32
N1DCS.RSTA30064 | 19282 | 调压站备用通道 |  | float32
N1DCS.RSTA30065 | 19283 | #1流量计算机工况体积流量 |  | float32
N1DCS.RSTA30067 | 19284 | #1流量计算机标况体积流量 |  | float32
N1DCS.RSTA30069 | 19285 | #1流量计算机能量流量 |  | float32
N1DCS.RSTA30071 | 19286 | #1流量计算机工况体积累计量 |  | float32
N1DCS.RSTA30073 | 19287 | #1流量计算机标况体积累计量 |  | float32
N1DCS.RSTA30075 | 19288 | #1流量计算机能量累计量(总热量) |  | float32
N1DCS.RSTA30077 | 19289 | 调压站备用通道 |  | float32
N1DCS.RSTA30079 | 19290 | 调压站备用通道 |  | float32
N1DCS.RSTA40001 | 19291 | #1热水加热器水侧调阀阀位指令 |  | float32
N1DCS.RSTA40001SP | 19292 | #1热水加热器水侧调阀阀位指令 |  | float32
N1DCS.RSTA40002 | 19293 | #2热水加热器水侧调阀阀位指令 |  | float32
N1DCS.RSTA40002SP | 19294 | #2热水加热器水侧调阀阀位指令 |  | float32
N1DCS.RSTA40003 | 19295 | #1热水加热器水侧调阀温度设定 |  | float32
N1DCS.RSTA40003SP | 19296 | #1热水加热器水侧调阀温度设定 |  | float32
N1DCS.RSTA40004 | 19297 | #2热水加热器水侧调阀温度设定 |  | float32
N1DCS.RSTA40004SP | 19298 | #2热水加热器水侧调阀温度设定 |  | float32
N1DCS.RSTA40005 | 19299 | 调压站备用通道 |  | float32
N1DCS.RSTA40006 | 19300 | 调压站备用通道 |  | float32
N1DCS.RSTA40007 | 19301 | 调压站备用通道 |  | float32
N1DCS.RSTA40008 | 19302 | 调压站备用通道 |  | float32
N1DCS.RSTA40009 | 19303 | 调压站备用通道 |  | float32
N1DCS.RSTA40010 | 19304 | 调压站备用通道 |  | float32
N1DCS.RSTA40011 | 19305 | 调压站备用通道 |  | float32
N1DCS.RSTA40012 | 19306 | 调压站备用通道 |  | float32
N1DCS.RSTA40013 | 19307 | 调压站备用通道 |  | float32
N1DCS.RSTA40014 | 19308 | 调压站备用通道 |  | float32
N1DCS.RSTA40015 | 19309 | 调压站备用通道 |  | float32
N1DCS.RSTA40016 | 19310 | #2流量计算机压力 |  | float32
N1DCS.RSTA40017 | 19311 | #2流量计算机温度 |  | float32
N1DCS.RSTA40018 | 19312 | #2流量计相对密度rd |  | float32
N1DCS.RSTA40019 | 19313 | #2流量计热值Hs（低位） |  | float32
N1DCS.RSTA40020 | 19314 | #2流量计氮气摩尔百分数N2 |  | float32
N1DCS.RSTA40021 | 19315 | #2流量计二氧化炭摩尔百分数CO2 |  | float32
N1DCS.RSTA40022 | 19316 | #2流量计甲烷摩尔百分数C1 |  | float32
N1DCS.RSTA40023 | 19317 | #2流量计乙烷摩尔百分数C2 |  | float32
N1DCS.RSTA40024 | 19318 | #2流量计丙烷摩尔百分数C3 |  | float32
N1DCS.RSTA40025 | 19319 | #2流量计异丁烷摩尔百分数iC4 |  | float32
N1DCS.RSTA40026 | 19320 | #2流量计正丁烷摩尔百分数nC4 |  | float32
N1DCS.RSTA40027 | 19321 | #2流量计异戊烷摩尔百分数iC5 |  | float32
N1DCS.RSTA40028 | 19322 | #2流量计正戊烷摩尔百分数nC5 |  | float32
N1DCS.RSTA40029 | 19323 | #2流量计己烷摩尔百分数nC6 |  | float32
N1DCS.RSTA40030 | 19324 | #2流量计庚烷摩尔百分数nC7 |  | float32
N1DCS.RSTA40031 | 19325 | #2流量计辛烷摩尔百分数nC8 |  | float32
N1DCS.RSTA40032 | 19326 | #2流量计壬烷摩尔百分数nC9 |  | float32
N1DCS.RSTA40033 | 19327 | #2流量计新戊烷摩尔百分数neoC5 |  | float32
N1DCS.RSTA40034 | 19328 | #2超声波流量计平均声速 |  | float32
N1DCS.RSTA40035 | 19329 | #2超声波流量计平均流速 |  | float32
N1DCS.RSTA40036 | 19330 | 调压站备用通道 |  | float32
N1DCS.RSTA40037 | 19331 | 调压站备用通道 |  | float32
N1DCS.RSTA40038 | 19332 | 调压站备用通道 |  | float32
N1DCS.RSTA40039 | 19333 | 调压站备用通道 |  | float32
N1DCS.RSTA40040 | 19334 | 启动锅炉调压模块出口流量计压力 |  | float32
N1DCS.RSTA40041 | 19335 | 启动锅炉调压模块出口流量计压力 |  | float32
N1DCS.RSTA40042 | 19336 | 调压站备用通道 |  | float32
N1DCS.RSTA40043 | 19337 | #2流量计算机工况体积流量 |  | float32
N1DCS.RSTA40045 | 19338 | #2流量计算机标况体积流量 |  | float32
N1DCS.RSTA40047 | 19339 | #2流量计算机能量流量 |  | float32
N1DCS.RSTA40049 | 19340 | #2流量计算机工况体积累计量 |  | float32
N1DCS.RSTA40051 | 19341 | #2流量计算机标况体积累计量 |  | float32
N1DCS.RSTA40053 | 19342 | #2流量计算机能量累计值(总热量) |  | float32
N1DCS.RSTA40055 | 19343 | 调压站涡轮流量计工况体积流量 |  | float32
N1DCS.RSTA40057 | 19344 | 调压站涡轮流量计标况体积流量 |  | float32
N1DCS.RSTA40059 | 19345 | 调压站涡轮流量计工况体积累积量 |  | float32
N1DCS.RSTA40061 | 19346 | 调压站涡轮流量计标况体积累积量 |  | float32
N1DCS.10MKE01CE01A | 19347 | #1 SFC隔离变绕组A相绕组温度 | ℃ | float32
N1DCS.10MKE01CE01B | 19348 | #1 SFC隔离变绕组B相绕组温度 | ℃ | float32
N1DCS.10MKE01CE01C | 19349 | #1 SFC隔离变绕组C相绕组温度 | ℃ | float32
N1DCS.J0BFA00CE201 | 19350 | 380V机组公用A段母线AC线电压 |  | float32
N1DCS.J0BFA00GS001I | 19351 | 380V机组公用段分段开关电流 |  | float32
N1DCS.J0BFA08EGS101I | 19352 | #1检修和材料库电源一45A085电流 |  | float32
N1DCS.J0BFB08EGS101I | 19353 | #1检修和材料库电源二45B085电流 |  | float32
N1DCS.J0BFT10GS001I | 19354 | 机组公用A变6kV侧开关电流 |  | float32
N1DCS.J0BFT10GS002I | 19355 | 机组公用A变380V侧开关电流 |  | float32
N1DCS.J0BHT30GS001I | 19356 | 厂区公用A变6kV侧开关电流 |  | float32
N1DCS.J0BHT50GS001I | 19357 | 补给水A变6kV侧开关电流 |  | float32
N1DCS.J0BHT70GS001I | 19358 | 进气冷却A变6kV侧开关电流 |  | float32
N1DCS.J0BLA00GS201I | 19359 | 机组公用A至#1照明MCC段开关电流 |  | float32
N1DCS.J0BLA00GS202I | 19360 | 机组公用B至#1照明MCC段开关电流 |  | float32
N1DCS.J0BLC00GS201I | 19361 | 机组公用A至#1检修MCC段开关电流 |  | float32
N1DCS.J0BLC00GS202I | 19362 | 机组公用B至#1检修MCC段开关电流 |  | float32
N1DCS.J0BLE00GS201I | 19363 | 机组公用A至集控楼MCC段开关电流 |  | float32
N1DCS.J0BLF00GS201I | 19364 | 机组公用A至联合间MCC段开关电流 |  | float32
N1DCS.J0BLG00GS201I | 19365 | 机组公用A至GIS楼MCC段开关电流 |  | float32
N1DCS.J0BLH00GS201I | 19366 | 机组公用A至启动炉MCC段开关电流 |  | float32
N1DCS.Y0BCT01CE301 | 19367 | #1高备变油温1 | ℃ | float32
N1DCS.Y0BCT01CE302 | 19368 | #1高备变油温2 | ℃ | float32
N1DCS.Y0BCT01CE303 | 19369 | #1高备变绕组温度 | ℃ | float32
N1DCS.Y0BCT01CE501 | 19370 | #1高备变主表有功电度 | kWh | float32
N1DCS.Y0BCT01CE502 | 19371 | #1高备变主表无功电度 | kWh | float32
N1DCS.Y0BCT01CE503 | 19372 | #1高备变副表有功电度 | kWh | float32
N1DCS.Y0BCT01CE504 | 19373 | #1高备变副表无功电度 | kWh | float32
N1DCS.Y0BHT10GS001I | 19374 | 生产办公A楼变6kV侧开关电流 |  | float32
N1DCS.Y0BCT01CE501CI | 19375 | #1高备变主表有功电度 |  | float32
N1DCS.Y0BCT01CE502CI | 19376 | #1高备变主表无功电度 |  | float32
N1DCS.Y0BCT01CE503CI | 19377 | #1高备变副表有功电度 |  | float32
N1DCS.Y0BCT01CE504CI | 19378 | #1高备变副表无功电度 |  | float32
N1DCS.20MKE01CE01A | 19379 | #2 SFC隔离变绕组A相绕组温度 | ℃ | float32
N1DCS.20MKE01CE01B | 19380 | #2 SFC隔离变绕组B相绕组温度 | ℃ | float32
N1DCS.20MKE01CE01C | 19381 | #2 SFC隔离变绕组C相绕组温度 | ℃ | float32
N1DCS.J0BFA09EGS101I | 19382 | #2检修和材料库电源一45A095电流 |  | float32
N1DCS.J0BFB00CE201 | 19383 | 380V机组公用B段母线AC线电压 |  | float32
N1DCS.J0BFB09EGS101I | 19384 | #2检修和材料库电源二45B095电流 |  | float32
N1DCS.J0BFT20GS001I | 19385 | 机组公用B变6kV侧开关电流 |  | float32
N1DCS.J0BFT20GS002I | 19386 | 机组公用B变380V侧开关电流 |  | float32
N1DCS.J0BHT40GS001I | 19387 | 厂区公用B变6kV侧开关电流 |  | float32
N1DCS.J0BHT60GS001I | 19388 | 补给水B变6kV侧开关电流 |  | float32
N1DCS.J0BHT80GS001I | 19389 | #2进气冷却变6kV侧开关电流 |  | float32
N1DCS.J0BLB00GS201I | 19390 | 机组公用A至#2照明MCC段开关电流 |  | float32
N1DCS.J0BLB00GS202I | 19391 | 机组公用B至#2照明MCC段开关电流 |  | float32
N1DCS.J0BLD00GS201I | 19392 | 机组公用A至#2检修MCC段开关电流 |  | float32
N1DCS.J0BLD00GS202I | 19393 | 机组公用B至#2检修MCC段开关电流 |  | float32
N1DCS.J0BLE00GS202I | 19394 | 机组公用B至集控楼MCC段开关电流 |  | float32
N1DCS.J0BLF00GS202I | 19395 | 机组公用B至联合间MCC段开关电流 |  | float32
N1DCS.J0BLG00GS202I | 19396 | 机组公用B至GIS楼MCC段开关电流 |  | float32
N1DCS.J0BLH00GS202I | 19397 | 机组公用B至启动炉MCC段开关电流 |  | float32
N1DCS.Y0BHT20GS001I | 19398 | 生产办公楼B变6kV侧开关电流 |  | float32
N1DCS.10MAA50CP111 | 19399 | 高压缸前后压差#1 | MPa | float32
N1DCS.10MAA50CP112 | 19400 | 高压缸前后压差#2 | MPa | float32
N1DCS.10MAA50CP113 | 19401 | 高压缸前后压差#3 | MPa | float32
N1DCS.10MAA50CT321 | 19402 | 高压排汽蒸汽温度 1# |  | float32
N1DCS.10MAA50CT322 | 19403 | 高压排汽蒸汽温度 2# | ℃ | float32
N1DCS.10MAA50CT323 | 19404 | 高压排汽蒸汽温度 3# |  | float32
N1DCS.10MAA50CT621A_XQ01 | 19405 | Ovation Control Builder |  | float32
N1DCS.10MAA50CT622A_XQ01 | 19406 | Ovation Control Builder |  | float32
N1DCS.10MAA50CT623A_XQ01 | 19407 | Ovation Control Builder |  | float32
N1DCS.10MAA50FT621_XQ01 | 19408 | 高压排汽蒸汽温度（3选后） |  | float32
N1DCS.10MAB50CT321 | 19409 | 中压排汽蒸汽温度 1# | ℃ | float32
N1DCS.10MAB50CT322 | 19410 | 中压排汽蒸汽温度 2# | ℃ | float32
N1DCS.10MAB50FT621_XQ01 | 19411 | Ovation Control Builder |  | float32
N1DCS.10MAC10CT671_XQ01 | 19412 | Ovation Control Builder |  | float32
N1DCS.10MAC10CT672_XQ01 | 19413 | Ovation Control Builder |  | float32
N1DCS.10MAC10CT673_XQ01 | 19414 | Ovation Control Builder |  | float32
N1DCS.10MAC10FT611A_XQ01 | 19415 | 低压缸末级叶片温度(2选后) |  | float32
N1DCS.10MAC10FT671_XQ01 | 19416 | Ovation Control Builder |  | float32
N1DCS.10MAD11CT314A | 19417 | #1支持轴承前右下温度A | ℃ | float32
N1DCS.10MAD11CT314B | 19418 | #1支持轴承前右下温度B | ℃ | float32
N1DCS.10MAD11CT314C | 19419 | #1支持轴承前右下温度C | ℃ | float32
N1DCS.10MAD11CT318A | 19420 | #1支持轴承后右下温度A | ℃ | float32
N1DCS.10MAD11CT318B | 19421 | #1支持轴承后右下温度B | ℃ | float32
N1DCS.10MAD11CT318C | 19422 | #1支持轴承后右下温度C | ℃ | float32
N1DCS.10MAD11CY121 | 19423 | #1径向轴承壳振1 | mm/s | float32
N1DCS.10MAD11CY122 | 19424 | #1径向轴承壳振2 | mm/s | float32
N1DCS.10MAD12CT311A | 19425 | #2支持轴承前左上温度A | ℃ | float32
N1DCS.10MAD12CT311B | 19426 | #2支持轴承前左上温度B | ℃ | float32
N1DCS.10MAD12CT311C | 19427 | #2支持轴承前左上温度C | ℃ | float32
N1DCS.10MAD12CT312A | 19428 | #2支持轴承前右上温度A | ℃ | float32
N1DCS.10MAD12CT312B | 19429 | #2支持轴承前右上温度B | ℃ | float32
N1DCS.10MAD12CT312C | 19430 | #2支持轴承前右上温度C | ℃ | float32
N1DCS.10MAD12CT313A | 19431 | #2支持轴承前左下温度A | ℃ | float32
N1DCS.10MAD12CT313B | 19432 | #2支持轴承前左下温度B | ℃ | float32
N1DCS.10MAD12CT313C | 19433 | #2支持轴承前左下温度C | ℃ | float32
N1DCS.10MAD12CT314A | 19434 | #2支持轴承前右下温度A | ℃ | float32
N1DCS.10MAD12CT314B | 19435 | #2支持轴承前右下温度B | ℃ | float32
N1DCS.10MAD12CT314C | 19436 | #2支持轴承前右下温度C | ℃ | float32
N1DCS.10MAD12CT331A | 19437 | 推力轴承前左上温度A | ℃ | float32
N1DCS.10MAD12CT331B | 19438 | 推力轴承前左上温度B | ℃ | float32
N1DCS.10MAD12CT331C | 19439 | 推力轴承前左上温度C | ℃ | float32
N1DCS.10MAD12CT332A | 19440 | 推力轴承前右上温度A | ℃ | float32
N1DCS.10MAD12CT332B | 19441 | 推力轴承前右上温度B | ℃ | float32
N1DCS.10MAD12CT332C | 19442 | 推力轴承前右上温度C | ℃ | float32
N1DCS.10MAD12CT333A | 19443 | 推力轴承前左下温度A | ℃ | float32
N1DCS.10MAD12CT333B | 19444 | 推力轴承前左下温度B | ℃ | float32
N1DCS.10MAD12CT333C | 19445 | 推力轴承前左下温度C | ℃ | float32
N1DCS.10MAD12CT334A | 19446 | 推力轴承前右下温度A | ℃ | float32
N1DCS.10MAD12CT334B | 19447 | 推力轴承前右下温度B | ℃ | float32
N1DCS.10MAD12CT334C | 19448 | 推力轴承前右下温度C | ℃ | float32
N1DCS.10MAD12CY111 | 19449 | 轴向位移1# | mm | float32
N1DCS.10MAD12CY112 | 19450 | 轴向位移2# | mm | float32
N1DCS.10MAD12CY113 | 19451 | 轴向位移3# | mm | float32
N1DCS.10MAD12CY121 | 19452 | #2径向轴承壳振1 | mm/s | float32
N1DCS.10MAD12CY122 | 19453 | #2径向轴承壳振2 | mm/s | float32
N1DCS.10MAD13CT311A | 19454 | #3支持轴承汽轮机侧前左上温度A | ℃ | float32
N1DCS.10MAD13CT311B | 19455 | #3支持轴承汽轮机侧前左上温度B |  | float32
N1DCS.10MAD13CT311C | 19456 | #3支持轴承汽轮机侧前左上温度C |  | float32
N1DCS.10MAD13CT312A | 19457 | #3支持轴承汽轮机侧前右上温度A |  | float32
N1DCS.10MAD13CT312B | 19458 | #3支持轴承汽轮机侧前右上温度B |  | float32
N1DCS.10MAD13CT312C | 19459 | #3支持轴承汽轮机侧前右上温度C |  | float32
N1DCS.10MAD13CT313A | 19460 | #3支持轴承汽轮机侧前左下温度A | ℃ | float32
N1DCS.10MAD13CT313B | 19461 | #3支持轴承汽轮机侧前左下温度B | ℃ | float32
N1DCS.10MAD13CT313C | 19462 | #3支持轴承汽轮机侧前左下温度C | ℃ | float32
N1DCS.10MAD13CT314A | 19463 | #3支持轴承汽轮机侧前右下温度A |  | float32
N1DCS.10MAD13CT314B | 19464 | #3支持轴承汽轮机侧前右下温度B |  | float32
N1DCS.10MAD13CT314C | 19465 | #3支持轴承汽轮机侧前右下温度C |  | float32
N1DCS.10MAD13CT315A | 19466 | #3支持轴承汽轮机侧后右下温度A |  | float32
N1DCS.10MAD13CT315B | 19467 | #3支持轴承汽轮机侧后右下温度B | ℃ | float32
N1DCS.10MAD13CT315C | 19468 | #3支持轴承汽轮机侧后右下温度C | ℃ | float32
N1DCS.10MAD13CY121 | 19469 | #3径向轴承壳振1 | mm/s | float32
N1DCS.10MAD13CY122 | 19470 | #3径向轴承壳振2 | mm/s | float32
N1DCS.10MAG01CP101 | 19471 | 凝汽器真空1# | kPa | float32
N1DCS.10MAG01CP102 | 19472 | 凝汽器真空2# | kPa | float32
N1DCS.10MAG01CP103 | 19473 | 凝汽器真空3# | kPa | float32
N1DCS.10MAG01FP101_XQ01 | 19474 | 凝汽器真空(选择后) |  | float32
N1DCS.10MAV10CL121 | 19475 | 润滑油液位1# | mm | float32
N1DCS.10MAV10CL122 | 19476 | 润滑油液位2# | mm | float32
N1DCS.10MAV10CL123 | 19477 | 润滑油液位3# | mm | float32
N1DCS.10MAV10FL121_XQ01 | 19478 | Ovation Control Builder |  | float32
N1DCS.10MAV42CP116 | 19479 | 润滑油母管压力1# | MPa | float32
N1DCS.10MAV42CP117 | 19480 | 润滑油母管压力2# | MPa | float32
N1DCS.10MAV42CP118 | 19481 | 润滑油母管压力3# | MPa | float32
N1DCS.10MAV42FP116_XQ01 | 19482 | Ovation Control Builder |  | float32
N1DCS.10MAX01CP101_DEH | 19483 | 控制油泵出口压力1# | MPa | float32
N1DCS.10MAX01CP102_DEH | 19484 | 控制油泵出口压力2# | MPa | float32
N1DCS.10MAX01CP103_DEH | 19485 | 控制油泵出口压力3# | MPa | float32
N1DCS.10MAX01FP103_XQ01 | 19486 | Ovation Control Builder |  | float32
N1DCS.10MKD11CT013A | 19487 | #1汽轮发电机轴承左下温度A |  | float32
N1DCS.10MKD11CT013B | 19488 | #1汽轮发电机轴承左下温度B |  | float32
N1DCS.10MKD11CT014A | 19489 | #1汽轮发电机轴承右下温度A |  | float32
N1DCS.10MKD11CT014B | 19490 | #1汽轮发电机轴承右下温度B |  | float32
N1DCS.10MKD11CY121 | 19491 | #4轴承壳振1 | mm/s | float32
N1DCS.10MKD11CY122 | 19492 | #4轴承壳振2 | mm/s | float32
N1DCS.10MKD12CT013A | 19493 | #2汽轮发电机轴承左下温度A |  | float32
N1DCS.10MKD12CT013B | 19494 | #2汽轮发电机轴承左下温度B |  | float32
N1DCS.10MKD12CT014A | 19495 | #2汽轮发电机轴承右下温度A |  | float32
N1DCS.10MKD12CT014B | 19496 | #2汽轮发电机轴承右下温度B |  | float32
N1DCS.10MKD12CY121 | 19497 | #5轴承壳振1 | mm/s | float32
N1DCS.10MKD12CY122 | 19498 | #5轴承壳振2 | mm/s | float32
N1DCS.D41P1B1L5C9 | 19499 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D41P1B1L6C9 | 19500 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D41P1B1L7C9 | 19501 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D41P1B3L4C9 | 19502 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D41P1B3L5C9 | 19503 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D41P1B3L6C9 | 19504 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D41P1B3L7C9 | 19505 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D41P1B4L1C9 | 19506 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D41P1B4L2C9 | 19507 | TC冷端温度补偿点 | DEGC | float32
N1DCS.10MAA50FT350 | 19508 | 高压缸上下温差 |  | float32
N1DCS.10MAB50FT350 | 19509 | 中压缸上下温差 |  | float32
N1DCS.10MAD12CY | 19510 | Ovation Control Builder |  | float32
N1DCS.GYGSXBWC | 19511 | 高压缸上下中壁温差 |  | float32
N1DCS.ZYGSXBWC | 19512 | 中压缸上下中壁温差 |  | float32
N1DCS.10CJA00DP200_XQ05 | 19513 | Ovation Control Builder |  | float32
N1DCS.10CJA01DP100_DEH | 19514 | 主蒸汽压力设定(1/102) | MPa | float32
N1DCS.10CJA01DP200_DEH | 19515 | 再热蒸汽压力设定 | MPa | float32
N1DCS.10CJA01DP300 | 19516 | 低压蒸汽压力设定 | MPa | float32
N1DCS.10LBA10CP901_PFD | 19517 | 高压主汽门前蒸汽压力（Bar） |  | float32
N1DCS.10LBA10CP901_PFD11 | 19518 | Ovation Control Builder |  | float32
N1DCS.10LBA10CP901_XQ01 | 19519 | 高压主汽门前蒸汽压力（三选中） |  | float32
N1DCS.10LBA20CP104 | 19520 | 高压主汽门前蒸汽压力#1 | MPa | float32
N1DCS.10LBA20CP104_XQ01 | 19521 | 高压主汽门前蒸汽压力#1 |  | float32
N1DCS.10LBA20CP105 | 19522 | 高压主汽门前蒸汽压力#2 | MPa | float32
N1DCS.10LBA20CP105_XQ01 | 19523 | 高压主汽门前蒸汽压力#2 |  | float32
N1DCS.10LBA20CP106 | 19524 | 高压主汽门前蒸汽压力#3 | MPa | float32
N1DCS.10LBA20CP106_XQ01 | 19525 | 高压主汽门前蒸汽压力#3 |  | float32
N1DCS.10LBA90CP104 | 19526 | 低压主汽门前蒸汽压力#1 | MPa | float32
N1DCS.10LBA90CP104_XQ01 | 19527 | 补汽主汽门前压力#1 | MPa | float32
N1DCS.10LBA90CP105 | 19528 | 低压主汽门前蒸汽压力#2 | MPa | float32
N1DCS.10LBA90CP105_XQ01 | 19529 | 补汽主汽门前压力#2 | MPa | float32
N1DCS.10LBA90CP106 | 19530 | 低压主汽门前蒸汽压力#3 | MPa | float32
N1DCS.10LBA90CP106_XQ01 | 19531 | 补汽主汽门前压力#3 | MPa | float32
N1DCS.10LBA90CP901_PZD | 19532 | 低压主汽门前蒸汽压力（Bar） |  | float32
N1DCS.10LBA90CP901_PZD11 | 19533 | Ovation Control Builder |  | float32
N1DCS.10LBA90CP901_XQ01 | 19534 | 低压主汽门前蒸汽压力（选择后） |  | float32
N1DCS.10LBB10CP901_PHZ | 19535 | 中压主汽门前蒸汽压力（Bar） |  | float32
N1DCS.10LBB10CP901_PHZ11 | 19536 | 中压主汽门前蒸汽压力 |  | float32
N1DCS.10LBB10CP901_XQ01 | 19537 | 中压主汽门前蒸汽压力（选择后） |  | float32
N1DCS.10LBB50CP104 | 19538 | 中压主汽前蒸汽压力#1 | MPa | float32
N1DCS.10LBB50CP104_XQ01 | 19539 | 中压主汽门前蒸汽压力#1 |  | float32
N1DCS.10LBB50CP105 | 19540 | 中压主汽门前蒸汽压力#2 | MPa | float32
N1DCS.10LBB50CP105_XQ01 | 19541 | 中压主汽门前蒸汽压力#2 |  | float32
N1DCS.10LBB50CP106 | 19542 | 中压主汽门前蒸汽压力#3 | MPa | float32
N1DCS.10LBB50CP106_XQ01 | 19543 | 中压主汽门前蒸汽压力#3 |  | float32
N1DCS.10LBB51CP901_XQ01 | 19544 | Ovation Control Builder |  | float32
N1DCS.10LBC40CG152 | 19545 | 高排调节阀力矩反馈 | % | float32
N1DCS.10LBC40CP101 | 19546 | 高压排汽蒸汽压力1# | MPa | float32
N1DCS.10LBC40CP101_XQ01 | 19547 | 高压排气蒸汽压力#1 |  | float32
N1DCS.10LBC40CP102 | 19548 | 高压排汽蒸汽压力2# | MPa | float32
N1DCS.10LBC40CP102_XQ01 | 19549 | 高压排气蒸汽压力#2 |  | float32
N1DCS.10LBC40CP103 | 19550 | 高压排汽蒸汽压力3# | MPa | float32
N1DCS.10LBC40CP103_XQ01 | 19551 | 高压排气蒸汽压力#3 |  | float32
N1DCS.10LBC40FP101_XQ01 | 19552 | 高压排汽蒸汽压力（3选中） |  | float32
N1DCS.10LBD20CP102 | 19553 | 冷再抽汽减压阀前压力 | MPa | float32
N1DCS.10LBD40CG151 | 19554 | 中压抽汽快关调节阀阀位反馈 |  | float32
N1DCS.10LBD40CP102 | 19555 | 热再抽汽减压阀前压力 | MPa | float32
N1DCS.10LBS45AA001_SETP | 19556 | Ovation Control Builder |  | float32
N1DCS.10LBS45AA001_XQ02 | 19557 | Ovation Control Builder |  | float32
N1DCS.10LBS45AA012A | 19558 | 中压抽汽快关调节阀控制设定 | % | float32
N1DCS.10LBS45AA101_TRACKV | 19559 | Ovation Control Builder |  | float32
N1DCS.10LBS45CG151_XQ01 | 19560 | 中压抽汽快关调节阀阀位反馈 |  | float32
N1DCS.10LBS46AA001_SETP | 19561 | 高排抽汽压力设定值 |  | float32
N1DCS.10LBS46AA001_XQ02 | 19562 | Ovation Control Builder |  | float32
N1DCS.10LBS46AA012A | 19563 | 高压抽汽快关调节阀控制设定 | % | float32
N1DCS.10LBS46AA101_TRACKV | 19564 |  |  | float32
N1DCS.10LBS46CG151 | 19565 | 高压抽汽快关调节阀阀位反馈 | % | float32
N1DCS.10LBS46CG151_XQ01 | 19566 | 高压抽气快关调节阀阀位反馈 |  | float32
N1DCS.10MAA11CG051 | 19567 | 高压主汽门阀位 |  | float32
N1DCS.10MAA11CG151_XQ01 | 19568 | 高压主汽阀阀位反馈 |  | float32
N1DCS.10MAA12AA012 | 19569 | Ovation Control Builder |  | float32
N1DCS.10MAA12AA012_T | 19570 | Ovation Control Builder |  | float32
N1DCS.10MAA12CG051 | 19571 | 高压调门阀位 | % | float32
N1DCS.10MAA12CG151_XQ01 | 19572 | 高压调阀阀位反馈 |  | float32
N1DCS.10MAA12DG010_BFD | 19573 | 高调门阀限 |  | float32
N1DCS.10MAA12DG010_BFDV | 19574 | 高调门阀限 |  | float32
N1DCS.10MAA12DG010_OUT | 19575 | Ovation Control Builder |  | float32
N1DCS.10MAA12DG010_TRACKV | 19576 | 高调门阀限跟踪 |  | float32
N1DCS.10MAA12DG050_HPCMD | 19577 | Ovation Control Builder |  | float32
N1DCS.10MAA12DG050_YFDR | 19578 | 高调门阀位设定值 |  | float32
N1DCS.10MAA50CP101 | 19579 | 高调门阀后蒸汽压力1# | MPa | float32
N1DCS.10MAA50CP101_XQ01 | 19580 | Ovation Control Builder |  | float32
N1DCS.10MAA50CP102 | 19581 | 高调门阀后蒸汽压力2# | MPa | float32
N1DCS.10MAA50CP102_XQ01 | 19582 | Ovation Control Builder |  | float32
N1DCS.10MAA50CP103 | 19583 | 高调门阀后蒸汽压力3# | MPa | float32
N1DCS.10MAA50CP103_XQ01 | 19584 | Ovation Control Builder |  | float32
N1DCS.10MAA50CP111_XQ01 | 19585 | 高压缸前后压差#1 |  | float32
N1DCS.10MAA50CP112_XQ01 | 19586 | 高压缸前后压差#2 |  | float32
N1DCS.10MAA50CP113_XQ01 | 19587 | 高压缸前后压差#3 |  | float32
N1DCS.10MAA50DP111_XQ01 | 19588 | 高压缸压比 |  | float32
N1DCS.10MAA50FP011_XQ01 | 19589 | 高调门阀后蒸汽压力（3选中） |  | float32
N1DCS.10MAA50FP011_XQ02 | 19590 | 高排抽汽时高排压力低限 |  | float32
N1DCS.10MAA50FP111_XQ01 | 19591 | 高压缸前后压差(3选后) |  | float32
N1DCS.10MAB11AA012_SPT | 19592 | Ovation Control Builder |  | float32
N1DCS.10MAB11CG151_XQ01 | 19593 | 中压主汽门阀位反馈 |  | float32
N1DCS.10MAB12AA012 | 19594 | Ovation Control Builder |  | float32
N1DCS.10MAB12AA012_T | 19595 | Ovation Control Builder |  | float32
N1DCS.10MAB12CG051 | 19596 | 中压调门阀位 |  | float32
N1DCS.10MAB12CG151_XQ01 | 19597 | 中压调门阀位反馈 |  | float32
N1DCS.10MAB12DG010_BAF | 19598 | 中调门阀限 |  | float32
N1DCS.10MAB12DG010_BAFV | 19599 | 中调门阀限 |  | float32
N1DCS.10MAB12DG010_OUT | 19600 | Ovation Control Builder |  | float32
N1DCS.10MAB12DG010_TRACKV | 19601 | Ovation Control Builder |  | float32
N1DCS.10MAB12DG050_IPCMD | 19602 | Ovation Control Builder |  | float32
N1DCS.10MAB12DG050_YAFR | 19603 | 中压调门阀位设定 |  | float32
N1DCS.10MAB21CG051 | 19604 | 中压主汽门阀位 |  | float32
N1DCS.10MAB50CP101 | 19605 | 中调门阀后蒸汽压力 | MPa | float32
N1DCS.10MAB50CP101_XQ01 | 19606 | 中压调门后蒸汽压力 |  | float32
N1DCS.10MAC10CP101 | 19607 | 低压缸进汽压力 #1 | MPa | float32
N1DCS.10MAC10CP101_XQ01 | 19608 | 低压缸进汽压力#1 |  | float32
N1DCS.10MAC10CP102 | 19609 | 低压缸进汽压力 #2 | MPa | float32
N1DCS.10MAC10CP102_XQ01 | 19610 | 低压缸进汽压力#2 |  | float32
N1DCS.10MAC10CP103 | 19611 | 低压缸进汽压力 #3 | MPa | float32
N1DCS.10MAC10CP103_XQ01 | 19612 | 低压缸进汽压力#3 |  | float32
N1DCS.10MAC10CP901_XQ01 | 19613 | Ovation Control Builder |  | float32
N1DCS.10MAC10CP901_XQ02 | 19614 | Ovation Control Builder |  | float32
N1DCS.10MAC10CP901_XQ09 | 19615 | Ovation Control Builder |  | float32
N1DCS.10MAC46AA012A | 19616 | 低压补汽调阀控制设定 |  | float32
N1DCS.10MAC46CG151 | 19617 | 低压补汽调阀阀位反馈 | % | float32
N1DCS.10MAC46CG151_XQ01 | 19618 | 低压补汽调门阀位反馈 |  | float32
N1DCS.10MAC46DG010_BZD | 19619 | 低调门阀限 |  | float32
N1DCS.10MAC46DG010_BZDV | 19620 | 低调阀阀限 |  | float32
N1DCS.10MAC46DG010_OUT | 19621 | Ovation Control Builder |  | float32
N1DCS.10MAC46DG010_TRACKV | 19622 | Ovation Control Builder |  | float32
N1DCS.10MAC46DG050_LPCMD | 19623 | Ovation Control Builder |  | float32
N1DCS.10MAG01FP101_XQ21 | 19624 | Ovation Control Builder |  | float32
N1DCS.10MAL11AA151T_XQ01 | 19625 | 高压主汽门疏水阀指令 | % | float32
N1DCS.10MAL11CG151_XQ01 | 19626 | 高压调门前疏水阀位反馈 | % | float32
N1DCS.10MAN52CG161_XQ01 | 19627 | Ovation Control Builder |  | float32
N1DCS.10MAN52CP001_XQ01 | 19628 | Ovation Control Builder |  | float32
N1DCS.10MAV10FL121_XQ21 | 19629 | Ovation Control Builder |  | float32
N1DCS.10MAV42FP116_XQ21 | 19630 | Ovation Control Builder |  | float32
N1DCS.10MAX01FP103_XQ21 | 19631 | Ovation Control Builder |  | float32
N1DCS.10MAY01CS118 | 19632 | 汽机实际转速（去电厂LED） | rpm | float32
N1DCS.10MAY10EC001_DNTS | 19633 | 汽机停止顺控步序号 |  | float32
N1DCS.10MAY10EC001_DPT51 | 19634 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DPT52 | 19635 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DPT53 | 19636 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DT54 | 19637 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DT55 | 19638 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DT56 | 19639 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DT57 | 19640 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DT58 | 19641 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DT59 | 19642 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DT60 | 19643 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_DT61 | 19644 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT1 | 19645 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT10 | 19646 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT11 | 19647 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT12 | 19648 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT13 | 19649 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT14 | 19650 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT15 | 19651 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT16 | 19652 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT17 | 19653 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT18 | 19654 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT19 | 19655 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT2 | 19656 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT20 | 19657 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT21 | 19658 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT22 | 19659 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT23 | 19660 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT24 | 19661 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT25 | 19662 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT3 | 19663 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT4 | 19664 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT5 | 19665 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT6 | 19666 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT7 | 19667 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT8 | 19668 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPT9 | 19669 | Ovation Control Builder |  | float32
N1DCS.10MAY10EC001_UPTS | 19670 | 汽机启动顺控步序号 |  | float32
N1DCS.10MAY10FT910_LEFT_TIME | 19671 | 暖机剩余时间 |  | float32
N1DCS.10MKA01CE003A | 19672 | 发电机功率#1 | MW | float32
N1DCS.10MKA01CE003B | 19673 | 发电机功率#2 | MW | float32
N1DCS.10MKA01CE003C | 19674 | 发电机功率#3 | MW | float32
N1DCS.10MKA01CE903_PEL | 19675 | #1机负荷 | MW | float32
N1DCS.10MKA01CE903_PELKOR | 19676 | 发电机功率（百分比） |  | float32
N1DCS.10MKA02CE901_DEH | 19677 | 汽轮发电机实际功率 | MW | float32
N1DCS.10MKA10FA101 | 19678 | 协调控制负荷设定#1 | MW | float32
N1DCS.10MKA10FA102_DEH | 19679 | 协调控制负荷设定#2 | MW | float32
N1DCS.10MKA10FA103_DEH | 19680 | 频率偏差 | rpm | float32
N1DCS.10MYA01CS001_XQ01 | 19681 | Ovation Control Builder |  | float32
N1DCS.10MYA01CS001_XQ02 | 19682 | Ovation Control Builder |  | float32
N1DCS.10MYA01CS011C | 19683 | 汽轮机转速 1 |  | float32
N1DCS.10MYA01CS012C | 19684 | 汽轮机转速 2 |  | float32
N1DCS.10MYA01CS013C | 19685 | 汽轮机转速 3 |  | float32
N1DCS.10MYA01CS021C | 19686 | 汽轮机转速 4 |  | float32
N1DCS.10MYA01CS022C | 19687 | 汽轮机转速 5 |  | float32
N1DCS.10MYA01CS023C | 19688 | 汽轮机转速 6 |  | float32
N1DCS.10MYA01CS901_NT | 19689 | 汽轮机转速（HZ） |  | float32
N1DCS.10MYA01CS901_XQ01 | 19690 | 汽轮机转速 |  | float32
N1DCS.10MYA01CS901C_DEH | 19691 | 汽轮机转速(去远动) | rpm | float32
N1DCS.10MYA01DG010_OS | 19692 | 外部负荷设定 |  | float32
N1DCS.10MYA01DG010_OSV | 19693 | 负荷设定参考（百分比） |  | float32
N1DCS.10MYA01DG010_OSV2 | 19694 | 负荷设定参考(MW) |  | float32
N1DCS.10MYA01DG010_OSX | 19695 | 协调控制负荷设定值 |  | float32
N1DCS.10MYA01DG010_OSX2 | 19696 | Ovation Control Builder |  | float32
N1DCS.10MYA01DG010_P100 | 19697 | Ovation Control Builder |  | float32
N1DCS.10MYA01DG010_VGOS | 19698 | 负荷设定 |  | float32
N1DCS.10MYA01DG011_OSGI | 19699 | 内部进汽设定值梯度 |  | float32
N1DCS.10MYA01DG020_XQ01 | 19700 | TABx0.01 |  | float32
N1DCS.10MYA01DG020_XQ02 | 19701 | TAB值 |  | float32
N1DCS.10MYA01DG110C | 19702 | 负荷设定参考 | MW | float32
N1DCS.10MYA01DP010_FDS | 19703 | 实时高压压力设定值 |  | float32
N1DCS.10MYA01DP010_FDSV | 19704 | 延时高压压力设定值 |  | float32
N1DCS.10MYA01DP010_FDSVK | 19705 | 修正的延时高压压力设定值 |  | float32
N1DCS.10MYA01DP010_FDSX | 19706 | 高压压力设定(来自Drop1) |  | float32
N1DCS.10MYA01DP010_FDXW | 19707 | 主蒸汽压力控制偏差 |  | float32
N1DCS.10MYA01DP010_VGFDS | 19708 | 高压压力设定(手动) |  | float32
N1DCS.10MYA01DP011_DGD | 19709 | 压力限制偏置值 |  | float32
N1DCS.10MYA01DP011_DVD | 19710 | 初压模式偏置值 |  | float32
N1DCS.10MYA01DP020_EGVS | 19711 | Ovation Control Builder |  | float32
N1DCS.10MYA01DP020_HZS | 19712 | 实时再热压力设定值bar |  | float32
N1DCS.10MYA01DP020_HZSV | 19713 | 延时再热压力设定值bar |  | float32
N1DCS.10MYA01DP020_HZSX | 19714 | 再热蒸汽压力设定 |  | float32
N1DCS.10MYA01DP020_VGHZS | 19715 | 再热蒸汽压力手动设定值 |  | float32
N1DCS.10MYA01DP020_XQ03 | 19716 | Ovation Control Builder |  | float32
N1DCS.10MYA01DP030_VGZDS | 19717 | 中压压力设定(手动) |  | float32
N1DCS.10MYA01DP030_ZDS | 19718 | 实时低压压力设定值 |  | float32
N1DCS.10MYA01DP030_ZDSV | 19719 | 延时低压压力设定值 |  | float32
N1DCS.10MYA01DP030_ZDSX | 19720 | 低压压力设定值 |  | float32
N1DCS.10MYA01DP050_P120Y | 19721 | 主蒸汽压力输出限值 |  | float32
N1DCS.10MYA01DP050_YFDPR | 19722 | 高压主蒸汽压力控制输出 |  | float32
N1DCS.10MYA01DP060_YHZPR | 19723 | 再热压力控制器输出值 |  | float32
N1DCS.10MYA01DP070_YZDPR | 19724 | 低压压力控制器输出 |  | float32
N1DCS.10MYA01DP090_PIRY | 19725 | Ovation Control Builder |  | float32
N1DCS.10MYA01DP090_YHVDR | 19726 | 高压压比控制器输出 |  | float32
N1DCS.10MYA01DS010_NS | 19727 | Ovation Control Builder |  | float32
N1DCS.10MYA01DS010_NS0 | 19728 | Ovation Control Builder |  | float32
N1DCS.10MYA01DS010_NSV | 19729 | 延时转速设定值 |  | float32
N1DCS.10MYA01DS010_OFBY | 19730 | 转速设定值上升梯度 |  | float32
N1DCS.10MYA01DS010_UFBY | 19731 | 转速设定值下降梯度 |  | float32
N1DCS.10MYA01DS010_VGNS | 19732 | Ovation Control Builder |  | float32
N1DCS.10MYA01DT050_PIRY | 19733 | Ovation Control Builder |  | float32
N1DCS.10MYA01DT050_YHATR | 19734 | 高排温度控制器输出 |  | float32
N1DCS.10MYA01DU011_OFBN | 19735 | 转速设定值梯度上限 |  | float32
N1DCS.10MYA01DU011_OFBO | 19736 | 进汽设定值梯度上限 |  | float32
N1DCS.10MYA01DU011_UFBN | 19737 | 转速设定值梯度下限 |  | float32
N1DCS.10MYA01DU011_UFBO | 19738 | 进汽设定值梯度下限 |  | float32
N1DCS.10MYA01DU011_XQ51 | 19739 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU011_XQ52 | 19740 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU050_DNY | 19741 | 转速控制偏差 |  | float32
N1DCS.10MYA01DU050_FREQT | 19742 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU050_N410 | 19743 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU050_N420 | 19744 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU050_N490 | 19745 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU050_SET | 19746 | 转速/负荷控制偏差 |  | float32
N1DCS.10MYA01DU050_WY | 19747 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU050_YNOR | 19748 | 转速控制器输出值 |  | float32
N1DCS.10MYA01DU050_YNOR2 | 19749 | 负荷控制器输出值 |  | float32
N1DCS.10MYA01DU060_AF14 | 19750 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU060_AFMUS | 19751 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU060_INV | 19752 | Ovation Control Builder |  | float32
N1DCS.10MYA01DU060_OSAF | 19753 | 中压调门进汽设定值 |  | float32
N1DCS.10MYA01DU060_OSFD | 19754 | 高压调门进汽设定值 |  | float32
N1DCS.10MYA01DU060_OSZD | 19755 | 低压调门进汽设定值 |  | float32
N1DCS.10MYA01DU060_PFDFE1 | 19756 | 实际主蒸汽信号 |  | float32
N1DCS.10MYA01DU060_PFDN | 19757 | 高主门前蒸汽压力与额定压力比值 |  | float32
N1DCS.10MYA01DU060_TABS | 19758 | TAB控制器输出 |  | float32
N1DCS.10MYA01DU060_YAF | 19759 | 中压调门阀位控制器设定值 |  | float32
N1DCS.10MYA01DU060_YR | 19760 | 中央小选块输出 |  | float32
N1DCS.10MYA01DU060_YRFD | 19761 | 高压调门阀位控制器设定值 |  | float32
N1DCS.10MYA01DU060_YRKOR | 19762 | 进汽修正 |  | float32
N1DCS.10MYA01DU060_YZD | 19763 | 低压调门阀位控制器设定值 |  | float32
N1DCS.10MYA01EZ400_XQ01 | 19764 | Ovation Control Builder |  | float32
N1DCS.10NAA01CP101 | 19765 | 热网抽汽调阀后压力（高排）#1 | MPa | float32
N1DCS.10NAA01CP101_XQ01 | 19766 | 冷再抽气减压阀前压力 |  | float32
N1DCS.10NAA01CP102 | 19767 | 热网抽汽调阀后压力（高排）#2 | MPa | float32
N1DCS.10NAA01CP102_XQ01 | 19768 | Ovation Control Builder |  | float32
N1DCS.10NAA01CP103 | 19769 | 热网抽汽调阀后压力（高排）#3 | MPa | float32
N1DCS.10NAA01CP103_XQ01 | 19770 | Ovation Control Builder |  | float32
N1DCS.10NAA01FP101_XQ01 | 19771 | 冷再抽汽减压阀前压力（3选中） |  | float32
N1DCS.10NAA02CP101_XQ01 | 19772 | 热再抽汽减压阀阀前压力 |  | float32
N1DCS.10NAA02CP102 | 19773 | 中压抽汽蒸汽压力(调阀后)#2 | MPa | float32
N1DCS.10NAA02CP102_XQ01 | 19774 | Ovation Control Builder |  | float32
N1DCS.10NAA02CP103 | 19775 | 中压抽汽蒸汽压力(调阀后)#3 | MPa | float32
N1DCS.10NAA02CP103_XQ01 | 19776 | Ovation Control Builder |  | float32
N1DCS.10NAA02FP101_XQ01 | 19777 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_BOILER | 19778 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_FLOW | 19779 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SCVAREA | 19780 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMEXTRA_HP | 19781 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMEXTRA_IP | 19782 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMHPB | 19783 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMHP_EXH_P | 19784 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMIDUP | 19785 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMIPB | 19786 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMLPB | 19787 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMPFD | 19788 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIMPHZ | 19789 | Ovation Control Builder |  | float32
N1DCS.10SIM01EZ001_SIVAREA | 19790 | Ovation Control Builder |  | float32
N1DCS.1_1_7_COIL_1_KSERVO_A | 19791 | Ovation Control Builder |  | float32
N1DCS.1_1_7_COIL_2_KSERVO_A | 19792 | Ovation Control Builder |  | float32
N1DCS.1_1_8_COIL_1_KSERVO_A | 19793 | Ovation Control Builder |  | float32
N1DCS.1_1_8_COIL_2_KSERVO_A | 19794 | Ovation Control Builder |  | float32
N1DCS.AFOB | 19795 | 中压调门阀门进汽起点 |  | float32
N1DCS.AFOE | 19796 | 中压调门阀门进汽终点 |  | float32
N1DCS.BEGME | 19797 | 测量范围上限限值 |  | float32
N1DCS.BONTGT | 19798 | Ovation Control Builder |  | float32
N1DCS.DGDI | 19799 | Ovation Control Builder |  | float32
N1DCS.DNKUPA | 19800 | Ovation Control Builder |  | float32
N1DCS.DNKUPE | 19801 | Ovation Control Builder |  | float32
N1DCS.ENTGT | 19802 | Ovation Control Builder |  | float32
N1DCS.FBMAX | 19803 | 最大允许裕度 |  | float32
N1DCS.FDNOM | 19804 | Ovation Control Builder |  | float32
N1DCS.FDPRKP | 19805 | 主蒸汽压力控制器比例系数 |  | float32
N1DCS.FDPRTN | 19806 | Ovation Control Builder |  | float32
N1DCS.FDSHMI | 19807 | 实时高压压力设定值（显示） |  | float32
N1DCS.FDSVG | 19808 | 延时主蒸汽压力设定值梯度 |  | float32
N1DCS.FDSVG2 | 19809 | 延时主蒸汽压力设定值梯度2 |  | float32
N1DCS.FDSVHMI | 19810 | 延时高压压力设定值（显示） |  | float32
N1DCS.GDNGD | 19811 | Ovation Control Builder |  | float32
N1DCS.GDNT | 19812 | 转速控制偏差限制值 |  | float32
N1DCS.GNSR | 19813 | Ovation Control Builder |  | float32
N1DCS.GNTGRD | 19814 | Ovation Control Builder |  | float32
N1DCS.GSP1A | 19815 | Ovation Control Builder |  | float32
N1DCS.GSP1E | 19816 | Ovation Control Builder |  | float32
N1DCS.GSP2A | 19817 | Ovation Control Builder |  | float32
N1DCS.GSP2E | 19818 | Ovation Control Builder |  | float32
N1DCS.GTAB | 19819 | Ovation Control Builder |  | float32
N1DCS.GV_1_1_7_COIL1 | 19820 | 1_1_7 COIL1 VOLTAGE |  | float32
N1DCS.GV_1_1_7_COIL2 | 19821 | 1_1_7 COIL2 VOLTAGE |  | float32
N1DCS.GV_COMMAND | 19822 | GV 11CH COMMAND |  | float32
N1DCS.GV_DEMOD | 19823 |  |  | float32
N1DCS.GV_SPO | 19824 | Ovation Control Builder |  | float32
N1DCS.GV_STAT_POINT | 19825 | GV 14CH STAT |  | float32
N1DCS.GWHF | 19826 | Ovation Control Builder |  | float32
N1DCS.GWLF | 19827 | Ovation Control Builder |  | float32
N1DCS.GYRKOR | 19828 | 修正的进汽设定值限制值 |  | float32
N1DCS.HATNOM | 19829 | Ovation Control Builder |  | float32
N1DCS.HATRKP | 19830 | Ovation Control Builder |  | float32
N1DCS.HATRTS | 19831 | Ovation Control Builder |  | float32
N1DCS.HPE_RATE | 19832 | Ovation Control Builder |  | float32
N1DCS.HPETGT | 19833 | Ovation Control Builder |  | float32
N1DCS.HVDNOM | 19834 | Ovation Control Builder |  | float32
N1DCS.HVDRKP | 19835 | Ovation Control Builder |  | float32
N1DCS.HVDRTS | 19836 | Ovation Control Builder |  | float32
N1DCS.HZNOM | 19837 | Ovation Control Builder |  | float32
N1DCS.HZPRKP | 19838 | Ovation Control Builder |  | float32
N1DCS.HZPRTN | 19839 | Ovation Control Builder |  | float32
N1DCS.HZSHMI | 19840 | 实时再热压力设定值显示 |  | float32
N1DCS.HZSVG | 19841 | Ovation Control Builder |  | float32
N1DCS.HZSVG2 | 19842 | Ovation Control Builder |  | float32
N1DCS.HZSVHMI | 19843 | 延时再热压力设定值显示 |  | float32
N1DCS.IPE_RATE | 19844 | Ovation Control Builder |  | float32
N1DCS.IPETGT | 19845 | Ovation Control Builder |  | float32
N1DCS.IV_1_1_8_COIL1 | 19846 | 1_1_8 COIL1 VOLTAGE |  | float32
N1DCS.IV_1_1_8_COIL2 | 19847 | 1_1_8 COIL2 VOLTAGE |  | float32
N1DCS.IV_COMMAND | 19848 | IV 11CH COMMAND |  | float32
N1DCS.IV_DEMOD | 19849 |  |  | float32
N1DCS.IV_SPO | 19850 | Ovation Control Builder |  | float32
N1DCS.IV_STAT_POINT | 19851 | IV 14CH STAT |  | float32
N1DCS.KDN | 19852 | 转速控制器比例前馈 |  | float32
N1DCS.KOS | 19853 | 进汽控制器比例前馈 |  | float32
N1DCS.NNOM | 19854 | 额定转速 |  | float32
N1DCS.NORKP | 19855 | Ovation Control Builder |  | float32
N1DCS.NORTN | 19856 | 转速/进汽控制积分时间 |  | float32
N1DCS.NORTS | 19857 | Ovation Control Builder |  | float32
N1DCS.NORTT | 19858 | Ovation Control Builder |  | float32
N1DCS.NSGP | 19859 | Ovation Control Builder |  | float32
N1DCS.NSOG | 19860 | Ovation Control Builder |  | float32
N1DCS.NSS | 19861 | 超速试验转速设定值 |  | float32
N1DCS.NSUG | 19862 | Ovation Control Builder |  | float32
N1DCS.NSVG | 19863 | Ovation Control Builder |  | float32
N1DCS.NSVGSY | 19864 | 转速设定值同期时的梯度 |  | float32
N1DCS.NSYN | 19865 | 同期转速 |  | float32
N1DCS.NT1 | 19866 | Ovation Control Builder |  | float32
N1DCS.NT2 | 19867 | Ovation Control Builder |  | float32
N1DCS.NT3 | 19868 | Ovation Control Builder |  | float32
N1DCS.NTGTMA | 19869 | Ovation Control Builder |  | float32
N1DCS.NTGTME | 19870 | Ovation Control Builder |  | float32
N1DCS.NTKD | 19871 | Ovation Control Builder |  | float32
N1DCS.NTKG | 19872 | Ovation Control Builder |  | float32
N1DCS.NTTD | 19873 | Ovation Control Builder |  | float32
N1DCS.NTTF | 19874 | Ovation Control Builder |  | float32
N1DCS.NTTG | 19875 | Ovation Control Builder |  | float32
N1DCS.NWART | 19876 | 暖机转速 |  | float32
N1DCS.OSGOG | 19877 | Ovation Control Builder |  | float32
N1DCS.OSGUG | 19878 | Ovation Control Builder |  | float32
N1DCS.OSVG | 19879 | 延时的进汽设定值梯度 |  | float32
N1DCS.PNOM | 19880 | 额定负荷 |  | float32
N1DCS.RVP_1_1_7_KSERVO_ALG_I | 19881 | Ovation Control Builder |  | float32
N1DCS.RVP_1_1_7_KSERVODB_ALG_I | 19882 | Ovation Control Builder |  | float32
N1DCS.RVP_1_1_8_KSERVO_ALG_I | 19883 | Ovation Control Builder |  | float32
N1DCS.RVP_1_1_8_KSERVODB_ALG_I | 19884 | Ovation Control Builder |  | float32
N1DCS.STATHF | 19885 | Ovation Control Builder |  | float32
N1DCS.STATLF | 19886 | Ovation Control Builder |  | float32
N1DCS.STATNR | 19887 | 转速控制不等率 |  | float32
N1DCS.TABMA | 19888 | 汽机启动及升程器允许值起点 |  | float32
N1DCS.TABME | 19889 | 汽机启动及升程器允许值终点 |  | float32
N1DCS.TABSHMI | 19890 | TAB控制器输出百分比 |  | float32
N1DCS.TEST_LA | 19891 | test |  | float32
N1DCS.TWFCH | 19892 | Ovation Control Builder |  | float32
N1DCS.VGBAFV | 19893 | Ovation Control Builder |  | float32
N1DCS.VGBFDV | 19894 | Ovation Control Builder |  | float32
N1DCS.VGBZDV | 19895 | Ovation Control Builder |  | float32
N1DCS.VGFDS1 | 19896 | Ovation Control Builder |  | float32
N1DCS.VGHZS1 | 19897 | Ovation Control Builder |  | float32
N1DCS.VGNS1 | 19898 | Ovation Control Builder |  | float32
N1DCS.VGOS1 | 19899 | Ovation Control Builder |  | float32
N1DCS.VGOSG1 | 19900 | 负荷速率设定 |  | float32
N1DCS.VGSD1 | 19901 | Ovation Control Builder |  | float32
N1DCS.VGZDS1 | 19902 | Ovation Control Builder |  | float32
N1DCS.W150Y | 19903 | Ovation Control Builder |  | float32
N1DCS.W160Y | 19904 | Ovation Control Builder |  | float32
N1DCS.W170Y | 19905 | Ovation Control Builder |  | float32
N1DCS.W180Y | 19906 | Ovation Control Builder |  | float32
N1DCS.W230Y | 19907 | Ovation Control Builder |  | float32
N1DCS.YFDPG1 | 19908 | 主蒸汽压力输出限值1 |  | float32
N1DCS.YFDPG2 | 19909 | 主蒸汽压力输出限值2 |  | float32
N1DCS.YFDPRHMI | 19910 | 高压主蒸汽压力控制输出(百分比) |  | float32
N1DCS.YHATGO | 19911 | Ovation Control Builder |  | float32
N1DCS.YHATGU | 19912 | Ovation Control Builder |  | float32
N1DCS.YHVDGO | 19913 | Ovation Control Builder |  | float32
N1DCS.YHVDGU | 19914 | Ovation Control Builder |  | float32
N1DCS.YHZPG1 | 19915 | 热再压力控制器输出限值1 |  | float32
N1DCS.YHZPG2 | 19916 | 热再压力控制器输出限值2 |  | float32
N1DCS.YNORHMI | 19917 | 转速/负荷控制器输出百分比 |  | float32
N1DCS.YRHMI | 19918 | 中央小选输出百分比 |  | float32
N1DCS.YZDPG1 | 19919 | Ovation Control Builder |  | float32
N1DCS.YZDPG2 | 19920 | Ovation Control Builder |  | float32
N1DCS.ZDNOM | 19921 | Ovation Control Builder |  | float32
N1DCS.ZDPRKP | 19922 | Ovation Control Builder |  | float32
N1DCS.ZDPRTN | 19923 | Ovation Control Builder |  | float32
N1DCS.ZDSHMI | 19924 | 实时低压压力设定值（显示） |  | float32
N1DCS.ZDSVG | 19925 | Ovation Control Builder |  | float32
N1DCS.ZDSVG2 | 19926 | Ovation Control Builder |  | float32
N1DCS.ZDSVHMI | 19927 | 延时低压压力设定值（显示） |  | float32
N1DCS.10MYA01CS902_NT | 19928 | Ovation Control Builder |  | float32
N1DCS.GTFWSC | 19929 | Ovation Control Builder |  | float32
N1DCS.ZTFWSC | 19930 | Ovation Control Builder |  | float32
N1DCS.10LBA20CT007_TEMP | 19931 | Ovation Control Builder |  | float32
N1DCS.10LBA20CT007_XQ01 | 19932 | 高压主汽门前蒸汽温度 |  | float32
N1DCS.10LBA20CT007_XQ03 | 19933 | Ovation Control Builder |  | float32
N1DCS.10LBA20CT307A | 19934 | 高压主汽门前蒸汽温度1# | ℃ | float32
N1DCS.10LBA20CT308A | 19935 | 主汽门前蒸汽温度2# |  | float32
N1DCS.10LBA20CT309A | 19936 | 主汽门前蒸汽温度3# |  | float32
N1DCS.10LBA90CT001_XQ01 | 19937 | 低压主汽门前蒸汽温度 |  | float32
N1DCS.10LBA90CT301A | 19938 | 低压主汽门前蒸汽温度 | ℃ | float32
N1DCS.10LBB50CP111 | 19939 | 中压抽汽调节阀前后差压1 | MPa | float32
N1DCS.10LBB50CP112 | 19940 | 中压抽汽调节阀前后差压2 | MPa | float32
N1DCS.10LBB50CT007_XQ01 | 19941 | 中压主汽门前蒸汽温度（选择后） |  | float32
N1DCS.10LBB50CT007_XQ03 | 19942 | Ovation Control Builder |  | float32
N1DCS.10LBB50CT307A | 19943 | 中压主汽门前蒸汽温度1# | ℃ | float32
N1DCS.10LBB50CT308A | 19944 | 中压主汽门前蒸汽温度2# | ℃ | float32
N1DCS.10LBB50CT309A | 19945 | 中压主汽门前蒸汽温度3# | ℃ | float32
N1DCS.10LBC40CT301 | 19946 | 高排逆止门前蒸汽温度 | ℃ | float32
N1DCS.10MAA11CT121A_XQ01 | 19947 | 高压主汽门内壁温度A（100%） |  | float32
N1DCS.10MAA11CT122A_XQ01 | 19948 | 高压主汽门中壁温度A（50%） |  | float32
N1DCS.10MAA11CT321 | 19949 | 高压主汽门内壁温度A（100%） | ℃ | float32
N1DCS.10MAA11CT322 | 19950 | 高压主汽门中壁温度A（50%） | ℃ | float32
N1DCS.10MAA12CT121A_XQ01 | 19951 | Ovation Control Builder |  | float32
N1DCS.10MAA12CT122A_XQ01 | 19952 | 高压调节汽门中壁温度A（50%） |  | float32
N1DCS.10MAA12CT321 | 19953 | 高压调节汽门内壁温度A（100%） | ℃ | float32
N1DCS.10MAA12CT322 | 19954 | 高压调节汽门中壁温度A（50%） | ℃ | float32
N1DCS.10MAA50CT104A_XQ01 | 19955 | Ovation Control Builder |  | float32
N1DCS.10MAA50CT105A_XQ01 | 19956 | Ovation Control Builder |  | float32
N1DCS.10MAA50CT106A_XQ01 | 19957 | Ovation Control Builder |  | float32
N1DCS.10MAA50CT131A_XQ01 | 19958 | 高压缸内壁温度A（100%） |  | float32
N1DCS.10MAA50CT132A_XQ01 | 19959 | 高压缸内壁温度A（50%） |  | float32
N1DCS.10MAA50CT141A_XQ01 | 19960 | 高压缸外壁温（50%） |  | float32
N1DCS.10MAA50CT142A_XQ01 | 19961 | Ovation Control Builder |  | float32
N1DCS.10MAA50CT143A_XQ01 | 19962 | Ovation Control Builder |  | float32
N1DCS.10MAA50CT304 | 19963 | 高压调节门后蒸汽温度1 | ℃ | float32
N1DCS.10MAA50CT305 | 19964 | 高压调节门后蒸汽温度2 | ℃ | float32
N1DCS.10MAA50CT306 | 19965 | 高压调节门后蒸汽温度3 | ℃ | float32
N1DCS.10MAA50CT331 | 19966 | 高压缸内壁温度A（100%） | ℃ | float32
N1DCS.10MAA50CT332 | 19967 | 高压缸中壁温度A（50%） | ℃ | float32
N1DCS.10MAA50CT341 | 19968 | 高压缸外壁温（50%） | ℃ | float32
N1DCS.10MAA50CT342 | 19969 | 高压缸中壁温（50%） | ℃ | float32
N1DCS.10MAA50CT343 | 19970 | 高压缸内壁温（50%） | ℃ | float32
N1DCS.10MAA50CT351 | 19971 | 高压缸上中壁温A | ℃ | float32
N1DCS.10MAA50CT352 | 19972 | 高压缸下中壁温A | ℃ | float32
N1DCS.10MAA50FT004A_XQ01 | 19973 | 高压调节门后蒸汽温度 |  | float32
N1DCS.10MAA50FT051_XQ01 | 19974 | 高压缸左右温差 |  | float32
N1DCS.10MAA50FT051_XQ02 | 19975 | 高压缸上下温差 |  | float32
N1DCS.10MAB50CT311 | 19976 | 中压内缸进汽口壁温1 | ℃ | float32
N1DCS.10MAB50CT312 | 19977 | 中压内缸进汽口壁温2 | ℃ | float32
N1DCS.10MAB50CT313 | 19978 | 中压内缸进汽口壁温3 | ℃ | float32
N1DCS.10MAB50CT351 | 19979 | 中压缸上中壁温度A | ℃ | float32
N1DCS.10MAB50CT352 | 19980 | 中压缸中下壁温度A | ℃ | float32
N1DCS.10MAB50FT011A_XQ01 | 19981 | Ovation Control Builder |  | float32
N1DCS.10MAB50FT011A_XQ02 | 19982 | Ovation Control Builder |  | float32
N1DCS.10MAB50FT011A_XQ03 | 19983 | Ovation Control Builder |  | float32
N1DCS.10MAC10CT181A_XQ01 | 19984 | Ovation Control Builder |  | float32
N1DCS.10MAC10CT182A_XQ01 | 19985 | Ovation Control Builder |  | float32
N1DCS.10MAC10CT311 | 19986 | 末级蒸汽温度1#(静叶环温度) | ℃ | float32
N1DCS.10MAC10CT312 | 19987 | 末级蒸汽温度2#(静叶环温度) | ℃ | float32
N1DCS.10MAC10CT313 | 19988 | 末级蒸汽温度3#(静叶环温度) | ℃ | float32
N1DCS.10MAC10CT381 | 19989 | 低压后缸支柱壁温上 | ℃ | float32
N1DCS.10MAC10CT382 | 19990 | 低压后缸支柱壁温下 | ℃ | float32
N1DCS.10MAC10CT383 | 19991 | 低压排汽支架温度1#（排汽温度） | ℃ | float32
N1DCS.10MAC10CT384A | 19992 | 低压排汽支架温度2#（排汽温度） | ℃ | float32
N1DCS.10MAC10CT385 | 19993 | 低压排汽支架温度3#（排汽温度） | ℃ | float32
N1DCS.10MAD11CY141 | 19994 | #1径向轴承轴振（X） | μm | float32
N1DCS.10MAD11CY142 | 19995 | #1径向轴承轴振（Y） | μm | float32
N1DCS.10MAD12CY141 | 19996 | #2径向轴承轴振（X） | μm | float32
N1DCS.10MAD12CY142 | 19997 | #2径向轴承轴振（Y） | μm | float32
N1DCS.10MAD13CY101 | 19998 | #3径向轴承处转子膨胀 | mm | float32
N1DCS.10MAD13CY141 | 19999 | #3径向轴承轴振（X） | μm | float32
N1DCS.10MAD13CY142 | 20000 | #3径向轴承轴振（Y） | μm | float32
N1DCS.10MAY01EP144_TA | 20001 | 高压转子温度1 |  | float32
N1DCS.10MAY01EP144_TMGR | 20002 | 高压转子温度3 |  | float32
N1DCS.10MAY01EP144_TMSH | 20003 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP144_XQ01 | 20004 | 高压转子温度3(绝对值) |  | float32
N1DCS.10MAY01EP144_XQ02 | 20005 | 高压转子温度2 |  | float32
N1DCS.10MAY01EP144_XQ03 | 20006 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP144_Z1TMGR | 20007 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP144_Z1TMS | 20008 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP145_TA | 20009 | 中压转子温度1 |  | float32
N1DCS.10MAY01EP145_TMGR | 20010 | 中压转子温度3 |  | float32
N1DCS.10MAY01EP145_XQ02 | 20011 | 中压转子温度2 |  | float32
N1DCS.10MAY01EP145_XQ03 | 20012 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP145_Z1TMGR | 20013 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP145_Z1TMS | 20014 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP150_XQ06 | 20015 | 最小上升温度裕度 |  | float32
N1DCS.10MAY01EP150_XQ07 | 20016 | 最小下降温度裕度 |  | float32
N1DCS.10MAY01EP150_XQ16 | 20017 | 上升温度裕度 |  | float32
N1DCS.10MAY01EP151_DT | 20018 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP151_TM | 20019 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP151_XQ06 | 20020 | 高压主汽门上升温度裕度 |  | float32
N1DCS.10MAY01EP151_XQ07 | 20021 | 高压主汽门下降温度裕度 |  | float32
N1DCS.10MAY01EP152_DT | 20022 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP152_TM | 20023 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP152_XQ04 | 20024 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP152_XQ06 | 20025 | 高压调节门上升温度裕度 |  | float32
N1DCS.10MAY01EP152_XQ07 | 20026 | 高压调节门下降温度裕度 |  | float32
N1DCS.10MAY01EP153_DT | 20027 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP153_TM | 20028 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP153_XQ04 | 20029 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP153_XQ06 | 20030 | 高压缸上升温度裕度 |  | float32
N1DCS.10MAY01EP153_XQ07 | 20031 | 高压缸下降温度裕度 |  | float32
N1DCS.10MAY01EP154_DDTUS | 20032 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_DPMUF | 20033 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_DPMUN | 20034 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_DPMUS | 20035 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_DPMUT | 20036 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_DT | 20037 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_TA | 20038 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_TEMP | 20039 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_XQ01 | 20040 | 高压转子温度3 |  | float32
N1DCS.10MAY01EP154_XQ02 | 20041 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_XQ04 | 20042 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_XQ06 | 20043 | 高压转子上升温度裕度 |  | float32
N1DCS.10MAY01EP154_XQ07 | 20044 | 高压转子下降温度裕度 |  | float32
N1DCS.10MAY01EP154_XQ10 | 20045 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP154_XQ14 | 20046 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_DDTUS | 20047 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_DPMUF | 20048 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_DPMUN | 20049 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_DPMUS | 20050 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_DPMUT | 20051 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_DT | 20052 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_XQ01 | 20053 | 中压缸轮毂温度 |  | float32
N1DCS.10MAY01EP155_XQ02 | 20054 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_XQ04 | 20055 | 中压缸转子允许温差 |  | float32
N1DCS.10MAY01EP155_XQ06 | 20056 | 中压转子上升温度裕度 |  | float32
N1DCS.10MAY01EP155_XQ07 | 20057 | 中压转子下降温度裕度 |  | float32
N1DCS.10MAY01EP155_XQ10 | 20058 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP155_XQ14 | 20059 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP181_DE | 20060 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP181_F1 | 20061 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP181_IN | 20062 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP181_MIN | 20063 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP181_RRDOW | 20064 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP181_RRUP | 20065 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP181_SPCINP | 20066 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP181_XQ01 | 20067 | 最佳高压蒸汽参数 |  | float32
N1DCS.10MAY01EP181_XQ02 | 20068 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP182_DE | 20069 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP182_F2 | 20070 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP182_IN | 20071 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP182_RRDOW | 20072 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP182_RRUP | 20073 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP182_SPCINP | 20074 | Ovation Control Builder |  | float32
N1DCS.10MAY01EP182_XQ01 | 20075 | 最佳中压蒸汽参数 |  | float32
N1DCS.10MAY01EP182_XQ04 | 20076 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT001_XQ02 | 20077 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT001_XQ11 | 20078 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT002_XQ02 | 20079 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT002_XQ11 | 20080 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT004_TEMP | 20081 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT004_XQ02 | 20082 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT004_XQ11 | 20083 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT005_XQ02 | 20084 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT005_XQ11 | 20085 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT006_XQ02 | 20086 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT006_XQ11 | 20087 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT007A_XQ11 | 20088 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT007B_XQ11 | 20089 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT008_XQ11 | 20090 | Ovation Control Builder |  | float32
N1DCS.10MAY10FT014_TEMP | 20091 | Ovation Control Builder |  | float32
N1DCS.10MKD11CY141 | 20092 | #4轴承轴振（X） | μm | float32
N1DCS.10MKD11CY142 | 20093 | #4轴承轴振（Y） | μm | float32
N1DCS.10MKD12CY141 | 20094 | #5轴承轴振（X） | μm | float32
N1DCS.10MKD12CY142 | 20095 | #5轴承轴振（Y） | μm | float32
N1DCS.10MYA01EP150_DDTUV | 20096 | Ovation Control Builder |  | float32
N1DCS.D43P1B1L1C9 | 20097 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D43P1B1L2C9 | 20098 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D43P1B2L6C9 | 20099 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D43P1B2L7C9 | 20100 | TC冷端温度补偿点 | DEGC | float32
N1DCS.D43P1B2L8C9 | 20101 | TC冷端温度补偿点 | DEGC | float32
N1DCS.IP_TEMP_TRIP | 20102 | Ovation Control Builder |  | float32
N1DCS.IP_TEMP_WARN | 20103 | Ovation Control Builder |  | float32
N1DCS.10LBA20CT007_SP | 20104 | 主蒸汽温度限值 |  | float32
N1DCS.10LBA20CT901 | 20105 | 高压主汽门前蒸汽温度 |  | float32
N1DCS.10LBB50CT007_SP | 20106 | 热再蒸汽温度限值 |  | float32
N1DCS.10LBB50CT901 | 20107 | 中压主汽门前蒸汽温度 |  | float32
N1DCS.GYZZQGRD | 20108 | 高压主蒸汽过热度 |  | float32
N1DCS.10AGC0022 | 20109 | #1机组远方AGC投入状态 |  | digital
N1DCS.10AGC0023 | 20110 | #1机组远方AGC投入允许 |  | digital
N1DCS.10AGC0024 | 20111 | #1机组总负荷增闭锁信号 |  | digital
N1DCS.10AGC0025 | 20112 | #1机组总负荷减闭锁信号 |  | digital
N1DCS.10CAE01EY301XB51 | 20113 | #1炉保护跳闸通道A（至燃机） |  | digital
N1DCS.10CAE01EY302XB51 | 20114 | #1炉保护跳闸通道B（至燃机） |  | digital
N1DCS.10CAE01EY303XB51 | 20115 | #1炉保护跳闸通道C（至燃机） |  | digital
N1DCS.10CBA00FU002 | 20116 | 负荷遥控模式 |  | digital
N1DCS.10CBA00FU003 | 20117 | 开高压疏水阀（1% LOAD关）24VDC |  | digital
N1DCS.10CBA00FU004 | 20118 | 开中压疏水阀（2% LOAD关）24VDC |  | digital
N1DCS.10CJA00EA001DEH1 | 20119 | DCS发出启动#1机启顺控指令 |  | digital
N1DCS.10CJA00EA001DEH2 | 20120 | DCS发出启动#1机停顺控指令 |  | digital
N1DCS.10CJA01EC001XB01 | 20121 | GAS SYS READY |  | digital
N1DCS.10CJA01EC001XB07 | 20122 | DCS发出允许#2机同期信号 |  | digital
N1DCS.10CJA01EC001XB09 | 20123 | DCS允许#2机增负荷 |  | digital
N1DCS.10CJA01EC001XB10 | 20124 | DCS一次调频投入 |  | digital
N1DCS.10CJA01EC001XB12 | 20125 | DCS STOP UNLOADING |  | digital
N1DCS.10CJA01EC001XB13 | 20126 | DCS STOP LOADING |  | digital
N1DCS.10CJA01EC001XB14 | 20127 | DCS复位燃机跳闸 |  | digital
N1DCS.10CJA01EC001XB16 | 20128 | DCS投入负荷快速速率 |  | digital
N1DCS.10CJA01EC001YB08 | 20129 | DCS投入负荷正常速率 |  | digital
N1DCS.10CJA06DU001XT | 20130 | 负荷控制协调方式请求 |  | digital
N1DCS.10CRA02TOPMU13 | 20131 | #1机一次调频信号 |  | digital
N1DCS.10CSA01PF | 20132 | 机组辅助盘1电源消失 |  | digital
N1DCS.10CSA02PF | 20133 | 机组辅助盘2电源消失 |  | digital
N1DCS.10CSA51PF | 20134 | #1机热力配电柜1电源消失 |  | digital
N1DCS.10CSA52PF | 20135 | #1机热力配电柜2电源消失 |  | digital
N1DCS.10CSC01PF | 20136 | 第一套机组APS电源盘电源消失 |  | digital
N1DCS.10CSC31PF | 20137 | 第一套机组UPS电源盘电源消失 |  | digital
N1DCS.10CZTSOE01 | 20138 | 手动打闸停#1机（SOE） |  | digital
N1DCS.10CZTSOE02 | 20139 | 手动启动#1机#1润滑油泵（SOE） |  | digital
N1DCS.10CZTSOE03 | 20140 | 手动启动#1机#2润滑油泵（SOE） |  | digital
N1DCS.10CZTSOE04 | 20141 | 手动启动#1机柴油发电机（SOE） |  | digital
N1DCS.10CZTSOE05 | 20142 | 手动打闸停#2机（SOE） |  | digital
N1DCS.10CZTSOE06 | 20143 | 手动关闭调压站火警阀（SOE） |  | digital
N1DCS.10CZTSOE07 | 20144 | 手动解列#1发电机（SOE） |  | digital
N1DCS.10CZTSOE08 | 20145 | 手动打开真空破坏气动门（SOE） |  | digital
N1DCS.10CZTSOE09 | 20146 | 手动开高压过热器PCV阀（SOE） |  | digital
N1DCS.10CZTSOE10 | 20147 | 手动开中压过热器排汽门（SOE） |  | digital
N1DCS.10CZTSOE11 | 20148 | 手动开低压过热器排汽门（SOE） |  | digital
N1DCS.10CZTSOE12 | 20149 | 手动启动#1机应急油泵（SOE） |  | digital
N1DCS.10CZTSOE13 | 20150 | 手动启动#2机#1润滑油泵（SOE） |  | digital
N1DCS.10CZTSOE14 | 20151 | 手动启动#2机#2润滑油泵（SOE） |  | digital
N1DCS.10CZTSOE15 | 20152 | 手动启动#2机应急油泵（SOE） |  | digital
N1DCS.10CZTSOE16 | 20153 | 手动解列#2发电机（SOE） |  | digital
N1DCS.10CZTSOE17 | 20154 | 手动打开高包启动放水门（SOE） |  | digital
N1DCS.10CZTSOE18 | 20155 | 手动打开中包启动放水门（SOE） |  | digital
N1DCS.10CZTSOE19 | 20156 | 手动打开低包启动放水门（SOE） |  | digital
N1DCS.10DCSTOTCS01 | 20157 | MAKE GT READY |  | digital
N1DCS.10HYY01EY001BDEH | 20158 | #1炉联跳#1机通道2 |  | digital
N1DCS.10HYY01EY001CDEH | 20159 | #1炉联跳#1机通道3 |  | digital
N1DCS.10HYY01EY001DSOE | 20160 | #1炉保护跳闸（SOE） |  | digital
N1DCS.10LBA10AA402CP | 20161 | 高压主汽母管疏水气动门1全关位 |  | digital
N1DCS.10LBA10AA402F | 20162 | 高压主汽母管疏水气动门1无电源 |  | digital
N1DCS.10LBA10AA402OD/CD | 20163 | 高压主汽母管疏水门1关/开指令 |  | digital
N1DCS.10LBA10AA402OP | 20164 | 高压主汽母管疏水气动门1全开位 |  | digital
N1DCS.10LBA10AA404CP | 20165 | 高压主汽母管疏水气动门2全关位 |  | digital
N1DCS.10LBA10AA404F | 20166 | 高压主汽母管疏水气动门2无电源 |  | digital
N1DCS.10LBA10AA404OD/CD | 20167 | 高压主汽母管疏水门2关/开指令 |  | digital
N1DCS.10LBA10AA404OP | 20168 | 高压主汽母管疏水气动门2全开位 |  | digital
N1DCS.10LBA10CPX3_MRE | 20169 | 高压主汽压力坏点 |  | digital
N1DCS.10LBA20AA402CP | 20170 | 低压主汽门前疏水气动门全关位 |  | digital
N1DCS.10LBA20AA402F | 20171 | 低压主汽门前疏水气动门无电源 |  | digital
N1DCS.10LBA20AA402OD/CD | 20172 | 低压主汽门前疏水门关/开指令 |  | digital
N1DCS.10LBA20AA402OP | 20173 | 低压主汽门前疏水气动门全开位 |  | digital
N1DCS.10LBA20AA406CP | 20174 | 低压主汽母管疏水气动门全关位 |  | digital
N1DCS.10LBA20AA406F | 20175 | 低压主汽母管疏水气动门无电源 |  | digital
N1DCS.10LBA20AA406OD/CD | 20176 | 低压主汽母管疏水门关/开指令 |  | digital
N1DCS.10LBA20AA406OP | 20177 | 低压主汽母管疏水气动门全开位 |  | digital
N1DCS.10LBA20CPX2_MRE | 20178 | 低压蒸汽母管压力坏点 |  | digital
N1DCS.10LBB10AA402CP | 20179 | 高温再热蒸汽母管疏水门全关位 |  | digital
N1DCS.10LBB10AA402F | 20180 | 高温再热蒸汽母管疏水门无电源 |  | digital
N1DCS.10LBB10AA402OD/CD | 20181 | 高温再热汽母管疏水门关/开指令 |  | digital
N1DCS.10LBB10AA402OP | 20182 | 高温再热蒸汽母管疏水门全开位 |  | digital
N1DCS.10LBB10AA404CP | 20183 | 中旁阀前疏水气动门全关位 |  | digital
N1DCS.10LBB10AA404F | 20184 | 中旁阀前疏水气动门无电源 |  | digital
N1DCS.10LBB10AA404OD/CD | 20185 | 中旁阀前疏水气动门关/开指令 |  | digital
N1DCS.10LBB10AA404OP | 20186 | 中旁阀前疏水气动门全开位 |  | digital
N1DCS.10LBB10CPX2_MRE | 20187 | 高温再热蒸汽压力坏点 |  | digital
N1DCS.10LBC10AA001CP | 20188 | 高排逆止门全关位 |  | digital
N1DCS.10LBC10AA001F | 20189 | 高排逆止门无电源 |  | digital
N1DCS.10LBC10AA001OD | 20190 | 高排逆止门打开/关闭指令 |  | digital
N1DCS.10LBC10AA001OP | 20191 | 高排逆止门全开位 |  | digital
N1DCS.10LBC10AA404CP | 20192 | 高排逆止门后疏水气动门全关位 |  | digital
N1DCS.10LBC10AA404F | 20193 | 高排逆止门后疏水气动门无电源 |  | digital
N1DCS.10LBC10AA404OD/CD | 20194 | 高排逆止门后疏水门关/开指令 |  | digital
N1DCS.10LBC10AA404OP | 20195 | 高排逆止门后疏水气动门全开位 |  | digital
N1DCS.10LBC10AA406CP | 20196 | 冷再疏水气动门全关位 |  | digital
N1DCS.10LBC10AA406F | 20197 | 冷再疏水气动门无电源 |  | digital
N1DCS.10LBC10AA406OD/CD | 20198 | 冷再疏水气动门关闭/打开指令 |  | digital
N1DCS.10LBC10AA406OP | 20199 | 冷再疏水气动门全开位 |  | digital
N1DCS.10LBC10CL001HH | 20200 | 高排逆止门前疏水罐液位高高 |  | digital
N1DCS.10LBC10CL002H | 20201 | 高排逆止门前疏水罐液位高 |  | digital
N1DCS.10LBC10CL003HH | 20202 | 高排逆止门后疏水罐液位高高 |  | digital
N1DCS.10LBC10CL004H | 20203 | 高排逆止门后疏水罐液位高 |  | digital
N1DCS.10LBC10CL005HH | 20204 | 冷再冷段疏水罐液位高高 |  | digital
N1DCS.10LBC10CL006H | 20205 | 冷再冷段疏水罐液位高 |  | digital
N1DCS.10LBH10AA101CD | 20206 | 高排通风阀快关指令 |  | digital
N1DCS.10LBH10AA101CP | 20207 | 高排通风阀全关位置 |  | digital
N1DCS.10LBH10AA101F | 20208 | 高排通风阀电源消失 |  | digital
N1DCS.10LBH10AA101OD | 20209 | 高排通风阀打开指令 |  | digital
N1DCS.10LBH10AA101OP | 20210 | 高排通风阀全开位置 |  | digital
N1DCS.10LBH10AA402CP | 20211 | 高排通风阀前疏水气动门全关位 |  | digital
N1DCS.10LBH10AA402F | 20212 | 高排通风阀前疏水气动门无电源 |  | digital
N1DCS.10LBH10AA402OD/CD | 20213 | 高排通风阀前疏水门关/开指令 |  | digital
N1DCS.10LBH10AA402OP | 20214 | 高排通风阀前疏水气动门全开位 |  | digital
N1DCS.10LCB11AP001TP1 | 20215 | #1凝结水泵已停止 |  | digital
N1DCS.10LCB12AP002TP1 | 20216 | #2凝结水泵已停止 |  | digital
N1DCS.10LCE12AA001CP | 20217 | 凝结水至低旁减温水气动门全关位 |  | digital
N1DCS.10LCE12AA101CP | 20218 | 凝结水至低旁减温水调节门全关位 |  | digital
N1DCS.10LCE12AA101OP | 20219 | 凝结水至低旁减温水调节门全开位 |  | digital
N1DCS.10LCE15AA001CP | 20220 | 凝结水至中旁减温水气动门全关位 |  | digital
N1DCS.10LCE15AA101CP | 20221 | 凝结水至中旁减温水调节门全关位 |  | digital
N1DCS.10LCE15AA101OP | 20222 | 凝结水至中旁减温水调节门全开位 |  | digital
N1DCS.10MAA11CG051CP | 20223 | 高压主汽门全关位置 |  | digital
N1DCS.10MAA11CG051OP | 20224 | 高压主汽门全开位置 |  | digital
N1DCS.10MAA12CG051CP | 20225 | 高压调节阀全关位置 |  | digital
N1DCS.10MAA12CG051OP | 20226 | 高压调节阀全开位置 |  | digital
N1DCS.10MAA50EZ110SOE | 20227 | #1机高压缸前后差压保护动作 |  | digital
N1DCS.10MAA50EZ120SOE | 20228 | #1机高压主蒸汽温度高保护动作 |  | digital
N1DCS.10MAB11CG051DEH | 20229 | 中压主汽门全关位置 |  | digital
N1DCS.10MAB11CG051OP | 20230 | 中压主汽门全开位置 |  | digital
N1DCS.10MAB12CG051CP | 20231 | 中压调节门全关位置 |  | digital
N1DCS.10MAB12CG051OP | 20232 | 中压调节门全开位置 |  | digital
N1DCS.10MAC10EZ220SOE | 20233 | #1机低排温度高保护动作 |  | digital
N1DCS.10MAC11FF001 | 20234 | 热网故障 |  | digital
N1DCS.10MAD11EZ100SOE | 20235 | #1机轴承金属温度高保护动作 |  | digital
N1DCS.10MAD12EZ310SOE | 20236 | #1机轴向位移大保护动作 |  | digital
N1DCS.10MAG10EZ110SOE | 20237 | #1机凝汽器真空低保护动作 |  | digital
N1DCS.10MAJ21AP001TP1 | 20238 | #1真空泵已停止 |  | digital
N1DCS.10MAJ22AP001TP1 | 20239 | #2真空泵已停止 |  | digital
N1DCS.10MAJ30AA002OP | 20240 | 真空破坏气动门全开位置 |  | digital
N1DCS.10MAL11AA051CP | 20241 | 高压调节阀前疏水气动门全关位 |  | digital
N1DCS.10MAL11AA051F | 20242 | 高压调节阀前疏水气动门无电源 |  | digital
N1DCS.10MAL11AA051OD/CD | 20243 | 高压调节阀前疏水门关/开指令 |  | digital
N1DCS.10MAL11AA051OP | 20244 | 高压调节阀前疏水气动门全开位 |  | digital
N1DCS.10MAL23AA051CP | 20245 | 中压主汽门前疏水门全关位置 |  | digital
N1DCS.10MAL23AA051F | 20246 | 中压主汽门前疏水门电源消失 |  | digital
N1DCS.10MAL23AA051OD/CD | 20247 | 中压主汽门前疏水门关/开指令 |  | digital
N1DCS.10MAL23AA051OP | 20248 | 中压主汽门前疏水门全开位置 |  | digital
N1DCS.10MAL26AA051CP | 20249 | 中压调节阀前疏水门全关位置 |  | digital
N1DCS.10MAL26AA051F | 20250 | 中压调节阀前疏水门电源消失 |  | digital
N1DCS.10MAL26AA051OD/CD | 20251 | 中压调节阀前疏水门关/开指令 |  | digital
N1DCS.10MAL26AA051OP | 20252 | 中压调节阀前疏水门全开位置 |  | digital
N1DCS.10MAL65AA051CP | 20253 | 高排逆止门前疏水气动门全关位 |  | digital
N1DCS.10MAL65AA051F | 20254 | 高排逆止门前疏水门电源消失 |  | digital
N1DCS.10MAL65AA051OD/CD | 20255 | 高排逆止门前疏水门关/开指令 |  | digital
N1DCS.10MAL65AA051OP | 20256 | 高排逆止门前疏水门全开位置 |  | digital
N1DCS.10MAN10AA001CP | 20257 | 凝结水至高旁减温水气动门全关位 |  | digital
N1DCS.10MAN10AA001OD | 20258 | 凝结水至高旁减温水门关/开指令 |  | digital
N1DCS.10MAN10AA001OP | 20259 | 凝结水至高旁减温水气动门全开位 |  | digital
N1DCS.10MAN10AA101AUTO | 20260 | 高旁阀在自动模式 |  | digital
N1DCS.10MAN10AA101CD | 20261 | 高旁阀快关指令 |  | digital
N1DCS.10MAN10AA101CP | 20262 | 高旁阀全关位置 |  | digital
N1DCS.10MAN10AA101CPDO | 20263 | 高旁阀全关位置(至DROP8) |  | digital
N1DCS.10MAN10AA101F | 20264 | 高旁阀故障 |  | digital
N1DCS.10MAN10AA101OD | 20265 | 高旁阀快开指令 |  | digital
N1DCS.10MAN10AA101OP | 20266 | 高旁阀全开位置 |  | digital
N1DCS.10MAN10AA101SC | 20267 | 高旁阀安全关指令 |  | digital
N1DCS.10MAN10AA102AUTO | 20268 | 高旁减温水调节阀在自动模式 |  | digital
N1DCS.10MAN10AA102CD | 20269 | 高旁减温水调节阀快关指令 |  | digital
N1DCS.10MAN10AA102CP | 20270 | 高旁减温水调节阀全关位置 |  | digital
N1DCS.10MAN10AA102F | 20271 | 高旁减温水调节阀故障 |  | digital
N1DCS.10MAN10AA102OD | 20272 | 高旁减温水调节阀快开指令 |  | digital
N1DCS.10MAN10AA102OP | 20273 | 高旁减温水调节阀全开位置 |  | digital
N1DCS.10MAN10AC101CP | 20274 | 高旁阀全关位置 |  | digital
N1DCS.10MAN10CPX2_MRE | 20275 | 高旁阀后蒸汽压力坏点 |  | digital
N1DCS.10MAN10CTX2_MRE | 20276 | 高旁阀后蒸汽温度坏点 |  | digital
N1DCS.10MAN10GH001FF | 20277 | 高压旁路油站过载 |  | digital
N1DCS.10MAN10GH001LL1 | 20278 | 高压旁路油站油位低 |  | digital
N1DCS.10MAN10GH001LL2 | 20279 | 高压旁路油站油位低低 |  | digital
N1DCS.10MAN10GH001PDH | 20280 | 高压旁路油站过滤器阻塞 |  | digital
N1DCS.10MAN10GH001PF1 | 20281 | 高压旁路油站电源1故障 |  | digital
N1DCS.10MAN10GH001PF2 | 20282 | 高压旁路油站电源2故障 |  | digital
N1DCS.10MAN10GH001PH1 | 20283 | 高压旁路油站油压高 |  | digital
N1DCS.10MAN10GH001PH2 | 20284 | 高压旁路油站油压高高 |  | digital
N1DCS.10MAN10GH001PL1 | 20285 | 高压旁路油站油压低 |  | digital
N1DCS.10MAN10GH001PL2 | 20286 | 高压旁路油站油压低低 |  | digital
N1DCS.10MAN10GH001RD1 | 20287 | 高压旁路油站#1油泵启动指令 |  | digital
N1DCS.10MAN10GH001RD2 | 20288 | 高压旁路油站#2油泵启动指令 |  | digital
N1DCS.10MAN10GH001RP1 | 20289 | 高压旁路油站#1油泵在运行 |  | digital
N1DCS.10MAN10GH001RP2 | 20290 | 高压旁路油站#2油泵在运行 |  | digital
N1DCS.10MAN10GH001TD1 | 20291 | 高压旁路油站#1油泵停止指令 |  | digital
N1DCS.10MAN10GH001TD2 | 20292 | 高压旁路油站#2油泵停止指令 |  | digital
N1DCS.10MAN10GH001TH | 20293 | 高压旁路油站油温高 |  | digital
N1DCS.10MAN10GH001TP1 | 20294 | 高压旁路油站#1油泵已停止 |  | digital
N1DCS.10MAN10GH001TP2 | 20295 | 高压旁路油站#2油泵已停止 |  | digital
N1DCS.10MAN20AA101AUTO | 20296 | 中旁阀在自动模式 |  | digital
N1DCS.10MAN20AA101CD | 20297 | 中旁阀快关指令 |  | digital
N1DCS.10MAN20AA101CP | 20298 | 中旁阀全关位置 |  | digital
N1DCS.10MAN20AA101CPDO | 20299 | 中旁阀全关位置(至DROP8) |  | digital
N1DCS.10MAN20AA101F | 20300 | 中旁阀故障 |  | digital
N1DCS.10MAN20AA101OD | 20301 | 中旁阀快开指令 |  | digital
N1DCS.10MAN20AA101OP | 20302 | 中旁阀全开位置 |  | digital
N1DCS.10MAN20AA101SC1 | 20303 | 中旁阀安全关指令1 |  | digital
N1DCS.10MAN20AA101SC2 | 20304 | 中旁阀安全关指令2 |  | digital
N1DCS.10MAN20AC101CP | 20305 | 中旁阀全关位置 |  | digital
N1DCS.10MAN20CPX2_MRE | 20306 | 中旁阀后蒸汽压力坏点 |  | digital
N1DCS.10MAN20CTX2_MRE | 20307 | 中旁阀后蒸汽温度坏点 |  | digital
N1DCS.10MAN20GH001FF | 20308 | 中低压旁路油站过载 |  | digital
N1DCS.10MAN20GH001LL1 | 20309 | 中低压旁路油站油位低 |  | digital
N1DCS.10MAN20GH001LL2 | 20310 | 中低压旁路油站油位低低 |  | digital
N1DCS.10MAN20GH001PDH | 20311 | 中低压旁路油站过滤器阻塞 |  | digital
N1DCS.10MAN20GH001PF1 | 20312 | 中低压旁路油站电源1故障 |  | digital
N1DCS.10MAN20GH001PF2 | 20313 | 中低压旁路油站电源2故障 |  | digital
N1DCS.10MAN20GH001PH1 | 20314 | 中低压旁路油站油压高 |  | digital
N1DCS.10MAN20GH001PH2 | 20315 | 中低压旁路油站油压高高 |  | digital
N1DCS.10MAN20GH001PL1 | 20316 | 中低压旁路油站油压低 |  | digital
N1DCS.10MAN20GH001PL2 | 20317 | 中低压旁路油站油压低低 |  | digital
N1DCS.10MAN20GH001RD1 | 20318 | 中低压旁路油站#1油泵启动指令 |  | digital
N1DCS.10MAN20GH001RD2 | 20319 | 中低压旁路油站#2油泵启动指令 |  | digital
N1DCS.10MAN20GH001RP1 | 20320 | 中低压旁路油站#1油泵在运行 |  | digital
N1DCS.10MAN20GH001RP2 | 20321 | 中低压旁路油站#2油泵在运行 |  | digital
N1DCS.10MAN20GH001TD1 | 20322 | 中低压旁路油站#1油泵停止指令 |  | digital
N1DCS.10MAN20GH001TD2 | 20323 | 中低压旁路油站#1油泵停止指令 |  | digital
N1DCS.10MAN20GH001TH | 20324 | 中低压旁路油站油温高 |  | digital
N1DCS.10MAN20GH001TP1 | 20325 | 中低压旁路油站#1油泵已停止 |  | digital
N1DCS.10MAN20GH001TP2 | 20326 | 中低压旁路油站#2油泵已停止 |  | digital
N1DCS.10MAP10AA101AUTO | 20327 | 低旁阀在自动模式 |  | digital
N1DCS.10MAP10AA101CD | 20328 | 低旁阀快关指令 |  | digital
N1DCS.10MAP10AA101CP | 20329 | 低旁阀全关位置 |  | digital
N1DCS.10MAP10AA101CPDO | 20330 | 低旁阀全关位置(至DROP8) |  | digital
N1DCS.10MAP10AA101F | 20331 | 低旁阀故障 |  | digital
N1DCS.10MAP10AA101OD | 20332 | 低旁阀快开指令 |  | digital
N1DCS.10MAP10AA101OP | 20333 | 低旁阀全开位置 |  | digital
N1DCS.10MAP10AA101SC1 | 20334 | 低旁阀安全关指令1 |  | digital
N1DCS.10MAP10AA101SC2 | 20335 | 低旁阀安全关指令2 |  | digital
N1DCS.10MAP10AA404CP | 20336 | 低旁阀前疏水气动门全关位 |  | digital
N1DCS.10MAP10AA404F | 20337 | 低旁阀前疏水气动门无电源 |  | digital
N1DCS.10MAP10AA404OD/CD | 20338 | 低旁阀前疏水气动门关/开指令 |  | digital
N1DCS.10MAP10AA404OP | 20339 | 低旁阀前疏水气动门全开位 |  | digital
N1DCS.10MAP10CPX2_MRE | 20340 | 低旁阀后蒸汽压力坏点 |  | digital
N1DCS.10MAP10CTX2_MRE | 20341 | 低旁阀后蒸汽温度坏点 |  | digital
N1DCS.10MAY01CG151CP1 | 20342 | 所有主汽门已关闭1-去锅炉主保护 |  | digital
N1DCS.10MAY01CG151CP2 | 20343 | 所有主汽门已关闭2-去锅炉主保护 |  | digital
N1DCS.10MAY01EZ001SOE | 20344 | #1机本体保护动作 |  | digital
N1DCS.10MAY01EZ011SOE | 20345 | #1机超速保护动作 |  | digital
N1DCS.10MAY01EZ011_XK468 | 20346 | #1机遮断系统已遮断8 |  | digital
N1DCS.10MAY01EZ020SOE | 20347 | 手动打闸停#1机（SOE） |  | digital
N1DCS.10MAY10EZ011SOE | 20348 | #1机轴承振动大保护动作（SOE） |  | digital
N1DCS.10MBA10CS910 | 20349 | #2机停机(GT STOPPED) |  | digital
N1DCS.10MBY10DE010YB01 | 20350 | #2机负荷控制切至DCS设定 |  | digital
N1DCS.10MBY10DE020XB01 | 20351 | AGC可用 |  | digital
N1DCS.10MBY10DE020YB01 | 20352 | 一次调频投入/退出 |  | digital
N1DCS.10MBY10DE020YB06 | 20353 | #2机在运行 |  | digital
N1DCS.10MBY10DE020YB07 | 20354 | #2机已停止 |  | digital
N1DCS.10MBY10DT040YB01 | 20355 | IGV全开位（慢速速率） |  | digital
N1DCS.10MBY10DT040YB02 | 20356 | IGV全开位 |  | digital
N1DCS.10MBY10DU060YB01 | 20357 | #2机准备同期 |  | digital
N1DCS.10MBY10DU060YB02 | 20358 | #2机在转速控制方式 |  | digital
N1DCS.10MBY10DU060YB03 | 20359 | #2机在负荷控制方式 |  | digital
N1DCS.10MBY10DU060YB04 | 20360 | #2机在最大负荷限制控制方式 |  | digital
N1DCS.10MBY10DU060YB05 | 20361 | #2机在排气温度控制方式 |  | digital
N1DCS.10MBY10EE010XB02 | 20362 | #2机负荷控制切至DCS设定 |  | digital
N1DCS.10MBY10EE010YB02 | 20363 | DCS外部负荷设定投入 |  | digital
N1DCS.10MKA01DE120XB02 | 20364 | DCS发出#2机远方同期投入 |  | digital
N1DCS.10MKA01DE120XB03 | 20365 | DCS发出#2机自动同期投入 |  | digital
N1DCS.10MKA01DE120XB04 | 20366 | DCS发出#2机再同期请求 |  | digital
N1DCS.10MKA01DE120YB01 | 20367 | DCS发出#2机远方同期请求 |  | digital
N1DCS.10MKA01DE120YB02 | 20368 | DCS发出#2机自动同期请求 |  | digital
N1DCS.10MKA10CL001 | 20369 | #1发电机漏水1 |  | digital
N1DCS.10MKA10CL002 | 20370 | #1发电机漏水2 |  | digital
N1DCS.10MKA10CL003 | 20371 | #1发电机漏水3 |  | digital
N1DCS.10MKA10CL004 | 20372 | #1发电机漏水4 |  | digital
N1DCS.10MKA10CL005 | 20373 | #1发电机漏水5 |  | digital
N1DCS.10MKA10CL006 | 20374 | #1发电机漏水6 |  | digital
N1DCS.10MYA01CS901H | 20375 | #1机转速大于2951RPM |  | digital
N1DCS.10MYA01CS901L | 20376 | #1机转速大于600RPM |  | digital
N1DCS.10MYA01DG010 | 20377 | 负荷控制投入（协调方式） |  | digital
N1DCS.10MYA01DU010 | 20378 | 负荷控制投入 |  | digital
N1DCS.10MYB01EC001YB01 | 20379 | #2机无火焰通道A |  | digital
N1DCS.10MYB01EC002YB01 | 20380 | #2机无火焰通道A |  | digital
N1DCS.10MYB01EC003YB01 | 20381 | #2机无火焰通道A |  | digital
N1DCS.10MYB01EC051YB01 | 20382 | #2机已停止 |  | digital
N1DCS.10MYB01EC061YB01 | 20383 | #2机盘车已退出通道1 |  | digital
N1DCS.10MYB01EC062YB01 | 20384 | #2机盘车已退出通道2 |  | digital
N1DCS.10MYB01EC063YB01 | 20385 | #2机盘车已退出通道3 |  | digital
N1DCS.10MYB01EC304YB01 | 20386 | #2机甩负荷通道1 |  | digital
N1DCS.10MYB01EC305YB01 | 20387 | #2机甩负荷通道2 |  | digital
N1DCS.10MYB01EC306YB01 | 20388 | #2机甩负荷通道3 |  | digital
N1DCS.10MYB01EU001YB01 | 20389 | #2机跳闸信号（至DCS） |  | digital
N1DCS.10MYB01EU001YB11 | 20390 | #2机跳闸信号（至DCS） |  | digital
N1DCS.10MYB01EU001YB21 | 20391 | #2机跳闸信号（至DCS） |  | digital
N1DCS.10MYB01EZ001YB01 | 20392 | #2机跳闸信号（至SER） |  | digital
N1DCS.10MYB10DE010YB01 | 20393 | #2机负荷快速速率投入 |  | digital
N1DCS.10MYB10DE010YB02 | 20394 | #2机负荷正常速率投入 |  | digital
N1DCS.10MYB10EE101XB01 | 20395 | DCS发出停#2机指令 |  | digital
N1DCS.10MYB10EE102XB02 | 20396 | DCS发出启#2机指令 |  | digital
N1DCS.10PFMPUTIN | 20397 | #1机组一次调频投入/退出 |  | digital
N1DCS.10PGA11AP001TP1 | 20398 | #1闭式冷却水泵已停止 |  | digital
N1DCS.10PGA12AP001TP1 | 20399 | #2闭式冷却水泵已停止 |  | digital
N1DCS.10TCSTODCS01 | 20400 | #2机已准备就绪 |  | digital
N1DCS.10TSIDI1 | 20401 | #1机零转速报警 |  | digital
N1DCS.10TSIDI10 | 20402 | #1机偏心大报警1 |  | digital
N1DCS.10TSIDI11 | 20403 | #1机偏心大报警2 |  | digital
N1DCS.10TSIDI12 | 20404 | #1机轴承盖振大报警1 |  | digital
N1DCS.10TSIDI13 | 20405 | #1机轴承盖振大报警2 |  | digital
N1DCS.10TSIDI14 | 20406 | #1机左高压缸热膨胀大报警 |  | digital
N1DCS.10TSIDI15 | 20407 | #1机右高压缸热膨胀大报警 |  | digital
N1DCS.10TSIDI16 | 20408 | #1机装置\OK\"状态" |  | digital
N1DCS.10TSIDI17 | 20409 | #1机主电源失电报警 |  | digital
N1DCS.10TSIDI18 | 20410 | #1机副电源失电报警 |  | digital
N1DCS.10TSIDI19 | 20411 | #1机主、副电源失电报警 |  | digital
N1DCS.10TSIDI2 | 20412 | #1机转速大报警1 |  | digital
N1DCS.10TSIDI20 | 20413 | #1机24VDC失电报警 |  | digital
N1DCS.10TSIDI3 | 20414 | #1机转速大报警2 |  | digital
N1DCS.10TSIDI4 | 20415 | #1机轴振动大报警1 |  | digital
N1DCS.10TSIDI5 | 20416 | #1机轴振动大报警2 |  | digital
N1DCS.10TSIDI6 | 20417 | #1机轴向位移大报警1 |  | digital
N1DCS.10TSIDI7 | 20418 | #1机轴向位移大报警2 |  | digital
N1DCS.10TSIDI8 | 20419 | #1机高压及低压缸胀差大报警1 |  | digital
N1DCS.10TSIDI9 | 20420 | #1机高压及低压缸胀差大报警2 |  | digital
N1DCS.11AEA01EA100_XB05 | 20421 | #2主变220KV断路器允许同期 |  | digital
N1DCS.11BBE00EG001_XB27 | 20422 | #1 SFC 6KV母线低电压信号 |  | digital
N1DCS.11MKY01EZ120_XB01 | 20423 | #2发电机保护A装置失电/装置闭锁 |  | digital
N1DCS.11MKY01EZ122_XB01 | 20424 | #2发电机保护A告警总信号 |  | digital
N1DCS.11MKY01EZ220_XB01 | 20425 | #2发电机保护B装置失电/装置闭锁 |  | digital
N1DCS.11MKY01EZ222_XB01 | 20426 | #2发电机保护B告警总信号 |  | digital
N1DCS.AGCOFF | 20427 | AGC已退出 |  | digital
N1DCS.AGCON | 20428 | AGC已投入 |  | digital
N1DCS.DEHHIPRSCTL | 20429 | 高中压压力控制后备模式 |  | digital
N1DCS.DEHLPRSCTL | 20430 | 低压蒸汽压力控制后备模式 |  | digital
N1DCS.DI | 20431 | 开关量 |  | digital
N1DCS.GT_FIRE | 20432 | #2机在运行 |  | digital
N1DCS.HPBCL | 20433 | 高旁阀已关闭 |  | digital
N1DCS.HPBFOLLOW | 20434 | 高旁阀压力控制后备模式 |  | digital
N1DCS.HPBMAN | 20435 | 高旁阀在手动模式 |  | digital
N1DCS.HPBPRATE0 | 20436 | 高旁阀压力设定值下降速率为0 |  | digital
N1DCS.HPBPUPRATEMAX | 20437 | 高旁阀压力设定值上升速率最大 |  | digital
N1DCS.HPBSPYCL | 20438 | 高旁减温水调节阀已关闭 |  | digital
N1DCS.HPBSPYOP | 20439 | 高旁减温水调节阀已打开 |  | digital
N1DCS.HPBYCVFASTCLS | 20440 | 高旁阀快关指令 |  | digital
N1DCS.HPBYCVFASTOP | 20441 | 高旁阀快开指令 |  | digital
N1DCS.HPBYSPYCVCLS | 20442 | 高旁减温水调节阀快关指令 |  | digital
N1DCS.HPBYSPYCVOP | 20443 | 高旁减温水调节阀快开指令 |  | digital
N1DCS.HPMINPOS | 20444 | 高旁阀最小阀位模式 |  | digital
N1DCS.HPTARGETSETP | 20445 | 高旁阀后备模式压力设定值高限 |  | digital
N1DCS.HRSGCOLD | 20446 | #1炉冷态模式启动 |  | digital
N1DCS.HRSGHOT | 20447 | #1炉热态模式启动 |  | digital
N1DCS.HRSGWARM | 20448 | #1炉温态模式启动 |  | digital
N1DCS.IPBCL | 20449 | 中旁阀已关闭 |  | digital
N1DCS.IPBFOLLOW | 20450 | 中旁阀压力控制后备模式 |  | digital
N1DCS.IPBMAN | 20451 | 中旁阀在手动模式 |  | digital
N1DCS.IPBPRATE0 | 20452 | 中旁阀压力设定值下降速率为0 |  | digital
N1DCS.IPBPUPRATEMAX | 20453 | 中旁阀压力设定值上升速率最大 |  | digital
N1DCS.IPBSPYCL | 20454 | 中旁减温水调节阀已关闭 |  | digital
N1DCS.IPBSPYOP | 20455 | 中旁减温水调节阀已打开 |  | digital
N1DCS.IPBYCVFASTCLS | 20456 | 中旁阀快关指令 |  | digital
N1DCS.IPBYCVFASTOP | 20457 | 中旁阀快开指令 |  | digital
N1DCS.IPMINPOS | 20458 | 中旁阀最小阀位模式 |  | digital
N1DCS.IPTARGETSETP | 20459 | 中旁阀后备模式压力设定值高限 |  | digital
N1DCS.LPBCL | 20460 | 低旁阀已关闭 |  | digital
N1DCS.LPBFOLLOW | 20461 | 低旁阀压力控制后备模式 |  | digital
N1DCS.LPBMAN | 20462 | 低旁阀在手动模式 |  | digital
N1DCS.LPBPRATE0 | 20463 | 低旁阀压力设定值下降速率为0 |  | digital
N1DCS.LPBPUPRATEMAX | 20464 | 低旁阀压力设定值上升速率最大 |  | digital
N1DCS.LPBSPYCL | 20465 | 低旁减温水调节阀已关闭 |  | digital
N1DCS.LPBSPYOP | 20466 | 低旁减温水调节阀已打开 |  | digital
N1DCS.LPBYCVFASTCLS | 20467 | 低旁阀快关指令 |  | digital
N1DCS.LPBYCVFASTOP | 20468 | 低旁阀快开指令 |  | digital
N1DCS.LPMINPOS | 20469 | 低旁阀最小阀位模式 |  | digital
N1DCS.LPTARGETSETP | 20470 | 低旁阀后备模式压力设定值高限 |  | digital
N1DCS.ONE1 | 20471 | 开关量1 |  | digital
N1DCS.OPHIBYPS | 20472 | 停#1机时开高中压旁路 |  | digital
N1DCS.TURBDRNHP_CL | 20473 | #1机高压疏水阀组关闭指令 |  | digital
N1DCS.TURBDRNHP_OP | 20474 | #1机高压疏水阀组打开指令 |  | digital
N1DCS.TURBDRNHPCP | 20475 | #1机高压疏水阀组均已关闭 |  | digital
N1DCS.TURBDRNHPOP | 20476 | #1机高压疏水门组均已全开 |  | digital
N1DCS.TURBDRNIP_CL | 20477 | #1机中压疏水阀组关闭指令 |  | digital
N1DCS.TURBDRNIP_OP | 20478 | #1机中压疏水阀组打开指令 |  | digital
N1DCS.TURBDRNIPCP | 20479 | #1机中压疏水阀组均已关闭 |  | digital
N1DCS.TURBDRNIPOP | 20480 | #1机中压疏水门组均已全开 |  | digital
N1DCS.TURBDRNLP_CL | 20481 | #1机低压疏水阀组关闭指令 |  | digital
N1DCS.TURBDRNLP_OP | 20482 | #1机低压疏水阀组打开指令 |  | digital
N1DCS.TURBDRNLPCP | 20483 | #1机低压疏水阀组均已关闭 |  | digital
N1DCS.TURBDRNLPOP | 20484 | #1机低压疏水门组均已全开 |  | digital
N1DCS.ZERO1 | 20485 | 开关量0 |  | digital
N1DCS.AGCOK | 20486 | AGC总指令与负荷反馈偏差<10 |  | digital
N1DCS.AGCOKORNOTCCS1 | 20487 | AGC已投入/CCS已退出 |  | digital
N1DCS.AGCPMT1 | 20488 | AGC投入允许 |  | digital
N1DCS.AGCREADY | 20489 | AGC已就绪 |  | digital
N1DCS.ANYGTRB1 | 20490 | Ovation Control Builder |  | digital
N1DCS.CCSMODE1 | 20491 | CCS已投入 |  | digital
N1DCS.CCSNOTAGC1 | 20492 | CCS已投入且AGC已退出 |  | digital
N1DCS.CCSPMT | 20493 | CCS投入允许 |  | digital
N1DCS.DCS_AUXOK1 | 20494 | #1机润滑油、控制油系统运行正常 |  | digital
N1DCS.DCS_DRNWTR1 | 20495 | #1机疏水系统运行正常 |  | digital
N1DCS.DCS_GLANDSTEAMON1 | 20496 | #1机轴封系统运行正常 |  | digital
N1DCS.DCSETSTRIPRSPB | 20497 | ETS跳闸首出复位指令 |  | digital
N1DCS.DCSSTOPTURB | 20498 | DCS停止#1机 |  | digital
N1DCS.DCSTRIPTURB | 20499 | Ovation Control Builder |  | digital
N1DCS.DEHTRIPPED | 20500 | #1机跳闸 |  | digital
N1DCS.EXT_LOADSET_SEL | 20501 | #2机负荷设定在DCS控制 |  | digital
N1DCS.FC_MODE | 20502 | 纯凝模式 |  | digital
N1DCS.GOUP | 20503 | 高中压旁路冲转状态 |  | digital
N1DCS.GOUPMOD | 20504 | 手动投入高中压旁路冲转模式 |  | digital
N1DCS.GT_CTR_REMOTE | 20505 | #2机允许CCS控制 |  | digital
N1DCS.GT_REMOTE_PER | 20506 | #2机允许CCS控制 |  | digital
N1DCS.GTCBOFF1 | 20507 | #2发电机已解列 |  | digital
N1DCS.GTCBON1 | 20508 | #2发电机已并网 |  | digital
N1DCS.GTCCSONDMD1 | 20509 | 燃机CCS投入请求 |  | digital
N1DCS.GTCCSONDMDPMT1 | 20510 | 燃机CCS投入请求允许 |  | digital
N1DCS.GTCCSPMT1 | 20511 | #2机负荷>120且负荷在DCS控制 |  | digital
N1DCS.GTFIRING | 20512 | #2机在运行（有火焰） |  | digital
N1DCS.GTHINTERLOCK | 20513 | #2机跳闸信号（联跳#1炉） |  | digital
N1DCS.GTLOAD_AUTO1 | 20514 | Ovation Control Builder |  | digital
N1DCS.GTNOFIRE1 | 20515 | #2机无火焰通道1 |  | digital
N1DCS.GTNOFIRE2 | 20516 | #2机无火焰通道2 |  | digital
N1DCS.GTNOFIRE3 | 20517 | #2机无火焰通道3 |  | digital
N1DCS.GTPCTR1 | 20518 | #2机盘车已退出通道1(ESD) |  | digital
N1DCS.GTPCTR2 | 20519 | #2机盘车已退出通道2(ESD) |  | digital
N1DCS.GTPCTR3 | 20520 | #2机盘车已退出通道3(ESD) |  | digital
N1DCS.GTRB | 20521 | #2机发生RB |  | digital
N1DCS.GTRB1 | 20522 | #2机发生RB通道1 |  | digital
N1DCS.GTRB2 | 20523 | #2机发生RB通道2 |  | digital
N1DCS.GTREJ1 | 20524 | #2机甩负荷通道1(ESD) |  | digital
N1DCS.GTREJ2 | 20525 | #2机甩负荷通道2(ESD) |  | digital
N1DCS.GTREJ3 | 20526 | #2机甩负荷通道3(ESD) |  | digital
N1DCS.GTRUN1 | 20527 | #2机在运行 |  | digital
N1DCS.GTSTOP1 | 20528 | #2机已停止 |  | digital
N1DCS.GTTRIP | 20529 | #2机已跳闸 |  | digital
N1DCS.HINTERLOCK | 20530 | Ovation Control Builder |  | digital
N1DCS.HREXHOT | 20531 | #1炉极热态模式启动 |  | digital
N1DCS.HRSGRUN | 20532 | #1炉在运行 |  | digital
N1DCS.HRSGSTOP | 20533 | #1炉已停止 |  | digital
N1DCS.HSELFC_MODE | 20534 | #1机组纯凝模式 |  | digital
N1DCS.HSELPC_MODE | 20535 | #1机组抽凝模式 |  | digital
N1DCS.HSTRUPMODESEL | 20536 | #1炉在任一启动方式（冷、温、热 |  | digital
N1DCS.HTRIPDMD | 20537 | #1炉跳闸信号（联跳燃机） |  | digital
N1DCS.IGVFOP | 20538 | IGV全开(慢速速率) |  | digital
N1DCS.IGVOP | 20539 | IGV全开 |  | digital
N1DCS.LIFTPUMPS_1OF2ON | 20540 | 至少一台顶轴油泵在运行 |  | digital
N1DCS.LIFTPUMPS_ALLOFF1 | 20541 | 顶轴油泵均已停止 |  | digital
N1DCS.LOAD_PW_OK | 20542 | Ovation Control Builder |  | digital
N1DCS.LOADATMAX1 | 20543 | #1机组总负荷设定>高限值 |  | digital
N1DCS.LOADATMIN1 | 20544 | #1机组总负荷设定<低限值 |  | digital
N1DCS.LOADGO1 | 20545 | 负荷开始增减 |  | digital
N1DCS.LOADHOLD1 | 20546 | 负荷停止增减/保持原值 |  | digital
N1DCS.LOADSP_AUTO1 | 20547 | #1机组负荷设定在自动模式 |  | digital
N1DCS.MONITORRE | 20548 | 光字牌声音报警 |  | digital
N1DCS.MONTH_CHG | 20549 | 月份变化 |  | digital
N1DCS.NOTCCSMODE1 | 20550 | CCS已退出 |  | digital
N1DCS.OPCACT | 20551 | OPC动作（DEH至DCS） |  | digital
N1DCS.OPLBYPS | 20552 | 停#1机时打开低旁阀 |  | digital
N1DCS.PC_MODE | 20553 | #1机组抽凝模式 |  | digital
N1DCS.RB1PUTIN | 20554 | #1炉跳闸联锁#2机RB保护投入 |  | digital
N1DCS.RBOCCUR1 | 20555 | #2机RB回路1 |  | digital
N1DCS.RBOCCUR2 | 20556 | #2机RB回路2 |  | digital
N1DCS.RBORNOTCCS1 | 20557 | #2机发生RB或CCS已退出 |  | digital
N1DCS.RBPUTIN | 20558 | 凝结水泵跳闸联锁#2机RB保护投入 |  | digital
N1DCS.SPTINTRHRSG | 20559 | 停#1机联锁停余热锅炉 |  | digital
N1DCS.STBPSTOPMODE | 20560 | 旁路停机模式 |  | digital
N1DCS.STCBOFF1 | 20561 | #1发电机已解列 |  | digital
N1DCS.STCBON1 | 20562 | #1发电机已并网 |  | digital
N1DCS.STOPTURBCMD | 20563 | DCS停止#1机指令 |  | digital
N1DCS.STRUN | 20564 | #1机负荷>20MW |  | digital
N1DCS.THINTERLOCK | 20565 | #2机跳闸信号（联跳#1炉） |  | digital
N1DCS.TURBLATCHED1 | 20566 | #1机无遮断信号 |  | digital
N1DCS.TURBRUN | 20567 | #1机无遮断信号 |  | digital
N1DCS.TURBTRIP1 | 20568 | #1机已遮断 |  | digital
N1DCS.TURBTRIPACKOK1 | 20569 | #1机打闸已确认（APS停机） |  | digital
N1DCS.YEAR_CHG | 20570 | 年份变化 |  | digital
N1DCS.10LBD20AA001CD | 20571 | #1机冷再供热电动门关闭指令 |  | digital
N1DCS.10LBD20AA001CP | 20572 | #1机冷再供热电动门全关位置 |  | digital
N1DCS.10LBD20AA001F | 20573 | #1机冷再供热电动门综合故障 |  | digital
N1DCS.10LBD20AA001OD | 20574 | #1机冷再供热电动门打开指令 |  | digital
N1DCS.10LBD20AA001OP | 20575 | #1机冷再供热电动门全开位置 |  | digital
N1DCS.10LBD20AA001RC | 20576 | #1机冷再供热电动门在远控 |  | digital
N1DCS.10LBD20AA002CD | 20577 | 冷再供热逆止门后电动门关指令 |  | digital
N1DCS.10LBD20AA002CP | 20578 | 冷再供热逆止门后电动门全关位 |  | digital
N1DCS.10LBD20AA002F | 20579 | 冷再供热逆止门后电动门综合故障 |  | digital
N1DCS.10LBD20AA002OD | 20580 | 冷再供热逆止门后电动门开指令 |  | digital
N1DCS.10LBD20AA002OP | 20581 | 冷再供热逆止门后电动门全开位 |  | digital
N1DCS.10LBD20AA002RC | 20582 | 冷再供热逆止门后电动门在远控 |  | digital
N1DCS.10LBD20AA402CP | 20583 | 冷再供热母管气动疏水门全关位 |  | digital
N1DCS.10LBD20AA402F | 20584 | 冷再供热母管气动疏水门无电源 |  | digital
N1DCS.10LBD20AA402OD/CD | 20585 | 冷再供热母管气动疏水门开指令 |  | digital
N1DCS.10LBD20AA402OP | 20586 | 冷再供热母管气动疏水门全开位 |  | digital
N1DCS.10LBD20AC001AUTO | 20587 | 冷再供热减温减压器在自动模式 |  | digital
N1DCS.10LBD20AC001DVHI | 20588 | 冷再供热减压器指令、反馈偏差大 |  | digital
N1DCS.10LBD20AC001F | 20589 | 冷再供热减温减压调阀综合故障 |  | digital
N1DCS.10LBD20AC001RC | 20590 | 冷再供热减温减压调阀在远控 |  | digital
N1DCS.10LBD20AC001SPDH | 20591 | 冷再供热减压器设定、反馈偏差大 |  | digital
N1DCS.10LBD40AA001CD | 20592 | #1机热再供热电动门关指令 |  | digital
N1DCS.10LBD40AA001CP | 20593 | #1机热再供热电动门全关位 |  | digital
N1DCS.10LBD40AA001F | 20594 | #1机热再供热电动门综合故障 |  | digital
N1DCS.10LBD40AA001OD | 20595 | #1机热再供热电动门开指令 |  | digital
N1DCS.10LBD40AA001OP | 20596 | #1机热再供热电动门全开位 |  | digital
N1DCS.10LBD40AA001RC | 20597 | #1机热再供热电动门在远控 |  | digital
N1DCS.10LBD40AA002CD | 20598 | 热再供热逆止门后电动门关指令 |  | digital
N1DCS.10LBD40AA002CP | 20599 | 热再供热逆止门后电动门全关位 |  | digital
N1DCS.10LBD40AA002F | 20600 | 热再供热逆止门后电动门综合故障 |  | digital
N1DCS.10LBD40AA002OD | 20601 | 热再供热逆止门后电动门开指令 |  | digital
N1DCS.10LBD40AA002OP | 20602 | 热再供热逆止门后电动门全开位 |  | digital
N1DCS.10LBD40AA002RC | 20603 | 热再供热逆止门后电动门在远控 |  | digital
N1DCS.10LBD40AA402CP | 20604 | 热再供热母管气动疏水门全关位 |  | digital
N1DCS.10LBD40AA402F | 20605 | 热再供热母管气动疏水门无电源 |  | digital
N1DCS.10LBD40AA402OD/CD | 20606 | 热再供热母管气动疏水门开指令 |  | digital
N1DCS.10LBD40AA402OP | 20607 | 热再供热母管气动疏水门全开位 |  | digital
N1DCS.10LBD40AC001AUTO | 20608 | 热再供热减温减压器在自动模式 |  | digital
N1DCS.10LBD40AC001DVHI | 20609 | 热再供热减压阀指令反馈偏差大 |  | digital
N1DCS.10LBD40AC001F | 20610 | 热再供热减温减压调阀综合故障 |  | digital
N1DCS.10LBD40AC001RC | 20611 | 热再供热减温减压调阀在远控 |  | digital
N1DCS.10LBD40AC001SPDH | 20612 | 热再供热减压器设定、反馈偏差大 |  | digital
N1DCS.10LBD60AA001CD | 20613 | #1机供热母管电动门关闭指令 |  | digital
N1DCS.10LBD60AA001CP | 20614 | #1机供热母管电动门全关位置 |  | digital
N1DCS.10LBD60AA001F | 20615 | #1机供热母管电动门综合故障 |  | digital
N1DCS.10LBD60AA001OD | 20616 | #1机供热母管电动门打开指令 |  | digital
N1DCS.10LBD60AA001OP | 20617 | #1机供热母管电动门全开位置 |  | digital
N1DCS.10LBD60AA001RC | 20618 | #1机供热母管电动门在远控 |  | digital
N1DCS.10LBD80AA001CD | 20619 | 冷再抽汽至预留中压电动门关指令 |  | digital
N1DCS.10LBD80AA001CP | 20620 | 冷再抽汽至预留中压电动门全关位 |  | digital
N1DCS.10LBD80AA001F | 20621 | 冷再抽汽至预留中压电动门故障 |  | digital
N1DCS.10LBD80AA001OD | 20622 | 冷再抽汽至预留中压电动门开指令 |  | digital
N1DCS.10LBD80AA001OP | 20623 | 冷再抽汽至预留中压电动门全开位 |  | digital
N1DCS.10LBD80AA001RC | 20624 | 冷再抽汽至预留中压电动门在远控 |  | digital
N1DCS.10LBD80AA402CP | 20625 | 冷再抽汽至预留管道疏水门全关位 |  | digital
N1DCS.10LBD80AA402F | 20626 | 冷再抽汽至预留管道疏水门无电源 |  | digital
N1DCS.10LBD80AA402OD/CD | 20627 | 冷再抽汽至预留管疏水门关/开令 |  | digital
N1DCS.10LBD80AA402OP | 20628 | 冷再抽汽至预留管道疏水门全开位 |  | digital
N1DCS.10LBG11AA007CD | 20629 | 高排至辅汽母管供汽电动门关指令 |  | digital
N1DCS.10LBG11AA007CP | 20630 | 高排至辅汽母管供汽电动门全关位 |  | digital
N1DCS.10LBG11AA007F | 20631 | 高排至辅汽母管供汽电动门故障 |  | digital
N1DCS.10LBG11AA007OD | 20632 | 高排至辅汽母管供汽电动门开指令 |  | digital
N1DCS.10LBG11AA007OP | 20633 | 高排至辅汽母管供汽电动门全开位 |  | digital
N1DCS.10LBG11AA007RC | 20634 | 高排至辅汽母管供汽电动门在远控 |  | digital
N1DCS.10LBG11AC001AUTO | 20635 | 高排至辅汽母管供汽减压器在自动 |  | digital
N1DCS.10LBG11AC001DVHI | 20636 | 高排至辅汽减压器指令反馈偏差大 |  | digital
N1DCS.10LBG11AC001F | 20637 | 高排至辅汽母管供汽减压器故障 |  | digital
N1DCS.10LBG11AC001RC | 20638 | 高排至辅汽母管供汽减压器在远控 |  | digital
N1DCS.10LBG11AC001SPDH | 20639 | 高排至辅汽减压器设定反馈偏差大 |  | digital
N1DCS.10LBG21AA001CD | 20640 | 辅汽至#1机轴封供汽电动门关指令 |  | digital
N1DCS.10LBG21AA001CP | 20641 | 辅汽至#1机轴封供汽电动门全关位 |  | digital
N1DCS.10LBG21AA001F | 20642 | 辅汽至#1机轴封供汽电动门故障 |  | digital
N1DCS.10LBG21AA001OD | 20643 | 辅汽至#1机轴封供汽电动门开指令 |  | digital
N1DCS.10LBG21AA001OP | 20644 | 辅汽至#1机轴封供汽电动门全开位 |  | digital
N1DCS.10LBG21AA001RC | 20645 | 辅汽至#1机轴封供汽电动门在远控 |  | digital
N1DCS.10LBG22AA001CD | 20646 | 辅汽至#1机喷射器电动门关指令 |  | digital
N1DCS.10LBG22AA001CP | 20647 | 辅汽至#1机喷射器电动门全关位 |  | digital
N1DCS.10LBG22AA001F | 20648 | 辅汽至#1机喷射器电动门综合故障 |  | digital
N1DCS.10LBG22AA001OD | 20649 | 辅汽至#1机喷射器电动门打开指令 |  | digital
N1DCS.10LBG22AA001OP | 20650 | 辅汽至#1机喷射器电动门全开位 |  | digital
N1DCS.10LBG22AA001RC | 20651 | 辅汽至#1机喷射器电动门在远控 |  | digital
N1DCS.10LCE11AA001CD | 20652 | 凝结水至辅汽减温水电动门关指令 |  | digital
N1DCS.10LCE11AA001CP | 20653 | 凝结水至辅汽减温水电动门全关位 |  | digital
N1DCS.10LCE11AA001F | 20654 | 凝结水至辅汽减温水电动门故障 |  | digital
N1DCS.10LCE11AA001OD | 20655 | 凝结水至辅汽减温水电动门开指令 |  | digital
N1DCS.10LCE11AA001OP | 20656 | 凝结水至辅汽减温水电动门全开位 |  | digital
N1DCS.10LCE11AA001RC | 20657 | 凝结水至辅汽减温水电动门在远控 |  | digital
N1DCS.10LCE11AA101AUTO | 20658 | 凝结水至辅汽减温水调阀在自动 |  | digital
N1DCS.10LCE11AA101DVHI | 20659 | 辅汽减温水调阀指令反馈偏差大 |  | digital
N1DCS.10LCE11AA101F | 20660 | 凝结水至辅汽减温水调阀故障 |  | digital
N1DCS.10LCE11AA101RC | 20661 | 凝结水至辅汽减温水调阀在远控 |  | digital
N1DCS.10LCE11AA101SPDH | 20662 | 辅汽减温水调阀设定反馈偏差大 |  | digital
N1DCS.10LCE12AA001CD | 20663 | 凝结水至低旁减温水气动门关指令 |  | digital
N1DCS.10LCE12AA001F | 20664 | 凝结水至低旁减温水气动门无电源 |  | digital
N1DCS.10LCE12AA001OD | 20665 | 凝结水至低旁减温水气动门开指令 |  | digital
N1DCS.10LCE12AA001OP | 20666 | 凝结水至低旁减温水气动门全开位 |  | digital
N1DCS.10LCE12AA101AUTO | 20667 | 凝结水至低旁减温水调节阀在自动 |  | digital
N1DCS.10LCE12AA101CD | 20668 | 凝结水至低旁减温水调阀快关指令 |  | digital
N1DCS.10LCE12AA101F | 20669 | 凝结水至低旁减温水调节阀故障 |  | digital
N1DCS.10LCE12AA101OD | 20670 | 凝结水至低旁减温水调阀快开指令 |  | digital
N1DCS.10LCE13AA001CD | 20671 | 凝结水至热再减温水电动门关指令 |  | digital
N1DCS.10LCE13AA001CP | 20672 | 凝结水至热再减温水电动门全关位 |  | digital
N1DCS.10LCE13AA001F | 20673 | 凝结水至热再减温水电动门故障 |  | digital
N1DCS.10LCE13AA001OD | 20674 | 凝结水至热再减温水电动门开指令 |  | digital
N1DCS.10LCE13AA001OP | 20675 | 凝结水至热再减温水电动门全开位 |  | digital
N1DCS.10LCE13AA001RC | 20676 | 凝结水至热再减温水电动门在远控 |  | digital
N1DCS.10LCE13AA101AUTO | 20677 | 凝结水至热再减温水调阀在自动 |  | digital
N1DCS.10LCE13AA101DVHI | 20678 | 热再减温水调阀指令反馈偏差大 |  | digital
N1DCS.10LCE13AA101F | 20679 | 凝结水至热再减温水调阀故障 |  | digital
N1DCS.10LCE13AA101RC | 20680 | 凝结水至热再减温水调阀在远控 |  | digital
N1DCS.10LCE13AA101SPDH | 20681 | 热再减温水调阀设定反馈偏差大 |  | digital
N1DCS.10LCE15AA001CD | 20682 | 凝结水至中旁减温水气动门关指令 |  | digital
N1DCS.10LCE15AA001F | 20683 | 凝结水至中旁减温水气动门无电源 |  | digital
N1DCS.10LCE15AA001OD | 20684 | 凝结水至中旁减温水气动门开指令 |  | digital
N1DCS.10LCE15AA001OP | 20685 | 凝结水至中旁减温水气动门全开位 |  | digital
N1DCS.10LCE15AA101AUTO | 20686 | 凝结水至中旁减温水调节阀在自动 |  | digital
N1DCS.10LCE15AA101CD | 20687 | 凝结水至中旁减温水调阀快关指令 |  | digital
N1DCS.10LCE15AA101F | 20688 | 凝结水至中旁减温水调节阀故障 |  | digital
N1DCS.10LCE15AA101OD | 20689 | 凝结水至中旁减温水调阀快开指令 |  | digital
N1DCS.10LCE17AA001CD | 20690 | 凝结水至冷再减温水电动门关指令 |  | digital
N1DCS.10LCE17AA001CP | 20691 | 凝结水至冷再减温水电动门全关位 |  | digital
N1DCS.10LCE17AA001F | 20692 | 凝结水至冷再减温水电动门故障 |  | digital
N1DCS.10LCE17AA001OD | 20693 | 凝结水至冷再减温水电动门开指令 |  | digital
N1DCS.10LCE17AA001OP | 20694 | 凝结水至冷再减温水电动门全开位 |  | digital
N1DCS.10LCE17AA001RC | 20695 | 凝结水至冷再减温水电动门在远控 |  | digital
N1DCS.10LCE17AA101AUTO | 20696 | 凝结水至冷再减温水调阀在自动 |  | digital
N1DCS.10LCE17AA101DVHI | 20697 | 冷再减温水调阀指令反馈偏差大 |  | digital
N1DCS.10LCE17AA101F | 20698 | 凝结水至冷再减温水调阀故障 |  | digital
N1DCS.10LCE17AA101RC | 20699 | 凝结水至冷再减温水调阀在远控 |  | digital
N1DCS.10LCE17AA101SPDH | 20700 | 冷再减温水调阀设定反馈偏差大 |  | digital
N1DCS.10LCE18AA052CD | 20701 | 凝结水至轴封减温水电动门关指令 |  | digital
N1DCS.10LCE18AA052CP | 20702 | 凝结水至轴封减温水电动门全关位 |  | digital
N1DCS.10LCE18AA052F | 20703 | 凝结水至轴封减温水电动门无电源 |  | digital
N1DCS.10LCE18AA052OD | 20704 | 凝结水至轴封减温水电动门开指令 |  | digital
N1DCS.10LCE18AA052OP | 20705 | 凝结水至轴封减温水电动门全开位 |  | digital
N1DCS.10LCE18AA152AUTO | 20706 | 凝结水至轴封减温水调阀在自动 |  | digital
N1DCS.10LCE18AA152DVHI | 20707 | 轴封减温水调阀指令、反馈偏差大 |  | digital
N1DCS.10LCE18AA152SPDH | 20708 | 轴封减温水调阀设定、反馈偏差大 |  | digital
N1DCS.10LCE19AA101AUTO | 20709 | 凝汽器水幕喷水气动阀在自动 |  | digital
N1DCS.10LCE19AA101CP | 20710 | 凝汽器水幕喷水气动阀全关位 |  | digital
N1DCS.10LCE19AA101DVHI | 20711 | 凝汽器水幕喷水阀指令反馈偏差大 |  | digital
N1DCS.10LCE19AA101OD | 20712 | 凝汽器水幕喷水气动阀关/开指令 |  | digital
N1DCS.10LCE19AA101OP | 20713 | 凝汽器水幕喷水气动阀全开位 |  | digital
N1DCS.10LCE19AA101PF | 20714 | 凝汽器水幕喷水气动阀无电源 |  | digital
N1DCS.10LCE19AA101SPDH | 20715 | 凝汽器水幕喷水阀设定反馈偏差大 |  | digital
N1DCS.10LCE20AA101AUTO | 20716 | 疏水扩容器减温水调阀在自动 |  | digital
N1DCS.10LCE20AA101DVHI | 20717 | 疏扩减温水调阀指令反馈偏差大 |  | digital
N1DCS.10LCE20AA101SPDH | 20718 | 疏扩减温水调阀设定反馈偏差大 |  | digital
N1DCS.10LCM40AA403CD | 20719 | #1疏水泵出口真空电动门关闭指令 |  | digital
N1DCS.10LCM40AA403CP | 20720 | #1疏水泵出口真空电动门全关位置 |  | digital
N1DCS.10LCM40AA403F | 20721 | #1疏水泵出口真空电动门故障 |  | digital
N1DCS.10LCM40AA403OD | 20722 | #1疏水泵出口真空电动门打开指令 |  | digital
N1DCS.10LCM40AA403OP | 20723 | #1疏水泵出口真空电动门全开位置 |  | digital
N1DCS.10LCM40AA403RC | 20724 | #1疏水泵出口真空电动门在远控 |  | digital
N1DCS.10LCM40AA406CD | 20725 | #2疏水泵出口真空电动门关闭指令 |  | digital
N1DCS.10LCM40AA406CP | 20726 | #2疏水泵出口真空电动门全关位置 |  | digital
N1DCS.10LCM40AA406F | 20727 | #2疏水泵出口真空电动门故障 |  | digital
N1DCS.10LCM40AA406OD | 20728 | #2疏水泵出口真空电动门打开指令 |  | digital
N1DCS.10LCM40AA406OP | 20729 | #2疏水泵出口真空电动门全开位置 |  | digital
N1DCS.10LCM40AA406RC | 20730 | #2疏水泵出口真空电动门在远控 |  | digital
N1DCS.10LCM40AA407CD | 20731 | 疏扩放水至凝泵坑电动门关指令 |  | digital
N1DCS.10LCM40AA407CP | 20732 | 疏扩放水至凝泵坑电动门全关位 |  | digital
N1DCS.10LCM40AA407F | 20733 | 疏扩放水至凝泵坑电动门故障 |  | digital
N1DCS.10LCM40AA407OD | 20734 | 疏扩放水至凝泵坑电动门开指令 |  | digital
N1DCS.10LCM40AA407OP | 20735 | 疏扩放水至凝泵坑电动门全开位 |  | digital
N1DCS.10LCM40AA407RC | 20736 | 疏扩放水至凝泵坑电动门在远控 |  | digital
N1DCS.10LCM40AP001PF | 20737 | #1疏水泵综合故障 |  | digital
N1DCS.10LCM40AP001RC | 20738 | #1疏水泵已预选且远方控制 |  | digital
N1DCS.10LCM40AP001RD | 20739 | #1/#2疏水泵远方启动指令 |  | digital
N1DCS.10LCM40AP001RP | 20740 | #1疏水泵在运行 |  | digital
N1DCS.10LCM40AP001TD | 20741 | #1/#2疏水泵远方停止指令 |  | digital
N1DCS.10LCM40AP001TP | 20742 | #1疏水泵已停止 |  | digital
N1DCS.10LCM40AP002PF | 20743 | #2疏水泵综合故障 |  | digital
N1DCS.10LCM40AP002RC | 20744 | #2疏水泵已预选且远方控制 |  | digital
N1DCS.10LCM40AP002RD | 20745 | #2疏水泵启动指令 |  | digital
N1DCS.10LCM40AP002RP | 20746 | #2疏水泵在运行 |  | digital
N1DCS.10LCM40AP002TD | 20747 | #2疏水泵停止指令 |  | digital
N1DCS.10LCM40AP002TP | 20748 | #2疏水泵已停止 |  | digital
N1DCS.10MAL22AA051CP | 20749 | 高压缸气动疏水门1全关位置 |  | digital
N1DCS.10MAL22AA051F | 20750 | 高压缸气动疏水门1电源消失 |  | digital
N1DCS.10MAL22AA051OD/CD | 20751 | 高压缸气动疏水门1关闭/打开指令 |  | digital
N1DCS.10MAL22AA051OP | 20752 | 高压缸气动疏水门1全开位置 |  | digital
N1DCS.10MAL22AA053CP | 20753 | 高压缸气动疏水门2全关位置 |  | digital
N1DCS.10MAL22AA053F | 20754 | 高压缸气动疏水门2电源消失 |  | digital
N1DCS.10MAL22AA053OD/CD | 20755 | 高压缸气动疏水门2打开/关闭指令 |  | digital
N1DCS.10MAL22AA053OP | 20756 | 高压缸气动疏水门2全开位置 |  | digital
N1DCS.10MAL22AA054CP | 20757 | 高压缸气动疏水门3全关位置 |  | digital
N1DCS.10MAL22AA054F | 20758 | 高压缸气动疏水门3电源消失 |  | digital
N1DCS.10MAL22AA054OD/CD | 20759 | 高压缸气动疏水门3打开/关闭指令 |  | digital
N1DCS.10MAL22AA054OP | 20760 | 高压缸气动疏水门3全开位置 |  | digital
N1DCS.10MAL35AA051CP | 20761 | 中压缸气动疏水门1全关位置 |  | digital
N1DCS.10MAL35AA051F | 20762 | 中压缸气动疏水门1电源消失 |  | digital
N1DCS.10MAL35AA051OD/CD | 20763 | 中压缸气动疏水门1关闭/打开指令 |  | digital
N1DCS.10MAL35AA051OP | 20764 | 中压缸气动疏水门1全开位置 |  | digital
N1DCS.10MAL36AA051CP | 20765 | 中压缸气动疏水门2全关位置 |  | digital
N1DCS.10MAL36AA051F | 20766 | 中压缸气动疏水门2电源消失 |  | digital
N1DCS.10MAL36AA051OD/CD | 20767 | 中压缸气动疏水门2关闭/打开指令 |  | digital
N1DCS.10MAL36AA051OP | 20768 | 中压缸气动疏水门2全开位置 |  | digital
N1DCS.10MAL50AA051CP | 20769 | 低压缸气动疏水门全关位置 |  | digital
N1DCS.10MAL50AA051F | 20770 | 低压缸气动疏水门电源消失 |  | digital
N1DCS.10MAL50AA051OD/CD | 20771 | 低压缸气动疏水门关闭/打开指令 |  | digital
N1DCS.10MAL50AA051OP | 20772 | 低压缸气动疏水门全开位置 |  | digital
N1DCS.10MAW10AA151AUTO | 20773 | 辅汽至高、中压轴封调阀在自动 |  | digital
N1DCS.10MAW10AA151DVHI | 20774 | 高、中压轴封调阀指令反馈偏差大 |  | digital
N1DCS.10MAW10AA151SPDH | 20775 | 高、中压轴封调阀设定反馈偏差大 |  | digital
N1DCS.10MAW13AA151AUTO | 20776 | 辅汽至低压轴封调阀在自动 |  | digital
N1DCS.10MAW13AA151DVHI | 20777 | 低压轴封调阀指令、反馈偏差大 |  | digital
N1DCS.10MAW13AA151SPDH | 20778 | 低压轴封调阀设定、反馈偏差大 |  | digital
N1DCS.10MAW50AA151AUTO | 20779 | 轴封供汽溢流阀在自动 |  | digital
N1DCS.10MAW50AA151DVHI | 20780 | 轴封供汽溢流阀指令、反馈偏差大 |  | digital
N1DCS.10MAW50AA151SPDH | 20781 | 轴封供汽溢流阀设定、反馈偏差大 |  | digital
N1DCS.10MAW65AA051CP | 20782 | 高压缸轴封漏汽至中压缸门全关位 |  | digital
N1DCS.10MAW65AA051F | 20783 | 高压缸轴封漏汽至中压缸门无电源 |  | digital
N1DCS.10MAW65AA051OD/CD | 20784 | 高压缸轴封至中压缸门开/关指令 |  | digital
N1DCS.10MAW65AA051OP | 20785 | 高压缸轴封漏汽至中压缸门全开位 |  | digital
N1DCS.10MAW65AA052CP | 20786 | 高压缸轴封漏汽至凝汽器门全关位 |  | digital
N1DCS.10MAW65AA052F | 20787 | 高压缸轴封漏汽至凝汽器门无电源 |  | digital
N1DCS.10MAW65AA052OD/CD | 20788 | 高压缸轴封至凝汽器门开/关指令 |  | digital
N1DCS.10MAW65AA052OP | 20789 | 高压缸轴封漏汽至凝汽器门全开位 |  | digital
N1DCS.10MAW80AN001PF | 20790 | #1轴封风机综合故障 |  | digital
N1DCS.10MAW80AN001PS | 20791 | #1轴封风机保护动作 |  | digital
N1DCS.10MAW80AN001RC | 20792 | #1轴封风机远方控制 |  | digital
N1DCS.10MAW80AN001RD | 20793 | #1轴封风机启动指令 |  | digital
N1DCS.10MAW80AN001RP | 20794 | #1轴封风机在运行 |  | digital
N1DCS.10MAW80AN001TD | 20795 | #1轴封风机停止指令 |  | digital
N1DCS.10MAW80AN001TP | 20796 | #1轴封风机已停止 |  | digital
N1DCS.10MAW80AN002PF | 20797 | #2轴封风机综合故障 |  | digital
N1DCS.10MAW80AN002PS | 20798 | #2轴封风机保护动作 |  | digital
N1DCS.10MAW80AN002RC | 20799 | #2轴封风机远方控制 |  | digital
N1DCS.10MAW80AN002RD | 20800 | #2轴封风机启动指令 |  | digital
N1DCS.10MAW80AN002RP | 20801 | #2轴封风机在运行 |  | digital
N1DCS.10MAW80AN002TD | 20802 | #2轴封风机停止指令 |  | digital
N1DCS.10MAW80AN002TP | 20803 | #2轴封风机已停止 |  | digital
N1DCS.10MAW80CL011H | 20804 | 轴封冷却器蒸汽入口液位高 |  | digital
N1DCS.AUXSTMSYS_SEQSTFINISH | 20805 | 辅汽系统启顺控已成功完成 |  | digital
N1DCS.GLDSTMSYS_SEQSPOK | 20806 | 轴封系统停顺控已成功完成 |  | digital
N1DCS.GLDSTMSYS_SEQSTFINISH | 20807 | 轴封系统启顺控已成功完成 |  | digital
N1DCS.HGLDHDRPRS_MRE | 20808 | #1机高中压轴封供汽母管压力坏点 |  | digital
N1DCS.HGLDHDRTEM_MRE | 20809 | #1机高中压轴封供汽母管温度坏点 |  | digital
N1DCS.IPBYSPYCVCLS | 20810 | 中旁减温水调阀快关指令 |  | digital
N1DCS.IPBYSPYCVOP | 20811 | 中旁减温水调阀快开指令 |  | digital
N1DCS.J0LBG10CPX2_MRE | 20812 | 辅汽母管压力坏点 |  | digital
N1DCS.J0LBG10CTX2_MRE | 20813 | 辅汽母管温度坏点 |  | digital
N1DCS.LOWGLDSPLPRS_MRE | 20814 | #1机低压轴封供汽母管压力坏点 |  | digital
N1DCS.LOWGLDSPLTEM_MRE | 20815 | #1机低压轴封供汽母管温度坏点 |  | digital
N1DCS.LPBYSPYCVCLS | 20816 | 低旁减温水调阀快关指令 |  | digital
N1DCS.LPBYSPYCVOP | 20817 | 低旁减温水调阀快开指令 |  | digital
N1DCS.ONE2 | 20818 | 开关量1 |  | digital
N1DCS.ZERO2 | 20819 | 开关量0 |  | digital
N1DCS.DCSCOLDMODE1 | 20820 | 汽机冷态启动 |  | digital
N1DCS.DCSEXHOTMODE1 | 20821 | 汽机极热态态启动 |  | digital
N1DCS.DCSHOTMODE1 | 20822 | 汽机热态启动 |  | digital
N1DCS.DCSWARMMODE1 | 20823 | 汽机温态启动 |  | digital
N1DCS.HTQR | 20824 | 手动确认轴封电加热器已投入 |  | digital
N1DCS.QDGLZFQACKOK | 20825 | 手动确认启动锅炉供辅汽门已全开 |  | digital
N1DCS.QUERENNOCON | 20826 | 手动确认轴封系统不需要暖管 |  | digital
N1DCS.QUERENYESCON | 20827 | 手动确认轴封系统需要暖管 |  | digital
N1DCS.10CNSRPRCTACT1 | 20828 | 凝汽器保护动作通道1 |  | digital
N1DCS.10CNSRPRCTACT2 | 20829 | 凝汽器保护动作通道2 |  | digital
N1DCS.10CNSRPRCTACT3 | 20830 | 凝汽器保护动作通道3 |  | digital
N1DCS.10LBG21AA002CD | 20831 | 轴封电加热器进口电动门关闭指令 |  | digital
N1DCS.10LBG21AA002CP | 20832 | 轴封电加热器进口电动门全关位 |  | digital
N1DCS.10LBG21AA002OD | 20833 | 轴封电加热器进口电动门打开指令 |  | digital
N1DCS.10LBG21AA002OP | 20834 | 轴封电加热器进口电动门全开位 |  | digital
N1DCS.10LBG21AA002PF | 20835 | 轴封电加热器进口电动门故障 |  | digital
N1DCS.10LBG21AA002RC | 20836 | 轴封电加热器进口电动门在远控 |  | digital
N1DCS.10LBG21AA003CD | 20837 | 轴封电加热器出口电动门关闭指令 |  | digital
N1DCS.10LBG21AA003CP | 20838 | 轴封电加热器出口电动门全关位 |  | digital
N1DCS.10LBG21AA003OD | 20839 | 轴封电加热器出口电动门打开指令 |  | digital
N1DCS.10LBG21AA003OP | 20840 | 轴封电加热器出口电动门全开位 |  | digital
N1DCS.10LBG21AA003PF | 20841 | 轴封电加热器出口电动门故障 |  | digital
N1DCS.10LBG21AA003RC | 20842 | 轴封电加热器出口电动门在远控 |  | digital
N1DCS.10LBG21AC001PF | 20843 | 轴封电加热器综合故障 |  | digital
N1DCS.10LBG21AC001RC | 20844 | 轴封电加热器在远控 |  | digital
N1DCS.10LBG21AC001RCT | 20845 | 轴封电加热器允许接受温度设定 |  | digital
N1DCS.10LBG21AC001RD | 20846 | 轴封电加热器启动指令 |  | digital
N1DCS.10LBG21AC001RP | 20847 | 轴封电加热器在运行 |  | digital
N1DCS.10LBG21AC001TD | 20848 | 轴封电加热器停止指令 |  | digital
N1DCS.10LBG21AC001TP | 20849 | 轴封电加热器已停止 |  | digital
N1DCS.10LCA11AA001CD | 20850 | #1凝结水泵进口电动门关闭指令 |  | digital
N1DCS.10LCA11AA001CP | 20851 | #1凝结水泵进口电动门全关位置 |  | digital
N1DCS.10LCA11AA001F | 20852 | #1凝结水泵进口电动门综合故障 |  | digital
N1DCS.10LCA11AA001OD | 20853 | #1凝结水泵进口电动门打开指令 |  | digital
N1DCS.10LCA11AA001OP | 20854 | #1凝结水泵进口电动门全开位置 |  | digital
N1DCS.10LCA11AA001RC | 20855 | #1凝结水泵进口电动门在远控 |  | digital
N1DCS.10LCA11AA003CD | 20856 | #1凝结水泵出口电动门关闭指令 |  | digital
N1DCS.10LCA11AA003CP | 20857 | #1凝结水泵出口电动门全关位置 |  | digital
N1DCS.10LCA11AA003F | 20858 | #1凝结水泵出口电动门综合故障 |  | digital
N1DCS.10LCA11AA003OD | 20859 | #1凝结水泵出口电动门打开指令 |  | digital
N1DCS.10LCA11AA003OP | 20860 | #1凝结水泵出口电动门全开位置 |  | digital
N1DCS.10LCA11AA003RC | 20861 | #1凝结水泵出口电动门在远控 |  | digital
N1DCS.10LCA30AA101AUTO | 20862 | 凝结水再循环气动调节阀在自动 |  | digital
N1DCS.10LCA30AA101DVHI | 20863 | 凝结水再循环调阀指令反馈偏差大 |  | digital
N1DCS.10LCA30AA101SPDH | 20864 | 凝结水再循环调阀设定反馈偏差大 |  | digital
N1DCS.10LCA40AA002CD | 20865 | 凝结水无压放水电动门关闭指令 |  | digital
N1DCS.10LCA40AA002CP | 20866 | 凝结水无压放水电动门全关位置 |  | digital
N1DCS.10LCA40AA002F | 20867 | 凝结水无压放水电动门综合故障 |  | digital
N1DCS.10LCA40AA002OD | 20868 | 凝结水无压放水电动门打开指令 |  | digital
N1DCS.10LCA40AA002OP | 20869 | 凝结水无压放水电动门全开位置 |  | digital
N1DCS.10LCA40AA002RC | 20870 | 凝结水无压放水电动门在远控 |  | digital
N1DCS.10LCB11AP001CPDO | 20871 | #1凝结水泵已停止(至DROP9) |  | digital
N1DCS.10LCB11AP001PF | 20872 | #1凝结水泵综合故障 |  | digital
N1DCS.10LCB11AP001PS | 20873 | #1凝结水泵电气保护动作 |  | digital
N1DCS.10LCB11AP001RC | 20874 | #1凝结水泵远方控制 |  | digital
N1DCS.10LCB11AP001RD | 20875 | #1凝结水泵启动指令 |  | digital
N1DCS.10LCB11AP001RP | 20876 | #1凝结水泵在运行 |  | digital
N1DCS.10LCB11AP001SW | 20877 | #1凝结水泵试验位置 |  | digital
N1DCS.10LCB11AP001TD | 20878 | #1凝结水泵停止指令 |  | digital
N1DCS.10LCB11AP001TP | 20879 | #1凝结水泵已停止 |  | digital
N1DCS.10LCB11AP001YW | 20880 | #1凝结水泵工作位置 |  | digital
N1DCS.10LCB11GH001AUTO | 20881 | #1凝结水泵永磁控制在自动模式 |  | digital
N1DCS.10LCB11GH001RD1 | 20882 | #1凝泵#1永磁调速水泵启动指令 |  | digital
N1DCS.10LCB11GH001RD2 | 20883 | #1凝泵#2永磁调速水泵启动指令 |  | digital
N1DCS.10LCB11GH001SDVHI | 20884 | #1凝泵永磁控制指令反馈偏差大 |  | digital
N1DCS.10LCB11GH001SPDH | 20885 | #1凝泵永磁控制设定反馈偏差大 |  | digital
N1DCS.10LCB11GH001TD1 | 20886 | #1凝泵#1永磁调速水泵停止指令 |  | digital
N1DCS.10LCB11GH001TD2 | 20887 | #1凝泵#2永磁调速水泵停止指令 |  | digital
N1DCS.10LCE01AA001CD | 20888 | 凝结水杂用水母管电动门关闭指令 |  | digital
N1DCS.10LCE01AA001CP | 20889 | 凝结水杂用水母管电动门全关位 |  | digital
N1DCS.10LCE01AA001F | 20890 | 凝结水杂用水母管电门综合故障 |  | digital
N1DCS.10LCE01AA001OD | 20891 | 凝结水杂用水母管电动门开指令 |  | digital
N1DCS.10LCE01AA001OP | 20892 | 凝结水杂用水母管电动门全开位 |  | digital
N1DCS.10LCE01AA001RC | 20893 | 凝结水杂用水母管电动门在远控 |  | digital
N1DCS.10LCE16AA101AUTO | 20894 | 闭式水箱补水电动调节阀在自动 |  | digital
N1DCS.10LCE16AA101F | 20895 | 闭式水箱补水电动调节阀故障 |  | digital
N1DCS.10LCE16AA101RC | 20896 | 闭式水箱补水电动调节阀在远控 |  | digital
N1DCS.10LCR10AA001CD | 20897 | #1机组除盐水补水电动门关指令 |  | digital
N1DCS.10LCR10AA001CP | 20898 | #1机组除盐水补水电动门全关位 |  | digital
N1DCS.10LCR10AA001F | 20899 | #1机组除盐水补水电门综合故障 |  | digital
N1DCS.10LCR10AA001OD | 20900 | #1机组除盐水补水电动门开指令 |  | digital
N1DCS.10LCR10AA001OP | 20901 | #1机组除盐水补水电动门全开位 |  | digital
N1DCS.10LCR10AA001RC | 20902 | #1机组除盐水补水电动门在远控 |  | digital
N1DCS.10LCR10AA101AUTO | 20903 | 凝汽器正常补水电动调节阀在自动 |  | digital
N1DCS.10LCR10AA101DVHI | 20904 | 凝器正常补水调阀指令反馈偏差大 |  | digital
N1DCS.10LCR10AA101SPDH | 20905 | 凝器正常补水调阀设定反馈偏差大 |  | digital
N1DCS.10LCR10AA102AUTO | 20906 | 凝汽器启动补水电动调节阀在自动 |  | digital
N1DCS.10LCR10AA102DVHI | 20907 | 凝器启动补水调阀指令反馈偏差大 |  | digital
N1DCS.10LCR10AA102SPDH | 20908 | 凝器启动补水调阀设定反馈偏差大 |  | digital
N1DCS.10LCR14AA001CD | 20909 | 闭式水箱启动注水电动门关指令 |  | digital
N1DCS.10LCR14AA001CP | 20910 | 闭式水箱启动注水电动门全关位 |  | digital
N1DCS.10LCR14AA001F | 20911 | 闭式水箱启动注水电动门综合故障 |  | digital
N1DCS.10LCR14AA001OD | 20912 | 闭式水箱启动注水电动门开指令 |  | digital
N1DCS.10LCR14AA001OP | 20913 | 闭式水箱启动注水电动门全开位 |  | digital
N1DCS.10LCR14AA001RC | 20914 | 闭式水箱启动注水电动门在远控 |  | digital
N1DCS.10LDK10AA003CD | 20915 | 除铁过滤器升压气动门关指令 |  | digital
N1DCS.10LDK10AA003CP | 20916 | 除铁过滤器升压气动门全关位 |  | digital
N1DCS.10LDK10AA003OD | 20917 | 除铁过滤器升压气动门开指令 |  | digital
N1DCS.10LDK10AA003OP | 20918 | 除铁过滤器升压气动门全开位 |  | digital
N1DCS.10LDK10AA004CD | 20919 | 除铁过滤器出水电动门关指令 |  | digital
N1DCS.10LDK10AA004CP | 20920 | 除铁过滤器出水电动门全关位 |  | digital
N1DCS.10LDK10AA004F | 20921 | 除铁过滤器出水电动门综合故障 |  | digital
N1DCS.10LDK10AA004OD | 20922 | 除铁过滤器出水电动门开指令 |  | digital
N1DCS.10LDK10AA004OP | 20923 | 除铁过滤器出水电动门全开位 |  | digital
N1DCS.10LDK10AA004RC | 20924 | 除铁过滤器出水电动门在远控 |  | digital
N1DCS.10MAG10CL001H | 20925 | 凝汽器热井液位高高 |  | digital
N1DCS.10MAG10CL002L | 20926 | 凝汽器热井液位低低 |  | digital
N1DCS.10PAB11AA001CD | 20927 | 凝汽器循环水进水#1电动门关指令 |  | digital
N1DCS.10PAB11AA001CP | 20928 | 凝汽器循环水进水#1电动门全关位 |  | digital
N1DCS.10PAB11AA001F | 20929 | 凝汽器循环水进水#1电动门故障 |  | digital
N1DCS.10PAB11AA001OD | 20930 | 凝汽器循环水进水#1电动门开指令 |  | digital
N1DCS.10PAB11AA001OP | 20931 | 凝汽器循环水进水#1电动门全开位 |  | digital
N1DCS.10PAB11AA001RC | 20932 | 凝汽器循环水进水#1电动门在远控 |  | digital
N1DCS.10PAB21AA001CD | 20933 | 凝汽器循环水#1出水电动门关指令 |  | digital
N1DCS.10PAB21AA001CP | 20934 | 凝汽器循环水#1出水电动门全关位 |  | digital
N1DCS.10PAB21AA001F | 20935 | 凝汽器循环水#1出水电动门故障 |  | digital
N1DCS.10PAB21AA001OD | 20936 | 凝汽器循环水#1出水电动门开指令 |  | digital
N1DCS.10PAB21AA001OP | 20937 | 凝汽器循环水#1出水电动门全开位 |  | digital
N1DCS.10PAB21AA001RC | 20938 | 凝汽器循环水#1出水电动门在远控 |  | digital
N1DCS.10PAH10GH001RC | 20939 | 胶球清洗装置在远控 |  | digital
N1DCS.10PAH11AA002CD | 20940 | #1胶球泵出口电动门关闭指令 |  | digital
N1DCS.10PAH11AA002CP | 20941 | #1胶球泵出口电动门全关位置 |  | digital
N1DCS.10PAH11AA002F | 20942 | #1胶球泵出口电动门综合故障 |  | digital
N1DCS.10PAH11AA002OD | 20943 | #1胶球泵出口电动门打开指令 |  | digital
N1DCS.10PAH11AA002OP | 20944 | #1胶球泵出口电动门全开位置 |  | digital
N1DCS.10PAH11AP001PF | 20945 | #1胶球泵综合故障 |  | digital
N1DCS.10PAH11AP001RD | 20946 | #1胶球泵启动指令 |  | digital
N1DCS.10PAH11AP001RP | 20947 | #1胶球泵在运行 |  | digital
N1DCS.10PAH11AP001TD | 20948 | #1胶球泵停止指令 |  | digital
N1DCS.10PAH11AP001TP | 20949 | #1胶球泵已停止 |  | digital
N1DCS.10PAH11AT001F | 20950 | #1收球网综合故障 |  | digital
N1DCS.10PAH11AT001FX | 20951 | #1收球网反洗指令 |  | digital
N1DCS.10PAH11AT001FXP | 20952 | #1收球网在反洗位置 |  | digital
N1DCS.10PAH11AT001SQ | 20953 | #1收球网收球指令 |  | digital
N1DCS.10PAH11AT001SQP | 20954 | #1收球网在收球位置 |  | digital
N1DCS.10PAH11BB001CD | 20955 | #1装球室关闭指令 |  | digital
N1DCS.10PAH11BB001CP | 20956 | #1装球室全关位置 |  | digital
N1DCS.10PAH11BB001F | 20957 | #1装球室综合故障 |  | digital
N1DCS.10PAH11BB001OD | 20958 | #1装球室打开指令 |  | digital
N1DCS.10PAH11BB001OP | 20959 | #1装球室全开位置 |  | digital
N1DCS.10PCB10AA001CD | 20960 | 开式水电动过滤器进水门关指令 |  | digital
N1DCS.10PCB10AA001CP | 20961 | 开式水电动过滤器进水门全关位置 |  | digital
N1DCS.10PCB10AA001F | 20962 | 开式水电动过滤器进水门综合故障 |  | digital
N1DCS.10PCB10AA001OD | 20963 | 开式水电动过滤器进水门打开指令 |  | digital
N1DCS.10PCB10AA001OP | 20964 | 开式水电动过滤器进水门全开位置 |  | digital
N1DCS.10PCB10AA001RC | 20965 | 开式水电动过滤器进水门在远控 |  | digital
N1DCS.10PCB10AA002CD | 20966 | 开式水电动过滤器出水门关闭指令 |  | digital
N1DCS.10PCB10AA002CP | 20967 | 开式水电动过滤器出水门全关位置 |  | digital
N1DCS.10PCB10AA002F | 20968 | 开式水电动过滤器出水门综合故障 |  | digital
N1DCS.10PCB10AA002OD | 20969 | 开式水电动过滤器出水门打开指令 |  | digital
N1DCS.10PCB10AA002OP | 20970 | 开式水电动过滤器出水门全开位置 |  | digital
N1DCS.10PCB10AA002RC | 20971 | 开式水电动过滤器出水门在远控 |  | digital
N1DCS.10PCB10AA003CD | 20972 | 开式水电动过滤器旁路门关闭指令 |  | digital
N1DCS.10PCB10AA003CP | 20973 | 开式水电动过滤器旁路门全关位置 |  | digital
N1DCS.10PCB10AA003F | 20974 | 开式水电动过滤器旁路门综合故障 |  | digital
N1DCS.10PCB10AA003OD | 20975 | 开式水电动过滤器旁路门打开指令 |  | digital
N1DCS.10PCB10AA003OP | 20976 | 开式水电动过滤器旁路门全开位置 |  | digital
N1DCS.10PCB10AA003RC | 20977 | 开式水电动过滤器旁路门在远控 |  | digital
N1DCS.10PCB10GH501CD | 20978 | 开式水电动过滤器停止反冲洗指令 |  | digital
N1DCS.10PCB10GH501CP | 20979 | 开式水电动过滤器排污门门全关位 |  | digital
N1DCS.10PCB10GH501F | 20980 | 开式水电动过滤器滤水器电机故障 |  | digital
N1DCS.10PCB10GH501OD | 20981 | 开式水电动过滤器启动反冲洗指令 |  | digital
N1DCS.10PCB10GH501OP | 20982 | 开式水电动过滤器排污门门全开位 |  | digital
N1DCS.10PCB10GH501PF | 20983 | 开式水电动过滤器电源消失 |  | digital
N1DCS.10PCB10GH501RC | 20984 | 开式水电动过滤器在远控 |  | digital
N1DCS.10PCB10GH501W | 20985 | 开式水电动过滤器反冲洗进行中 |  | digital
N1DCS.10PCB11AA001CD | 20986 | #1开式水泵进口电动门关闭指令 |  | digital
N1DCS.10PCB11AA001CP | 20987 | #1开式水泵进口电动门全关位 |  | digital
N1DCS.10PCB11AA001F | 20988 | #1开式水泵进口电动门综合故障 |  | digital
N1DCS.10PCB11AA001OD | 20989 | #1开式水泵进口电动门打开指令 |  | digital
N1DCS.10PCB11AA001OP | 20990 | #1开式水泵进口电动门全开位 |  | digital
N1DCS.10PCB11AA001RC | 20991 | #1开式水泵进口电动门在远控 |  | digital
N1DCS.10PCB11AA002CD | 20992 | #1开式水泵出口电动门关闭指令 |  | digital
N1DCS.10PCB11AA002CP | 20993 | #1开式水泵出口电动门全关位 |  | digital
N1DCS.10PCB11AA002F | 20994 | #1开式水泵出口电动门综合故障 |  | digital
N1DCS.10PCB11AA002OD | 20995 | #1开式水泵出口电动门打开指令 |  | digital
N1DCS.10PCB11AA002OP | 20996 | #1开式水泵出口电动门全开位 |  | digital
N1DCS.10PCB11AA002RC | 20997 | #1开式水泵出口电动门在远控 |  | digital
N1DCS.10PCB11AP001PF | 20998 | #1开式水泵综合故障 |  | digital
N1DCS.10PCB11AP001RC | 20999 | #1开式水泵远方控制 |  | digital
N1DCS.10PCB11AP001RD | 21000 | #1开式水泵启动指令 |  | digital
N1DCS.10PCB11AP001RP | 21001 | #1开式水泵在运行 |  | digital
N1DCS.10PCB11AP001TD | 21002 | #1开式水泵停止指令 |  | digital
N1DCS.10PCB11AP001TP | 21003 | #1开式水泵已停止 |  | digital
N1DCS.10PCB13AA011CD | 21004 | #1真空泵冷却器开式进水门关指令 |  | digital
N1DCS.10PCB13AA011CP | 21005 | #1真空泵冷却器开式进水门全关位 |  | digital
N1DCS.10PCB13AA011F | 21006 | #1真空泵冷却器开式进水水门故障 |  | digital
N1DCS.10PCB13AA011OD | 21007 | #1真空泵冷却器开式进水门开指令 |  | digital
N1DCS.10PCB13AA011OP | 21008 | #1真空泵冷却器开式进水门全开位 |  | digital
N1DCS.10PCB13AA011RC | 21009 | #1真空泵冷却器开式进水门在远控 |  | digital
N1DCS.10PCB21AA001CD | 21010 | #1热交换器开式进水电动门关指令 |  | digital
N1DCS.10PCB21AA001CP | 21011 | #1热交换器开式进水电动门全关位 |  | digital
N1DCS.10PCB21AA001F | 21012 | #1热交换器开式进水电动门故障 |  | digital
N1DCS.10PCB21AA001OD | 21013 | #1热交换器开式进水电动门开指令 |  | digital
N1DCS.10PCB21AA001OP | 21014 | #1热交换器开式进水电动门全开位 |  | digital
N1DCS.10PCB21AA001RC | 21015 | #1热交换器开式进水电动门在远控 |  | digital
N1DCS.10PCB23AA011CD | 21016 | #1真空泵冷却器开式出水门关指令 |  | digital
N1DCS.10PCB23AA011CP | 21017 | #1真空泵冷却器开式出水门全关位 |  | digital
N1DCS.10PCB23AA011F | 21018 | #1真空泵冷却器开式出水门故障 |  | digital
N1DCS.10PCB23AA011OD | 21019 | #1真空泵冷却器开式出水门开指令 |  | digital
N1DCS.10PCB23AA011OP | 21020 | #1真空泵冷却器开式出水门全开位 |  | digital
N1DCS.10PCB23AA011RC | 21021 | #1真空泵冷却器开式出水门在远控 |  | digital
N1DCS.10PCB31AA001CD | 21022 | #1热交换器开式出水电动门关指令 |  | digital
N1DCS.10PCB31AA001CP | 21023 | #1热交换器开式出水电动门全关位 |  | digital
N1DCS.10PCB31AA001F | 21024 | #1热交换器开式出水电动门故障 |  | digital
N1DCS.10PCB31AA001OD | 21025 | #1热交换器开式出水电动门开指令 |  | digital
N1DCS.10PCB31AA001OP | 21026 | #1热交换器开式出水电动门全开位 |  | digital
N1DCS.10PCB31AA001RC | 21027 | #1热交换器开式出水电动门在远控 |  | digital
N1DCS.10PGA10CL101SPDH | 21028 | 闭式水箱补水调阀设定反馈偏差大 |  | digital
N1DCS.10PGA11AA001CD | 21029 | #1闭式水泵进口电动门关闭指令 |  | digital
N1DCS.10PGA11AA001CP | 21030 | #1闭式水泵进口电动门全关位置 |  | digital
N1DCS.10PGA11AA001F | 21031 | #1闭式水泵进口电动门综合故障 |  | digital
N1DCS.10PGA11AA001OD | 21032 | #1闭式水泵进口电动门打开指令 |  | digital
N1DCS.10PGA11AA001OP | 21033 | #1闭式水泵进口电动门全开位置 |  | digital
N1DCS.10PGA11AA001RC | 21034 | #1闭式水泵进口电动门在远控 |  | digital
N1DCS.10PGA11AA003CD | 21035 | #1闭式水泵出口电动门关闭指令 |  | digital
N1DCS.10PGA11AA003CP | 21036 | #1闭式水泵出口电动门全关位置 |  | digital
N1DCS.10PGA11AA003F | 21037 | #1闭式水泵出口电动门综合故障 |  | digital
N1DCS.10PGA11AA003OD | 21038 | #1闭式水泵出口电动门打开指令 |  | digital
N1DCS.10PGA11AA003OP | 21039 | #1闭式水泵出口电动门全开位置 |  | digital
N1DCS.10PGA11AA003RC | 21040 | #1闭式水泵出口电动门在远控 |  | digital
N1DCS.10PGA11AP001PF | 21041 | #1闭式水泵综合故障 |  | digital
N1DCS.10PGA11AP001PS | 21042 | #1闭式水泵电气保护动作 |  | digital
N1DCS.10PGA11AP001RC | 21043 | #1闭式水泵远方控制 |  | digital
N1DCS.10PGA11AP001RD | 21044 | #1闭式水泵启动指令 |  | digital
N1DCS.10PGA11AP001RP | 21045 | #1闭式水泵在运行 |  | digital
N1DCS.10PGA11AP001SW | 21046 | #1闭式水泵试验位置 |  | digital
N1DCS.10PGA11AP001TD | 21047 | #1闭式水泵停止指令 |  | digital
N1DCS.10PGA11AP001TP | 21048 | #1闭式水泵已停止 |  | digital
N1DCS.10PGA11AP001YW | 21049 | #1闭式水泵工作位置 |  | digital
N1DCS.10PGA21AA001CD | 21050 | #1热交换器闭式进水电动门关指令 |  | digital
N1DCS.10PGA21AA001CP | 21051 | #1热交换器闭式进水电动门全关位 |  | digital
N1DCS.10PGA21AA001F | 21052 | #1热交换器闭式进水电动门故障 |  | digital
N1DCS.10PGA21AA001OD | 21053 | #1热交换器闭式进水电动门开指令 |  | digital
N1DCS.10PGA21AA001OP | 21054 | #1热交换器闭式进水电动门全开位 |  | digital
N1DCS.10PGA21AA001RC | 21055 | #1热交换器闭式进水电动门在远控 |  | digital
N1DCS.10PGA21AA002CD | 21056 | #1热交换器闭式出水电动门关指令 |  | digital
N1DCS.10PGA21AA002CP | 21057 | #1热交换器闭式出水电动门全关位 |  | digital
N1DCS.10PGA21AA002F | 21058 | #1热交换器闭式出水电动门故障 |  | digital
N1DCS.10PGA21AA002OD | 21059 | #1热交换器闭式出水电动门开指令 |  | digital
N1DCS.10PGA21AA002OP | 21060 | #1热交换器闭式出水电动门全开位 |  | digital
N1DCS.10PGA21AA002RC | 21061 | #1热交换器闭式出水电动门在远控 |  | digital
N1DCS.CLCLGPMPA_PMT1 | 21062 | #1闭式水泵启动允许 |  | digital
N1DCS.CLCLGPMPA_SEQSTOK | 21063 | #1闭式水泵启顺控已成功完成 |  | digital
N1DCS.CLCLGPMPA_STPMT | 21064 | #1闭式水泵启动允许 |  | digital
N1DCS.CLCLGPMPA_TEMALM | 21065 | #1闭式水泵超温保护报警 |  | digital
N1DCS.CLCLGPMPA_TEMALMCUT | 21066 | #1闭式水泵超温保护功能解除 |  | digital
N1DCS.CLCLGPMPA_TP | 21067 | #1闭式水泵跳闸信号 |  | digital
N1DCS.CLCLGPMPAMANSTOP | 21068 | #1闭式水泵手动停止指令 |  | digital
N1DCS.CLCLGPMPASTOP | 21069 | #1闭式水泵已停止 |  | digital
N1DCS.CLCLGPMPATEMPMT | 21070 | #1闭式水泵温度允许 |  | digital
N1DCS.CLCLGPMPBSTOP | 21071 | #2闭式水泵已停止 |  | digital
N1DCS.CLCLGWTR_FILLACK | 21072 | 闭式冷却水系统注水确认 |  | digital
N1DCS.CLCLGWTR_SEQSTFINISH | 21073 | 闭式冷却水系统启顺控已成功完成 |  | digital
N1DCS.CLCLGWTRTENCY | 21074 | 热交换器闭式水管路畅通 |  | digital
N1DCS.CLGCHANLGOOD | 21075 | 热交换器开式水管路畅通 |  | digital
N1DCS.CNDHWLVL_MRE | 21076 | 凝汽器热井液位坏点 |  | digital
N1DCS.CNDPA_SEQSTOK | 21077 | #1凝结水泵启顺控已成功完成 |  | digital
N1DCS.CNDPMPA_PMT1 | 21078 | #1凝结水泵启动允许 |  | digital
N1DCS.CNDPMPA_STPMT | 21079 | #1凝结水泵启动允许 |  | digital
N1DCS.CNDPMPA_TEMALM | 21080 | #1凝结水泵超温保护报警 |  | digital
N1DCS.CNDPMPA_TEMALMCUT | 21081 | #1凝结水泵超温保护报警功能解除 |  | digital
N1DCS.CNDPMPA_TP | 21082 | #1凝结水泵跳闸信号 |  | digital
N1DCS.CNDPMPAMANSTOP | 21083 | #1凝结水泵手动停止指令 |  | digital
N1DCS.CNDPMPARUN | 21084 | #1凝结水泵在运行 |  | digital
N1DCS.CNDPMPARUN1 | 21085 | #1凝结水泵工频运行 |  | digital
N1DCS.CNDPMPARUN2 | 21086 | #1凝结水泵变频运行 |  | digital
N1DCS.CNDPMPASTOP | 21087 | #1凝结水泵已停止 |  | digital
N1DCS.CNDPMPATEMPMT | 21088 | #1凝结水泵温度允许 |  | digital
N1DCS.CNDWTRSYS_SEQSTFINISH | 21089 | 凝结水系统启顺控已成功完成 |  | digital
N1DCS.CNSRLVL_MRE | 21090 | 凝汽器热井液位坏点 |  | digital
N1DCS.L0LCE50AA101DVHI | 21091 | 闭式水箱补水调阀指令反馈偏差大 |  | digital
N1DCS.ONE3 | 21092 | 开关量1 |  | digital
N1DCS.OPNCIRPMPA_PMT | 21093 | #1开式水泵启动允许 |  | digital
N1DCS.OPNCIRPMPA_PMT1 | 21094 | #1开式水泵启动允许 |  | digital
N1DCS.OPNCIRPMPA_SEQSTOK | 21095 | #1开式水泵启顺控已成功完成 |  | digital
N1DCS.OPNCIRPMPA_TEMALM | 21096 | #1开式水泵温度保护 |  | digital
N1DCS.OPNCIRPMPA_TEMALMCUT | 21097 | #1开式水泵温度保护功能解除 |  | digital
N1DCS.OPNCIRPMPA_TP | 21098 | #1开式水泵跳闸信号 |  | digital
N1DCS.OPNCIRPMPAMANSTOP | 21099 | #1开式水泵手动停止指令 |  | digital
N1DCS.OPNCIRPMPATEMPMT | 21100 | #1开式水泵温度允许 |  | digital
N1DCS.OPNCIRWTR_SEQSTFINISH | 21101 | 开式水系统启顺控已成功完成 |  | digital
N1DCS.OPNWTRTENCY | 21102 | 热交换器开式水管路畅通 |  | digital
N1DCS.SELCLWTRCLRA | 21103 | 预选闭式水系统#1热交换器 |  | digital
N1DCS.SELCLWTRCLRB | 21104 | 预选闭式水系统#2热交换器 |  | digital
N1DCS.SELOPNCIRWTRCHANL_A | 21105 | 预选开式水电动过滤器通道 |  | digital
N1DCS.SELOPNCIRWTRCHANL_B | 21106 | 预选开式水电动过滤器旁路通道 |  | digital
N1DCS.SELOPNWTRCLRA | 21107 | 预选开式水系统#1热交换器 |  | digital
N1DCS.SELOPNWTRCLRB | 21108 | 预选开式水系统#2热交换器 |  | digital
N1DCS.SELVACMCLGSYSA | 21109 | 预选#1真空泵冷却器 |  | digital
N1DCS.SELVACMCLGSYSB | 21110 | 预选#2真空泵冷却器 |  | digital
N1DCS.STARTPULLWATERCOF | 21111 | Ovation Control Builder |  | digital
N1DCS.ZERO3 | 21112 | 开关量0 |  | digital
N1DCS.10LBG21AC001_PUT | 21113 | 轴封电加热器已连锁投入 |  | digital
N1DCS.CLCLGWTRSTRESET | 21114 | 闭式水系统启顺控复位指令 |  | digital
N1DCS.CNSRPRTCT | 21115 | 凝汽器保护动作 |  | digital
N1DCS.DEHALM001 | 21116 | #1机润滑油母管压力测量故障 |  | digital
N1DCS.DEHALM002 | 21117 | #1机润滑油母管压力＜0.25MPa |  | digital
N1DCS.DEHALM003 | 21118 | #1机润滑油箱液位测量故障 |  | digital
N1DCS.DEHALM004 | 21119 | #1机润滑油箱液位＜900mm |  | digital
N1DCS.DEHALM005 | 21120 | #1机润滑油箱液位＞1000mm |  | digital
N1DCS.DEHALM006 | 21121 | #1机凝汽器真空测量故障 |  | digital
N1DCS.DEHALM007 | 21122 | #1机凝汽器真空>20KPa |  | digital
N1DCS.DEHALM008 | 21123 | #1机EH油压力测量故障 |  | digital
N1DCS.DEHALM009 | 21124 | #1机EH油压力＜12MPa |  | digital
N1DCS.DEHALM010 | 21125 | #1机轴向位移测量故障 |  | digital
N1DCS.DEHALM011 | 21126 | #1机轴向位移＜-0.5mm |  | digital
N1DCS.DEHALM012 | 21127 | #1机轴向位移＞0.5mm |  | digital
N1DCS.DEHALM013 | 21128 | #1机DEH控制器站间通讯中断 |  | digital
N1DCS.DEHALM014 | 21129 | #2 CSI6300测试模式 |  | digital
N1DCS.DEHALM015 | 21130 | #1机高压缸排汽口温度测量故障 |  | digital
N1DCS.DEHALM016 | 21131 | #1机高压缸排汽口温度大于计算值 |  | digital
N1DCS.DEHALM017 | 21132 | #1机低压缸末级蒸汽温度＞180℃ |  | digital
N1DCS.DEHALM018 | 21133 | #1机低压缸末级蒸汽温度＞230℃ |  | digital
N1DCS.DEHALM019 | 21134 | #1机高压缸排汽口温度＞384℃ |  | digital
N1DCS.DEHALM020 | 21135 | #1机中压缸排汽蒸汽温度＞305℃ |  | digital
N1DCS.DEHALM021 | 21136 | #1机中压缸排汽蒸汽温度＞323℃ |  | digital
N1DCS.DEHALM022 | 21137 | #1机低压排汽支架温度测量故障 |  | digital
N1DCS.DEHALM023 | 21138 | #1机低压排汽支架温度＞70℃ |  | digital
N1DCS.DEHALM024 | 21139 | ＜47.5HZ且中压缸上下温差＞55℃ |  | digital
N1DCS.DEHALM025 | 21140 | #1机中压缸上下温差＞30℃ |  | digital
N1DCS.DEHALM026 | 21141 | 并网120s后中压缸上下温差>45℃ |  | digital
N1DCS.DEHALM027 | 21142 | #1机#1轴承前右下温度测量故障 |  | digital
N1DCS.DEHALM028 | 21143 | #1机#1轴承前右下温度＞90℃ |  | digital
N1DCS.DEHALM029 | 21144 | #1机#1轴承后右下温度测量故障 |  | digital
N1DCS.DEHALM030 | 21145 | #1机#1轴承后右下温度＞90℃ |  | digital
N1DCS.DEHALM031 | 21146 | #2径向轴承前左上温度测量故障 |  | digital
N1DCS.DEHALM032 | 21147 | #2径向轴承前左上温度＞90℃ |  | digital
N1DCS.DEHALM033 | 21148 | #2径向轴承前右上温度测量故障 |  | digital
N1DCS.DEHALM034 | 21149 | #2径向轴承前右上温度＞90℃ |  | digital
N1DCS.DEHALM035 | 21150 | #2径向轴承前左下温度测量故障 |  | digital
N1DCS.DEHALM036 | 21151 | #2径向轴承前左下温度＞90℃ |  | digital
N1DCS.DEHALM037 | 21152 | #2径向轴承前右下温度测量故障 |  | digital
N1DCS.DEHALM038 | 21153 | #2径向轴承前右下温度＞90℃ |  | digital
N1DCS.DEHALM039 | 21154 | #1机推力轴承前左上温度测量故障 |  | digital
N1DCS.DEHALM040 | 21155 | #1机推力轴承前左上温度＞90℃ |  | digital
N1DCS.DEHALM041 | 21156 | #1机推力轴承前右上温度测量故障 |  | digital
N1DCS.DEHALM042 | 21157 | #1机推力轴承前右上温度＞90℃ |  | digital
N1DCS.DEHALM043 | 21158 | #1机推力轴承前左下温度测量故障 |  | digital
N1DCS.DEHALM044 | 21159 | #1机推力轴承前左下温度＞90℃ |  | digital
N1DCS.DEHALM045 | 21160 | #1机推力轴承前右下温度测量故障 |  | digital
N1DCS.DEHALM046 | 21161 | #1机推力轴承前右下温度＞90℃ |  | digital
N1DCS.DEHALM047 | 21162 | #1机#3轴承前左上温度测量故障 |  | digital
N1DCS.DEHALM048 | 21163 | #1机#3轴承前左上温度＞90℃ |  | digital
N1DCS.DEHALM049 | 21164 | #1机#3轴承前右上温度测量故障 |  | digital
N1DCS.DEHALM050 | 21165 | #1机#3轴承前右上温度＞90℃ |  | digital
N1DCS.DEHALM051 | 21166 | #1机#3轴承前左下温度测量故障 |  | digital
N1DCS.DEHALM052 | 21167 | #1机#3轴承前左下温度＞90℃ |  | digital
N1DCS.DEHALM053 | 21168 | #1机#3轴承前右下温度测量故障 |  | digital
N1DCS.DEHALM054 | 21169 | #1机#3轴承前右下温度＞90℃ |  | digital
N1DCS.DEHALM055 | 21170 | #1机#3轴承后右下温度测量故障 |  | digital
N1DCS.DEHALM056 | 21171 | #1机#3轴承后右下温度＞90℃ |  | digital
N1DCS.DEHALM057 | 21172 | #1机#4轴承机端温度测量故障 |  | digital
N1DCS.DEHALM058 | 21173 | #1机#4轴承机端温度＞99℃ |  | digital
N1DCS.DEHALM059 | 21174 | #1机#4轴承励端温度测量故障 |  | digital
N1DCS.DEHALM060 | 21175 | #1机#4轴承励端温度＞99℃ |  | digital
N1DCS.DEHALM061 | 21176 | #1轴承座振动测量故障 |  | digital
N1DCS.DEHALM062 | 21177 | #1轴承座振动＞9.3mm/s |  | digital
N1DCS.DEHALM063 | 21178 | #2轴承座振动测量故障 |  | digital
N1DCS.DEHALM064 | 21179 | #2轴承座振动＞9.3mm/s |  | digital
N1DCS.DEHALM065 | 21180 | #3轴承座振动测量故障 |  | digital
N1DCS.DEHALM066 | 21181 | #3轴承座振动＞9.3mm/s |  | digital
N1DCS.DEHALM067 | 21182 | #1机紧急跳闸按钮通道1动作 |  | digital
N1DCS.DEHALM068 | 21183 | #1机紧急跳闸按钮通道2动作 |  | digital
N1DCS.DEHALM069 | 21184 | #1机紧急跳闸按钮通道3动作 |  | digital
N1DCS.DEHALM070 | 21185 | #1机#1转速探头故障 |  | digital
N1DCS.DEHALM071 | 21186 | #1机#2转速探头故障 |  | digital
N1DCS.DEHALM072 | 21187 | #1机#3转速探头故障 |  | digital
N1DCS.DEHALM073 | 21188 | #1机#1功率变送器故障 |  | digital
N1DCS.DEHALM074 | 21189 | #1机#2功率变送器故障 |  | digital
N1DCS.DEHALM075 | 21190 | #1机#3功率变送器故障 |  | digital
N1DCS.DEHALM076 | 21191 | #1机负荷＞20且高压缸压比＜1.08 |  | digital
N1DCS.DEHALM077 | 21192 | #1轴承振动测量故障 |  | digital
N1DCS.DEHALM078 | 21193 | #1轴承振动＞83um |  | digital
N1DCS.DEHALM079 | 21194 | #1轴承振动＞130um |  | digital
N1DCS.DEHALM080 | 21195 | #2轴承振动测量故障 |  | digital
N1DCS.DEHALM081 | 21196 | #2轴承振动＞83um |  | digital
N1DCS.DEHALM082 | 21197 | #2轴承振动＞130um |  | digital
N1DCS.DEHALM083 | 21198 | #3轴承振动测量故障 |  | digital
N1DCS.DEHALM084 | 21199 | #3轴承振动＞83um |  | digital
N1DCS.DEHALM085 | 21200 | #3轴承振动＞130um |  | digital
N1DCS.DEHALM086 | 21201 | #4轴承振动测量故障 |  | digital
N1DCS.DEHALM087 | 21202 | #4轴承振动＞83um |  | digital
N1DCS.DEHALM088 | 21203 | #4轴承振动＞130um |  | digital
N1DCS.DEHALM089 | 21204 | #5轴承振动测量故障 |  | digital
N1DCS.DEHALM090 | 21205 | #5轴承振动＞83um |  | digital
N1DCS.DEHALM091 | 21206 | #5轴承振动＞130um |  | digital
N1DCS.DEHALM092 | 21207 | 高压缸排汽口蒸汽过热度＜20℃ |  | digital
N1DCS.DEHALM093 | 21208 | 高压缸排汽口蒸汽过热度＜10℃ |  | digital
N1DCS.DEHALM094 | 21209 | 中压缸排汽蒸汽过热度＜20℃ |  | digital
N1DCS.DEHALM095 | 21210 | 中压缸排汽蒸汽过热度＜10℃ |  | digital
N1DCS.DEHALM096 | 21211 | #1机高压主汽门前蒸汽温度高 |  | digital
N1DCS.DEHALM097 | 21212 | #1机再热主汽门前蒸汽温度高 |  | digital
N1DCS.DEHALM098 | 21213 | #1机X准则计算故障 |  | digital
N1DCS.DEHALM099 | 21214 | #1机Z准则计算故障 |  | digital
N1DCS.DEHALM100 | 21215 | #1机Z准则计算故障 |  | digital
N1DCS.DEHALMALL | 21216 | #1机DEH光字牌报警总信号 |  | digital
N1DCS.DEHALMALL1 | 21217 | #1机DEH光字牌报警汇总信号 |  | digital
N1DCS.DEHALMUNACK | 21218 | #1机DEH光字牌报警手动确认指令 |  | digital
N1DCS.DEHALMUNACK1 | 21219 | #1机DEH光字牌报警手动确认指令 |  | digital
N1DCS.TALM001 | 21220 | 高压缸排汽口温度高(大于384℃） |  | digital
N1DCS.TALM002 | 21221 | 凝汽器真空低(大于-81KPa） |  | digital
N1DCS.TALM003 | 21222 | 凝汽器热井液位低(小于600mm） |  | digital
N1DCS.TALM004 | 21223 | #1机真空泵异常跳闸 |  | digital
N1DCS.TALM005 | 21224 | #1机真空泵超温报警 |  | digital
N1DCS.TALM006 | 21225 | 辅汽母管温度低(小于260℃） |  | digital
N1DCS.TALM006A | 21226 | 辅汽母管温度低(小于260℃） |  | digital
N1DCS.TALM007 | 21227 | #1机闭式水箱液位低(小于500℃） |  | digital
N1DCS.TALM008 | 21228 | #1机闭式冷却水泵异常跳闸 |  | digital
N1DCS.TALM009 | 21229 | #1机闭式冷却水泵超温报警 |  | digital
N1DCS.TALM010 | 21230 | #1机开式冷却水泵异常跳闸 |  | digital
N1DCS.TALM011 | 21231 | #1机开式冷却水泵超温报警 |  | digital
N1DCS.TALM012 | 21232 | #1机凝结水泵异常跳闸 |  | digital
N1DCS.TALM013 | 21233 | #1机凝结水泵超温报警 |  | digital
N1DCS.TALM014 | 21234 | #1机轴封风机异常跳闸 |  | digital
N1DCS.TALM015 | 21235 | #1机循环水泵异常跳闸 |  | digital
N1DCS.TALM016 | 21236 | #1机循环水泵超温报警 |  | digital
N1DCS.TALM017 | 21237 | 循环水前池液位低 |  | digital
N1DCS.TALM018 | 21238 | #1循环水泵冷却水加压泵跳闸 |  | digital
N1DCS.TALM019 | 21239 | #2循环水泵冷却水加压泵跳闸 |  | digital
N1DCS.TALM020 | 21240 | #1机润滑油箱液位高(大于1050mm |  | digital
N1DCS.TALM021 | 21241 | #1机润滑油箱液位低(小于850mm） |  | digital
N1DCS.TALM022 | 21242 | #1机润滑油泵异常跳闸 |  | digital
N1DCS.TALM023 | 21243 | #1机润滑油滤网压差高 |  | digital
N1DCS.TALM024 | 21244 | #1机润滑油供油母管压力低 |  | digital
N1DCS.TALM025 | 21245 | #1机应急润滑油泵异常跳闸 |  | digital
N1DCS.TALM026 | 21246 | #1机顶轴油泵异常跳闸 |  | digital
N1DCS.TALM027 | 21247 | #1机EH油泵异常跳闸 |  | digital
N1DCS.TALM028 | 21248 | #1机轴承振动大(大于83um） |  | digital
N1DCS.TALM029 | 21249 | #1机轴承座振动大(大于9.3mm/s） |  | digital
N1DCS.TALM030 | 21250 | #1机轴向位移大(大于0.5mm） |  | digital
N1DCS.TALM031 | 21251 | #1机高压缸压比低(小于1.5） |  | digital
N1DCS.TALM032 | 21252 | #1机转速高(大于3090rpm） |  | digital
N1DCS.TALM033 | 21253 | #1高压给水泵无启允许 |  | digital
N1DCS.TALM034 | 21254 | #2高压给水泵无启允许 |  | digital
N1DCS.TALM035 | 21255 | #1中压给水泵无启允许 |  | digital
N1DCS.TALM036 | 21256 | #2中压给水泵无启允许 |  | digital
N1DCS.TALM037 | 21257 | #1凝结水泵无启允许 |  | digital
N1DCS.TALM038 | 21258 | #2凝结水泵无启允许 |  | digital
N1DCS.TALM039 | 21259 | 低压省煤器#1再循环泵无启允许 |  | digital
N1DCS.TALM040 | 21260 | 低压省煤器#2再循环泵无启允许 |  | digital
N1DCS.TALM041 | 21261 | #1循环水泵无启允许 |  | digital
N1DCS.TALM042 | 21262 | #2循环水泵无启允许 |  | digital
N1DCS.TALM043 | 21263 | #1闭式水泵无启允许 |  | digital
N1DCS.TALM044 | 21264 | #2闭式水泵无启允许 |  | digital
N1DCS.TALM045 | 21265 | #1开式水泵无启允许 |  | digital
N1DCS.TALM046 | 21266 | #2开式水泵无启允许 |  | digital
N1DCS.TALM047 | 21267 | #1真空泵无启允许 |  | digital
N1DCS.TALM048 | 21268 | #2真空泵无启允许 |  | digital
N1DCS.TALM049 | 21269 | 任一EH油泵无启允许 |  | digital
N1DCS.TALM050 | 21270 | 高压给水气动调节阀在手动模式 |  | digital
N1DCS.TALM051 | 21271 | 中压给水气动调节阀在手动模式 |  | digital
N1DCS.TALM052 | 21272 | 低压给水气动调节阀在手动模式 |  | digital
N1DCS.TALM053 | 21273 | 高压给水泵变频器在手动模式 |  | digital
N1DCS.TALMALL | 21274 | #1机机炉光字牌报警总信号 |  | digital
N1DCS.TALMUNACK | 21275 | #1机机炉光字牌报警手动确认指令 |  | digital
N1DCS.THREEPICKTWO | 21276 | #1机轴承超温 |  | digital
N1DCS.10LCA12AA001CD | 21277 | #2凝结水泵进口电动门关闭指令 |  | digital
N1DCS.10LCA12AA001CP | 21278 | #2凝结水泵进口电动门全关位置 |  | digital
N1DCS.10LCA12AA001F | 21279 | #2凝结水泵进口电动门综合故障 |  | digital
N1DCS.10LCA12AA001OD | 21280 | #2凝结水泵进口电动门打开指令 |  | digital
N1DCS.10LCA12AA001OP | 21281 | #2凝结水泵进口电动门全开位置 |  | digital
N1DCS.10LCA12AA001RC | 21282 | #2凝结水泵进口电动门在远控 |  | digital
N1DCS.10LCA12AA003CD | 21283 | #2凝结水泵出口电动门关闭指令 |  | digital
N1DCS.10LCA12AA003CP | 21284 | #2凝结水泵出口电动门全关位置 |  | digital
N1DCS.10LCA12AA003F | 21285 | #2凝结水泵出口电动门综合故障 |  | digital
N1DCS.10LCA12AA003OD | 21286 | #2凝结水泵出口电动门打开指令 |  | digital
N1DCS.10LCA12AA003OP | 21287 | #2凝结水泵出口电动门全开位置 |  | digital
N1DCS.10LCA12AA003RC | 21288 | #2凝结水泵出口电动门在远控 |  | digital
N1DCS.10LCB12AP001CPDO | 21289 | #2凝结水泵已停止(至DROP9) |  | digital
N1DCS.10LCB12AP001SW | 21290 | #2凝结水泵试验位置 |  | digital
N1DCS.10LCB12AP001YW | 21291 | #2凝结水泵工作位置 |  | digital
N1DCS.10LCB12AP002PF | 21292 | #2凝结水泵综合故障 |  | digital
N1DCS.10LCB12AP002PS | 21293 | #2凝结水泵电气保护动作 |  | digital
N1DCS.10LCB12AP002RC | 21294 | #2凝结水泵远方控制 |  | digital
N1DCS.10LCB12AP002RD | 21295 | #2凝结水泵启动指令 |  | digital
N1DCS.10LCB12AP002RP | 21296 | #2凝结水泵在运行 |  | digital
N1DCS.10LCB12AP002TD | 21297 | #2凝结水泵停止指令 |  | digital
N1DCS.10LCB12AP002TP | 21298 | #2凝结水泵已停止 |  | digital
N1DCS.10LCB12GH001F1 | 21299 | #2凝泵#1永磁调速水泵故障 |  | digital
N1DCS.10LCB12GH001F2 | 21300 | #2凝泵#2永磁调速水泵故障 |  | digital
N1DCS.10LCB12GH001RD1 | 21301 | #2凝泵#1永磁调速水泵启动指令 |  | digital
N1DCS.10LCB12GH001RD2 | 21302 | #2凝泵#2永磁调速水泵启动指令 |  | digital
N1DCS.10LCB12GH001RP1 | 21303 | #2凝泵#1永磁调速水泵在运行 |  | digital
N1DCS.10LCB12GH001RP2 | 21304 | #2凝泵#2永磁调速水泵在运行 |  | digital
N1DCS.10LCB12GH001TD1 | 21305 | #2凝泵#1永磁调速水泵停止指令 |  | digital
N1DCS.10LCB12GH001TD2 | 21306 | #2凝泵#2永磁调速水泵停止指令 |  | digital
N1DCS.10LDB10AA501CD | 21307 | 除铁过滤器#1排气气动门关指令 |  | digital
N1DCS.10LDB10AA501CP | 21308 | 除铁过滤器#1排气气动门全关位 |  | digital
N1DCS.10LDB10AA501OD | 21309 | 除铁过滤器#1排气气动门开指令 |  | digital
N1DCS.10LDB10AA501OP | 21310 | 除铁过滤器#1排气气动门全开位 |  | digital
N1DCS.10LDB10AA502CD | 21311 | 除铁过滤器#2排气气动门关指令 |  | digital
N1DCS.10LDB10AA502CP | 21312 | 除铁过滤器#2排气气动门全关位 |  | digital
N1DCS.10LDB10AA502OD | 21313 | 除铁过滤器#2排气气动门开指令 |  | digital
N1DCS.10LDB10AA502OP | 21314 | 除铁过滤器#2排气气动门全开位 |  | digital
N1DCS.10LDB10GA001RC | 21315 | 1号机组除铁过滤器电磁阀箱在远? |  | digital
N1DCS.10LDK10AA002CD | 21316 | 除铁过滤器进口电动门关指令 |  | digital
N1DCS.10LDK10AA002CP | 21317 | 除铁过滤器进口电动门全关位 |  | digital
N1DCS.10LDK10AA002F | 21318 | 除铁过滤器进口电动门故障 |  | digital
N1DCS.10LDK10AA002OD | 21319 | 除铁过滤器进口电动门开指令 |  | digital
N1DCS.10LDK10AA002OP | 21320 | 除铁过滤器进口电动门全开位 |  | digital
N1DCS.10LDK10AA002RC | 21321 | 除铁过滤器进口电动门在远控 |  | digital
N1DCS.10LDK20AA002CD | 21322 | 除铁过滤器旁路电动门关指令 |  | digital
N1DCS.10LDK20AA002CP | 21323 | 除铁过滤器旁路电动门全关位 |  | digital
N1DCS.10LDK20AA002F | 21324 | 除铁过滤器旁路电动门故障 |  | digital
N1DCS.10LDK20AA002OD | 21325 | 除铁过滤器旁路电动门开指令 |  | digital
N1DCS.10LDK20AA002OP | 21326 | 除铁过滤器旁路电动门全开位 |  | digital
N1DCS.10LDK20AA002RC | 21327 | 除铁过滤器旁路电动门在远控 |  | digital
N1DCS.10PAB12AA001CD | 21328 | 凝汽器循环水进水#2电动门关指令 |  | digital
N1DCS.10PAB12AA001CP | 21329 | 凝汽器循环水进水#2电动门全关位 |  | digital
N1DCS.10PAB12AA001F | 21330 | 凝汽器循环水进水#2电动门故障 |  | digital
N1DCS.10PAB12AA001OD | 21331 | 凝汽器循环水进水#2电动门开指令 |  | digital
N1DCS.10PAB12AA001OP | 21332 | 凝汽器循环水进水#2电动门全开位 |  | digital
N1DCS.10PAB12AA001RC | 21333 | 凝汽器循环水进水#2电动门在远控 |  | digital
N1DCS.10PAB22AA001CD | 21334 | 凝汽器循环水#2出水电动门关指令 |  | digital
N1DCS.10PAB22AA001CP | 21335 | 凝汽器循环水#2出水电动门全关位 |  | digital
N1DCS.10PAB22AA001F | 21336 | 凝汽器循环水#2出水电动门故障 |  | digital
N1DCS.10PAB22AA001OD | 21337 | 凝汽器循环水#2出水电动门开指令 |  | digital
N1DCS.10PAB22AA001OP | 21338 | 凝汽器循环水#2出水电动门全开位 |  | digital
N1DCS.10PAB22AA001RC | 21339 | 凝汽器循环水#2出水电动门在远控 |  | digital
N1DCS.10PAH12AA002CD | 21340 | #2胶球泵出口电动门关闭指令 |  | digital
N1DCS.10PAH12AA002CP | 21341 | #2胶球泵出口电动门全关位置 |  | digital
N1DCS.10PAH12AA002F | 21342 | #2胶球泵出口电动门综合故障 |  | digital
N1DCS.10PAH12AA002OD | 21343 | #2胶球泵出口电动门打开指令 |  | digital
N1DCS.10PAH12AA002OP | 21344 | #2胶球泵出口电动门全开位置 |  | digital
N1DCS.10PAH12AP001PF | 21345 | #2胶球泵综合故障 |  | digital
N1DCS.10PAH12AP001RD | 21346 | #2胶球泵启动指令 |  | digital
N1DCS.10PAH12AP001RP | 21347 | #2胶球泵在运行 |  | digital
N1DCS.10PAH12AP001TD | 21348 | #2胶球泵停止指令 |  | digital
N1DCS.10PAH12AP001TP | 21349 | #2胶球泵已停止 |  | digital
N1DCS.10PAH12AT001F | 21350 | #2收球网综合故障 |  | digital
N1DCS.10PAH12AT001FX | 21351 | #2收球网反洗指令 |  | digital
N1DCS.10PAH12AT001FXP | 21352 | #2收球网在反洗位置 |  | digital
N1DCS.10PAH12AT001SQ | 21353 | #2收球网收球指令 |  | digital
N1DCS.10PAH12AT001SQP | 21354 | #2收球网在收球位置 |  | digital
N1DCS.10PAH12BB001CD | 21355 | #2装球室关闭指令 |  | digital
N1DCS.10PAH12BB001CP | 21356 | #2装球室全关位置 |  | digital
N1DCS.10PAH12BB001F | 21357 | #2装球室综合故障 |  | digital
N1DCS.10PAH12BB001OD | 21358 | #2装球室打开指令 |  | digital
N1DCS.10PAH12BB001OP | 21359 | #2装球室全开位置 |  | digital
N1DCS.10PCB11AA003CD | 21360 | #2开式水泵进口电动门关闭指令 |  | digital
N1DCS.10PCB11AA003CP | 21361 | #2开式水泵进口电动门全关位 |  | digital
N1DCS.10PCB11AA003F | 21362 | #2开式水泵进口电动门综合故障 |  | digital
N1DCS.10PCB11AA003OD | 21363 | #2开式水泵进口电动门打开指令 |  | digital
N1DCS.10PCB11AA003OP | 21364 | #2开式水泵进口电动门全开位 |  | digital
N1DCS.10PCB11AA003RC | 21365 | #2开式水泵进口电动门在远控 |  | digital
N1DCS.10PCB11AA004CD | 21366 | #2开式水泵出口电动门关闭指令 |  | digital
N1DCS.10PCB11AA004CP | 21367 | #2开式水泵出口电动门全关位 |  | digital
N1DCS.10PCB11AA004F | 21368 | #2开式水泵出口电动门综合故障 |  | digital
N1DCS.10PCB11AA004OD | 21369 | #2开式水泵出口电动门打开指令 |  | digital
N1DCS.10PCB11AA004OP | 21370 | #2开式水泵出口电动门全开位 |  | digital
N1DCS.10PCB11AA004RC | 21371 | #2开式水泵出口电动门在远控 |  | digital
N1DCS.10PCB11AP002PF | 21372 | #2开式水泵综合故障 |  | digital
N1DCS.10PCB11AP002RC | 21373 | #2开式水泵远方控制 |  | digital
N1DCS.10PCB11AP002RD | 21374 | #2开式水泵启动指令 |  | digital
N1DCS.10PCB11AP002RP | 21375 | #2开式水泵在运行 |  | digital
N1DCS.10PCB11AP002TD | 21376 | #2开式水泵停止指令 |  | digital
N1DCS.10PCB11AP002TP | 21377 | #2开式水泵已停止 |  | digital
N1DCS.10PCB13AA012CD | 21378 | #2真空泵冷却器开式进水门关指令 |  | digital
N1DCS.10PCB13AA012CP | 21379 | #2真空泵冷却器开式进水门全关位 |  | digital
N1DCS.10PCB13AA012F | 21380 | #2真空泵冷却器开式进水水门故障 |  | digital
N1DCS.10PCB13AA012OD | 21381 | #2真空泵冷却器开式进水门开指令 |  | digital
N1DCS.10PCB13AA012OP | 21382 | #2真空泵冷却器开式进水门全开位 |  | digital
N1DCS.10PCB13AA012RC | 21383 | #2真空泵冷却器开式进水门在远控 |  | digital
N1DCS.10PCB22AA001CD | 21384 | #2热交换器开式进水电动门关指令 |  | digital
N1DCS.10PCB22AA001CP | 21385 | #2热交换器开式进水电动门全关位 |  | digital
N1DCS.10PCB22AA001F | 21386 | #2热交换器开式进水电动门故障 |  | digital
N1DCS.10PCB22AA001OD | 21387 | #2热交换器开式进水电动门开指令 |  | digital
N1DCS.10PCB22AA001OP | 21388 | #2热交换器开式进水电动门全开位 |  | digital
N1DCS.10PCB22AA001RC | 21389 | #2热交换器开式进水电动门在远控 |  | digital
N1DCS.10PCB23AA012CD | 21390 | #2真空泵冷却器开式出水门关指令 |  | digital
N1DCS.10PCB23AA012CP | 21391 | #2真空泵冷却器开式出水门全关位 |  | digital
N1DCS.10PCB23AA012F | 21392 | #2真空泵冷却器开式出水门故障 |  | digital
N1DCS.10PCB23AA012OD | 21393 | #2真空泵冷却器开式出水门开指令 |  | digital
N1DCS.10PCB23AA012OP | 21394 | #2真空泵冷却器开式出水门全开位 |  | digital
N1DCS.10PCB23AA012RC | 21395 | #2真空泵冷却器开式出水门在远控 |  | digital
N1DCS.10PCB32AA001CD | 21396 | #2热交换器开式出水电动门关指令 |  | digital
N1DCS.10PCB32AA001CP | 21397 | #2热交换器开式出水电动门全关位 |  | digital
N1DCS.10PCB32AA001F | 21398 | #2热交换器开式出水电动门故障 |  | digital
N1DCS.10PCB32AA001OD | 21399 | #2热交换器开式出水电动门开指令 |  | digital
N1DCS.10PCB32AA001OP | 21400 | #2热交换器开式出水电动门全开位 |  | digital
N1DCS.10PCB32AA001RC | 21401 | #2热交换器开式出水电动门在远控 |  | digital
N1DCS.10PGA12AA001CD | 21402 | #2闭式水泵进口电动门关闭指令 |  | digital
N1DCS.10PGA12AA001CP | 21403 | #2闭式水泵进口电动门全关位置 |  | digital
N1DCS.10PGA12AA001F | 21404 | #2闭式水泵进口电动门综合故障 |  | digital
N1DCS.10PGA12AA001OD | 21405 | #2闭式水泵进口电动门打开指令 |  | digital
N1DCS.10PGA12AA001OP | 21406 | #2闭式水泵进口电动门全开位置 |  | digital
N1DCS.10PGA12AA001RC | 21407 | #2闭式水泵进口电动门在远控 |  | digital
N1DCS.10PGA12AA003CD | 21408 | #2闭式水泵出口电动门关闭指令 |  | digital
N1DCS.10PGA12AA003CP | 21409 | #2闭式水泵出口电动门全关位置 |  | digital
N1DCS.10PGA12AA003F | 21410 | #2闭式水泵出口电动门综合故障 |  | digital
N1DCS.10PGA12AA003OD | 21411 | #2闭式水泵出口电动门打开指令 |  | digital
N1DCS.10PGA12AA003OP | 21412 | #2闭式水泵出口电动门全开位置 |  | digital
N1DCS.10PGA12AA003RC | 21413 | #2闭式水泵出口电动门在远控 |  | digital
N1DCS.10PGA12AP001PF | 21414 | #2闭式水泵综合故障 |  | digital
N1DCS.10PGA12AP001PS | 21415 | #2闭式水泵电气保护动作 |  | digital
N1DCS.10PGA12AP001RC | 21416 | #2闭式水泵远方控制 |  | digital
N1DCS.10PGA12AP001RD | 21417 | #2闭式水泵启动指令 |  | digital
N1DCS.10PGA12AP001RP | 21418 | #2闭式水泵在运行 |  | digital
N1DCS.10PGA12AP001SW | 21419 | #2闭式水泵试验位置 |  | digital
N1DCS.10PGA12AP001TD | 21420 | #2闭式水泵停止指令 |  | digital
N1DCS.10PGA12AP001TP | 21421 | #2闭式水泵已停止 |  | digital
N1DCS.10PGA12AP001YW | 21422 | #2闭式水泵工作位置 |  | digital
N1DCS.10PGA22AA001CD | 21423 | #2热交换器闭式进水电动门关指令 |  | digital
N1DCS.10PGA22AA001CP | 21424 | #2热交换器闭式进水电动门全关位 |  | digital
N1DCS.10PGA22AA001F | 21425 | #2热交换器闭式进水电动门故障 |  | digital
N1DCS.10PGA22AA001OD | 21426 | #2热交换器闭式进水电动门开指令 |  | digital
N1DCS.10PGA22AA001OP | 21427 | #2热交换器闭式进水电动门全开位 |  | digital
N1DCS.10PGA22AA001RC | 21428 | #2热交换器闭式进水电动门在远控 |  | digital
N1DCS.10PGA22AA002CD | 21429 | #2热交换器闭式出水电动门关指令 |  | digital
N1DCS.10PGA22AA002CP | 21430 | #2热交换器闭式出水电动门全关位 |  | digital
N1DCS.10PGA22AA002F | 21431 | #2热交换器闭式出水电动门故障 |  | digital
N1DCS.10PGA22AA002OD | 21432 | #2热交换器闭式出水电动门开指令 |  | digital
N1DCS.10PGA22AA002OP | 21433 | #2热交换器闭式出水电动门全开位 |  | digital
N1DCS.10PGA22AA002RC | 21434 | #2热交换器闭式出水电动门在远控 |  | digital
N1DCS.10PGA26AA101AUTO | 21435 | #2发电机定冷水进水调节阀在自动 |  | digital
N1DCS.10PGA26AA101DVHI | 21436 | #2发电机定冷调阀指令反馈偏差大 |  | digital
N1DCS.10PGA26AA101F | 21437 | #2发电机定冷水进水调节阀故障 |  | digital
N1DCS.10PGA26AA101RC | 21438 | #2发电机定冷水进水调节阀在远控 |  | digital
N1DCS.10PGA26AA101SPDH | 21439 | #2发电机定冷调阀设定反馈偏差大 |  | digital
N1DCS.10PGA26AA102AUTO | 21440 | #2发电机氢冷器进水调节阀在自动 |  | digital
N1DCS.10PGA26AA102DVHI | 21441 | #2发电机氢冷调阀指令反馈偏差大 |  | digital
N1DCS.10PGA26AA102F | 21442 | #2发电机氢冷器进水调节阀故障 |  | digital
N1DCS.10PGA26AA102RC | 21443 | #2发电机氢冷器进水调节阀在远控 |  | digital
N1DCS.10PGA26AA102SPDH | 21444 | #2发电机氢冷调阀设定反馈偏差大 |  | digital
N1DCS.10PGA26AA103AUTO | 21445 | #2机润滑油冷却器进水调阀在自动 |  | digital
N1DCS.10PGA26AA103DVHI | 21446 | #2机滑油冷却调阀指令反馈偏差大 |  | digital
N1DCS.10PGA26AA103F | 21447 | #2机润滑油冷却器进水调节阀故障 |  | digital
N1DCS.10PGA26AA103RC | 21448 | #2机润滑油冷却器进水调阀在远控 |  | digital
N1DCS.10PGA26AA103SPDH | 21449 | #2机滑油冷却调阀设定反馈偏差大 |  | digital
N1DCS.10PGA32AA101AUTO | 21450 | #1机EH油冷却器进水调阀在自动 |  | digital
N1DCS.10PGA32AA101DVHI | 21451 | #1机EH油冷却调阀指令反馈偏差大 |  | digital
N1DCS.10PGA32AA101F | 21452 | #1机EH油冷却器进水调节阀故障 |  | digital
N1DCS.10PGA32AA101RC | 21453 | #1机EH油冷却器进水调阀在远控 |  | digital
N1DCS.10PGA32AA101SPDH | 21454 | #1机EH油冷却调阀设定反馈偏差大 |  | digital
N1DCS.10PGA33AA101AUTO | 21455 | #1机润滑油冷却器进水调阀在自动 |  | digital
N1DCS.10PGA33AA101DVHI | 21456 | #1机滑油冷却调阀指令反馈偏差大 |  | digital
N1DCS.10PGA33AA101F | 21457 | #1机润滑油冷却器进水调节阀故障 |  | digital
N1DCS.10PGA33AA101RC | 21458 | #1机润滑油冷却器进水调阀在远控 |  | digital
N1DCS.10PGA33AA101SPDH | 21459 | #1机滑油冷却调阀设定反馈偏差大 |  | digital
N1DCS.10PGA34AA101AUTO | 21460 | #1发电机空冷器进水调节阀在自动 |  | digital
N1DCS.10PGA34AA101DVHI | 21461 | #1发电机空冷调阀指令反馈偏差大 |  | digital
N1DCS.10PGA34AA101F | 21462 | #1发电机空冷器进水调节阀故障 |  | digital
N1DCS.10PGA34AA101RC | 21463 | #1发电机空冷器进水调节阀在远控 |  | digital
N1DCS.10PGA34AA101SPDH | 21464 | #1发电机空冷调阀设定反馈偏差大 |  | digital
N1DCS.CLCLGPMPB_PMT1 | 21465 | #2闭式水泵启动允许 |  | digital
N1DCS.CLCLGPMPB_SEQSTOK | 21466 | #2闭式水泵启顺控已成功完成 |  | digital
N1DCS.CLCLGPMPB_STPMT | 21467 | #2闭式水泵启动允许 |  | digital
N1DCS.CLCLGPMPB_TEMALM | 21468 | #2闭式水泵超温保护报警 |  | digital
N1DCS.CLCLGPMPB_TEMALMCUT | 21469 | #2闭式水泵超温保护功能解除 |  | digital
N1DCS.CLCLGPMPB_TP | 21470 | #2闭式水泵跳闸信号 |  | digital
N1DCS.CLCLGPMPBMANSTOP | 21471 | #2闭式水泵手动停止指令 |  | digital
N1DCS.CLCLGPMPBTEMPMT | 21472 | #2闭式水泵已停止 |  | digital
N1DCS.CNDPB_SEQSTOK | 21473 | #2凝结水泵启顺控已成功完成 |  | digital
N1DCS.CNDPMPB_PMT1 | 21474 | #2凝结水泵启动允许 |  | digital
N1DCS.CNDPMPB_STPMT | 21475 | #2凝结水泵启动允许 |  | digital
N1DCS.CNDPMPB_TEMALM | 21476 | #2凝结水泵超温报警 |  | digital
N1DCS.CNDPMPB_TEMALMCUT | 21477 | #2凝结水泵温度保护功能解除 |  | digital
N1DCS.CNDPMPB_TP | 21478 | #2凝结水泵跳闸信号 |  | digital
N1DCS.CNDPMPBTEMPMT | 21479 | #2凝结水泵温度允许 |  | digital
N1DCS.ONE4 | 21480 | 开关量1 |  | digital
N1DCS.OPNCIRPMPB_PMT | 21481 | #2开式水泵启动允许 |  | digital
N1DCS.OPNCIRPMPB_PMT1 | 21482 | #2开式水泵启动允许 |  | digital
N1DCS.OPNCIRPMPB_SEQSTOK | 21483 | #2开式水泵启顺控已成功完成 |  | digital
N1DCS.OPNCIRPMPB_TEMALM | 21484 | #2开式水泵温度报警 |  | digital
N1DCS.OPNCIRPMPB_TEMALMCUT | 21485 | #2开式水泵超温保护报警功能解除 |  | digital
N1DCS.OPNCIRPMPB_TP | 21486 | #2开式水泵跳闸信号 |  | digital
N1DCS.OPNCIRPMPBMANSTOP | 21487 | #2开式水泵手动停止指令 |  | digital
N1DCS.OPNCIRPMPBTEMPMT | 21488 | #2开式水泵温度允许 |  | digital
N1DCS.ZERO4 | 21489 | 开关量0 |  | digital
N1DCS.10LCB12GH001AUTO | 21490 | #2凝结水泵永磁调速控制器在自动 |  | digital
N1DCS.10LCB12GH001DVHI | 21491 | #2凝泵永磁调速指令反馈偏差大 |  | digital
N1DCS.10LCB12GH001SPDH | 21492 | #2凝泵永磁调速设定反馈偏差大 |  | digital
N1DCS.10LCB12GH001TP1 | 21493 | #2凝结水泵#1永磁调速水泵已停止 |  | digital
N1DCS.10LCB12GH001TP2 | 21494 | #2凝结水泵#2永磁调速水泵已停止 |  | digital
N1DCS.CNDPMPBMANSTOP | 21495 | #2凝结水泵逻辑发出停止指令 |  | digital
N1DCS.CNDPMPBPRT | 21496 | #2凝结水泵保护停指令 |  | digital
N1DCS.CNDPMPBRUN | 21497 | #2凝结水泵在运行 |  | digital
N1DCS.CNDPMPBRUN1 | 21498 | #2凝结水泵在运行 |  | digital
N1DCS.CNDPMPBRUN2 | 21499 | #2凝结水泵在运行 |  | digital
N1DCS.CNDPMPBSTOP | 21500 | #2凝结水泵已停止 |  | digital
N1DCS.FOUT11 | 21501 | Ovation Control Builder |  | digital
N1DCS.HXCTQ_SEQSPOK | 21502 | 除铁过滤器停顺控已完成 |  | digital
N1DCS.HXCTQ_SEQSTOK | 21503 | 除铁过滤器启顺控已完成 |  | digital
N1DCS.10CSF01LP | 21504 | #1循环水泵房热力配电柜电源故障 |  | digital
N1DCS.10MAG01GH001F1 | 21505 | 热井检漏装置泵过热故障 |  | digital
N1DCS.10MAG01GH001LLL | 21506 | 热井检漏装置样水液位过低 |  | digital
N1DCS.10MAG01GH001RP1 | 21507 | 热井检漏装置泵运行状态 |  | digital
N1DCS.10MAG21CL001H | 21508 | #1真空泵汽水分离器液位高 |  | digital
N1DCS.10MAG21CL002L | 21509 | #1真空泵汽水分离器液位低 |  | digital
N1DCS.10MAJ21AA001CD | 21510 | #1真空泵进口气动门2关闭指令 |  | digital
N1DCS.10MAJ21AA001CP | 21511 | #1真空泵进口气动门2全关位置 |  | digital
N1DCS.10MAJ21AA001F | 21512 | #1真空泵进口气动门2电源消失 |  | digital
N1DCS.10MAJ21AA001OD | 21513 | #1真空泵进口气动门2打开指令 |  | digital
N1DCS.10MAJ21AA001OP | 21514 | #1真空泵进口气动门2全开位置 |  | digital
N1DCS.10MAJ21AA007F | 21515 | #1真空泵汽水分离器补水阀无电源 |  | digital
N1DCS.10MAJ21AA007OD/CD | 21516 | #1真空泵分离器补水阀开/关指令 |  | digital
N1DCS.10MAJ21AA011CD | 21517 | #1真空泵进口气动门1关闭指令 |  | digital
N1DCS.10MAJ21AA011CP | 21518 | #1真空泵进口气动门1全关位置 |  | digital
N1DCS.10MAJ21AA011F | 21519 | #1真空泵进口气动门1电源消失 |  | digital
N1DCS.10MAJ21AA011OD | 21520 | #1真空泵进口气动门1打开指令 |  | digital
N1DCS.10MAJ21AA011OP | 21521 | #1真空泵进口气动门1全开位置 |  | digital
N1DCS.10MAJ21AP001PF | 21522 | #1真空泵综合故障 |  | digital
N1DCS.10MAJ21AP001RC | 21523 | #1真空泵远方控制 |  | digital
N1DCS.10MAJ21AP001RD | 21524 | #1真空泵启动指令 |  | digital
N1DCS.10MAJ21AP001RP | 21525 | #1真空泵在运行 |  | digital
N1DCS.10MAJ21AP001TD | 21526 | #1真空泵停止指令 |  | digital
N1DCS.10MAJ21AP001TP | 21527 | #1真空泵已停止 |  | digital
N1DCS.10MAJ23AA009CD | 21528 | 蒸汽喷射装置进口气动门关闭指令 |  | digital
N1DCS.10MAJ23AA009CP | 21529 | 蒸汽喷射装置进口气动门全关位置 |  | digital
N1DCS.10MAJ23AA009F | 21530 | 蒸汽喷射装置进口气动门电源消失 |  | digital
N1DCS.10MAJ23AA009OD | 21531 | 蒸汽喷射装置进口气动门打开指令 |  | digital
N1DCS.10MAJ23AA009OP | 21532 | 蒸汽喷射装置进口气动门全开位置 |  | digital
N1DCS.10MAJ23AA014CD | 21533 | 蒸汽喷射装置换热器放水门关指令 |  | digital
N1DCS.10MAJ23AA014CP | 21534 | 蒸汽喷射装置换热器放水门全关位 |  | digital
N1DCS.10MAJ23AA014F | 21535 | 蒸汽喷射装置换热器放水门无电源 |  | digital
N1DCS.10MAJ23AA014OD | 21536 | 蒸汽喷射装置换热器放水门开指令 |  | digital
N1DCS.10MAJ23AA014OP | 21537 | 蒸汽喷射装置换热器放水门全开位 |  | digital
N1DCS.10MAJ23AA016CD | 21538 | 喷射装置换热器汽侧出口门关指令 |  | digital
N1DCS.10MAJ23AA016CP | 21539 | 喷射装置换热器汽侧出口门全关位 |  | digital
N1DCS.10MAJ23AA016F | 21540 | 喷射装置换热器汽侧出口门无电源 |  | digital
N1DCS.10MAJ23AA016OD | 21541 | 喷射装置换热器汽侧出口门开指令 |  | digital
N1DCS.10MAJ23AA016OP | 21542 | 喷射装置换热器汽侧出口门全开位 |  | digital
N1DCS.10MAJ23AA101AUTO | 21543 | 蒸汽喷射装置压力调节阀在自动 |  | digital
N1DCS.10MAJ23AA101CP | 21544 | 蒸汽喷射装置压力调节阀全关位 |  | digital
N1DCS.10MAJ23AA101DVHI | 21545 | 喷射装置压力调阀指令反馈偏差大 |  | digital
N1DCS.10MAJ23AA101OP | 21546 | 蒸汽喷射装置压力调节阀全开位 |  | digital
N1DCS.10MAJ23AA101SPDH | 21547 | 喷射装置压力调阀设定反馈偏差大 |  | digital
N1DCS.10MAJ30AA002CD | 21548 | 凝汽器真空破坏气动门关闭指令 |  | digital
N1DCS.10MAJ30AA002CP | 21549 | 凝汽器真空破坏气动门门全关位置 |  | digital
N1DCS.10MAJ30AA002F | 21550 | 凝汽器真空破坏气动门电源消失 |  | digital
N1DCS.10MAJ30AA002OD | 21551 | 凝汽器真空破坏气动门打开指令 |  | digital
N1DCS.10MAV10AH001PF | 21552 | #1机润滑油箱#1电加热器综合故障 |  | digital
N1DCS.10MAV10AH001PS | 21553 | #1机润滑油箱#1电加热器保护动作 |  | digital
N1DCS.10MAV10AH001RC | 21554 | #1机润滑油箱#1电加热器远方控制 |  | digital
N1DCS.10MAV10AH001RD | 21555 | #1机润滑油箱#1电加热器启动指令 |  | digital
N1DCS.10MAV10AH001RP | 21556 | #1机润滑油箱#1电加热器在运行 |  | digital
N1DCS.10MAV10AH001TD | 21557 | #1机润滑油箱#1电加热器停止指令 |  | digital
N1DCS.10MAV10AH001TP | 21558 | #1机润滑油箱#1电加热器已停止 |  | digital
N1DCS.10MAV10AH002PF | 21559 | #1机润滑油箱#2电加热器综合故障 |  | digital
N1DCS.10MAV10AH002PS | 21560 | #1机润滑油箱#2电加热器保护动作 |  | digital
N1DCS.10MAV10AH002RC | 21561 | #1机润滑油箱#2电加热器远方控制 |  | digital
N1DCS.10MAV10AH002RD | 21562 | #1机润滑油箱#2电加热器启动指令 |  | digital
N1DCS.10MAV10AH002RP | 21563 | #1机润滑油箱#2电加热器在运行 |  | digital
N1DCS.10MAV10AH002TD | 21564 | #1机润滑油箱#2电加热器停止指令 |  | digital
N1DCS.10MAV10AH002TP | 21565 | #1机润滑油箱#2电加热器已停止 |  | digital
N1DCS.10MAV21AP021PF | 21566 | #1机#1润滑油泵综合故障 |  | digital
N1DCS.10MAV21AP021RC | 21567 | #1机#1润滑油泵远方控制 |  | digital
N1DCS.10MAV21AP021RD | 21568 | #1机#1润滑油泵启动指令 |  | digital
N1DCS.10MAV21AP021RP | 21569 | #1机#1润滑油泵在运行 |  | digital
N1DCS.10MAV21AP021TD | 21570 | #1机#1润滑油泵停止指令 |  | digital
N1DCS.10MAV21AP021TP | 21571 | #1机#1润滑油泵已停止 |  | digital
N1DCS.10MAV21CP005L | 21572 | #1机#1润滑油泵出口压力低 |  | digital
N1DCS.10MAV31AP001PF | 21573 | #1机#1顶轴油泵综合故障 |  | digital
N1DCS.10MAV31AP001RC | 21574 | #1机#1顶轴油泵远方控制 |  | digital
N1DCS.10MAV31AP001RD | 21575 | #1机#1顶轴油泵启动指令 |  | digital
N1DCS.10MAV31AP001RP | 21576 | #1机#1顶轴油泵在运行 |  | digital
N1DCS.10MAV31AP001TD | 21577 | #1机#1顶轴油泵停止指令 |  | digital
N1DCS.10MAV31AP001TP | 21578 | #1机#1顶轴油泵已停止 |  | digital
N1DCS.10MAV82AN001PF | 21579 | #1机#1润滑油风机综合故障 |  | digital
N1DCS.10MAV82AN001RC | 21580 | #1机#1润滑油风机远方控制 |  | digital
N1DCS.10MAV82AN001RD | 21581 | #1机#1润滑油风机启动指令 |  | digital
N1DCS.10MAV82AN001RP | 21582 | #1机#1润滑油风机在运行 |  | digital
N1DCS.10MAV82AN001TD | 21583 | #1机#1润滑油风机停止指令 |  | digital
N1DCS.10MAV82AN001TP | 21584 | #1机#1润滑油风机已停止 |  | digital
N1DCS.10MAX01AP001PF | 21585 | #1机#1EH油泵综合故障 |  | digital
N1DCS.10MAX01AP001PS | 21586 | #1机#1EH油泵保护动作 |  | digital
N1DCS.10MAX01AP001RC | 21587 | #1机#1EH油泵远方控制 |  | digital
N1DCS.10MAX01AP001RD | 21588 | #1机#1EH油泵启动指令 |  | digital
N1DCS.10MAX01AP001RP | 21589 | #1机#1EH油泵在运行 |  | digital
N1DCS.10MAX01AP001TD | 21590 | #1机#1EH油泵停止指令 |  | digital
N1DCS.10MAX01AP001TP | 21591 | #1机#1EH油泵已停止 |  | digital
N1DCS.10MAX01AP011PF | 21592 | #1机#1EH油循环泵综合故障 |  | digital
N1DCS.10MAX01AP011RC | 21593 | #1机#1EH油循环泵远方控制 |  | digital
N1DCS.10MAX01AP011RD | 21594 | #1机#1EH油循环泵启动指令 |  | digital
N1DCS.10MAX01AP011RP | 21595 | #1机#1EH油循环泵在运行 |  | digital
N1DCS.10MAX01AP011TD | 21596 | #1机#1EH油循环泵停止指令 |  | digital
N1DCS.10MAX01AP011TP | 21597 | #1机#1EH油循环泵已停止 |  | digital
N1DCS.10MAX01CP004L | 21598 | #1机#1EH油循环泵出口压力低 |  | digital
N1DCS.10MAX01CP011H | 21599 | #1机#1EH油泵出口滤网差压高 |  | digital
N1DCS.10MAX01CP013H | 21600 | #1机#1EH油循环滤网差压高 |  | digital
N1DCS.10PAA11AA001CD | 21601 | #1旋转滤网冲洗水电动门关指令 |  | digital
N1DCS.10PAA11AA001CP | 21602 | #1旋转滤网冲洗水电动门全关位 |  | digital
N1DCS.10PAA11AA001F | 21603 | #1旋转滤网冲洗水电动门综合故障 |  | digital
N1DCS.10PAA11AA001OD | 21604 | #1旋转滤网冲洗水电动门开指令 |  | digital
N1DCS.10PAA11AA001OP | 21605 | #1旋转滤网冲洗水电动门全开位 |  | digital
N1DCS.10PAB11AA002CD | 21606 | #1循环水泵出口液控蝶阀全关指令 |  | digital
N1DCS.10PAB11AA002CDH | 21607 | #1循环水泵出口液控蝶阀半关指令 |  | digital
N1DCS.10PAB11AA002CER | 21608 | #1循环水泵出口液控蝶阀不能全关 |  | digital
N1DCS.10PAB11AA002CGLJ | 21609 | #1循环水泵出口液控蝶阀关过力矩 |  | digital
N1DCS.10PAB11AA002CL | 21610 | #1循环水泵出口碟阀事故关阀指令 |  | digital
N1DCS.10PAB11AA002CP | 21611 | #1循环水泵出口液控蝶阀正在关 |  | digital
N1DCS.10PAB11AA002CP1 | 21612 | #1循环水泵出口液控蝶阀全关位置 |  | digital
N1DCS.10PAB11AA002L1 | 21613 | #1循环水泵出口液控蝶阀阀位1 |  | digital
N1DCS.10PAB11AA002L2 | 21614 | #1循环水泵出口液控蝶阀阀位2 |  | digital
N1DCS.10PAB11AA002LP | 21615 | #1循环水泵出口液控蝶阀在就地 |  | digital
N1DCS.10PAB11AA002OD | 21616 | #1循环水泵出口液控蝶阀全开指令 |  | digital
N1DCS.10PAB11AA002ODH | 21617 | #1循环水泵出口液控蝶阀半开指令 |  | digital
N1DCS.10PAB11AA002OER | 21618 | #1循环水泵出口液控蝶阀不能全开 |  | digital
N1DCS.10PAB11AA002OGLJ | 21619 | #1循环水泵出口液控蝶阀开过力矩 |  | digital
N1DCS.10PAB11AA002OLF | 21620 | #1循环水泵出口液控蝶阀滤油堵塞 |  | digital
N1DCS.10PAB11AA002OLL | 21621 | #1循环水泵出口液控蝶阀油位低 |  | digital
N1DCS.10PAB11AA002OP | 21622 | #1循环水泵出口液控蝶阀正在开 |  | digital
N1DCS.10PAB11AA002OP1 | 21623 | #1循环水泵出口液控蝶阀全开位置 |  | digital
N1DCS.10PAB11AA002POF | 21624 | #1循环水泵出口液控蝶阀电源故障 |  | digital
N1DCS.10PAB11AA002ST | 21625 | #1循环水泵出口液控蝶阀停止指令 |  | digital
N1DCS.10PAB11AA002YK | 21626 | #1循环水泵出口液控蝶阀在远控 |  | digital
N1DCS.10PAB11AA002YYF | 21627 | #1循环水泵出口液控蝶阀液压故障 |  | digital
N1DCS.10PAB11AT001CD | 21628 | #1旋转滤网急停指令 |  | digital
N1DCS.10PAB11AT001DSQD | 21629 | #1旋转滤网低速定时启动 |  | digital
N1DCS.10PAB11AT001F | 21630 | #1旋转滤网故障 |  | digital
N1DCS.10PAB11AT001JT | 21631 | #1旋转滤网已急停 |  | digital
N1DCS.10PAB11AT001LC | 21632 | #1旋转滤网本地模式 |  | digital
N1DCS.10PAB11AT001QZ | 21633 | #1旋转滤网轻载 |  | digital
N1DCS.10PAB11AT001RC | 21634 | #1旋转滤网在远控 |  | digital
N1DCS.10PAB11AT001RD1 | 21635 | #1旋转滤网低速启动指令 |  | digital
N1DCS.10PAB11AT001RD2 | 21636 | #1旋转滤网高速启动指令 |  | digital
N1DCS.10PAB11AT001RP | 21637 | #1旋转滤网运行 |  | digital
N1DCS.10PAB11AT001RP1 | 21638 | #1旋转滤网低速运行 |  | digital
N1DCS.10PAB11AT001RP2 | 21639 | #1旋转滤网高速运行 |  | digital
N1DCS.10PAB11AT001SL1 | 21640 | #1旋转滤网松链1 |  | digital
N1DCS.10PAB11AT001SL2 | 21641 | #1旋转滤网松链2 |  | digital
N1DCS.10PAB11AT001ZZ | 21642 | #1旋转滤网重载 |  | digital
N1DCS.10PAB41AP001PF | 21643 | #1循环水泵#1加压泵综合故障 |  | digital
N1DCS.10PAB41AP001PS | 21644 | #1循环水泵#1加压泵保护动作 |  | digital
N1DCS.10PAB41AP001RC | 21645 | #1循环水泵#1加压泵在远控 |  | digital
N1DCS.10PAB41AP001RD | 21646 | #1循环水泵#1加压泵启动指令 |  | digital
N1DCS.10PAB41AP001RP | 21647 | #1循环水泵#1加压泵在运行 |  | digital
N1DCS.10PAB41AP001TD | 21648 | #1循环水泵#1加压泵停止指令 |  | digital
N1DCS.10PAB41AP001TP | 21649 | #1循环水泵#1加压泵已停止 |  | digital
N1DCS.10PAB42AP001PF | 21650 | #1循环水泵#2加压泵综合故障 |  | digital
N1DCS.10PAB42AP001PS | 21651 | #1循环水泵#2加压泵保护动作 |  | digital
N1DCS.10PAB42AP001RC | 21652 | #1循环水泵#2加压泵在远控 |  | digital
N1DCS.10PAB42AP001RD | 21653 | #1循环水泵#2加压泵启动指令 |  | digital
N1DCS.10PAB42AP001RP | 21654 | #1循环水泵#2加压泵在运行 |  | digital
N1DCS.10PAB42AP001TD | 21655 | #1循环水泵#2加压泵停止指令 |  | digital
N1DCS.10PAB42AP001TP | 21656 | #1循环水泵#2加压泵已停止 |  | digital
N1DCS.10PAB43CF001L | 21657 | #1循环水泵冷却水进口流量低 |  | digital
N1DCS.10PAB61AA001OD/CD | 21658 | 生活水至#1循泵电磁阀开/关指令 |  | digital
N1DCS.10PAB61AA001PF | 21659 | 生活水至#1循泵电磁阀无电源 |  | digital
N1DCS.10PAC11AP001CO | 21660 | #1、#2循环水泵均在运行且同速 |  | digital
N1DCS.10PAC11AP001OD0 | 21661 | #1循环水泵备用联启指令 |  | digital
N1DCS.10PAC11AP001PF | 21662 | #1循泵控制电源消失及装置故障 |  | digital
N1DCS.10PAC11AP001PFH | 21663 | #1循环水泵高速控制电源消失 |  | digital
N1DCS.10PAC11AP001PS | 21664 | #1循环水泵电气保护动作 |  | digital
N1DCS.10PAC11AP001RC | 21665 | #1循环水泵远方控制状态 |  | digital
N1DCS.10PAC11AP001RCH | 21666 | #1循环水泵高速在远控 |  | digital
N1DCS.10PAC11AP001RD | 21667 | #1循环水泵合闸指令 |  | digital
N1DCS.10PAC11AP001RDH | 21668 | #1循环水泵高速合闸指令 |  | digital
N1DCS.10PAC11AP001RDL | 21669 | #1循环水泵低速合闸指令 |  | digital
N1DCS.10PAC11AP001RP | 21670 | #1循环水泵在运行 |  | digital
N1DCS.10PAC11AP001RPH | 21671 | #1循环水泵高速运行 |  | digital
N1DCS.10PAC11AP001RPL | 21672 | #1循环水泵低速运行 |  | digital
N1DCS.10PAC11AP001SW | 21673 | #1循环水泵试验位置 |  | digital
N1DCS.10PAC11AP001TD | 21674 | #1循环水泵跳闸指令 |  | digital
N1DCS.10PAC11AP001TDH | 21675 | #1循环水泵高速跳闸指令 |  | digital
N1DCS.10PAC11AP001TDL | 21676 | #1循环水泵低速跳闸指令 |  | digital
N1DCS.10PAC11AP001TP | 21677 | #1循环水泵已停止 |  | digital
N1DCS.10PAC11AP001TP1 | 21678 | #1循环水泵已停止 |  | digital
N1DCS.10PAC11AP001TPH | 21679 | #1循环水泵高速停止 |  | digital
N1DCS.10PAC11AP001TPH1 | 21680 | #1循环水泵高速停止 |  | digital
N1DCS.10PAC11AP001TPL | 21681 | #1循环水泵低速停止 |  | digital
N1DCS.10PAC11AP001TPL1 | 21682 | #1循环水泵低速停止 |  | digital
N1DCS.10PAC11AP001YW | 21683 | #1循环水泵工作位置 |  | digital
N1DCS.10PAC12AP001CO | 21684 | #3、#4循环水泵均在运行且同速 |  | digital
N1DCS.10PSA01AP001PF | 21685 | #1冷却塔排水池#1排污泵综合故障 |  | digital
N1DCS.10PSA01AP001RC | 21686 | #1冷却塔排水池#1排污泵在远控 |  | digital
N1DCS.10PSA01AP001RD | 21687 | #1冷却塔排水池#1排污泵启动指令 |  | digital
N1DCS.10PSA01AP001RP | 21688 | #1冷却塔排水池#1排污泵在运行 |  | digital
N1DCS.10PSA01AP001TD | 21689 | #1冷却塔排水池#1排污泵停止指令 |  | digital
N1DCS.10PSA01AP001TP | 21690 | #1冷却塔排水池#1排污泵已停止 |  | digital
N1DCS.CIRPMPA_STPMT | 21691 | #1循环水泵启动允许 |  | digital
N1DCS.CIRPMPA_TEMALM | 21692 | #1循环水泵温度报警 |  | digital
N1DCS.CIRPMPA_TEMPMT | 21693 | #1循环水泵温度允许 |  | digital
N1DCS.CIRPMPA_TEMTRIP | 21694 | #1循环水泵温度保护跳闸信号 |  | digital
N1DCS.CIRPMPA_TP | 21695 | #1循环水泵跳闸信号 |  | digital
N1DCS.CIRPMPAMANSTOP | 21696 | #1循环水泵手动停止指令 |  | digital
N1DCS.CIRWTRPMPA_SEQSPOK | 21697 | #1循环水泵停顺控已成功完成 |  | digital
N1DCS.CIRWTRPMPA_SEQSTOK | 21698 | #1循环水泵启顺控已成功完成 |  | digital
N1DCS.CIRWTRPMPAFRMODE | 21699 | #1循环水泵注水模式 |  | digital
N1DCS.CNSRVACM_MRE | 21700 | 凝汽器真空坏点 |  | digital
N1DCS.EHOILSYS_SEQOK | 21701 | EH油系统EH油泵启动完成 |  | digital
N1DCS.EHOILSYS_SEQSPOK | 21702 | EN油系统停顺控已成功完成 |  | digital
N1DCS.EHOILSYS_SEQSTOK | 21703 | EH油系统启顺控已成功完成 |  | digital
N1DCS.LUBOILBOXTEM_MRE | 21704 | #1机润滑油箱温度坏点 |  | digital
N1DCS.LUBOILHTR_STPMT | 21705 | #1机润滑油电加热器启允许 |  | digital
N1DCS.ONE5 | 21706 | 开关量1 |  | digital
N1DCS.ROTFLTRAHSPDMODE | 21707 | #1旋转滤网预选高速 |  | digital
N1DCS.ROTFLTRAINTRFLSH | 21708 | #1旋转滤网联锁冲洗中 |  | digital
N1DCS.ROTFLTRAINTRON | 21709 | #1旋转滤网冲洗联锁投入 |  | digital
N1DCS.TEST1 | 21710 | 测试 |  | digital
N1DCS.TURBDRNALLCP | 21711 | #1机本体疏水门均已全关 |  | digital
N1DCS.TURBDRNALLOP | 21712 | #1机本体疏水门均已全开 |  | digital
N1DCS.TURBOILSYS_SEQSTFINISH | 21713 | #1机润滑油系统启顺控已完成 |  | digital
N1DCS.TURBOILSYS_SEQSTOK | 21714 | #1机润滑油系统启顺控已完成 |  | digital
N1DCS.VACMPMPA_PMT | 21715 | #1真空泵启动允许 |  | digital
N1DCS.VACMPMPA_SEQSTOK | 21716 | #1真空泵启顺控已成功完成 |  | digital
N1DCS.VACMPMPA_TEMALM | 21717 | #1真空泵温度报警 |  | digital
N1DCS.VACMPMPA_TEMPMT | 21718 | #1真空泵温度允许 |  | digital
N1DCS.VACMPMPA_TEMTRIP | 21719 | #1真空泵温度保护跳闸信号 |  | digital
N1DCS.VACMPMPA_TP | 21720 | #1真空泵跳闸信号 |  | digital
N1DCS.VACMPMPAMANSTOP | 21721 | #1真空泵逻辑联锁停止指令 |  | digital
N1DCS.VACMSYS_SEQSTFINISH | 21722 | 抽真空系统启顺控已成功完成 |  | digital
N1DCS.ZERO5 | 21723 | 开关量0 |  | digital
N1DCS.10MAJ21AA007CL | 21724 | #1真空泵汽水分离器补水阀自动关 |  | digital
N1DCS.10MAJ21AA007OP | 21725 | #1真空泵汽水分离器补水阀自动开 |  | digital
N1DCS.1XBBY | 21726 | #1循环水泵在备用状态 |  | digital
N1DCS.2XBBY | 21727 | #2循环水泵在备用状态 |  | digital
N1DCS.CIRPMPA_ALM | 21728 | #1循环水泵启允许 |  | digital
N1DCS.CIRWTRSYS_SEQFINISH | 21729 | 循环水系统启顺控已完成 |  | digital
N1DCS.XZLWADSSP | 21730 | #1旋转滤网低速自动停止指令 |  | digital
N1DCS.XZLWADSST | 21731 | #1旋转滤网低速自动启动指令 |  | digital
N1DCS.XZLWAGSSP | 21732 | #1旋转滤网高速自动停止指令 |  | digital
N1DCS.XZLWAGSST | 21733 | #1旋转滤网高速自动启动指令 |  | digital
N1DCS.XZLWDISU | 21734 | #1旋转滤网预选低速 |  | digital
N1DCS.XZLWGAOSU | 21735 | #1旋转滤网预选高速 |  | digital
N1DCS.ZQPSSYS_SEQSPFINISH | 21736 | Ovation Control Builder |  | digital
N1DCS.ZQPSSYS_SEQSTFINISH | 21737 | Ovation Control Builder |  | digital
N1DCS.10LBD20CP001H1 | 21738 | 冷再快关调阀进油滤网差压高 |  | digital
N1DCS.10LBD20CP111L | 21739 | 冷再快关调阀进油压力低 |  | digital
N1DCS.10LBD20GH101ESDA | 21740 | 热再快关调阀ESD动作 |  | digital
N1DCS.10LBD20GH101FL | 21741 | 热再快关调阀反馈消失 |  | digital
N1DCS.10LBD20GH101LC | 21742 | 热再快关调阀就地控制 |  | digital
N1DCS.10LBD20GH101OL | 21743 | 热再快关调阀指令消失 |  | digital
N1DCS.10LBD20GH101PF1 | 21744 | 热再快关调阀正常电源消失 |  | digital
N1DCS.10LBD20GH101PF2 | 21745 | 热再快关调阀备用电源消失 |  | digital
N1DCS.10LBD20GH101PL | 21746 | 热再快关调阀供油压力低 |  | digital
N1DCS.10LBD20GH101TL | 21747 | 热再快关调阀跟踪丢失 |  | digital
N1DCS.10LBD40CP001H1 | 21748 | 热再快关调阀进油滤网差压高 |  | digital
N1DCS.10LBD40CP111L | 21749 | 热再快关调阀进油压力低 |  | digital
N1DCS.10LBD40GH101ESDA | 21750 | 冷再快关调阀ESD动作 |  | digital
N1DCS.10LBD40GH101FL | 21751 | 冷再快关调阀反馈消失 |  | digital
N1DCS.10LBD40GH101LC | 21752 | 冷再快关调阀就地控制 |  | digital
N1DCS.10LBD40GH101OL | 21753 | 冷再快关调阀指令消失 |  | digital
N1DCS.10LBD40GH101PF1 | 21754 | 冷再快关调阀正常电源消失 |  | digital
N1DCS.10LBD40GH101PF2 | 21755 | 冷再快关调阀备用电源消失 |  | digital
N1DCS.10LBD40GH101PL | 21756 | 冷再快关调阀供油压力低 |  | digital
N1DCS.10LBD40GH101TL | 21757 | 冷再快关调阀跟踪丢失 |  | digital
N1DCS.10MAC45CP001H1 | 21758 | 低压补汽主汽门进油滤网差压高 |  | digital
N1DCS.10MAC45CP002L1 | 21759 | 低压补汽主汽门进油压力低 |  | digital
N1DCS.10MAC45GH101ESDA | 21760 | 低压补汽主汽门ESD动作 |  | digital
N1DCS.10MAC45GH101LC | 21761 | 低压补汽主汽门就地控制 |  | digital
N1DCS.10MAC45GH101PF1 | 21762 | 低压补汽主汽门正常电源消失 |  | digital
N1DCS.10MAC45GH101PF2 | 21763 | 低压补汽主汽门备用电源消失 |  | digital
N1DCS.10MAC45GH101PSTF | 21764 | 低压补汽主汽门PST故障 |  | digital
N1DCS.10MAC46CP001H1 | 21765 | 低压补汽调门进油滤网差压高 |  | digital
N1DCS.10MAC46CP101L | 21766 | 低压补汽调门进油压力低 |  | digital
N1DCS.10MAC46GH101ESDA | 21767 | 低压补汽调门ESD动作 |  | digital
N1DCS.10MAC46GH101FL | 21768 | 低压补汽调门反馈消失 |  | digital
N1DCS.10MAC46GH101LC | 21769 | 低压补汽调门就地控制 |  | digital
N1DCS.10MAC46GH101OL | 21770 | 低压补汽调门指令消失 |  | digital
N1DCS.10MAC46GH101PF1 | 21771 | 低压补汽调门正常电源消失 |  | digital
N1DCS.10MAC46GH101PF2 | 21772 | 低压补汽调门备用电源消失 |  | digital
N1DCS.10MAC46GH101PL | 21773 | 低压补汽调门供油压力低 |  | digital
N1DCS.10MAC46GH101TL | 21774 | 低压补汽调门跟踪丢失 |  | digital
N1DCS.10MAG22CL001H | 21775 | #2真空泵汽水分离器液位高 |  | digital
N1DCS.10MAG22CL002L | 21776 | #2真空泵汽水分离器液位低 |  | digital
N1DCS.10MAJ22AA001CD | 21777 | #2真空泵进口气动门2关闭指令 |  | digital
N1DCS.10MAJ22AA001CP | 21778 | #2真空泵进口气动门2全关位置 |  | digital
N1DCS.10MAJ22AA001F | 21779 | #2真空泵进口气动门2电源消失 |  | digital
N1DCS.10MAJ22AA001OD | 21780 | #2真空泵进口气动门2打开指令 |  | digital
N1DCS.10MAJ22AA001OP | 21781 | #2真空泵进口气动门2全开位置 |  | digital
N1DCS.10MAJ22AA007CL | 21782 | #2真空泵汽水分离器补水阀自动关 |  | digital
N1DCS.10MAJ22AA007F | 21783 | #2真空泵汽水分离器补水阀无电源 |  | digital
N1DCS.10MAJ22AA007OD/CD | 21784 | #2真空泵分离器补水阀开/关指令 |  | digital
N1DCS.10MAJ22AA007OP | 21785 | #2真空泵汽水分离器补水阀自动开 |  | digital
N1DCS.10MAJ22AA011CD | 21786 | #2真空泵进口气动门1关闭指令 |  | digital
N1DCS.10MAJ22AA011CP | 21787 | #2真空泵进口气动门1全关位置 |  | digital
N1DCS.10MAJ22AA011F | 21788 | #2真空泵进口气动门1电源消失 |  | digital
N1DCS.10MAJ22AA011OD | 21789 | #2真空泵进口气动门1打开指令 |  | digital
N1DCS.10MAJ22AA011OP | 21790 | #2真空泵进口气动门1全开位置 |  | digital
N1DCS.10MAJ22AP001PF | 21791 | #2真空泵综合故障 |  | digital
N1DCS.10MAJ22AP001PS | 21792 | #2真空泵电气保护动作 |  | digital
N1DCS.10MAJ22AP001RC | 21793 | #2真空泵远方控制 |  | digital
N1DCS.10MAJ22AP001RD | 21794 | #2真空泵启动指令 |  | digital
N1DCS.10MAJ22AP001RP | 21795 | #2真空泵在运行 |  | digital
N1DCS.10MAJ22AP001TD | 21796 | #2真空泵停止指令 |  | digital
N1DCS.10MAJ22AP001TP | 21797 | #2真空泵已停止 |  | digital
N1DCS.10MAV10AH003PF | 21798 | #1机润滑油箱#3电加热器综合故障 |  | digital
N1DCS.10MAV10AH003PS | 21799 | #1机润滑油箱#3电加热器保护动作 |  | digital
N1DCS.10MAV10AH003RC | 21800 | #1机润滑油箱#3电加热器远方控制 |  | digital
N1DCS.10MAV10AH003RD | 21801 | #1机润滑油箱#3电加热器启动指令 |  | digital
N1DCS.10MAV10AH003RP | 21802 | #1机润滑油箱#3电加热器在运行 |  | digital
N1DCS.10MAV10AH003TD | 21803 | #1机润滑油箱#3电加热器停止指令 |  | digital
N1DCS.10MAV10AH003TP | 21804 | #1机润滑油箱#3电加热器已停止 |  | digital
N1DCS.10MAV10AH004PF | 21805 | #1机润滑油箱#4电加热器综合故障 |  | digital
N1DCS.10MAV10AH004PS | 21806 | #1机润滑油箱#4电加热器保护动作 |  | digital
N1DCS.10MAV10AH004RC | 21807 | #1机润滑油箱#4电加热器远方控制 |  | digital
N1DCS.10MAV10AH004RD | 21808 | #1机润滑油箱#4电加热器启动指令 |  | digital
N1DCS.10MAV10AH004RP | 21809 | #1机润滑油箱#4电加热器在运行 |  | digital
N1DCS.10MAV10AH004TD | 21810 | #1机润滑油箱#4电加热器停止指令 |  | digital
N1DCS.10MAV10AH004TP | 21811 | #1机润滑油箱#4电加热器已停止 |  | digital
N1DCS.10MAV10CT011 | 21812 | #1机润滑油箱温度高 |  | digital
N1DCS.10MAV10CT012 | 21813 | #1机润滑油箱温度低 |  | digital
N1DCS.10MAV21AA321OD/CD | 21814 | #1机滑油泵出口电磁阀开/关指令 |  | digital
N1DCS.10MAV21AA321PF | 21815 | #1机滑油泵出口电磁阀无电源 |  | digital
N1DCS.10MAV21AP022PF | 21816 | #1机#2润滑油泵综合故障 |  | digital
N1DCS.10MAV21AP022RC | 21817 | #1机#2润滑油泵远方控制 |  | digital
N1DCS.10MAV21AP022RD | 21818 | #1机#2润滑油泵启动指令 |  | digital
N1DCS.10MAV21AP022RP | 21819 | #1机#2润滑油泵在运行 |  | digital
N1DCS.10MAV21AP022TD | 21820 | #1机#2润滑油泵停止指令 |  | digital
N1DCS.10MAV21AP022TP | 21821 | #1机#2润滑油泵已停止 |  | digital
N1DCS.10MAV21CP001L | 21822 | #1机润滑油泵出口母管压力低 |  | digital
N1DCS.10MAV21CP006L | 21823 | #1机#2润滑油泵出口压力低 |  | digital
N1DCS.10MAV24AP001PF | 21824 | #1机润滑油应急油泵综合故障 |  | digital
N1DCS.10MAV24AP001PS | 21825 | #1机润滑油应急油泵保护动作 |  | digital
N1DCS.10MAV24AP001RC | 21826 | #1机润滑油应急油泵远方控制 |  | digital
N1DCS.10MAV24AP001RD | 21827 | #1机润滑油应急油泵启动指令 |  | digital
N1DCS.10MAV24AP001RP | 21828 | #1机润滑油应急油泵在运行 |  | digital
N1DCS.10MAV24AP001TD | 21829 | #1机润滑油应急油泵停止指令 |  | digital
N1DCS.10MAV24AP001TP | 21830 | #1机润滑油应急油泵已停止 |  | digital
N1DCS.10MAV24CP001L | 21831 | #1机润滑油应急油泵出口压力低 |  | digital
N1DCS.10MAV32AP001PF | 21832 | #1机#2顶轴油泵综合故障 |  | digital
N1DCS.10MAV32AP001RC | 21833 | #1机#2顶轴油泵远方控制 |  | digital
N1DCS.10MAV32AP001RD | 21834 | #1机#2顶轴油泵启动指令 |  | digital
N1DCS.10MAV32AP001RP | 21835 | #1机#2顶轴油泵在运行 |  | digital
N1DCS.10MAV32AP001TD | 21836 | #1机#2顶轴油泵停止指令 |  | digital
N1DCS.10MAV32AP001TP | 21837 | #1机#2顶轴油泵已停止 |  | digital
N1DCS.10MAV35CP016H | 21838 | #1机顶轴油泵出口母管滤网差压高 |  | digital
N1DCS.10MAV42AA322OD/CD | 21839 | 润滑油母管试验电磁阀1开/关指令 |  | digital
N1DCS.10MAV42AA322PF | 21840 | 润滑油母管试验电磁阀1无电源 |  | digital
N1DCS.10MAV42AA329OD/CD | 21841 | 润滑油母管试验电磁阀2开/关指令 |  | digital
N1DCS.10MAV42AA329PF | 21842 | 润滑油母管试验电磁阀2无电源 |  | digital
N1DCS.10MAV42CP013H | 21843 | #1机润滑油泵出口母管滤网差压高 |  | digital
N1DCS.10MAV42CP019L | 21844 | #1机润滑油母管压力低 |  | digital
N1DCS.10MAV51AA012OD/CD | 21845 | #1机盘车电磁门打开/关闭指令 |  | digital
N1DCS.10MAV51AA012PF | 21846 | #1机盘车电磁门电源消失 |  | digital
N1DCS.10MAV82AN002PF | 21847 | #1机#2润滑油风机综合故障 |  | digital
N1DCS.10MAV82AN002RC | 21848 | #1机#2润滑油风机远方控制 |  | digital
N1DCS.10MAV82AN002RD | 21849 | #1机#2润滑油风机启动指令 |  | digital
N1DCS.10MAV82AN002RP | 21850 | #1机#2润滑油风机在运行 |  | digital
N1DCS.10MAV82AN002TD | 21851 | #1机#2润滑油风机停止指令 |  | digital
N1DCS.10MAV82AN002TP | 21852 | #1机#2润滑油风机已停止 |  | digital
N1DCS.10MAX01AP002PF | 21853 | #1机#2EH油泵综合故障 |  | digital
N1DCS.10MAX01AP002PS | 21854 | #1机#2EH油泵保护动作 |  | digital
N1DCS.10MAX01AP002RC | 21855 | #1机#2EH油泵远方控制 |  | digital
N1DCS.10MAX01AP002RD | 21856 | #1机#2EH油泵启动指令 |  | digital
N1DCS.10MAX01AP002RP | 21857 | #1机#2EH油泵在运行 |  | digital
N1DCS.10MAX01AP002TD | 21858 | #1机#2EH油泵停止指令 |  | digital
N1DCS.10MAX01AP002TP | 21859 | #1机#2EH油泵已停止 |  | digital
N1DCS.10MAX01AP012PF | 21860 | #1机#2EH油循环泵综合故障 |  | digital
N1DCS.10MAX01AP012RC | 21861 | #1机#2EH油循环泵远方控制 |  | digital
N1DCS.10MAX01AP012RD | 21862 | #1机#2EH油循环泵启动指令 |  | digital
N1DCS.10MAX01AP012RP | 21863 | #1机#2EH油循环泵在运行 |  | digital
N1DCS.10MAX01AP012TD | 21864 | #1机#2EH油循环泵停止指令 |  | digital
N1DCS.10MAX01AP012TP | 21865 | #1机#2EH油循环泵已停止 |  | digital
N1DCS.10MAX01CL001X0 | 21866 | #1机EH油箱液位 |  | digital
N1DCS.10MAX01CL001X0H | 21867 | #1机EH油箱液位高 |  | digital
N1DCS.10MAX01CL001X0LL | 21868 | #1机EH油箱液位低低 |  | digital
N1DCS.10MAX01CL002L | 21869 | #1机EH油箱液位低 |  | digital
N1DCS.10MAX01CL002LLL | 21870 | #1机EH油箱液位低低低 |  | digital
N1DCS.10MAX01CP005L | 21871 | #1机#2EH油循环泵出口压力低 |  | digital
N1DCS.10MAX01CP012H | 21872 | #1机#2EH油泵出口滤网差压高 |  | digital
N1DCS.10MAX01CP014H | 21873 | #1机#2EH油循环滤网差压高 |  | digital
N1DCS.10PAA12AA001CD | 21874 | #1旋转滤网冲洗水电动门关指令 |  | digital
N1DCS.10PAA12AA001CP | 21875 | #1旋转滤网冲洗水电动门全关位 |  | digital
N1DCS.10PAA12AA001F | 21876 | #1旋转滤网冲洗水电动门综合故障 |  | digital
N1DCS.10PAA12AA001OD | 21877 | #1旋转滤网冲洗水电动门开指令 |  | digital
N1DCS.10PAA12AA001OP | 21878 | #1旋转滤网冲洗水电动门全开位 |  | digital
N1DCS.10PAB10AA001CD | 21879 | 循环水母管电动联络门关闭指令 |  | digital
N1DCS.10PAB10AA001CP | 21880 | 循环水母管电动联络门全关位置 |  | digital
N1DCS.10PAB10AA001F | 21881 | 循环水母管电动联络门综合故障 |  | digital
N1DCS.10PAB10AA001OD | 21882 | 循环水母管电动联络门打开指令 |  | digital
N1DCS.10PAB10AA001OP | 21883 | 循环水母管电动联络门全开位置 |  | digital
N1DCS.10PAB10AA001RC | 21884 | 循环水母管电动联络门在远控 |  | digital
N1DCS.10PAB12AA002CD | 21885 | #2循环水泵出口液控蝶阀全关指令 |  | digital
N1DCS.10PAB12AA002CDH | 21886 | #2循环水泵出口液控蝶阀半关指令 |  | digital
N1DCS.10PAB12AA002CER | 21887 | #2循环水泵出口液控蝶阀不能全关 |  | digital
N1DCS.10PAB12AA002CGLJ | 21888 | #2循环水泵出口液控蝶阀关过力矩 |  | digital
N1DCS.10PAB12AA002CL | 21889 | #2循环水泵出口碟阀事故关阀指令 |  | digital
N1DCS.10PAB12AA002CP | 21890 | #2循环水泵出口液控蝶阀正在关 |  | digital
N1DCS.10PAB12AA002CP1 | 21891 | #2循环水泵出口液控蝶阀全关位置 |  | digital
N1DCS.10PAB12AA002L1 | 21892 | #2循环水泵出口液控蝶阀阀位1 |  | digital
N1DCS.10PAB12AA002L2 | 21893 | #2循环水泵出口液控蝶阀阀位2 |  | digital
N1DCS.10PAB12AA002LP | 21894 | #2循环水泵出口液控蝶阀在就地 |  | digital
N1DCS.10PAB12AA002OD | 21895 | #2循环水泵出口液控蝶阀全开指令 |  | digital
N1DCS.10PAB12AA002ODH | 21896 | #2循环水泵出口液控蝶阀半开指令 |  | digital
N1DCS.10PAB12AA002OER | 21897 | #2循环水泵出口液控蝶阀不能全开 |  | digital
N1DCS.10PAB12AA002OGLJ | 21898 | #2循环水泵出口液控蝶阀开过力矩 |  | digital
N1DCS.10PAB12AA002OLF | 21899 | #2循环水泵出口液控蝶阀滤油堵塞 |  | digital
N1DCS.10PAB12AA002OLL | 21900 | #2循环水泵出口液控蝶阀油位低 |  | digital
N1DCS.10PAB12AA002OP | 21901 | #2循环水泵出口液控蝶阀正在开 |  | digital
N1DCS.10PAB12AA002OP1 | 21902 | #2循环水泵出口液控蝶阀全开位置 |  | digital
N1DCS.10PAB12AA002POF | 21903 | #2循环水泵出口液控蝶阀电源故障 |  | digital
N1DCS.10PAB12AA002ST | 21904 | #2循环水泵出口液控蝶阀停止指令 |  | digital
N1DCS.10PAB12AA002YK | 21905 | #2循环水泵出口液控蝶阀在远控 |  | digital
N1DCS.10PAB12AA002YYF | 21906 | #2循环水泵出口液控蝶阀液压故障 |  | digital
N1DCS.10PAB12AT001CD | 21907 | #2旋转滤网急停指令 |  | digital
N1DCS.10PAB12AT001DSQD | 21908 | #2旋转滤网低速定时启动 |  | digital
N1DCS.10PAB12AT001F | 21909 | #2旋转滤网故障 |  | digital
N1DCS.10PAB12AT001JT | 21910 | #2旋转滤网已急停 |  | digital
N1DCS.10PAB12AT001LC | 21911 | #2旋转滤网本地模式 |  | digital
N1DCS.10PAB12AT001QZ | 21912 | #2旋转滤网轻载 |  | digital
N1DCS.10PAB12AT001RC | 21913 | #2旋转滤网在远控 |  | digital
N1DCS.10PAB12AT001RD1 | 21914 | #2旋转滤网低速启动指令 |  | digital
N1DCS.10PAB12AT001RD2 | 21915 | #2旋转滤网高速启动指令 |  | digital
N1DCS.10PAB12AT001RP | 21916 | #2旋转滤网运行 |  | digital
N1DCS.10PAB12AT001RP1 | 21917 | #2旋转滤网低速运行 |  | digital
N1DCS.10PAB12AT001RP2 | 21918 | #2旋转滤网高速运行 |  | digital
N1DCS.10PAB12AT001SL1 | 21919 | #2旋转滤网松链1 |  | digital
N1DCS.10PAB12AT001SL2 | 21920 | #2旋转滤网松链2 |  | digital
N1DCS.10PAB12AT001ZZ | 21921 | #2旋转滤网重载 |  | digital
N1DCS.10PAB31AA002CD | 21922 | 循环水母管至循泵冷却水门关指令 |  | digital
N1DCS.10PAB31AA002CP | 21923 | 循环水母管至循泵冷却水门全关位 |  | digital
N1DCS.10PAB31AA002OD | 21924 | 循环水母管至循泵冷却水门开指令 |  | digital
N1DCS.10PAB31AA002OP | 21925 | 循环水母管至循泵冷却水门全开位 |  | digital
N1DCS.10PAB51AP001PF | 21926 | #2循环水泵#1加压泵综合故障 |  | digital
N1DCS.10PAB51AP001PS | 21927 | #2循环水泵#1加压泵保护动作 |  | digital
N1DCS.10PAB51AP001RC | 21928 | #2循环水泵#1加压泵在远控 |  | digital
N1DCS.10PAB51AP001RD | 21929 | #2循环水泵#1加压泵启动指令 |  | digital
N1DCS.10PAB51AP001RP | 21930 | #2循环水泵#1加压泵在运行 |  | digital
N1DCS.10PAB51AP001TD | 21931 | #2循环水泵#1加压泵停止指令 |  | digital
N1DCS.10PAB51AP001TP | 21932 | #2循环水泵#1加压泵已停止 |  | digital
N1DCS.10PAB52AP001PF | 21933 | #2循环水泵#2加压泵综合故障 |  | digital
N1DCS.10PAB52AP001PS | 21934 | #2循环水泵#2加压泵保护动作 |  | digital
N1DCS.10PAB52AP001RC | 21935 | #2循环水泵#2加压泵在远控 |  | digital
N1DCS.10PAB52AP001RD | 21936 | #2循环水泵#2加压泵启动指令 |  | digital
N1DCS.10PAB52AP001RP | 21937 | #2循环水泵#2加压泵在运行 |  | digital
N1DCS.10PAB52AP001TD | 21938 | #2循环水泵#2加压泵停止指令 |  | digital
N1DCS.10PAB52AP001TP | 21939 | #2循环水泵#2加压泵已停止 |  | digital
N1DCS.10PAB53CF001L | 21940 | #2循环水泵冷却水进口流量低 |  | digital
N1DCS.10PAB62AA001OD/CD | 21941 | 生活水至#2循泵电磁阀开/关指令 |  | digital
N1DCS.10PAB62AA001PF | 21942 | 生活水至#2循泵电磁阀无电源 |  | digital
N1DCS.10PAC12AP001LP | 21943 | #1、#2循环水泵均在运行且同速 |  | digital
N1DCS.10PAC12AP001PF | 21944 | #2循泵控制电源消失及装置故障 |  | digital
N1DCS.10PAC12AP001PFH | 21945 | #2循环水泵高速控制电源消失 |  | digital
N1DCS.10PAC12AP001PFL | 21946 | #2循环水泵低速控制电源消失 |  | digital
N1DCS.10PAC12AP001RC | 21947 | #2循环水泵在远控 |  | digital
N1DCS.10PAC12AP001RCH | 21948 | #2循环水泵高速在远控 |  | digital
N1DCS.10PAC12AP001RCL | 21949 | #2循环水泵低速在远控 |  | digital
N1DCS.10PAC12AP001RD | 21950 | #2循环水泵合闸指令 |  | digital
N1DCS.10PAC12AP001RDH | 21951 | #2循环水泵高速合闸指令 |  | digital
N1DCS.10PAC12AP001RDL | 21952 | #2循环水泵低速合闸指令 |  | digital
N1DCS.10PAC12AP001RP | 21953 | #2循环水泵在运行 |  | digital
N1DCS.10PAC12AP001RPH | 21954 | #2循环水泵高速运行 |  | digital
N1DCS.10PAC12AP001RPL | 21955 | #2循环水泵低速运行 |  | digital
N1DCS.10PAC12AP001SW | 21956 | #2循环水泵试验位置 |  | digital
N1DCS.10PAC12AP001TD | 21957 | #2循环水泵跳闸指令 |  | digital
N1DCS.10PAC12AP001TD0 | 21958 | #2循环水泵跳闸指令 |  | digital
N1DCS.10PAC12AP001TDH | 21959 | #2循环水泵高速跳闸指令 |  | digital
N1DCS.10PAC12AP001TDL | 21960 | #2循环水泵低速跳闸指令 |  | digital
N1DCS.10PAC12AP001TP | 21961 | #2循环水泵已停止 |  | digital
N1DCS.10PAC12AP001TP1 | 21962 | #2循环水泵已停止 |  | digital
N1DCS.10PAC12AP001TPH | 21963 | #2循环水泵高速停止 |  | digital
N1DCS.10PAC12AP001TPH1 | 21964 | #2循环水泵高速停止 |  | digital
N1DCS.10PAC12AP001TPL | 21965 | #2循环水泵低速停止 |  | digital
N1DCS.10PAC12AP001TPL1 | 21966 | #2循环水泵低速停止 |  | digital
N1DCS.10PAC12AP001YW | 21967 | #2循环水泵工作位置 |  | digital
N1DCS.10PAR01AA001CD | 21968 | #1冷却塔进口电动蝶门关闭指令 |  | digital
N1DCS.10PAR01AA001CP | 21969 | #1冷却塔进口电动蝶门全关位置 |  | digital
N1DCS.10PAR01AA001F | 21970 | #1冷却塔进口电动蝶门综合故障 |  | digital
N1DCS.10PAR01AA001OD | 21971 | #1冷却塔进口电动蝶门打开指令 |  | digital
N1DCS.10PAR01AA001OP | 21972 | #1冷却塔进口电动蝶门全开位置 |  | digital
N1DCS.10PAR01AA001RC | 21973 | #1冷却塔进口电动蝶门在远控 |  | digital
N1DCS.10PAR01AA002AUTO | 21974 | #1冷却塔进口流量调节门在自动 |  | digital
N1DCS.10PAR01AA002DVHI | 21975 | #1冷却塔进口调门指令反馈偏差大 |  | digital
N1DCS.10PAR01AA002F | 21976 | #1冷却塔进口流量调节门故障 |  | digital
N1DCS.10PAR01AA002RC | 21977 | #1冷却塔进口流量调节门在远控 |  | digital
N1DCS.10PAR01AA002SPDH | 21978 | #1冷却塔进口调门速度反馈偏差大 |  | digital
N1DCS.10PSA02AP001PF | 21979 | #1冷却塔排水池#2排污泵综合故障 |  | digital
N1DCS.10PSA02AP001RC | 21980 | #1冷却塔排水池#2排污泵在远控 |  | digital
N1DCS.10PSA02AP001RD | 21981 | #1冷却塔排水池#2排污泵启动指令 |  | digital
N1DCS.10PSA02AP001RP | 21982 | #1冷却塔排水池#2排污泵在运行 |  | digital
N1DCS.10PSA02AP001TD | 21983 | #1冷却塔排水池#2排污泵停止指令 |  | digital
N1DCS.10PSA02AP001TP | 21984 | #1冷却塔排水池#2排污泵已停止 |  | digital
N1DCS.CIRPMPB_STPMT | 21985 | #2循环水泵启动允许 |  | digital
N1DCS.CIRPMPB_TEMALM | 21986 | #2循环水泵温度报警 |  | digital
N1DCS.CIRPMPB_TEMPMT | 21987 | #2循环水泵温度允许 |  | digital
N1DCS.CIRPMPB_TEMTRIP | 21988 | #2循环水泵温度保护跳闸信号 |  | digital
N1DCS.CIRPMPB_TP | 21989 | #2循环水泵跳闸信号 |  | digital
N1DCS.CIRPMPBMANSTOP | 21990 | #2循环水泵手动停止指令 |  | digital
N1DCS.CIRWTRPMPB_SEQSPOK | 21991 | #2循环水泵停顺控已成功完成 |  | digital
N1DCS.CIRWTRPMPB_SEQSTOK | 21992 | #2循环水泵启顺控已成功完成 |  | digital
N1DCS.CIRWTRPMPBFRMODE | 21993 | #2循环水泵注水模式 |  | digital
N1DCS.CLEANOILBOXLVL_MRE | 21994 | 净油箱液位坏点 |  | digital
N1DCS.DCEMGOILP_BK | 21995 | #1机应急油泵联锁备用投入 |  | digital
N1DCS.EHOILSPLPRS_MRE | 21996 | #1机EH供油压力坏点 |  | digital
N1DCS.ONE6 | 21997 | 开关量1 |  | digital
N1DCS.ROTFLTRBHSPDMODE | 21998 | #2旋转滤网预选高速 |  | digital
N1DCS.ROTFLTRBINTRFLSH | 21999 | #2旋转滤网联锁冲洗中 |  | digital
N1DCS.ROTFLTRBINTRON | 22000 | #2旋转滤网冲洗联锁投入 |  | digital
N1DCS.VACMPMPB_PMT | 22001 | #2真空泵启动允许 |  | digital
N1DCS.VACMPMPB_SEQSTOK | 22002 | #2真空泵启顺控已成功完成 |  | digital
N1DCS.VACMPMPB_TEMALM | 22003 | #2真空泵温度报警 |  | digital
N1DCS.VACMPMPB_TEMPMT | 22004 | #2真空泵温度允许 |  | digital
N1DCS.VACMPMPB_TEMTRIP | 22005 | #2真空泵超温保护跳闸 |  | digital
N1DCS.VACMPMPB_TP | 22006 | #2真空泵跳闸信号 |  | digital
N1DCS.VACMPMPBMANSTOP | 22007 | #2真空泵逻辑联锁停止指令 |  | digital
N1DCS.ZERO6 | 22008 | 开关量0 |  | digital
N1DCS.2XZLWDISU | 22009 | #2旋转滤网预选低速 |  | digital
N1DCS.2XZLWGAOSU | 22010 | #2旋转滤网预选高速 |  | digital
N1DCS.CIRPMPB_ALM | 22011 | #2循环水泵启允许 |  | digital
N1DCS.XZLWBDSSP | 22012 | #2旋转滤网低速自动停止指令 |  | digital
N1DCS.XZLWBDSST | 22013 | #2旋转滤网低速自动启动指令 |  | digital
N1DCS.XZLWBGSSP | 22014 | #2旋转滤网高速自动停止指令 |  | digital
N1DCS.XZLWBGSST | 22015 | #2旋转滤网高速自动启动指令 |  | digital
N1DCS.10CDB76XB01 | 22016 | 低压汽包水位摄像综合故障 |  | digital
N1DCS.10CDB76YB01 | 22017 | 低压汽包水位A侧画面显示 |  | digital
N1DCS.10CDB76YB02 | 22018 | 低压汽包水位B侧画面显示 |  | digital
N1DCS.10CDB76YB03 | 22019 | 低压汽包水位AB侧合成画面显示 |  | digital
N1DCS.10CDB76YB31 | 22020 | 高中低压汽包水位合成画面显示 |  | digital
N1DCS.10CDB77XB03 | 22021 | 低压汽包水位A侧超温报警 |  | digital
N1DCS.10CDB77YB01 | 22022 | 低压汽包水位A侧光圈+ |  | digital
N1DCS.10CDB77YB02 | 22023 | 低压汽包水位A侧光圈- |  | digital
N1DCS.10CDB77YB11 | 22024 | 低压汽包水位A侧变倍+ |  | digital
N1DCS.10CDB77YB12 | 22025 | 低压汽包水位A侧变倍- |  | digital
N1DCS.10CDB77YB21 | 22026 | 低压汽包水位A侧焦距+ |  | digital
N1DCS.10CDB77YB22 | 22027 | 低压汽包水位A侧焦距- |  | digital
N1DCS.10CDB78XB03 | 22028 | 低压汽包水位B侧超温报警 |  | digital
N1DCS.10CDB78YB01 | 22029 | 低压汽包水位B侧光圈+ |  | digital
N1DCS.10CDB78YB02 | 22030 | 低压汽包水位B侧光圈- |  | digital
N1DCS.10CDB78YB11 | 22031 | 低压汽包水位B侧变倍+ |  | digital
N1DCS.10CDB78YB12 | 22032 | 低压汽包水位B侧变倍- |  | digital
N1DCS.10CDB78YB21 | 22033 | 低压汽包水位B侧焦距+ |  | digital
N1DCS.10CDB78YB22 | 22034 | 低压汽包水位B侧焦距- |  | digital
N1DCS.10HAD70CL001F | 22035 | 低压汽包左电接点水位计故障 |  | digital
N1DCS.10HAD70CL001H | 22036 | 低压汽包左电接点水位计高I |  | digital
N1DCS.10HAD70CL001HH | 22037 | 低压汽包左电接点水位计高II |  | digital
N1DCS.10HAD70CL001HHH | 22038 | 低压汽包左电接点水位计高III |  | digital
N1DCS.10HAD70CL001L | 22039 | 低压汽包左电接点水位计低I |  | digital
N1DCS.10HAD70CL001LL | 22040 | 低压汽包左电接点水位计低II |  | digital
N1DCS.10HAD70CL001LLL | 22041 | 低压汽包左电接点水位计低III |  | digital
N1DCS.10HAD70CL002F | 22042 | 低压汽包右电接点水位计故障 |  | digital
N1DCS.10HAD70CL002H | 22043 | 低压汽包右电接点水位计高I |  | digital
N1DCS.10HAD70CL002HH | 22044 | 低压汽包右电接点水位计高II |  | digital
N1DCS.10HAD70CL002HHH | 22045 | 低压汽包右电接点水位计高III |  | digital
N1DCS.10HAD70CL002L | 22046 | 低压汽包右电接点水位计低I |  | digital
N1DCS.10HAD70CL002LL | 22047 | 低压汽包右电接点水位计低II |  | digital
N1DCS.10HAD70CL002LLL | 22048 | 低压汽包右电接点水位计低III |  | digital
N1DCS.10HAD70CLHH1 | 22049 | 低压汽包液位1高高高 |  | digital
N1DCS.10HAD70CLHH2 | 22050 | 低压汽包液位2高高高 |  | digital
N1DCS.10HAD70CLHH3 | 22051 | 低压汽包液位3高高高 |  | digital
N1DCS.10HAD70CLLL1 | 22052 | 低压汽包液位1低低低 |  | digital
N1DCS.10HAD70CLLL2 | 22053 | 低压汽包液位2低低低 |  | digital
N1DCS.10HAD70CLLL3 | 22054 | 低压汽包液位3低低低 |  | digital
N1DCS.10HAD74AA401CD | 22055 | 低压蒸发器定排电动门关指令 |  | digital
N1DCS.10HAD74AA401CP | 22056 | 低压蒸发器定排电动门关到位 |  | digital
N1DCS.10HAD74AA401F | 22057 | 低压蒸发器定排电动门故障 |  | digital
N1DCS.10HAD74AA401OD | 22058 | 低压蒸发器定排电动门开指令 |  | digital
N1DCS.10HAD74AA401OP | 22059 | 低压蒸发器定排电动门开到位 |  | digital
N1DCS.10HAD74AA401RC | 22060 | 低压蒸发器定排电动门在远控 |  | digital
N1DCS.10HAD75AA001CD | 22061 | 低压汽包连排电动门关指令 |  | digital
N1DCS.10HAD75AA001CP | 22062 | 低压汽包连排电动门关到位 |  | digital
N1DCS.10HAD75AA001F | 22063 | 低压汽包连排电动门故障 |  | digital
N1DCS.10HAD75AA001OD | 22064 | 低压汽包连排电动门开指令 |  | digital
N1DCS.10HAD75AA001OP | 22065 | 低压汽包连排电动门开到位 |  | digital
N1DCS.10HAD75AA001RC | 22066 | 低压汽包连排电动门在远控 |  | digital
N1DCS.10HAD76AA001CD | 22067 | 低压汽包启动放水电动门关指令 |  | digital
N1DCS.10HAD76AA001CP | 22068 | 低压汽包启动放水电动门关到位 |  | digital
N1DCS.10HAD76AA001F | 22069 | 低压汽包启动放水电动门故障 |  | digital
N1DCS.10HAD76AA001OD | 22070 | 低压汽包启动放水电动门开指令 |  | digital
N1DCS.10HAD76AA001OP | 22071 | 低压汽包启动放水电动门开到位 |  | digital
N1DCS.10HAD76AA001RC | 22072 | 低压汽包启动放水电动门在远控 |  | digital
N1DCS.10HAD76AA002CD | 22073 | 低压汽包启动放水调节门关指令 |  | digital
N1DCS.10HAD76AA002CP | 22074 | 低压汽包启动放水调节门关到位 |  | digital
N1DCS.10HAD76AA002F | 22075 | 低压汽包启动放水调节门故障 |  | digital
N1DCS.10HAD76AA002OD | 22076 | 低压汽包启动放水调节门开指令 |  | digital
N1DCS.10HAD76AA002OP | 22077 | 低压汽包启动放水调节门开到位 |  | digital
N1DCS.10HAD76AA002RC | 22078 | 低压汽包启动放水调节门在远控 |  | digital
N1DCS.10HAH70AA502CD | 22079 | 低压饱和蒸汽放空电动门关指令 |  | digital
N1DCS.10HAH70AA502CP | 22080 | 低压饱和蒸汽放空电动门关到位 |  | digital
N1DCS.10HAH70AA502F | 22081 | 低压饱和蒸汽放空电动门故障 |  | digital
N1DCS.10HAH70AA502OD | 22082 | 低压饱和蒸汽放空电动门开指令 |  | digital
N1DCS.10HAH70AA502OP | 22083 | 低压饱和蒸汽放空电动门开到位 |  | digital
N1DCS.10HAH70AA502RC | 22084 | 低压饱和蒸汽放空电动门在远控 |  | digital
N1DCS.10HAJ80AA502CD | 22085 | 一级再热器进口集箱放空门关指令 |  | digital
N1DCS.10HAJ80AA502CP | 22086 | 一级再热器进口集箱放空门关到位 |  | digital
N1DCS.10HAJ80AA502F | 22087 | 一级再热器进口集箱放空门故障 |  | digital
N1DCS.10HAJ80AA502OD | 22088 | 一级再热器进口集箱放空门开指令 |  | digital
N1DCS.10HAJ80AA502OP | 22089 | 一级再热器进口集箱放空门开到位 |  | digital
N1DCS.10HAJ80AA502RC | 22090 | 一级再热器进口集箱放空门在远控 |  | digital
N1DCS.10HAJ80AA504CD | 22091 | 一级再热器出口集箱放空门关指令 |  | digital
N1DCS.10HAJ80AA504CP | 22092 | 一级再热器出口集箱放空门关到位 |  | digital
N1DCS.10HAJ80AA504F | 22093 | 一级再热器出口集箱放空门故障 |  | digital
N1DCS.10HAJ80AA504OD | 22094 | 一级再热器出口集箱放空门开指令 |  | digital
N1DCS.10HAJ80AA504OP | 22095 | 一级再热器出口集箱放空门开到位 |  | digital
N1DCS.10HAJ80AA504RC | 22096 | 一级再热器出口集箱放空门在远控 |  | digital
N1DCS.10HAJ81AA402CD | 22097 | 一级再热器连接管疏水门关指令 |  | digital
N1DCS.10HAJ81AA402CP | 22098 | 一级再热器连接管疏水门关到位 |  | digital
N1DCS.10HAJ81AA402F | 22099 | 一级再热器连接管疏水门故障 |  | digital
N1DCS.10HAJ81AA402OD | 22100 | 一级再热器连接管疏水门开指令 |  | digital
N1DCS.10HAJ81AA402OP | 22101 | 一级再热器连接管疏水门开到位 |  | digital
N1DCS.10HAJ81AA402RC | 22102 | 一级再热器连接管疏水门在远控 |  | digital
N1DCS.10HAJ81AA404CD | 22103 | 二级再热器进口疏水电动门关指令 |  | digital
N1DCS.10HAJ81AA404CP | 22104 | 二级再热器进口疏水电动门关到位 |  | digital
N1DCS.10HAJ81AA404F | 22105 | 二级再热器进口疏水电动门故障 |  | digital
N1DCS.10HAJ81AA404OD | 22106 | 二级再热器进口疏水电动门开指令 |  | digital
N1DCS.10HAJ81AA404OP | 22107 | 二级再热器进口疏水电动门开到位 |  | digital
N1DCS.10HAJ81AA404RC | 22108 | 二级再热器进口疏水电动门在远控 |  | digital
N1DCS.10LAA70AA501CD | 22109 | #1炉除氧头放空电动门关指令 |  | digital
N1DCS.10LAA70AA501CP | 22110 | #1炉除氧头放空电动门关到位 |  | digital
N1DCS.10LAA70AA501F | 22111 | #1炉除氧头放空电动门故障 |  | digital
N1DCS.10LAA70AA501OD | 22112 | #1炉除氧头放空电动门开指令 |  | digital
N1DCS.10LAA70AA501OP | 22113 | #1炉除氧头放空电动门开到位 |  | digital
N1DCS.10LAA70AA501RC | 22114 | #1炉除氧头放空电动门在远控 |  | digital
N1DCS.10LAB70AA101_MRE | 22115 | #1炉低压汽包液位坏点 |  | digital
N1DCS.10LAF80AA002CD | 22116 | 一级再热器减温水电动门关指令 |  | digital
N1DCS.10LAF80AA002CP | 22117 | 一级再热器减温水电动门关到位 |  | digital
N1DCS.10LAF80AA002F | 22118 | 一级再热器减温水电动门故障 |  | digital
N1DCS.10LAF80AA002OD | 22119 | 一级再热器减温水电动门开指令 |  | digital
N1DCS.10LAF80AA002OP | 22120 | 一级再热器减温水电动门开到位 |  | digital
N1DCS.10LAF80AA002RC | 22121 | 一级再热器减温水电动门在远控 |  | digital
N1DCS.10LAF80AA004CD | 22122 | 二级再热器减温水电动门关指令 |  | digital
N1DCS.10LAF80AA004CP | 22123 | 二级再热器减温水电动门关到位 |  | digital
N1DCS.10LAF80AA004F | 22124 | 二级再热器减温水电动门故障 |  | digital
N1DCS.10LAF80AA004OD | 22125 | 二级再热器减温水电动门开指令 |  | digital
N1DCS.10LAF80AA004OP | 22126 | 二级再热器减温水电动门开到位 |  | digital
N1DCS.10LAF80AA004RC | 22127 | 二级再热器减温水电动门在远控 |  | digital
N1DCS.10LAF80AA101_MRE | 22128 | 一级再热器减温器后温度坏点 |  | digital
N1DCS.10LAF80AA102_MRE | 22129 | 热再主蒸汽温度坏点 |  | digital
N1DCS.10LBA70AA402CD | 22130 | 低压过热器出口疏水电动门关指令 |  | digital
N1DCS.10LBA70AA402CP | 22131 | 低压过热器出口疏水电动门关到位 |  | digital
N1DCS.10LBA70AA402F | 22132 | 低压过热器出口疏水电动门故障 |  | digital
N1DCS.10LBA70AA402OD | 22133 | 低压过热器出口疏水电动门开指令 |  | digital
N1DCS.10LBA70AA402OP | 22134 | 低压过热器出口疏水电动门开到位 |  | digital
N1DCS.10LBA70AA402RC | 22135 | 低压过热器出口疏水电动门在远控 |  | digital
N1DCS.10LBA70AA502CD | 22136 | 低压过热器启动排汽电动门关指令 |  | digital
N1DCS.10LBA70AA502CP | 22137 | 低压过热器启动排汽电动门关到位 |  | digital
N1DCS.10LBA70AA502F | 22138 | 低压过热器启动排汽电动门故障 |  | digital
N1DCS.10LBA70AA502OD | 22139 | 低压过热器启动排汽电动门开指令 |  | digital
N1DCS.10LBA70AA502OP | 22140 | 低压过热器启动排汽电动门开到位 |  | digital
N1DCS.10LBA70AA502RC | 22141 | 低压过热器启动排汽电动门在远控 |  | digital
N1DCS.10LBB80AA502CD | 22142 | 热再主蒸汽启动排气电动门关指令 |  | digital
N1DCS.10LBB80AA502CP | 22143 | 热再主蒸汽启动排气电动门关到位 |  | digital
N1DCS.10LBB80AA502F | 22144 | 热再主蒸汽启动排气电动门故障 |  | digital
N1DCS.10LBB80AA502OD | 22145 | 热再主蒸汽启动排气电动门开指令 |  | digital
N1DCS.10LBB80AA502OP | 22146 | 热再主蒸汽启动排气电动门开到位 |  | digital
N1DCS.10LBB80AA502RC | 22147 | 热再主蒸汽启动排气电动门在远控 |  | digital
N1DCS.10LBC80AA402CD | 22148 | 冷再进口疏水罐疏水电动门关指令 |  | digital
N1DCS.10LBC80AA402CP | 22149 | 冷再进口疏水罐疏水电动门关到位 |  | digital
N1DCS.10LBC80AA402F | 22150 | 冷再进口疏水罐疏水电动门故障 |  | digital
N1DCS.10LBC80AA402OD | 22151 | 冷再进口疏水罐疏水电动门开指令 |  | digital
N1DCS.10LBC80AA402OP | 22152 | 冷再进口疏水罐疏水电动门开到位 |  | digital
N1DCS.10LBC80AA402RC | 22153 | 冷再进口疏水罐疏水电动门在远控 |  | digital
N1DCS.10LBC80CL001 | 22154 | 一级再热器进口疏水罐液位高 |  | digital
N1DCS.10LBG70AA002CD | 22155 | 辅汽至#1炉除氧头电动门关指令 |  | digital
N1DCS.10LBG70AA002CP | 22156 | 辅汽至#1炉除氧头电动门关到位 |  | digital
N1DCS.10LBG70AA002F | 22157 | 辅汽至#1炉除氧头电动门故障 |  | digital
N1DCS.10LBG70AA002OD | 22158 | 辅汽至#1炉除氧头电动门开指令 |  | digital
N1DCS.10LBG70AA002OP | 22159 | 辅汽至#1炉除氧头电动门开到位 |  | digital
N1DCS.10LBG70AA002RC | 22160 | 辅汽至#1炉除氧头电动门在远控 |  | digital
N1DCS.10LBG70AA101_MRE | 22161 | 辅汽至#1炉除氧头调节阀偏差大 |  | digital
N1DCS.10LCC70AA502CD | 22162 | #1炉低压省煤器放空电动门关指令 |  | digital
N1DCS.10LCC70AA502CP | 22163 | #1炉低压省煤器放空电动门关到位 |  | digital
N1DCS.10LCC70AA502F | 22164 | #1炉低压省煤器放空电动门故障 |  | digital
N1DCS.10LCC70AA502OD | 22165 | #1炉低压省煤器放空电动门开指令 |  | digital
N1DCS.10LCC70AA502OP | 22166 | #1炉低压省煤器放空电动门开到位 |  | digital
N1DCS.10LCC70AA502RC | 22167 | #1炉低压省煤器放空电动门在远控 |  | digital
N1DCS.10LCC71AA101_MRE | 22168 | 低省再循环泵出口调阀偏差大 |  | digital
N1DCS.10LCC71AA101OP | 22169 | 低省再循环泵出口调阀开到位 |  | digital
N1DCS.10LCC72AA003CD | 22170 | #1再循环泵出口电动门关指令 |  | digital
N1DCS.10LCC72AA003CP | 22171 | #1再循环泵出口电动门关到位 |  | digital
N1DCS.10LCC72AA003F | 22172 | #1再循环泵出口电动门故障 |  | digital
N1DCS.10LCC72AA003OD | 22173 | #1再循环泵出口电动门开指令 |  | digital
N1DCS.10LCC72AA003OP | 22174 | #1再循环泵出口电动门开到位 |  | digital
N1DCS.10LCC72AA003RC | 22175 | #1再循环泵出口电动门在远控 |  | digital
N1DCS.10LCC72AP001DY | 22176 | #1再循环泵电机加热器投/退指令 |  | digital
N1DCS.10LCC72AP001PF | 22177 | 低压省煤器#1再循环泵综合故障 |  | digital
N1DCS.10LCC72AP001RC | 22178 | 低压省煤器#1再循环泵在远控 |  | digital
N1DCS.10LCC72AP001RD | 22179 | 低压省煤器#1再循环泵启动指令 |  | digital
N1DCS.10LCC72AP001RP | 22180 | 低压省煤器#1再循环泵在运行 |  | digital
N1DCS.10LCC72AP001RP1 | 22181 | #1再循环泵电机电加热器在运行 |  | digital
N1DCS.10LCC72AP001TD | 22182 | 低压省煤器#1再循环泵停止指令 |  | digital
N1DCS.10LCC72AP001TP | 22183 | 低压省煤器#1再循环泵已停止 |  | digital
N1DCS.10LCC72CP101_OK | 22184 | #1再循环泵出口压力正常 |  | digital
N1DCS.10LCC73AA003CD | 22185 | #2再循环泵出口电动门关指令 |  | digital
N1DCS.10LCC73AA003CP | 22186 | #2再循环泵出口电动门关到位 |  | digital
N1DCS.10LCC73AA003F | 22187 | #2再循环泵出口电动门故障 |  | digital
N1DCS.10LCC73AA003OD | 22188 | #2再循环泵出口电动门开指令 |  | digital
N1DCS.10LCC73AA003OP | 22189 | #2再循环泵出口电动门开到位 |  | digital
N1DCS.10LCC73AA003RC | 22190 | #2再循环泵出口电动门在远控 |  | digital
N1DCS.10LCC73AP001DY | 22191 | #2再循环泵电机加热器投/退指令 |  | digital
N1DCS.10LCC73AP001PF | 22192 | 低压省煤器#2再循环泵综合故障 |  | digital
N1DCS.10LCC73AP001RC | 22193 | 低压省煤器#2再循环泵在远控 |  | digital
N1DCS.10LCC73AP001RD | 22194 | 低压省煤器#2再循环泵启动指令 |  | digital
N1DCS.10LCC73AP001RP | 22195 | 低压省煤器#2再循环泵在运行 |  | digital
N1DCS.10LCC73AP001RP1 | 22196 | #2再循环泵电机电加热器在运行 |  | digital
N1DCS.10LCC73AP001TD | 22197 | 低压省煤器#2再循环泵停止指令 |  | digital
N1DCS.10LCC73AP001TP | 22198 | 低压省煤器#2再循环泵已停止 |  | digital
N1DCS.10LCC73CP101_OK | 22199 | #2再循环泵出口压力正常 |  | digital
N1DCS.10LCQ74AA101_MRE | 22200 | #1炉连排至定排气动调节阀偏差大 |  | digital
N1DCS.HRSGPRCT | 22201 | #1余热锅炉保护动作 |  | digital
N1DCS.LP_DRN_ACD | 22202 | 低压系统疏水门自动关 |  | digital
N1DCS.LPDRUMCP_MRE | 22203 | 低压汽包压力坏点 |  | digital
N1DCS.LPDRUMCTD_MRE | 22204 | 低压汽包下外壁温坏点 |  | digital
N1DCS.LPDRUMCTU_MRE | 22205 | 低压汽包上外壁温坏点 |  | digital
N1DCS.LPDRUMLVL_AL | 22206 | 低压汽包液位（计算后）报警 |  | digital
N1DCS.LPDRUMLVL_HI | 22207 | 低压汽包液位（计算后）高 |  | digital
N1DCS.LPDRUMLVL_HII | 22208 | 低压汽包液位（计算后）高高 |  | digital
N1DCS.LPDRUMLVL_HIII | 22209 | 低压汽包液位（计算后）高高高 |  | digital
N1DCS.LPDRUMLVL_HIII1 | 22210 | 低压汽包液位1（计算后）高高高 |  | digital
N1DCS.LPDRUMLVL_HIII2 | 22211 | 低压汽包液位2（计算后）高高高 |  | digital
N1DCS.LPDRUMLVL_HIII3 | 22212 | 低压汽包液位3（计算后）高高高 |  | digital
N1DCS.LPDRUMLVL_LII | 22213 | 低压汽包液位（计算后）低低 |  | digital
N1DCS.LPDRUMLVL_LIII | 22214 | 低压汽包液位（计算后）低低低 |  | digital
N1DCS.LPDRUMLVL_LIII1 | 22215 | 低压汽包液位1（计算后）低低低 |  | digital
N1DCS.LPDRUMLVL_LIII2 | 22216 | 低压汽包液位2（计算后）低低低 |  | digital
N1DCS.LPDRUMLVL_LIII3 | 22217 | 低压汽包液位3（计算后）低低低 |  | digital
N1DCS.LPDRUMLVL_MRE | 22218 | 低压汽包液位（计算后）坏点 |  | digital
N1DCS.LPDSTCF_MRE | 22219 | 低压主蒸汽流量（计算后）坏点 |  | digital
N1DCS.LPDSTCP_MRE | 22220 | 低压主蒸汽压力坏点 |  | digital
N1DCS.LPDSTCP_OK | 22221 | 低压主蒸汽压力正常（高于0.1MPa |  | digital
N1DCS.LPDSTCT_MRE | 22222 | 低压主蒸汽温度坏点 |  | digital
N1DCS.LPDWTCF_MRE | 22223 | 低压汽包给水流量(计算后)坏点 |  | digital
N1DCS.LPDWTCF_NORM | 22224 | 低压汽包给水流量(计算后)正常 |  | digital
N1DCS.LPDWTCT_MRE | 22225 | 低压省煤器出口温度坏点 |  | digital
N1DCS.LPECON_SEQFINSH | 22226 | 低省再循环系统启顺控已完成 |  | digital
N1DCS.LPECON_SEQST_OK | 22227 | 低省再循环系统已投运 |  | digital
N1DCS.LPECONPA_OK | 22228 | #1低省再循环泵运行正常 |  | digital
N1DCS.LPECONPA_STRPEM | 22229 | #1低省再循环泵启动允许 |  | digital
N1DCS.LPECONPA_TEMALM | 22230 | #1低省再循环泵超温保护报警 |  | digital
N1DCS.LPECONPA_TEMALMCUT | 22231 | #1低省再循环泵温度报警功能解除 |  | digital
N1DCS.LPECONPA_TEMPMT | 22232 | #1低省再循环泵温度允许 |  | digital
N1DCS.LPECONPA_TP | 22233 | #1低省再循环泵保护跳闸信号 |  | digital
N1DCS.LPECONPAMANSTOP | 22234 | #1低省再循环泵手动跳闸 |  | digital
N1DCS.LPECONPB_OK | 22235 | #2低省再循环泵运行正常 |  | digital
N1DCS.LPECONPB_STRPEM | 22236 | #2低省再循环泵启动允许 |  | digital
N1DCS.LPECONPB_TEMALM | 22237 | #2低省再循环泵超温保护报警 |  | digital
N1DCS.LPECONPB_TEMALMCUT | 22238 | #2低省再循环泵温度报警功能解除 |  | digital
N1DCS.LPECONPB_TEMPMT | 22239 | #2低省再循环泵温度允许 |  | digital
N1DCS.LPECONPB_TP | 22240 | #2低省再循环泵保护跳闸信号 |  | digital
N1DCS.LPECONPBMANSTOP | 22241 | #2低省再循环泵手动跳闸 |  | digital
N1DCS.LPFW_SEQST_KB1G | 22242 | 手动确认低压给水管道系统已排空 |  | digital
N1DCS.LPFW_SEQSTFINSH | 22243 | 低压汽包上水顺控已完成 |  | digital
N1DCS.LPFW3ELE | 22244 | 低压给水在三冲量调节 |  | digital
N1DCS.LPMS_SEQSTFINISH | 22245 | 低压主汽升温升压顺控已完成 |  | digital
N1DCS.ONE7 | 22246 | 开关量1 |  | digital
N1DCS.RH2_DRN_ACD | 22247 | 一级再热器进口疏水电动门自动关 |  | digital
N1DCS.RH2INSTCT_MRE | 22248 | 一级再热器减温器后温度坏点 |  | digital
N1DCS.RH2OUTSTCP_MRE | 22249 | 二级再热器出口蒸汽压力坏点 |  | digital
N1DCS.RH2OUTSTCT_MRE | 22250 | 二级再热器出口蒸汽温度坏点 |  | digital
N1DCS.ZERO7 | 22251 | 开关量0 |  | digital
N1DCS.10HAD70CLBS1 | 22252 | 低压汽包液位1（计算后）高高高 |  | digital
N1DCS.10HAD70CLBS2 | 22253 | 低压汽包液位2（计算后）高高高 |  | digital
N1DCS.10HAD70CLBS3 | 22254 | 低压汽包液位3（计算后）高高高 |  | digital
N1DCS.10LAB70AA101_AUTO | 22255 | 低压给水气动调节阀在自动 |  | digital
N1DCS.10LAB70AA101DVHI | 22256 | 低压给水调节阀指令反馈偏差大 |  | digital
N1DCS.10LAF80AA101_AUTO | 22257 | 一级再热器减温水调节阀在自动 |  | digital
N1DCS.10LAF80AA101BHG | 22258 | Ovation Control Builder |  | digital
N1DCS.10LAF80AA101BHG1 | 22259 | Ovation Control Builder |  | digital
N1DCS.10LAF80AA102_AUTO | 22260 | 二级再热器减温水调节阀在自动 |  | digital
N1DCS.10LAF80AA102BHG | 22261 | Ovation Control Builder |  | digital
N1DCS.10LAF80AA102BHG1 | 22262 | Ovation Control Builder |  | digital
N1DCS.BALM001 | 22263 | #1炉高压给水泵异常跳闸 |  | digital
N1DCS.BALM002 | 22264 | #1炉高压给水泵超温报警 |  | digital
N1DCS.BALM003 | 22265 | #1炉高压汽包液位（计算后）高高 |  | digital
N1DCS.BALM004 | 22266 | #1炉高压汽包液位（计算后）低低 |  | digital
N1DCS.BALM005 | 22267 | #1炉高压省煤器出口水温高 |  | digital
N1DCS.BALM006 | 22268 | 高压汽包上、下外壁温差大于60 |  | digital
N1DCS.BALM007 | 22269 | #1炉高压主蒸汽压力高（13.5） |  | digital
N1DCS.BALM008 | 22270 | #1炉中压给水泵异常跳闸 |  | digital
N1DCS.BALM009 | 22271 | #1炉中压给水泵超温报警 |  | digital
N1DCS.BALM010 | 22272 | #1炉中压汽包液位（计算后）高高 |  | digital
N1DCS.BALM011 | 22273 | #1炉中压汽包液位（计算后）低低 |  | digital
N1DCS.BALM012 | 22274 | 中压汽包上、下外壁温差大于60 |  | digital
N1DCS.BALM013 | 22275 | #1炉热再主蒸汽压力高（3.3） |  | digital
N1DCS.BALM014 | 22276 | #1炉低压汽包液位（计算后）高高 |  | digital
N1DCS.BALM015 | 22277 | #1炉低压汽包液位（计算后）低低 |  | digital
N1DCS.BALM016 | 22278 | 低压汽包上、下外壁温差大于60 |  | digital
N1DCS.BALM017 | 22279 | #1炉低省再循环泵异常跳闸 |  | digital
N1DCS.BALM018 | 22280 | #1炉低省再循环泵超温报警 |  | digital
N1DCS.BALM019 | 22281 | #1炉入口烟气压力高（大于6KPa） |  | digital
N1DCS.BALM020 | 22282 | #1炉烟囱出口挡板未在全开位置 |  | digital
N1DCS.BALM021 | 22283 | 高压给水泵稀油站润滑油泵跳闸 |  | digital
N1DCS.BALM022 | 22284 | 调压站火警阀未全开或故障 |  | digital
N1DCS.BALM023 | 22285 | #1炉保护跳闸信号 |  | digital
N1DCS.BALM024 | 22286 | #2机跳闸 |  | digital
N1DCS.BALM025 | 22287 | #1机跳闸 |  | digital
N1DCS.BALM026 | 22288 | #2机跳闸 |  | digital
N1DCS.BALM027 | 22289 | #1机跳闸 |  | digital
N1DCS.BALM028 | 22290 | 启动锅炉测点异常 |  | digital
N1DCS.BALM029 | 22291 | 汽机侧高压主蒸汽温度突变30℃ |  | digital
N1DCS.BALM030 | 22292 | 汽机侧热再主蒸汽温度突变30℃ |  | digital
N1DCS.BALM031 | 22293 | 锅炉侧热再主蒸汽温度突变50℃ |  | digital
N1DCS.BALM032 | 22294 | 锅炉侧高压主蒸汽温度突变50℃ |  | digital
N1DCS.BALMALL | 22295 | #1炉光字牌报警汇总 |  | digital
N1DCS.BALMUNACK | 22296 | #1炉光字牌报警手动确认指令 |  | digital
N1DCS.GSD | 22297 | Ovation Control Builder |  | digital
N1DCS.GSD1 | 22298 | Ovation Control Builder |  | digital
N1DCS.GSD2 | 22299 | Ovation Control Builder |  | digital
N1DCS.HGF | 22300 | Ovation Control Builder |  | digital
N1DCS.HPDSTCTSC | 22301 | 锅炉侧高压主蒸汽温度突降50℃ |  | digital
N1DCS.HPDSTCTSC1 | 22302 | 汽机侧高压主蒸汽温度突降30℃ |  | digital
N1DCS.HPDSTCTSCM | 22303 | 锅炉侧高压主蒸汽温度突升50℃ |  | digital
N1DCS.HPDSTCTSCM1 | 22304 | 汽机侧高压主蒸汽温度突升30℃ |  | digital
N1DCS.J0LBG22CT301DEVHIG1 | 22305 | 启动锅炉出口主蒸汽温度偏差大 |  | digital
N1DCS.LPDRUMCTC | 22306 | 低压汽包上、下外壁温差小于50 |  | digital
N1DCS.LPDRUMLVLDEVHI | 22307 | 低压给水调阀设定、反馈偏差大 |  | digital
N1DCS.LPFW3ELE1 | 22308 | 低压给水在单冲量调节 |  | digital
N1DCS.QDLGRWDD | 22309 | 启动炉出口主蒸汽温度低（280） |  | digital
N1DCS.QDLGRWDG | 22310 | 启动炉出口主蒸汽温度高（340） |  | digital
N1DCS.RH2OUTSTCTSC | 22311 | 热再主蒸汽温度突变 |  | digital
N1DCS.RHDSTCTSC | 22312 | 锅炉侧热再主蒸汽温度突降50℃ |  | digital
N1DCS.RHDSTCTSC1 | 22313 | 汽机侧热再主蒸汽温度突升30℃ |  | digital
N1DCS.RHDSTCTSCM | 22314 | 锅炉侧热再主蒸汽温度突升50℃ |  | digital
N1DCS.RHDSTCTSCM1 | 22315 | 汽机侧热再主蒸汽温度突降30℃ |  | digital
N1DCS.TBALMALL | 22316 | 机炉光字牌报警汇总 |  | digital
N1DCS.TBALMUNACK | 22317 | 机炉光字牌报警手动确认指令 |  | digital
N1DCS.10CDB76YB11 | 22318 | 中压汽包液位A侧画面显示 |  | digital
N1DCS.10CDB76YB12 | 22319 | 中压汽包液位B侧画面显示 |  | digital
N1DCS.10CDB76YB13 | 22320 | 中压汽包液位AB侧合成画面显示 |  | digital
N1DCS.10CDB76YB23 | 22321 | 高汽包液位AB侧合成画面显示 |  | digital
N1DCS.10CDB79XB03 | 22322 | 中压汽包液位A侧超温报警 |  | digital
N1DCS.10CDB79YB01 | 22323 | 中压汽包液位A侧光圈+ |  | digital
N1DCS.10CDB79YB02 | 22324 | 中压汽包液位A侧光圈- |  | digital
N1DCS.10CDB79YB11 | 22325 | 中压汽包液位A侧变倍+ |  | digital
N1DCS.10CDB79YB12 | 22326 | 中压汽包液位A侧变倍- |  | digital
N1DCS.10CDB79YB21 | 22327 | 中压汽包液位A侧焦距+ |  | digital
N1DCS.10CDB79YB22 | 22328 | 中压汽包液位A侧焦距- |  | digital
N1DCS.10CDB80XB03 | 22329 | 中压汽包液位B侧超温报警 |  | digital
N1DCS.10CDB80YB01 | 22330 | 中压汽包液位B侧光圈+ |  | digital
N1DCS.10CDB80YB02 | 22331 | 中压汽包液位B侧光圈- |  | digital
N1DCS.10CDB80YB11 | 22332 | 中压汽包液位B侧变倍+ |  | digital
N1DCS.10CDB80YB12 | 22333 | 中压汽包液位B侧变倍- |  | digital
N1DCS.10CDB80YB21 | 22334 | 中压汽包液位B侧焦距+ |  | digital
N1DCS.10CDB80YB22 | 22335 | 中压汽包液位B侧焦距- |  | digital
N1DCS.10CJJ030PCDI | 22336 | OPC动作(锅炉主保护) |  | digital
N1DCS.10CNSRPRCTACT1DI | 22337 | 凝汽器保护动作通道1 |  | digital
N1DCS.10CNSRPRCTACT2DI | 22338 | 凝汽器保护动作通道2 |  | digital
N1DCS.10CNSRPRCTACT3DI | 22339 | 凝汽器保护动作通道3 |  | digital
N1DCS.10CSB51PF | 22340 | 锅炉热力配电柜电源消失 |  | digital
N1DCS.10HAD70CLHH1DI | 22341 | 低压汽包液位1（计算后）高高高 |  | digital
N1DCS.10HAD70CLHH2DI | 22342 | 低压汽包液位2（计算后）高高高 |  | digital
N1DCS.10HAD70CLHH3DI | 22343 | 低压汽包液位3（计算后）高高高 |  | digital
N1DCS.10HAD70CLLL1DI | 22344 | 低压汽包液位1（计算后）低低低 |  | digital
N1DCS.10HAD70CLLL2DI | 22345 | 低压汽包液位2（计算后）低低低 |  | digital
N1DCS.10HAD70CLLL3DI | 22346 | 低压汽包液位3（计算后）低低低 |  | digital
N1DCS.10HAD80CL001F | 22347 | 中压汽包左电接点液位计故障 |  | digital
N1DCS.10HAD80CL001H | 22348 | 中压汽包左电接点液位计高I |  | digital
N1DCS.10HAD80CL001HH | 22349 | 中压汽包左电接点液位计高II |  | digital
N1DCS.10HAD80CL001HHH | 22350 | 中压汽包左电接点液位计高III |  | digital
N1DCS.10HAD80CL001L | 22351 | 中压汽包左电接点液位计低I |  | digital
N1DCS.10HAD80CL001LL | 22352 | 中压汽包左电接点液位计低II |  | digital
N1DCS.10HAD80CL001LLL | 22353 | 中压汽包左电接点液位计低III |  | digital
N1DCS.10HAD80CL002F | 22354 | 中压汽包右电接点液位计故障 |  | digital
N1DCS.10HAD80CL002H | 22355 | 中压汽包右电接点液位计高I |  | digital
N1DCS.10HAD80CL002HH | 22356 | 中压汽包右电接点液位计高II |  | digital
N1DCS.10HAD80CL002HHH | 22357 | 中压汽包右电接点液位计高III |  | digital
N1DCS.10HAD80CL002L | 22358 | 中压汽包右电接点液位计低I |  | digital
N1DCS.10HAD80CL002LL | 22359 | 中压汽包右电接点液位计低II |  | digital
N1DCS.10HAD80CL002LLL | 22360 | 中压汽包右电接点液位计低III |  | digital
N1DCS.10HAD84AA401CD | 22361 | 中压蒸发器定排电动门关指令 |  | digital
N1DCS.10HAD84AA401CP | 22362 | 中压蒸发器定排电动门关到位 |  | digital
N1DCS.10HAD84AA401F | 22363 | 中压蒸发器定排电动门故障 |  | digital
N1DCS.10HAD84AA401OD | 22364 | 中压蒸发器定排电动门开指令 |  | digital
N1DCS.10HAD84AA401OP | 22365 | 中压蒸发器定排电动门开到位 |  | digital
N1DCS.10HAD84AA401RC | 22366 | 中压蒸发器定排电动门在远控 |  | digital
N1DCS.10HAD85AA001CD | 22367 | 中压汽包连排电动门关指令 |  | digital
N1DCS.10HAD85AA001CP | 22368 | 中压汽包连排电动门关到位 |  | digital
N1DCS.10HAD85AA001F | 22369 | 中压汽包连排电动门故障 |  | digital
N1DCS.10HAD85AA001OD | 22370 | 中压汽包连排电动门开指令 |  | digital
N1DCS.10HAD85AA001OP | 22371 | 中压汽包连排电动门开到位 |  | digital
N1DCS.10HAD85AA001RC | 22372 | 中压汽包连排电动门在远控 |  | digital
N1DCS.10HAD86AA001CD | 22373 | 中压汽包启动放水电动门关指令 |  | digital
N1DCS.10HAD86AA001CP | 22374 | 中压汽包启动放水电动门关到位 |  | digital
N1DCS.10HAD86AA001F | 22375 | 中压汽包启动放水电动门故障 |  | digital
N1DCS.10HAD86AA001OD | 22376 | 中压汽包启动放水电动门开指令 |  | digital
N1DCS.10HAD86AA001OP | 22377 | 中压汽包启动放水电动门开到位 |  | digital
N1DCS.10HAD86AA001RC | 22378 | 中压汽包启动放水电动门在远控 |  | digital
N1DCS.10HAD86AA002CD | 22379 | 中压汽包启动放水调节门关指令 |  | digital
N1DCS.10HAD86AA002CP | 22380 | 中压汽包启动放水调节门关到位 |  | digital
N1DCS.10HAD86AA002F | 22381 | 中压汽包启动放水调节门故障 |  | digital
N1DCS.10HAD86AA002OD | 22382 | 中压汽包启动放水调节门开指令 |  | digital
N1DCS.10HAD86AA002OP | 22383 | 中压汽包启动放水调节门开到位 |  | digital
N1DCS.10HAD86AA002RC | 22384 | 中压汽包启动放水调节门在远控 |  | digital
N1DCS.10HAD90CLHH1DI | 22385 | 高压汽包液位1（计算后）高高高 |  | digital
N1DCS.10HAD90CLHH2DI | 22386 | 高压汽包液位2（计算后）高高高 |  | digital
N1DCS.10HAD90CLHH3DI | 22387 | 高压汽包液位3（计算后）高高高 |  | digital
N1DCS.10HAD90CLLL1DI | 22388 | 高压汽包液位1（计算后）低低低 |  | digital
N1DCS.10HAD90CLLL2DI | 22389 | 高压汽包液位2（计算后）低低低 |  | digital
N1DCS.10HAD90CLLL3DI | 22390 | 高压汽包液位3（计算后）低低低 |  | digital
N1DCS.10HAH80AA502CD | 22391 | 中压饱和蒸汽放空电动门关到位 |  | digital
N1DCS.10HAH80AA502CP | 22392 | 中压饱和蒸汽放空电动门关到位 |  | digital
N1DCS.10HAH80AA502F | 22393 | 中压饱和蒸汽放空电动门故障 |  | digital
N1DCS.10HAH80AA502OD | 22394 | 中压饱和蒸汽放空电动门开指令 |  | digital
N1DCS.10HAH80AA502OP | 22395 | 中压饱和蒸汽放空电动门开到位 |  | digital
N1DCS.10HAH80AA502RC | 22396 | 中压饱和蒸汽放空电动门在远控 |  | digital
N1DCS.10HNE70AA001CD | 22397 | 烟囱出口挡板关指令 |  | digital
N1DCS.10HNE70AA001CP | 22398 | 烟囱出口挡板关到位 |  | digital
N1DCS.10HNE70AA001F | 22399 | 烟囱出口挡板故障 |  | digital
N1DCS.10HNE70AA001OD | 22400 | 烟囱出口挡板开指令 |  | digital
N1DCS.10HNE70AA001OP | 22401 | 烟囱出口挡板开到位 |  | digital
N1DCS.10HNE70AA001RC | 22402 | 烟囱出口挡板远控 |  | digital
N1DCS.10HYY01EY001ASOE | 22403 | #1炉停机通道1（SOE） |  | digital
N1DCS.10HYY01EY001BSOE | 22404 | #1炉停机通道2（SOE） |  | digital
N1DCS.10HYY01EY001CSOE | 22405 | #1炉停机通道3（SOE） |  | digital
N1DCS.10HYY01EY001DSOE_DO | 22406 | #1炉停机SOE(送至DROP1) |  | digital
N1DCS.10LAB81AA001CD | 22407 | #1中压给水泵出口电动门关指令 |  | digital
N1DCS.10LAB81AA001CP | 22408 | #1中压给水泵出口电动门关到位 |  | digital
N1DCS.10LAB81AA001F | 22409 | #1中压给水泵出口电动门故障 |  | digital
N1DCS.10LAB81AA001OD | 22410 | #1中压给水泵出口电动门开指令 |  | digital
N1DCS.10LAB81AA001OP | 22411 | #1中压给水泵出口电动门开到位 |  | digital
N1DCS.10LAB81AA001RC | 22412 | #1中压给水泵出口电动门在远控 |  | digital
N1DCS.10LAB81AP001FW | 22413 | #1中压给水泵工作位置 |  | digital
N1DCS.10LAB81AP001PF | 22414 | #1中压给水泵综合故障 |  | digital
N1DCS.10LAB81AP001PS | 22415 | #1中压给水泵保护动作 |  | digital
N1DCS.10LAB81AP001RC | 22416 | #1中压给水泵在远控 |  | digital
N1DCS.10LAB81AP001RD | 22417 | #1中压给水泵启动指令 |  | digital
N1DCS.10LAB81AP001RP | 22418 | #1中压给水泵在运行 |  | digital
N1DCS.10LAB81AP001SW | 22419 | #1中压给水泵试验位置 |  | digital
N1DCS.10LAB81AP001TD | 22420 | #1中压给水泵停止指令 |  | digital
N1DCS.10LAB81AP001TP | 22421 | #1中压给水泵已停止 |  | digital
N1DCS.10LAB81AP001TP1 | 22422 | #1中压给水泵已停止 |  | digital
N1DCS.10LAB82AP001TP1 | 22423 | #2中压给水泵已停止 |  | digital
N1DCS.10LAB82AP001TP2DI | 22424 | #2中压给水泵已停止 |  | digital
N1DCS.10LAB83AA101_AUTO | 22425 | 中压给水调节阀在自动 |  | digital
N1DCS.10LAB83AA101_MRE | 22426 | 中压给水调节阀报警 |  | digital
N1DCS.10LAB91AA001CD | 22427 | #1高压给水泵出口电动门关指令 |  | digital
N1DCS.10LAB91AA001CP | 22428 | #1高压给水泵出口电动门关到位 |  | digital
N1DCS.10LAB91AA001F | 22429 | #1高压给水泵出口电动门故障 |  | digital
N1DCS.10LAB91AA001OD | 22430 | #1高压给水泵出口电动门开指令 |  | digital
N1DCS.10LAB91AA001OP | 22431 | #1高压给水泵出口电动门开到位 |  | digital
N1DCS.10LAB91AA001RC | 22432 | #1高压给水泵出口电动门在远控 |  | digital
N1DCS.10LAB91AP001FW | 22433 | #1高压给水泵工作位置 |  | digital
N1DCS.10LAB91AP001PF | 22434 | #1高压给水泵综合故障 |  | digital
N1DCS.10LAB91AP001PS | 22435 | #1高压给水泵电气保护动作 |  | digital
N1DCS.10LAB91AP001RC | 22436 | #1高压给水泵在远控 |  | digital
N1DCS.10LAB91AP001RP | 22437 | #1高压给水泵在运行 |  | digital
N1DCS.10LAB91AP001SW | 22438 | #1高压给水泵试验位置 |  | digital
N1DCS.10LAB91AP001TP | 22439 | #1高压给水泵已停止 |  | digital
N1DCS.10LAB91AP001TP1 | 22440 | #1高压给水泵已停止 |  | digital
N1DCS.10LAB91CS001 | 22441 | #1高压给水泵反转 |  | digital
N1DCS.10LAB92AP001TP1 | 22442 | #2高压给水泵已停止 |  | digital
N1DCS.10LAB92AP001TP2DI | 22443 | #2高压给水泵已停止 |  | digital
N1DCS.10LAC91AP001EH004 | 22444 | #1高压给水泵高压柜QS1合闸位置 |  | digital
N1DCS.10LAC91AP001EH005 | 22445 | #1高压给水泵高压柜QS3合闸位置 |  | digital
N1DCS.10LAC91AP001RD | 22446 | #1高压给水泵6KV开关合闸指令 |  | digital
N1DCS.10LAC91AP001TD | 22447 | #1高压给水泵6KV开关分闸指令 |  | digital
N1DCS.10LAC91GX0001RP1 | 22448 | #1高压给水泵变频器在运行 |  | digital
N1DCS.10LBA80AA001CD | 22449 | 中压主蒸汽电动门关指令 |  | digital
N1DCS.10LBA80AA001CP | 22450 | 中压主蒸汽电动门关到位 |  | digital
N1DCS.10LBA80AA001F | 22451 | 中压主蒸汽电动门故障 |  | digital
N1DCS.10LBA80AA001OD | 22452 | 中压主蒸汽电动门开指令 |  | digital
N1DCS.10LBA80AA001OP | 22453 | 中压主蒸汽电动门开到位 |  | digital
N1DCS.10LBA80AA001RC | 22454 | 中压主蒸汽电动门在远控 |  | digital
N1DCS.10LBA80AA402CD | 22455 | 中压主蒸汽疏水至定排门关指令 |  | digital
N1DCS.10LBA80AA402CP | 22456 | 中压主蒸汽疏水至定排门关到位 |  | digital
N1DCS.10LBA80AA402F | 22457 | 中压主蒸汽疏水至定排门故障 |  | digital
N1DCS.10LBA80AA402OD | 22458 | 中压主蒸汽疏水至定排门开指令 |  | digital
N1DCS.10LBA80AA402OP | 22459 | 中压主蒸汽疏水至定排门开到位 |  | digital
N1DCS.10LBA80AA402RC | 22460 | 中压主蒸汽疏水至定排门在远控 |  | digital
N1DCS.10LBA80AA502CD | 22461 | 中压主蒸汽启动排汽电动门关指令 |  | digital
N1DCS.10LBA80AA502CP | 22462 | 中压主蒸汽启动排汽电动门关到位 |  | digital
N1DCS.10LBA80AA502F | 22463 | 中压主蒸汽启动排汽电动门故障 |  | digital
N1DCS.10LBA80AA502OD | 22464 | 中压主蒸汽启动排汽电动门开指令 |  | digital
N1DCS.10LBA80AA502OP | 22465 | 中压主蒸汽启动排汽电动门开到位 |  | digital
N1DCS.10LBA80AA502RC | 22466 | 中压主蒸汽启动排汽电动门在远控 |  | digital
N1DCS.10LCB11AP001CPDI | 22467 | #1凝结水泵已停止(锅炉主保护) |  | digital
N1DCS.10LCB12AP001CPDI | 22468 | #2凝结水泵已停止(锅炉主保护) |  | digital
N1DCS.10MAN10AA101CPDI | 22469 | 高旁阀全关(锅炉主保护) |  | digital
N1DCS.10MAN20AA101CPDI | 22470 | 中旁阀全关(锅炉主保护) |  | digital
N1DCS.10MAP10AA101CPDI | 22471 | 低旁阀全关(锅炉主保护) |  | digital
N1DCS.10MAY01EZ011_XK463 | 22472 | #1机遮断系统已遮断3 |  | digital
N1DCS.10MAY01EZ011_XK464 | 22473 | #1机遮断系统已遮断4 |  | digital
N1DCS.10MAY01EZ011_XK465 | 22474 | #1机遮断系统已遮断5 |  | digital
N1DCS.10MYB01EU301 | 22475 | #2机跳闸至DCS通道A |  | digital
N1DCS.10MYB01EU302 | 22476 | #2机跳闸至DCS通道B |  | digital
N1DCS.10MYB01EU303 | 22477 | #2机跳闸至DCS通道C |  | digital
N1DCS.10MYY01EZ011_XK465 | 22478 | #1机遮断系统已遮断5 |  | digital
N1DCS.10QFB80CD | 22479 | #1炉压缩空气净化分配装置停指令 |  | digital
N1DCS.10QFB80OD | 22480 | #1炉压缩空气净化分配装置启指令 |  | digital
N1DCS.10QFB80P | 22481 | #1炉压缩空气净化分配装置在运行 |  | digital
N1DCS.10QFB80RC | 22482 | #1炉压缩空气净化分配装置在远控 |  | digital
N1DCS.10XAV91CL001 | 22483 | #1高压给水泵稀油站油箱液位低 |  | digital
N1DCS.10XAV91CP001 | 22484 | #1高压给水泵稀油站滤网差压高低 |  | digital
N1DCS.10XAV91GH001AP1RD | 22485 | #1高压给水泵稀油站#1油泵启指令 |  | digital
N1DCS.10XAV91GH001AP1TD | 22486 | #1高压给水泵稀油站#1油泵停指令 |  | digital
N1DCS.10XAV91GH001AP2RD | 22487 | #1高压给水泵稀油站#2油泵启指令 |  | digital
N1DCS.10XAV91GH001AP2TD | 22488 | #1高压给水泵稀油站#2油泵停指令 |  | digital
N1DCS.10XAV91GH001HTRD | 22489 | #1高压给水泵稀油站加热器启指令 |  | digital
N1DCS.10XAV91GH001HTTD | 22490 | #1高压给水泵稀油站加热器停指令 |  | digital
N1DCS.10XAV91GH001PF | 22491 | #1高给泵稀油站重大故障停主机 |  | digital
N1DCS.10XAV91GH001RC1 | 22492 | #1高压给水泵稀油站远程备妥 |  | digital
N1DCS.10XAV91GH001RC2 | 22493 | #1高压给水泵稀油站允许主机启动 |  | digital
N1DCS.10XAV91GH001RD1 | 22494 | #1高压给水泵稀油站远程驱动 |  | digital
N1DCS.10XAV91GH001RD2 | 22495 | #1高压给水泵在运行（送至稀油站 |  | digital
N1DCS.10XAV91GH001RP1 | 22496 | #1高给泵稀油站#1油泵在运行 |  | digital
N1DCS.10XAV91GH001RP2 | 22497 | #1高给泵稀油站#2油泵在运行 |  | digital
N1DCS.10XAV91GH001RP3 | 22498 | #1高给泵稀油站电加热器已投入 |  | digital
N1DCS.10XAV91GH002PF1 | 22499 | #1高压给水泵稀油站轻故障 |  | digital
N1DCS.HPFWPA_RUN | 22500 | #1高压给水泵在运行(工频或变频) |  | digital
N1DCS.HPFWPA_STOP | 22501 | #1高压给水泵已停止(工频和变频) |  | digital
N1DCS.HPFWPA_STRPEM | 22502 | #1高压给水泵启动允许 |  | digital
N1DCS.HPFWPA_TEMPEM | 22503 | #1高压给水泵温度允许 |  | digital
N1DCS.HPFWPA_TEMPRT | 22504 | #1高压给水泵温度保护信号 |  | digital
N1DCS.HPFWPA_TP | 22505 | #1高压给水泵跳闸信号 |  | digital
N1DCS.HPFWPAMANSTOP | 22506 | #1高压给水泵手动停止指令 |  | digital
N1DCS.HPFWPARUN | 22507 | #1高压给水泵在运行 |  | digital
N1DCS.IPDRUMCP_MRE | 22508 | 中压汽包压力坏点 |  | digital
N1DCS.IPDRUMCTD_MRE | 22509 | 中压汽包下外壁温坏点 |  | digital
N1DCS.IPDRUMCTU_MRE | 22510 | 中压汽包上外壁温坏点 |  | digital
N1DCS.IPDRUMLVL_AL | 22511 | 中压汽包液位（计算后）报警 |  | digital
N1DCS.IPDRUMLVL_HI | 22512 | 中压汽包液位（计算后）高 |  | digital
N1DCS.IPDRUMLVL_HII | 22513 | 中压汽包液位（计算后）高高 |  | digital
N1DCS.IPDRUMLVL_HIII | 22514 | 中压汽包液位（计算后）高高高 |  | digital
N1DCS.IPDRUMLVL_HIII1 | 22515 | 中压汽包液位1（计算后）高高高 |  | digital
N1DCS.IPDRUMLVL_HIII2 | 22516 | 中压汽包液位2（计算后）高高高 |  | digital
N1DCS.IPDRUMLVL_HIII3 | 22517 | 中压汽包液位3（计算后）高高高 |  | digital
N1DCS.IPDRUMLVL_LII | 22518 | 中压汽包液位（计算后）低低 |  | digital
N1DCS.IPDRUMLVL_LIII | 22519 | 中压汽包液位（计算后）低低低 |  | digital
N1DCS.IPDRUMLVL_LIII1 | 22520 | 中压汽包液位1（计算后）低低低 |  | digital
N1DCS.IPDRUMLVL_LIII2 | 22521 | 中压汽包液位2（计算后）低低低 |  | digital
N1DCS.IPDRUMLVL_LIII3 | 22522 | 中压汽包液位3（计算后）低低低 |  | digital
N1DCS.IPDRUMLVL_MRE | 22523 | 中压汽包液位（计算后）坏点 |  | digital
N1DCS.IPDRUMLVLDEVHI | 22524 | 中压给水调节阀设定、反馈偏差大 |  | digital
N1DCS.IPDSTCF_MRE | 22525 | 中压主蒸汽流量（计算后）坏点 |  | digital
N1DCS.IPDSTCP_MRE | 22526 | 中压主蒸汽压力坏点 |  | digital
N1DCS.IPDSTCT_MRE | 22527 | 中压主蒸汽温度坏点 |  | digital
N1DCS.IPDWTCF_MRE | 22528 | 中压给水流量（计算后）坏点 |  | digital
N1DCS.IPDWTCF_NORM | 22529 | 中压给水流量正常（大于80t/h） |  | digital
N1DCS.IPDWTCT_MRE | 22530 | 中压给水温度坏点 |  | digital
N1DCS.IPFW_SEQSTFINSH | 22531 | 中压汽包上水顺控已完成 |  | digital
N1DCS.IPFW3ELE | 22532 | 中压给水在三冲量调节 |  | digital
N1DCS.IPFWPA_STRPEM | 22533 | #1中压给水泵启动允许 |  | digital
N1DCS.IPFWPA_TEMPEM | 22534 | #1中压给水泵温度允许 |  | digital
N1DCS.IPFWPA_TEMPRT | 22535 | #1中压给水泵温度保护信号 |  | digital
N1DCS.IPFWPA_TP | 22536 | #1中压给水泵保护跳闸指令 |  | digital
N1DCS.IPFWPAMANSTOP | 22537 | #1中压给水泵手动停止指令 |  | digital
N1DCS.IPMS_SEQSTFINISH | 22538 | 中压主汽升温升压顺控已完成 |  | digital
N1DCS.ONE8 | 22539 | 开关量1 |  | digital
N1DCS.ZERO8 | 22540 | 开关量0 |  | digital
N1DCS.10HAD80CLBS1 | 22541 | 中压汽包液位1（计算后）高高高 |  | digital
N1DCS.10HAD80CLBS2 | 22542 | 中压汽包液位2（计算后）高高高 |  | digital
N1DCS.10HAD80CLBS3 | 22543 | 中压汽包液位3（计算后）高高高 |  | digital
N1DCS.10LAB83AA101DVHI | 22544 | 中压给水调节阀指令、反馈偏差大 |  | digital
N1DCS.CLOSEZHONGYAPAIOK | 22545 | Ovation Control Builder |  | digital
N1DCS.CZYLMZI | 22546 | Ovation Control Builder |  | digital
N1DCS.DCSTRIPTURB1 | 22547 | 锅炉保护跳闸联跳汽机 |  | digital
N1DCS.GTHINTERLOCK1 | 22548 | #2机跳闸至DCS（3取2后） |  | digital
N1DCS.GYGSPMPABP | 22549 | #1高压给水泵在变频位置 |  | digital
N1DCS.GYGSPMPAGP | 22550 | #1高压给水泵在工频位置 |  | digital
N1DCS.HPFWPA_SEQBPSTFINISH | 22551 | #1高压给水泵变频启顺控已完成 |  | digital
N1DCS.HPFWPA_SEQSTFINISH | 22552 | #1高压给水泵工频启顺控已完成 |  | digital
N1DCS.HRSGTRIP1 | 22553 | 高压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTRIP10 | 22554 | 烟囱挡板未在全开位置 |  | digital
N1DCS.HRSGTRIP11 | 22555 | OPC或汽机跳闸30s后任一旁路未开 |  | digital
N1DCS.HRSGTRIP12 | 22556 | 凝汽器真空低(大于30KPa） |  | digital
N1DCS.HRSGTRIP13 | 22557 | #1炉手动跳闸指令 |  | digital
N1DCS.HRSGTRIP14 | 22558 | 燃机联锁跳余热锅炉 |  | digital
N1DCS.HRSGTRIP1A | 22559 | 高压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTRIP2 | 22560 | 高压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTRIP2A | 22561 | 高压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTRIP3 | 22562 | 中压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTRIP3A | 22563 | 中压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTRIP4 | 22564 | 中压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTRIP4A | 22565 | 中压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTRIP5 | 22566 | 低压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTRIP5A | 22567 | 低压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTRIP6 | 22568 | 低压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTRIP6A | 22569 | 低压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTRIP7 | 22570 | #1炉高压给水泵全停 |  | digital
N1DCS.HRSGTRIP8 | 22571 | #1炉中压给水泵全停 |  | digital
N1DCS.HRSGTRIP9 | 22572 | #1机凝结水泵全停 |  | digital
N1DCS.HRSGTRIPPP | 22573 | 余热锅炉保护跳闸指令 |  | digital
N1DCS.HRSGTRIPRSPB1 | 22574 | #1炉跳闸信号复位 |  | digital
N1DCS.IPFW3ELE1 | 22575 | 中压给水在单冲量调节 |  | digital
N1DCS.10CDB76XB21 | 22576 | 高压汽包液位摄像综合故障 |  | digital
N1DCS.10CDB76YB21 | 22577 | 高压汽包液位A侧画面显示 |  | digital
N1DCS.10CDB76YB22 | 22578 | 高压汽包液位B侧画面显示 |  | digital
N1DCS.10CDB81XB03 | 22579 | 高压汽包液位A侧超温报警 |  | digital
N1DCS.10CDB81YB01 | 22580 | 高压汽包液位A侧光圈+ |  | digital
N1DCS.10CDB81YB02 | 22581 | 高压汽包液位A侧光圈- |  | digital
N1DCS.10CDB81YB11 | 22582 | 高压汽包液位A侧变倍+ |  | digital
N1DCS.10CDB81YB12 | 22583 | 高压汽包液位A侧变倍- |  | digital
N1DCS.10CDB81YB21 | 22584 | 高压汽包液位A侧焦距+ |  | digital
N1DCS.10CDB81YB22 | 22585 | 高压汽包液位A侧焦距- |  | digital
N1DCS.10CDB82XB03 | 22586 | 高压汽包液位B侧超温报警 |  | digital
N1DCS.10CDB82YB01 | 22587 | 高压汽包液位B侧光圈+ |  | digital
N1DCS.10CDB82YB02 | 22588 | 高压汽包液位B侧光圈- |  | digital
N1DCS.10CDB82YB11 | 22589 | 高压汽包液位B侧变倍+ |  | digital
N1DCS.10CDB82YB12 | 22590 | 高压汽包液位B侧变倍- |  | digital
N1DCS.10CDB82YB21 | 22591 | 高压汽包液位B侧焦距+ |  | digital
N1DCS.10CDB82YB22 | 22592 | 高压汽包液位B侧焦距- |  | digital
N1DCS.10GUC01GH001PF | 22593 | #1炉电梯井集水坑液位高报警 |  | digital
N1DCS.10HAC90AA502CD | 22594 | 高压省煤器放空气电动门关指令 |  | digital
N1DCS.10HAC90AA502CP | 22595 | 高压省煤器放空气电动门关到位 |  | digital
N1DCS.10HAC90AA502F | 22596 | 高压省煤器放空气电动门故障 |  | digital
N1DCS.10HAC90AA502OD | 22597 | 高压省煤器放空气电动门开指令 |  | digital
N1DCS.10HAC90AA502OP | 22598 | 高压省煤器放空气电动门开到位 |  | digital
N1DCS.10HAC90AA502RC | 22599 | 高压省煤器放空气电动门在远控 |  | digital
N1DCS.10HAD90CL001F | 22600 | 高压汽包左电接点液位计故障 |  | digital
N1DCS.10HAD90CL001H | 22601 | 高压汽包左电接点液位计高I |  | digital
N1DCS.10HAD90CL001HH | 22602 | 高压汽包左电接点液位计高II |  | digital
N1DCS.10HAD90CL001HHH | 22603 | 高压汽包左电接点液位计高III |  | digital
N1DCS.10HAD90CL001L | 22604 | 高压汽包左电接点液位计低I |  | digital
N1DCS.10HAD90CL001LL | 22605 | 高压汽包左电接点液位计低II |  | digital
N1DCS.10HAD90CL001LLL | 22606 | 高压汽包左电接点液位计低III |  | digital
N1DCS.10HAD90CL002F | 22607 | 高压汽包右电接点液位计故障 |  | digital
N1DCS.10HAD90CL002H | 22608 | 高压汽包右电接点液位计高I |  | digital
N1DCS.10HAD90CL002HH | 22609 | 高压汽包右电接点液位计高II |  | digital
N1DCS.10HAD90CL002HHH | 22610 | 高压汽包右电接点液位计高III |  | digital
N1DCS.10HAD90CL002L | 22611 | 高压汽包右电接点液位计低I |  | digital
N1DCS.10HAD90CL002LL | 22612 | 高压汽包右电接点液位计低II |  | digital
N1DCS.10HAD90CL002LLL | 22613 | 高压汽包右电接点液位计低III |  | digital
N1DCS.10HAD90CLHH1 | 22614 | 高压汽包液位1（计算后）高高高 |  | digital
N1DCS.10HAD90CLHH2 | 22615 | 高压汽包液位2（计算后）高高高 |  | digital
N1DCS.10HAD90CLHH3 | 22616 | 高压汽包液位3（计算后）高高高 |  | digital
N1DCS.10HAD90CLLL1 | 22617 | 高压汽包液位1（计算后）低低低 |  | digital
N1DCS.10HAD90CLLL2 | 22618 | 高压汽包液位2（计算后）低低低 |  | digital
N1DCS.10HAD90CLLL3 | 22619 | 高压汽包液位3（计算后）低低低 |  | digital
N1DCS.10HAD91AA405CD | 22620 | 高压蒸发器定排电动门关指令 |  | digital
N1DCS.10HAD91AA405CP | 22621 | 高压蒸发器定排电动门关到位 |  | digital
N1DCS.10HAD91AA405F | 22622 | 高压蒸发器定排电动门故障 |  | digital
N1DCS.10HAD91AA405OD | 22623 | 高压蒸发器定排电动门开指令 |  | digital
N1DCS.10HAD91AA405OP | 22624 | 高压蒸发器定排电动门开到位 |  | digital
N1DCS.10HAD91AA405RC | 22625 | 高压蒸发器定排电动门在远控 |  | digital
N1DCS.10HAD95AA001CD | 22626 | 高压汽包连排电动门关指令 |  | digital
N1DCS.10HAD95AA001CP | 22627 | 高压汽包连排电动门关到位 |  | digital
N1DCS.10HAD95AA001F | 22628 | 高压汽包连排电动门故障 |  | digital
N1DCS.10HAD95AA001OD | 22629 | 高压汽包连排电动门开指令 |  | digital
N1DCS.10HAD95AA001OP | 22630 | 高压汽包连排电动门开到位 |  | digital
N1DCS.10HAD95AA001RC | 22631 | 高压汽包连排电动门在远控 |  | digital
N1DCS.10HAD96AA001CD | 22632 | 高压汽包启动放水电动门关指令 |  | digital
N1DCS.10HAD96AA001CP | 22633 | 高压汽包启动放水电动门关到位 |  | digital
N1DCS.10HAD96AA001F | 22634 | 高压汽包启动放水电动门故障 |  | digital
N1DCS.10HAD96AA001OD | 22635 | 高压汽包启动放水电动门开指令 |  | digital
N1DCS.10HAD96AA001OP | 22636 | 高压汽包启动放水电动门开到位 |  | digital
N1DCS.10HAD96AA001RC | 22637 | 高压汽包启动放水电动门在远控 |  | digital
N1DCS.10HAD96AA002CD | 22638 | 高压汽包启动放水调节门关指令 |  | digital
N1DCS.10HAD96AA002CP | 22639 | 高压汽包启动放水调节门关到位 |  | digital
N1DCS.10HAD96AA002F | 22640 | 高压汽包启动放水调节门故障 |  | digital
N1DCS.10HAD96AA002OD | 22641 | 高压汽包启动放水调节门开指令 |  | digital
N1DCS.10HAD96AA002OP | 22642 | 高压汽包启动放水调节门开到位 |  | digital
N1DCS.10HAD96AA002RC | 22643 | 高压汽包启动放水调节门在远控 |  | digital
N1DCS.10HAH90AA402CD | 22644 | 高压一级过热器疏水电动门关指令 |  | digital
N1DCS.10HAH90AA402CP | 22645 | 高压一级过热器疏水电动门关到位 |  | digital
N1DCS.10HAH90AA402F | 22646 | 高压一级过热器疏水电动门故障 |  | digital
N1DCS.10HAH90AA402OD | 22647 | 高压一级过热器疏水电动门开指令 |  | digital
N1DCS.10HAH90AA402OP | 22648 | 高压一级过热器疏水电动门开到位 |  | digital
N1DCS.10HAH90AA402RC | 22649 | 高压一级过热器疏水电动门在远控 |  | digital
N1DCS.10HAH90AA412CD | 22650 | 高压二级过热器疏水电动门关指令 |  | digital
N1DCS.10HAH90AA412CP | 22651 | 高压二级过热器疏水电动门关到位 |  | digital
N1DCS.10HAH90AA412F | 22652 | 高压二级过热器疏水电动门故障 |  | digital
N1DCS.10HAH90AA412OD | 22653 | 高压二级过热器疏水电动门开指令 |  | digital
N1DCS.10HAH90AA412OP | 22654 | 高压二级过热器疏水电动门开到位 |  | digital
N1DCS.10HAH90AA412RC | 22655 | 高压二级过热器疏水电动门在远控 |  | digital
N1DCS.10HAH90AA502CD | 22656 | 高压饱和蒸汽放空电动门关指令 |  | digital
N1DCS.10HAH90AA502CP | 22657 | 高压饱和蒸汽放空电动门关到位 |  | digital
N1DCS.10HAH90AA502F | 22658 | 高压饱和蒸汽放空电动门故障 |  | digital
N1DCS.10HAH90AA502OD | 22659 | 高压饱和蒸汽放空电动门开指令 |  | digital
N1DCS.10HAH90AA502OP | 22660 | 高压饱和蒸汽放空电动门开到位 |  | digital
N1DCS.10HAH90AA502RC | 22661 | 高压饱和蒸汽放空电动门在远控 |  | digital
N1DCS.10HAH90AA504CD | 22662 | 高压二级过热器出口放空门关指令 |  | digital
N1DCS.10HAH90AA504CP | 22663 | 高压二级过热器出口放空门关到位 |  | digital
N1DCS.10HAH90AA504F | 22664 | 高压二级过热器出口放空门故障 |  | digital
N1DCS.10HAH90AA504OD | 22665 | 高压二级过热器出口放空门开指令 |  | digital
N1DCS.10HAH90AA504OP | 22666 | 高压二级过热器出口放空门到位 |  | digital
N1DCS.10HAH90AA504RC | 22667 | 高压二级过热器出口放空门在远控 |  | digital
N1DCS.10LAB82AA001CD | 22668 | #2中压给水泵出口电动门关指令 |  | digital
N1DCS.10LAB82AA001CP | 22669 | #2中压给水泵出口电动门关到位 |  | digital
N1DCS.10LAB82AA001F | 22670 | #2中压给水泵出口电动门故障 |  | digital
N1DCS.10LAB82AA001OD | 22671 | #2中压给水泵出口电动门开指令 |  | digital
N1DCS.10LAB82AA001OP | 22672 | #2中压给水泵出口电动门开到位 |  | digital
N1DCS.10LAB82AA001RC | 22673 | #2中压给水泵出口电动门在远控 |  | digital
N1DCS.10LAB82AP001FW | 22674 | #2中压给水泵工作位置 |  | digital
N1DCS.10LAB82AP001PF | 22675 | #2中压给水泵综合故障 |  | digital
N1DCS.10LAB82AP001PS | 22676 | #2中压给水泵保护动作 |  | digital
N1DCS.10LAB82AP001RC | 22677 | #2中压给水泵在远控 |  | digital
N1DCS.10LAB82AP001RD | 22678 | #2中压给水泵启动指令 |  | digital
N1DCS.10LAB82AP001RP | 22679 | #2中压给水泵在运行 |  | digital
N1DCS.10LAB82AP001SW | 22680 | #2中压给水泵试验位置 |  | digital
N1DCS.10LAB82AP001TD | 22681 | #2中压给水泵停止指令 |  | digital
N1DCS.10LAB82AP001TP | 22682 | #2中压给水泵已停止 |  | digital
N1DCS.10LAB82AP001TP2 | 22683 | #2中压给水泵已停止 |  | digital
N1DCS.10LAB90AA101_AUTO | 22684 | 高压给水调节阀在自动 |  | digital
N1DCS.10LAB90AA101DVHI | 22685 | 高压给水调节阀指令反馈偏差大 |  | digital
N1DCS.10LAB92AA001CD | 22686 | #2高压给水泵出口电动门关指令 |  | digital
N1DCS.10LAB92AA001CP | 22687 | #2高压给水泵出口电动门关到位 |  | digital
N1DCS.10LAB92AA001F | 22688 | #2高压给水泵出口电动门故障 |  | digital
N1DCS.10LAB92AA001OD | 22689 | #2高压给水泵出口电动门开指令 |  | digital
N1DCS.10LAB92AA001OP | 22690 | #2高压给水泵出口电动门开到位 |  | digital
N1DCS.10LAB92AA001RC | 22691 | #2高压给水泵出口电动门远控 |  | digital
N1DCS.10LAB92AP001FW | 22692 | #2高压给水泵工作位置 |  | digital
N1DCS.10LAB92AP001PF | 22693 | #2高压给水泵综合故障 |  | digital
N1DCS.10LAB92AP001PS | 22694 | #2高压给水泵电气保护动作 |  | digital
N1DCS.10LAB92AP001RC | 22695 | #2高压给水泵在远控 |  | digital
N1DCS.10LAB92AP001RP | 22696 | #2高压给水泵在运行 |  | digital
N1DCS.10LAB92AP001SW | 22697 | #2高压给水泵试验位置 |  | digital
N1DCS.10LAB92AP001TP | 22698 | #2高压给水泵已停止 |  | digital
N1DCS.10LAB92AP001TP2 | 22699 | #2高压给水泵已停止 |  | digital
N1DCS.10LAB92CS001 | 22700 | #2高压给水泵反转 |  | digital
N1DCS.10LAC91_A | 22701 | #1高压给水泵在变频模式 |  | digital
N1DCS.10LAC91_B | 22702 | #2高压给水泵在变频模式 |  | digital
N1DCS.10LAC91GX0001_AUTO | 22703 | 高压给水泵变频器在自动 |  | digital
N1DCS.10LAC91GX0001_DVHI | 22704 | 高压给水泵变频器指令反馈偏差大 |  | digital
N1DCS.10LAC91GX0001_SPDH | 22705 | 高压给水泵变频器设定反馈偏差大 |  | digital
N1DCS.10LAC91GX0001CR | 22706 | 高压给水泵变频器充电中指示 |  | digital
N1DCS.10LAC91GX0001DC | 22707 | 高压给水泵变频器在DCS控制 |  | digital
N1DCS.10LAC91GX0001ED | 22708 | 高压给水泵变频器紧急停机指令 |  | digital
N1DCS.10LAC91GX0001LF | 22709 | 高压给水泵变频器轻故障指示 |  | digital
N1DCS.10LAC91GX0001LVLAUTO | 22710 | 高压给水泵变频器在三冲量调节 |  | digital
N1DCS.10LAC91GX0001PW | 22711 | 高压给水泵变频器启允许 |  | digital
N1DCS.10LAC91GX0001RD1 | 22712 | 高压给水泵变频器启动指令 |  | digital
N1DCS.10LAC91GX0001RP2 | 22713 | #2高压给水泵在变频运行 |  | digital
N1DCS.10LAC91GX0001RS | 22714 | 高压给水泵变频器复位指令 |  | digital
N1DCS.10LAC91GX0001SF | 22715 | 高压给水泵重故障指示 |  | digital
N1DCS.10LAC91GX0001TD1 | 22716 | 高压给水泵变频器停止指令 |  | digital
N1DCS.10LAC92AP001EH004 | 22717 | #2高压给水泵高压柜QS2合闸位置 |  | digital
N1DCS.10LAC92AP001EH005 | 22718 | #2高压给水泵高压柜QS4合闸位置 |  | digital
N1DCS.10LAC92AP001RD | 22719 | #2高压给水泵6KV开关合闸指令 |  | digital
N1DCS.10LAC92AP001TD | 22720 | #2高压给水泵6KV开关跳闸指令 |  | digital
N1DCS.10LAE90AA002CD | 22721 | 高压二级过热器减温水门关指令 |  | digital
N1DCS.10LAE90AA002CP | 22722 | 高压二级过热器减温水门关到位 |  | digital
N1DCS.10LAE90AA002F | 22723 | 高压二级过热器减温水门故障 |  | digital
N1DCS.10LAE90AA002OD | 22724 | 高压二级过热器减温水门开指令 |  | digital
N1DCS.10LAE90AA002OP | 22725 | 高压二级过热器减温水门开到位 |  | digital
N1DCS.10LAE90AA002RC | 22726 | 高压二级过热器减温水门在远控 |  | digital
N1DCS.10LAE90AA004CD | 22727 | 高压主蒸汽减温水电动门关指令 |  | digital
N1DCS.10LAE90AA004CP | 22728 | 高压主蒸汽减温水电动门关到位 |  | digital
N1DCS.10LAE90AA004F | 22729 | 高压主蒸汽减温水电动门故障 |  | digital
N1DCS.10LAE90AA004OD | 22730 | 高压主蒸汽减温水电动门开指令 |  | digital
N1DCS.10LAE90AA004OP | 22731 | 高压主蒸汽减温水电动门开到位 |  | digital
N1DCS.10LAE90AA004RC | 22732 | 高压主蒸汽减温水电动门在远控 |  | digital
N1DCS.10LAE90AA101_MRE | 22733 | 高压二级过热器减温水调阀报警 |  | digital
N1DCS.10LAE90AA102_MRE | 22734 | 高压主蒸汽减温水调阀报警 |  | digital
N1DCS.10LAE91AA101_AUTO | 22735 | 高压省煤器旁路调节阀在自动 |  | digital
N1DCS.10LAE91AA101_DVHI | 22736 | 高省旁路调阀指令反馈偏差大 |  | digital
N1DCS.10LAE91AA101_SPDH | 22737 | 高省旁路调阀设定反馈偏差大 |  | digital
N1DCS.10LBA90AA192CD | 22738 | 高压主蒸汽出口PCV阀关指令 |  | digital
N1DCS.10LBA90AA192CP | 22739 | 高压主蒸汽出口PCV阀关到位 |  | digital
N1DCS.10LBA90AA192OD | 22740 | 高压主蒸汽出口PCV阀开指令 |  | digital
N1DCS.10LBA90AA192OP | 22741 | 高压主蒸汽出口PCV阀开到位 |  | digital
N1DCS.10LBA90AA502CD | 22742 | 高压主蒸汽启动排汽电动门关指令 |  | digital
N1DCS.10LBA90AA502CP | 22743 | 高压主蒸汽启动排汽电动门关到位 |  | digital
N1DCS.10LBA90AA502F | 22744 | 高压主蒸汽启动排汽电动门故障 |  | digital
N1DCS.10LBA90AA502OD | 22745 | 高压主蒸汽启动排汽电动门开指令 |  | digital
N1DCS.10LBA90AA502OP | 22746 | 高压主蒸汽启动排汽电动门开到位 |  | digital
N1DCS.10LBA90AA502RC | 22747 | 高压主蒸汽启排汽电动门在远控 |  | digital
N1DCS.10LBG90AA001CD | 22748 | 辅汽至高压蒸发器电动门关指令 |  | digital
N1DCS.10LBG90AA001CP | 22749 | 辅汽至高压蒸发器电动门关到位 |  | digital
N1DCS.10LBG90AA001F | 22750 | 辅汽至高压蒸发器电动门故障 |  | digital
N1DCS.10LBG90AA001OD | 22751 | 辅汽至高压蒸发器电动门开指令 |  | digital
N1DCS.10LBG90AA001OP | 22752 | 辅汽至高压蒸发器电动门开到位 |  | digital
N1DCS.10LBG90AA001RC | 22753 | 辅汽至高压蒸发器电动门在远控 |  | digital
N1DCS.10XAV92CL001 | 22754 | #2高压给水泵稀油站油箱液位低 |  | digital
N1DCS.10XAV92CP001 | 22755 | #2高压给水泵稀油站滤网差压高 |  | digital
N1DCS.10XAV92GH001AP1RD | 22756 | #2高压给水泵稀油站#1油泵启指令 |  | digital
N1DCS.10XAV92GH001AP1TD | 22757 | #2高压给水泵稀油站#1油泵停指令 |  | digital
N1DCS.10XAV92GH001AP2RD | 22758 | #2高压给水泵稀油站#2油泵启指令 |  | digital
N1DCS.10XAV92GH001AP2TD | 22759 | #2高压给水泵稀油站#2油泵停指令 |  | digital
N1DCS.10XAV92GH001HTRD | 22760 | #2高压给水泵稀油站加热器启指令 |  | digital
N1DCS.10XAV92GH001HTTD | 22761 | #2高压给水泵稀油站加热器停指令 |  | digital
N1DCS.10XAV92GH001PF | 22762 | #2高给泵稀油站重大故障停主机 |  | digital
N1DCS.10XAV92GH001RC1 | 22763 | #2高压给水泵稀油站远程备妥 |  | digital
N1DCS.10XAV92GH001RC2 | 22764 | #2高压给水泵稀油站允许主机启动 |  | digital
N1DCS.10XAV92GH001RD1 | 22765 | #2高压给水泵稀油站远程驱动 |  | digital
N1DCS.10XAV92GH001RD2 | 22766 | #2高压给水泵在运行（送至稀油站 |  | digital
N1DCS.10XAV92GH001RP1 | 22767 | #2高给泵稀油站#1油泵在运行 |  | digital
N1DCS.10XAV92GH001RP2 | 22768 | #2高给泵稀油站#2油泵在运行 |  | digital
N1DCS.10XAV92GH001RP3 | 22769 | #2高给泵稀油站电加热器已投入 |  | digital
N1DCS.10XAV92GH002PF1 | 22770 | #2高压给水泵稀油站轻故障 |  | digital
N1DCS.GYSJGRQJKWD_MRE | 22771 | 高压三级过热器进口温度坏点 |  | digital
N1DCS.HP_DRN_ACD | 22772 | 高压蒸汽疏水门自动关 |  | digital
N1DCS.HPDRUMCP_MRE | 22773 | 高压汽包压力坏点 |  | digital
N1DCS.HPDRUMCTD_MRE | 22774 | 高压汽包下外壁温坏点 |  | digital
N1DCS.HPDRUMCTU_MRE | 22775 | 高压汽包上外壁温坏点 |  | digital
N1DCS.HPDRUMCTU2_MRE | 22776 | 高压汽包上内壁温坏点 |  | digital
N1DCS.HPDRUMLVL_AL | 22777 | 高压汽包液位（计算后）报警 |  | digital
N1DCS.HPDRUMLVL_HI | 22778 | 高压汽包液位（计算后）高 |  | digital
N1DCS.HPDRUMLVL_HII | 22779 | 高压汽包液位（计算后）高高 |  | digital
N1DCS.HPDRUMLVL_HIII | 22780 | 高压汽包液位（计算后）高高高 |  | digital
N1DCS.HPDRUMLVL_HIII1 | 22781 | 高压汽包液位1（计算后）高高高 |  | digital
N1DCS.HPDRUMLVL_HIII2 | 22782 | 高压汽包液位2（计算后）高高高 |  | digital
N1DCS.HPDRUMLVL_HIII3 | 22783 | 高压汽包液位3（计算后）高高高 |  | digital
N1DCS.HPDRUMLVL_LII | 22784 | 高压汽包液位（计算后）低低 |  | digital
N1DCS.HPDRUMLVL_LIII | 22785 | 高压汽包液位（计算后）低低低 |  | digital
N1DCS.HPDRUMLVL_LIII1 | 22786 | 高压汽包液位1（计算后）低低低 |  | digital
N1DCS.HPDRUMLVL_LIII2 | 22787 | 高压汽包液位2（计算后）低低低 |  | digital
N1DCS.HPDRUMLVL_LIII3 | 22788 | 高压汽包液位3（计算后）低低低 |  | digital
N1DCS.HPDRUMLVL_MRE | 22789 | 高压汽包液位（计算后）报警 |  | digital
N1DCS.HPDRUMLVLDEVHI | 22790 | 高压给水调阀设定反馈偏差大 |  | digital
N1DCS.HPDSTCF_MRE | 22791 | 高压主蒸汽流量（计算后）坏点 |  | digital
N1DCS.HPDSTCP_MRE | 22792 | 高压主蒸汽压力坏点 |  | digital
N1DCS.HPDSTCT_MRE | 22793 | 高压主蒸汽温度坏点 |  | digital
N1DCS.HPDWTCF_MRE | 22794 | 高压汽包给水流量(计算后)坏点 |  | digital
N1DCS.HPDWTCF_NORM | 22795 | 高压汽包给水流量(计算后)正常 |  | digital
N1DCS.HPDWTCT_MRE | 22796 | 高压汽包给水温度坏点 |  | digital
N1DCS.HPFW_SEQSTFINSH | 22797 | 高压汽包上水顺控已完成 |  | digital
N1DCS.HPFW3ELE | 22798 | 高压给水在三冲量调节 |  | digital
N1DCS.HPFWP_FRQ_RUN | 22799 | 任一高压给水泵在变频运行 |  | digital
N1DCS.HPFWP_FRQ_STOP | 22800 | 2台高压给水泵变频已停止 |  | digital
N1DCS.HPFWPB_RUN | 22801 | #2高压给水泵在运行(工频或变频) |  | digital
N1DCS.HPFWPB_STOP | 22802 | #2高压给水泵已停止(工频和变频) |  | digital
N1DCS.HPFWPB_STRPEM | 22803 | #2高压给水泵启动允许 |  | digital
N1DCS.HPFWPB_TEMPEM | 22804 | #2高压给水泵温度允许 |  | digital
N1DCS.HPFWPB_TEMPRT | 22805 | #2高压给水泵温度保护信号 |  | digital
N1DCS.HPFWPB_TP | 22806 | #2高压给水泵跳闸信号 |  | digital
N1DCS.HPFWPBMANSTOP | 22807 | #2高压给水泵手动停止指令 |  | digital
N1DCS.HPFWPBRUN | 22808 | #2高压给水泵在运行 |  | digital
N1DCS.HPMS_SEQSTFINISH | 22809 | 高压主汽升温升压顺控已完成 |  | digital
N1DCS.IPFWPB_STRPEM | 22810 | #2中压给水泵启动允许 |  | digital
N1DCS.IPFWPB_TEMPEM | 22811 | #2中压给水泵温度允许 |  | digital
N1DCS.IPFWPB_TEMPRT | 22812 | #2中压给水泵温度保护信号 |  | digital
N1DCS.IPFWPB_TP | 22813 | #2中压给水泵跳闸信号 |  | digital
N1DCS.IPFWPBMANSTOP | 22814 | #2中压给水泵手动停止指令 |  | digital
N1DCS.ONE9 | 22815 | 开关量1 |  | digital
N1DCS.ZERO9 | 22816 | 开关量0 |  | digital
N1DCS.10HAD90CLBS1 | 22817 | 高压汽包液位1（计算后）高高高 |  | digital
N1DCS.10HAD90CLBS2 | 22818 | 高压汽包液位2（计算后）高高高 |  | digital
N1DCS.10HAD90CLBS3 | 22819 | 高压汽包液位3（计算后）高高高 |  | digital
N1DCS.10LAC91GX0001LVLAUTO1 | 22820 | 高压变频器在单冲量调节 |  | digital
N1DCS.10LAE90AA002RC_N | 22821 | Ovation Control Builder |  | digital
N1DCS.10LAE90AA101_AUTO | 22822 | 高压二级过热器减温水调阀在自动 |  | digital
N1DCS.10LAE90AA101BHG | 22823 | Ovation Control Builder |  | digital
N1DCS.10LAE90AA101BHG1 | 22824 | Ovation Control Builder |  | digital
N1DCS.10LAE90AA101BHG2 | 22825 | Ovation Control Builder |  | digital
N1DCS.10LAE90AA102_AUTO | 22826 | 高压主蒸汽减温水调节阀在自动 |  | digital
N1DCS.10LAE90AA102BHG | 22827 | Ovation Control Builder |  | digital
N1DCS.10LAE90AA102BHG1 | 22828 | Ovation Control Builder |  | digital
N1DCS.10LAE90AA102BHG2 | 22829 | Ovation Control Builder |  | digital
N1DCS.10LAE90AA102PIDDVDI | 22830 | 高压主汽减温水阀设定反馈偏差大 |  | digital
N1DCS.10LAE91AA101CP | 22831 | 高压二级过热器减温水调阀全关位 |  | digital
N1DCS.CLOSEGAOYAPAIOK | 22832 | Ovation Control Builder |  | digital
N1DCS.CNSRVACMLOW | 22833 | Ovation Control Builder |  | digital
N1DCS.CZYLMZ | 22834 | 高压过热器出口压力正常(大于6.4 |  | digital
N1DCS.FAS | 22835 | Ovation Control Builder |  | digital
N1DCS.GYGSPMPBBP | 22836 | #2高压给水泵在变频位置 |  | digital
N1DCS.GYGSPMPBGP | 22837 | #2高压给水泵在工频位置 |  | digital
N1DCS.HPBPLVLDEVHI | 22838 | 高给变频器设定反馈偏差大 |  | digital
N1DCS.HPDRUMCT_MRE | 22839 | 高压汽包壁温坏点 |  | digital
N1DCS.HPDRUMCTC | 22840 | 高压汽包上下壁温差<60度 |  | digital
N1DCS.HPFW3ELE1 | 22841 | 高压给水在单冲量调节 |  | digital
N1DCS.HPFWPB_SEQBPSTFINISH | 22842 | #2高压给水泵变频启顺控已完成 |  | digital
N1DCS.HPFWPB_SEQSTFINISH | 22843 | #2高压给水泵工频启顺控已完成 |  | digital
N1DCS.HRSGTP1 | 22844 | 高压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTP10 | 22845 | 烟囱挡板全关 |  | digital
N1DCS.HRSGTP11 | 22846 | OPC或汽机跳闸30S后任一旁路未开 |  | digital
N1DCS.HRSGTP12 | 22847 | 凝汽器真空低跳闸联跳锅炉 |  | digital
N1DCS.HRSGTP13 | 22848 | 手动保护跳锅炉 |  | digital
N1DCS.HRSGTP14 | 22849 | 燃机保护跳闸联跳锅炉 |  | digital
N1DCS.HRSGTP1A | 22850 | 高压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTP2 | 22851 | 高压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTP2A | 22852 | 高压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTP3 | 22853 | 中压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTP3A | 22854 | 中压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTP4 | 22855 | 中压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTP4A | 22856 | 中压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTP5 | 22857 | 低压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTP5A | 22858 | 低压汽包液位（计算后）高高高 |  | digital
N1DCS.HRSGTP6 | 22859 | 低压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTP6A | 22860 | 低压汽包液位（计算后）低低低 |  | digital
N1DCS.HRSGTP7 | 22861 | 高压给水泵全停 |  | digital
N1DCS.HRSGTP8 | 22862 | 中压给水泵全停 |  | digital
N1DCS.HRSGTP9 | 22863 | 凝结水泵全停 |  | digital
N1DCS.HRSGTRIP | 22864 | 余热锅炉保护跳闸 |  | digital
N1DCS.HRSGTRIPRSPB | 22865 | 余热锅炉保护跳闸复位 |  | digital
N1DCS.KJK | 22866 | Ovation Control Builder |  | digital
N1DCS.KJK1 | 22867 | Ovation Control Builder |  | digital
N1DCS.KJK2 | 22868 | Ovation Control Builder |  | digital
N1DCS.WJG | 22869 | 主汽温降大 |  | digital
N1DCS.10AVC0025 | 22870 | AVC下位机遥信电源消失 |  | digital
N1DCS.10AVC0026 | 22871 | AVC投入/退出信号 |  | digital
N1DCS.10BBA00EH001 | 22872 | 6KV IA段母线PT保护装置故障 |  | digital
N1DCS.10BBA00EH002 | 22873 | 6kV IA段母线过压报警 |  | digital
N1DCS.10BBA00EH003 | 22874 | 6kV IA段母线低压报警 |  | digital
N1DCS.10BBA00EH004 | 22875 | 6kV IA段母线失压报警 |  | digital
N1DCS.10BBA00EH005 | 22876 | 6kV IA段母线接地报警 |  | digital
N1DCS.10BBA00EH006 | 22877 | 6kV IA段母线谐振报警 |  | digital
N1DCS.10BBA00EH101 | 22878 | 6KV IA段工作进线PT异常 |  | digital
N1DCS.10BBA00EH102 | 22879 | 6KV IA段工作进线PT保护小车位置 |  | digital
N1DCS.10BBA00GS001PF | 22880 | 6KV IA段工作开关保护异常总信号 |  | digital
N1DCS.10BBA00GS001PF1 | 22881 | 6KV IA段工作开关弧光保护故障 |  | digital
N1DCS.10BBA00GS001PS | 22882 | 6KV IA段工作开关弧光保护动作 |  | digital
N1DCS.10BBA00GS001RC | 22883 | 6kV IA段工作电源开关远方控制 |  | digital
N1DCS.10BBA00GS001RD | 22884 | 6kV IA段工作电源进线开关合指令 |  | digital
N1DCS.10BBA00GS001RP | 22885 | 6KV IA段工作进线开关合闸位置 |  | digital
N1DCS.10BBA00GS001SW | 22886 | 6KV IA段工作进线开关试验位置 |  | digital
N1DCS.10BBA00GS001TD | 22887 | 6kV IA段工作电源进线开关分指令 |  | digital
N1DCS.10BBA00GS001TP | 22888 | 6KV IA段工作进线开关分闸位置 |  | digital
N1DCS.10BBA00GS001TP1 | 22889 | 6KV IA段工作进线开关分闸位置 |  | digital
N1DCS.10BBA00GS001YW | 22890 | 6kV IA段工作进线开关工作位置 |  | digital
N1DCS.10BBB00EH201 | 22891 | 6kV IB段备用进线PT异常 |  | digital
N1DCS.10BBB00EH202 | 22892 | 6kV IB段备用进线PT保护小车位置 |  | digital
N1DCS.10BBB00GS001TP1 | 22893 | 6KV IB段工作进线开关分闸位置 |  | digital
N1DCS.10BBB00GS002PF | 22894 | 6kV IB段备用电源保护异常总信号 |  | digital
N1DCS.10BBB00GS002RC | 22895 | 6kV IB段备用电源开关远方控制 |  | digital
N1DCS.10BBB00GS002RD | 22896 | 6kV IB段备用电源进线开关合指令 |  | digital
N1DCS.10BBB00GS002RP | 22897 | 6kV IB段备用电源开关合闸位置 |  | digital
N1DCS.10BBB00GS002SW | 22898 | 6kV IB段备用电源开关试验位置 |  | digital
N1DCS.10BBB00GS002TD | 22899 | 6kV IB段备用电源进线开关分指令 |  | digital
N1DCS.10BBB00GS002TP | 22900 | 6kV IB段备用电源开关分闸位置 |  | digital
N1DCS.10BBB00GS002YW | 22901 | 6kV IB段备用电源开关工作位置 |  | digital
N1DCS.10BBB13GS001PF | 22902 | SFC隔离变馈线开关综合故障 |  | digital
N1DCS.10BBB13GS001PS | 22903 | SFC隔离变馈线开关电气保护动作 |  | digital
N1DCS.10BBB13GS001RP | 22904 | SFC隔离变馈线开关合闸位置 |  | digital
N1DCS.10BBB13GS001TP | 22905 | SFC隔离变馈线开关分闸位置 |  | digital
N1DCS.10BFA00EH201 | 22906 | 380V工作PC IA段母线电压低 |  | digital
N1DCS.10BFA00EH202 | 22907 | 380V工作PC IA段PT保护装置故障 |  | digital
N1DCS.10BFA00EH203 | 22908 | 380V工作PC IA段PT刀熔开关分位 |  | digital
N1DCS.10BFA00GS201PF | 22909 | 工作PC IA至保安段开关综合故障 |  | digital
N1DCS.10BFA00GS201RC | 22910 | 工作PC IA至保安段开关在远方 |  | digital
N1DCS.10BFA00GS201RD | 22911 | 工作PC IA至保安段开关合闸指令 |  | digital
N1DCS.10BFA00GS201RP | 22912 | 工作PC IA至保安段开关合闸位置 |  | digital
N1DCS.10BFA00GS201TD | 22913 | 工作PC IA至保安段开关分闸指令 |  | digital
N1DCS.10BFA00GS201TP | 22914 | 工作PC IA至保安段开关分闸位置 |  | digital
N1DCS.10BFB00GS001_PUT | 22915 | 机组工作PC段分段开关联锁投入 |  | digital
N1DCS.10BFB00GS001L_PUT | 22916 | 工作PC段分段开关允许并联运行 |  | digital
N1DCS.10BFB00GS001PF | 22917 | 机组工作PC段分段开关综合故障 |  | digital
N1DCS.10BFB00GS001RC | 22918 | 机组工作PC段分段开关远方控制 |  | digital
N1DCS.10BFB00GS001RD | 22919 | 机组工作PC段分段开关合闸指令 |  | digital
N1DCS.10BFB00GS001RP | 22920 | 机组工作PC段分段开关合闸位置 |  | digital
N1DCS.10BFB00GS001TD | 22921 | 机组工作PC段分段开关分闸指令 |  | digital
N1DCS.10BFB00GS001TP | 22922 | 机组工作PC段分段开关分闸位置 |  | digital
N1DCS.10BFT10GS101PF | 22923 | 工作IA变6kV侧开关综合故障 |  | digital
N1DCS.10BFT10GS101PS | 22924 | 工作IA变6kV侧开关保护动作 |  | digital
N1DCS.10BFT10GS101RC | 22925 | 工作IA变6kV侧开关远方控制 |  | digital
N1DCS.10BFT10GS101RD | 22926 | 工作IA变6kV侧开关合闸指令 |  | digital
N1DCS.10BFT10GS101RP | 22927 | 工作IA变6kV侧开关合闸位置 |  | digital
N1DCS.10BFT10GS101SW | 22928 | 工作IA变6kV侧开关试验位置 |  | digital
N1DCS.10BFT10GS101TD | 22929 | 工作IA变6kV侧开关分闸指令 |  | digital
N1DCS.10BFT10GS101TP | 22930 | 工作IA变6kV侧开关分闸位置 |  | digital
N1DCS.10BFT10GS101YW | 22931 | 工作IA变6kV侧开关工作位置 |  | digital
N1DCS.10BFT10GS102PF | 22932 | 工作IA变380V侧开关综合故障 |  | digital
N1DCS.10BFT10GS102RC | 22933 | 工作IA变380V侧开关远方控制 |  | digital
N1DCS.10BFT10GS102RD | 22934 | 工作IA变380V侧开关合闸指令 |  | digital
N1DCS.10BFT10GS102RP | 22935 | 工作IA变380V侧开关合闸位置 |  | digital
N1DCS.10BFT10GS102TD | 22936 | 工作IA变380V侧开关分闸指令 |  | digital
N1DCS.10BFT10GS102TP | 22937 | 工作IA变380V侧开关分闸位置 |  | digital
N1DCS.10BJA00GS201RP | 22938 | 工作PCIA至#1机MCCA开关合闸位置 |  | digital
N1DCS.10BJA00GS201TP | 22939 | 工作PCIA至#1机MCCA开关分闸位置 |  | digital
N1DCS.10BJB00GS201RP | 22940 | 工作PCIA至#1机MCCB开关合闸位置 |  | digital
N1DCS.10BJB00GS201TP | 22941 | 工作PCIA至#1机MCCB开关分闸位置 |  | digital
N1DCS.10BJC00GS201RP | 22942 | 工作PC IA至余炉MCC开关合闸位置 |  | digital
N1DCS.10BJC00GS201TP | 22943 | 工作PC IA至余炉MCC开关分闸位置 |  | digital
N1DCS.10BJD00GS201PF | 22944 | 工作PCIA至#2机MCCA开关综合故障 |  | digital
N1DCS.10BJD00GS201RC | 22945 | 工作PCIA至#2机MCCA开关远方控制 |  | digital
N1DCS.10BJD00GS201RD | 22946 | 工作PC IA至#2机MCC A开关合闸令 |  | digital
N1DCS.10BJD00GS201RP | 22947 | 工作PCIA至#2机MCCA开关合闸位置 |  | digital
N1DCS.10BJD00GS201TD | 22948 | 工作PC IA至#2机MCC A开关分闸令 |  | digital
N1DCS.10BJD00GS201TP | 22949 | 工作PCIA至#2机MCCA开关分闸位置 |  | digital
N1DCS.10BJE00GS201PF | 22950 | 工作PCIA至#2机MCCB开关综合故障 |  | digital
N1DCS.10BJE00GS201RC | 22951 | 工作PCIA至#2机MCCB开关远方控制 |  | digital
N1DCS.10BJE00GS201RD | 22952 | 工作PC IA至#2机MCC B开关合闸令 |  | digital
N1DCS.10BJE00GS201RP | 22953 | 工作PCIA至#2机MCCB开关合闸位置 |  | digital
N1DCS.10BJE00GS201TD | 22954 | 工作PC IA至#2机MCC B开关分闸令 |  | digital
N1DCS.10BJE00GS201TP | 22955 | 工作PCIA至#2机MCCB开关分闸位置 |  | digital
N1DCS.10BNA00GS201PF | 22956 | 保安段至#2机EMCC段开关综合故障 |  | digital
N1DCS.10BNA00GS201RC | 22957 | 保安段至#2机EMCC段开关远方控制 |  | digital
N1DCS.10BNA00GS201RD | 22958 | 保安段至#2机EMCC段馈线开关合闸 |  | digital
N1DCS.10BNA00GS201RP | 22959 | 保安段至#2机EMCC段开关合闸位置 |  | digital
N1DCS.10BNA00GS201TD | 22960 | 保安段至#2机EMCC段馈线开关分闸 |  | digital
N1DCS.10BNA00GS201TP | 22961 | 保安段至#2机EMCC段开关分闸位置 |  | digital
N1DCS.10CBQ01EH1_FL | 22962 | #1机组6kV A段快切装置故障 |  | digital
N1DCS.10CBQ01EH101 | 22963 | 6kV IA段快切装置启动正常切换 |  | digital
N1DCS.10CBQ01EH102 | 22964 | 6kV IA段快切装置手动闭锁 |  | digital
N1DCS.10CBQ01EH103 | 22965 | 6kV IA段快切装置远方复归 |  | digital
N1DCS.10CBQ01EH104 | 22966 | 6kV IA段快切装置合工作 |  | digital
N1DCS.10CBQ01EH105 | 22967 | 6kV IA段快切装置合备用 |  | digital
N1DCS.10CBQ01EH106 | 22968 | 6kV IA段快切装置总告警 |  | digital
N1DCS.10CBQ01EH107 | 22969 | 6kV IA段快切装置切换完毕 |  | digital
N1DCS.10CBQ01EH108 | 22970 | 6kV IA段快切装置电源失压 |  | digital
N1DCS.10CBQ01EH109 | 22971 | 6kV IA快切装置切换失败 |  | digital
N1DCS.10CBQ01EH110 | 22972 | 6kV IA段快切装置切换闭锁 |  | digital
N1DCS.10CBQ01EH111 | 22973 | 6kV IA段快切装置自动允许 |  | digital
N1DCS.10CBQ01EH112 | 22974 | 6kV IA段快切装置手动允许 |  | digital
N1DCS.10CBQ01EH113 | 22975 | 6kV IA段快切装置单操允许 |  | digital
N1DCS.11BAC01GS101TP2 | 22976 | #2发电机出口GCB开关分闸位(SOE) |  | digital
N1DCS.11CHA05EH116 | 22977 | #2主变油面温度高信号 |  | digital
N1DCS.11CHA05EH117 | 22978 | #1高厂变重瓦斯跳闸 |  | digital
N1DCS.11CHA05EH118 | 22979 | #1高厂变绕组温度过高跳闸 |  | digital
N1DCS.11CHA05EH119 | 22980 | #1高厂变本体突发压力跳闸 |  | digital
N1DCS.11CHA05EH120 | 22981 | #1高厂变油温高跳闸 |  | digital
N1DCS.11CHA05EH121 | 22982 | #2机励磁系统故障 |  | digital
N1DCS.11CHA05EH122 | 22983 | #2机励磁变温度保护跳闸 |  | digital
N1DCS.11CHA05EH123 | 22984 | #1高厂变轻瓦斯信号 |  | digital
N1DCS.11CHA05EH124 | 22985 | #1高厂变绕组温度高信号 |  | digital
N1DCS.11CHA05EH125 | 22986 | #1高厂变压力释放信号 |  | digital
N1DCS.11CHA05EH126 | 22987 | #1高厂变油位异常信号 |  | digital
N1DCS.11CHA05EH127 | 22988 | #1高厂变油温高信号 |  | digital
N1DCS.11CWA001PB006 | 22989 | 集控室操作台紧急跳闸指令 |  | digital
N1DCS.12AVC0021 | 22990 | DCS允许#1机AVC自动调节 |  | digital
N1DCS.12AVC0027 | 22991 | 增加#1机励磁信号 |  | digital
N1DCS.12AVC0028 | 22992 | 减少#1机励磁信号 |  | digital
N1DCS.12BAT01EH001 | 22993 | #1主变冷却器Ⅰ段电源运行 |  | digital
N1DCS.12BAT01EH002 | 22994 | #1主变冷却器Ⅱ段电源运行 |  | digital
N1DCS.12BAT01EH003 | 22995 | #1主变冷却器Ⅰ段电源故障 |  | digital
N1DCS.12BAT01EH004 | 22996 | #1主变冷却器Ⅱ段电源故障 |  | digital
N1DCS.12BAT01EH005 | 22997 | #1主变冷却器控制电源故障 |  | digital
N1DCS.12BAT01EH006 | 22998 | #1主变工作冷却器故障 |  | digital
N1DCS.12BAT01EH007 | 22999 | #1主变备用冷却器故障 |  | digital
N1DCS.12BAT01EH008 | 23000 | #1主变风冷全停 |  | digital
N1DCS.12BAT01EH009 | 23001 | #1主变辅助投入 |  | digital
N1DCS.12BAW20EH101 | 23002 | #1发电机PT端子箱空开分闸信号 |  | digital
N1DCS.12CBP01_PMT | 23003 | #1主变开关2201同期装置启允许 |  | digital
N1DCS.12CBP01EH201 | 23004 | #1主变开关2201同期允许(DEH来) |  | digital
N1DCS.12CBP01EH202 | 23005 | #1主变开关2201同期功角越限 |  | digital
N1DCS.12CBP01EH203 | 23006 | #1主变开关2201同期装置闭锁 |  | digital
N1DCS.12CBP01EH204 | 23007 | #1主变开关2201自动准同期启动 |  | digital
N1DCS.12CBP01EH205 | 23008 | #1主变开关2201自动准同期就绪 |  | digital
N1DCS.12CBP01EH206 | 23009 | #1主变开关2201同期失电告警 |  | digital
N1DCS.12CBP01EH207 | 23010 | #1主变开关2201同期总告警 |  | digital
N1DCS.12CBP01EJ511 | 23011 | #1主变2201自动准同期DTK投入 |  | digital
N1DCS.12CBP01EJ512 | 23012 | #1主变2201自动准同期DTK退出 |  | digital
N1DCS.12CBP01EJ513 | 23013 | #1主变2201自动准同期装置启动 |  | digital
N1DCS.12CBP01EJ514 | 23014 | #1主变2201自动准同期装置复位 |  | digital
N1DCS.12CBP01EJ515 | 23015 | 2201自动准同期装置紧急中断同期 |  | digital
N1DCS.12CBP01EJ518 | 23016 | #1主变开关2201同期请求(至DEH） |  | digital
N1DCS.12CEQ01EH001 | 23017 | #1发变组故障录波装置故障 |  | digital
N1DCS.12CEQ01EH002 | 23018 | #1发变组故障录波装置启动 |  | digital
N1DCS.12CEQ01EH003 | 23019 | #1发变组故障录波器失电报警 |  | digital
N1DCS.12CHA01EH101 | 23020 | #1发电机A套发电机差动跳闸 |  | digital
N1DCS.12CHA01EH102 | 23021 | #1发电机A套定子接地跳闸 |  | digital
N1DCS.12CHA01EH103 | 23022 | #1发电机A套匝间跳闸 |  | digital
N1DCS.12CHA01EH104 | 23023 | #1发电机A套过负荷跳闸 |  | digital
N1DCS.12CHA01EH105 | 23024 | #1发电机A套过电压保护跳闸 |  | digital
N1DCS.12CHA01EH106 | 23025 | #1发电机A套失磁保护跳闸 |  | digital
N1DCS.12CHA01EH107 | 23026 | #1发电机A套失步保护跳闸 |  | digital
N1DCS.12CHA01EH108 | 23027 | #1发电机A套负序过负荷跳闸 |  | digital
N1DCS.12CHA01EH109 | 23028 | #1发电机A套过励磁跳闸 |  | digital
N1DCS.12CHA01EH110 | 23029 | #1发电机A套频率保护跳闸 |  | digital
N1DCS.12CHA01EH111 | 23030 | #1发电机A套相间后备跳闸 |  | digital
N1DCS.12CHA01EH112 | 23031 | #1发电机A套误上电跳闸 |  | digital
N1DCS.12CHA01EH113 | 23032 | #1发电机A套逆功率跳闸 |  | digital
N1DCS.12CHA01EH114 | 23033 | #1发电机A套程序逆功率跳闸 |  | digital
N1DCS.12CHA01EH115 | 23034 | #1发电机A套启停机跳闸 |  | digital
N1DCS.12CHA01EH116 | 23035 | #1发电机A套低频保护跳闸 |  | digital
N1DCS.12CHA01EH117 | 23036 | #1发电机A套励磁后备跳闸 |  | digital
N1DCS.12CHA01EH118 | 23037 | #1主变A套非全相保护跳闸 |  | digital
N1DCS.12CHA01EH119 | 23038 | #1主变A套断路器闪络跳闸 |  | digital
N1DCS.12CHA01EH120 | 23039 | #1主变A套差动跳闸 |  | digital
N1DCS.12CHA01EH121 | 23040 | #1主变A套相间后备跳闸 |  | digital
N1DCS.12CHA01EH122 | 23041 | #1主变A套接地零序跳闸 |  | digital
N1DCS.12CHA01EH123 | 23042 | #1主变A套间隙零序跳闸 |  | digital
N1DCS.12CHA01EH124 | 23043 | #1发变组A套保护装置闭锁 |  | digital
N1DCS.12CHA01EH125 | 23044 | #1发变组A套保护装置报警 |  | digital
N1DCS.12CHA01EH126 | 23045 | #1发变组A套保护TA断线 |  | digital
N1DCS.12CHA01EH127 | 23046 | #1发变组A套保护TV断线 |  | digital
N1DCS.12CHA01EH128 | 23047 | #1发电机A套逆功率报警 |  | digital
N1DCS.12CHA01EH129 | 23048 | #1发电机A套过励磁报警 |  | digital
N1DCS.12CHA01EH130 | 23049 | #1发电机A套定子过负荷报警 |  | digital
N1DCS.12CHA01EH131 | 23050 | #1发电机A套负序过负荷报警 |  | digital
N1DCS.12CHA01EH132 | 23051 | #1发电机A套定子接地报警 |  | digital
N1DCS.12CHA01EH133 | 23052 | #1发电机A套频率报警 |  | digital
N1DCS.12CHA01EH134 | 23053 | #1主变A套保护切换继电器动作 |  | digital
N1DCS.12CHA01EH135 | 23054 | #1主变A套保护切换继电器失电 |  | digital
N1DCS.12CHA02EH101 | 23055 | #1主变B套差动保护动作 |  | digital
N1DCS.12CHA02EH102 | 23056 | #1发电机B套励磁主保护动作 |  | digital
N1DCS.12CHA02EH103 | 23057 | #1发电机B套差动保护动作 |  | digital
N1DCS.12CHA02EH104 | 23058 | #1发电机B套失灵启动保护动作 |  | digital
N1DCS.12CHA02EH105 | 23059 | #1主变B套非全相保护动作 |  | digital
N1DCS.12CHA02EH106 | 23060 | #1主变B套断口闪络保护动作 |  | digital
N1DCS.12CHA02EH107 | 23061 | #1发电机B套匝间保护动作 |  | digital
N1DCS.12CHA02EH108 | 23062 | #1发电机B套零序定子接地保护动 |  | digital
N1DCS.12CHA02EH109 | 23063 | #1发电机B套对称过负荷跳闸 |  | digital
N1DCS.12CHA02EH110 | 23064 | #1发电机B套负序过负荷跳闸 |  | digital
N1DCS.12CHA02EH111 | 23065 | #1发电机B套失磁保护动作 |  | digital
N1DCS.12CHA02EH112 | 23066 | #1发电机B套失步保护动作 |  | digital
N1DCS.12CHA02EH113 | 23067 | #1发电机B套过电压保护动作 |  | digital
N1DCS.12CHA02EH114 | 23068 | #1发电机B套过励磁保护动作 |  | digital
N1DCS.12CHA02EH115 | 23069 | #1发电机B套逆功率保护动作 |  | digital
N1DCS.12CHA02EH116 | 23070 | #1发电机B套频率异常跳闸 |  | digital
N1DCS.12CHA02EH117 | 23071 | #1发电机B套相间后备保护动作 |  | digital
N1DCS.12CHA02EH118 | 23072 | #1发电机B套起停机保护动作 |  | digital
N1DCS.12CHA02EH119 | 23073 | #1发电机B套误上电保护动作 |  | digital
N1DCS.12CHA02EH120 | 23074 | #1主变B套相间后备保护动作 |  | digital
N1DCS.12CHA02EH121 | 23075 | #1主变B套接地后备保护动作 |  | digital
N1DCS.12CHA02EH122 | 23076 | #1主变B套间隙后备保护动作 |  | digital
N1DCS.12CHA02EH123 | 23077 | #1机B套励磁后备与异常保护动 |  | digital
N1DCS.12CHA02EH124 | 23078 | #1机B套发变组保护TA异常 |  | digital
N1DCS.12CHA02EH125 | 23079 | #1机B套发变组保护TV异常 |  | digital
N1DCS.12CHA02EH126 | 23080 | #1机B套发变组保护差流越限 |  | digital
N1DCS.12CHA02EH127 | 23081 | #1主变B套启动通风告警 |  | digital
N1DCS.12CHA02EH128 | 23082 | #1发电机B套三次谐波定子接地 |  | digital
N1DCS.12CHA02EH129 | 23083 | #1机B套发变组保护装置告警 |  | digital
N1DCS.12CHA02EH130 | 23084 | #1机B套发变组保护失电告警 |  | digital
N1DCS.12CHA02EH131 | 23085 | #1机B套发变组保护失压告警 |  | digital
N1DCS.12CHA02EH132 | 23086 | #1机B套主变保护切换继电器动作 |  | digital
N1DCS.12CHA02EH133 | 23087 | #1机B套主变保护切换继电器失电 |  | digital
N1DCS.12CHA03EH101 | 23088 | #1机非电量保护装置闭锁 |  | digital
N1DCS.12CHA03EH102 | 23089 | #1机非电量保护装置报警 |  | digital
N1DCS.12CHA03EH103 | 23090 | #1主变非电量电源监视 |  | digital
N1DCS.12CHA03EH104 | 23091 | #1主变冷控失电延时跳闸 |  | digital
N1DCS.12CHA03EH105 | 23092 | #1机安稳装置切机 |  | digital
N1DCS.12CHA03EH106 | 23093 | #1主变本体重瓦斯跳闸 |  | digital
N1DCS.12CHA03EH107 | 23094 | #1主变油面温度高跳闸 |  | digital
N1DCS.12CHA03EH108 | 23095 | #1主变绕组温度高跳闸 |  | digital
N1DCS.12CHA03EH109 | 23096 | #1主变压力突变跳闸 |  | digital
N1DCS.12CHA03EH110 | 23097 | #1机母差及失灵联跳 |  | digital
N1DCS.12CHA03EH111 | 23098 | #1主变本体轻瓦斯信号 |  | digital
N1DCS.12CHA03EH112 | 23099 | #1主变绕组温度高信号 |  | digital
N1DCS.12CHA03EH113 | 23100 | #1主变油面温度高信号 |  | digital
N1DCS.12CHA03EH114 | 23101 | #1主变压力释放信号 |  | digital
N1DCS.12CHA03EH115 | 23102 | #1主变本体油位异常信号 |  | digital
N1DCS.12CHA03EH116 | 23103 | #1机励磁系统故障 |  | digital
N1DCS.12CHA03EH117 | 23104 | #1发电机转子一点接地保护跳闸 |  | digital
N1DCS.12CHA03EH118 | 23105 | #1机励磁变压器温度保护跳闸 |  | digital
N1DCS.12CHA03EH119 | 23106 | #1发变组操作箱第一控制回路断线 |  | digital
N1DCS.12CHA03EH120 | 23107 | #1发变组操作箱第二控制回路断线 |  | digital
N1DCS.12CHA03EH121 | 23108 | #1发变组操作箱第一出口跳闸 |  | digital
N1DCS.12CHA03EH122 | 23109 | #1发变组操作箱第二出口跳闸 |  | digital
N1DCS.12CHA03EH123 | 23110 | #1主变高压侧开关位置不一致 |  | digital
N1DCS.12CHA03EH124 | 23111 | #1机失步解列跳闸 |  | digital
N1DCS.12MKC01_ACK | 23112 | 励磁系统确认按钮 |  | digital
N1DCS.12MKC01_DPMT | 23113 | #1发电机减少励磁允许 |  | digital
N1DCS.12MKC01_UPMT | 23114 | #1发电机增加励磁允许 |  | digital
N1DCS.12MKC01EH001 | 23115 | #1机励磁系统励磁已投入 |  | digital
N1DCS.12MKC01EH002 | 23116 | #1机励磁系统励磁已退出 |  | digital
N1DCS.12MKC01EH003 | 23117 | #1机励磁系统自动控制已投入 |  | digital
N1DCS.12MKC01EH004 | 23118 | #1机励磁系统手动控制已投入 |  | digital
N1DCS.12MKC01EH005 | 23119 | #1机励磁系统就地控制已投入 |  | digital
N1DCS.12MKC01EH006 | 23120 | #1机励磁系统启动就绪 |  | digital
N1DCS.12MKC01EH007 | 23121 | #1机励磁系统故障 |  | digital
N1DCS.12MKC01EH008 | 23122 | #1机励磁系统过励限制 |  | digital
N1DCS.12MKC01EH009 | 23123 | #1机励磁系统欠励限制动作 |  | digital
N1DCS.12MKC01EH010 | 23124 | #1机励磁系统U/f限制动作 |  | digital
N1DCS.12MKC01EH011 | 23125 | #1机励磁系统起励失败 |  | digital
N1DCS.12MKC01EH012 | 23126 | #1机励磁系统设定值越限 |  | digital
N1DCS.12MKC01EH013 | 23127 | #1发电机定子电压检测故障 |  | digital
N1DCS.12MKC01EH014 | 23128 | #1机励磁系统无功调节已投入 |  | digital
N1DCS.12MKC01EH015 | 23129 | #1机励磁系统功率因数调节投入 |  | digital
N1DCS.12MKC01EH016 | 23130 | #1机励磁系统总报警 |  | digital
N1DCS.12MKC01EH017 | 23131 | #1机励磁系统控制通道1运行 |  | digital
N1DCS.12MKC01EH018 | 23132 | #1机励磁系统控制通道2运行 |  | digital
N1DCS.12MKC01EH019 | 23133 | #1机励磁系统有功率柜退出 |  | digital
N1DCS.12MKC01EH020 | 23134 | #1发电机灭磁开关合位 |  | digital
N1DCS.12MKC01EH021 | 23135 | #1发电机灭磁开关分位 |  | digital
N1DCS.12MKC01EH022 | 23136 | #1机灭磁开关分位 |  | digital
N1DCS.12MKC01EJ001 | 23137 | #1机励磁系统DCS增磁命令 |  | digital
N1DCS.12MKC01EJ002 | 23138 | #1机励磁系统DCS减磁命令 |  | digital
N1DCS.12MKC01EJ003 | 23139 | #1机励磁系统DCS起励 |  | digital
N1DCS.12MKC01EJ004 | 23140 | #1机励磁系统DCS灭磁 |  | digital
N1DCS.12MKC01EJ005 | 23141 | #1机励磁系统切换至自动模式 |  | digital
N1DCS.12MKC01EJ006 | 23142 | #1机励磁系统切换至手动模式 |  | digital
N1DCS.12MKC01EJ007 | 23143 | #1机励磁系统切至恒无功功率调节 |  | digital
N1DCS.12MKC01EJ008 | 23144 | #1机励磁系统切至恒功率因数调节 |  | digital
N1DCS.ECSALMA1 | 23145 |  |  | digital
N1DCS.ECSALMA2 | 23146 |  |  | digital
N1DCS.10CBQ01EH113A | 23147 | 6KV IA段快切装置切换允许 |  | digital
N1DCS.AVCEXCNDOWN | 23148 | AVC减磁 |  | digital
N1DCS.AVCEXCNUP | 23149 | AVC增磁 |  | digital
N1DCS.BALMALL1 | 23150 | 发电机漏水 |  | digital
N1DCS.BALMUNACK1 | 23151 | 发电机漏水确认 |  | digital
N1DCS.EALM001 | 23152 | 6KV IA段母线PT保护装置故障 |  | digital
N1DCS.EALM002 | 23153 | 6kV IA段母线过压报警 |  | digital
N1DCS.EALM003 | 23154 | 6kV IA段母线低压报警 |  | digital
N1DCS.EALM004 | 23155 | 6kV IA段母线失压报警 |  | digital
N1DCS.EALM005 | 23156 | 6kV IA段母线接地报警 |  | digital
N1DCS.EALM006 | 23157 | 6kV IA段母线谐振报警 |  | digital
N1DCS.EALM007 | 23158 | 6kV IA段快切装置启动正常切换 |  | digital
N1DCS.EALM008 | 23159 | 6kV IA段快切装置总告警 |  | digital
N1DCS.EALM009 | 23160 | 6KV IB段母线PT保护装置故障 |  | digital
N1DCS.EALM010 | 23161 | 6KV IB段母线过压报警 |  | digital
N1DCS.EALM011 | 23162 | 6KV IB段母线低压报警 |  | digital
N1DCS.EALM012 | 23163 | 6KV IB段母线失压报警 |  | digital
N1DCS.EALM013 | 23164 | 6KV IB段母线接地报警 |  | digital
N1DCS.EALM014 | 23165 | 6KV IB段母线谐振报警 |  | digital
N1DCS.EALM015 | 23166 | 6kV IB段快切装置启动正常切换 |  | digital
N1DCS.EALM016 | 23167 | 6kV IB段快切装置总告警 |  | digital
N1DCS.EALM017 | 23168 | 6KV IA段工作分支PT异常 |  | digital
N1DCS.EALM018 | 23169 | 6KV IB段工作分支PT异常 |  | digital
N1DCS.EALM019 | 23170 | 生产办公楼A变6kV侧开关异常跳闸 |  | digital
N1DCS.EALM020 | 23171 | 机组公用A变6kV侧开关异常跳闸 |  | digital
N1DCS.EALM021 | 23172 | 厂区公用A变6kV侧开关异常跳闸 |  | digital
N1DCS.EALM022 | 23173 | 补给水A变6kV侧开关异常跳闸 |  | digital
N1DCS.EALM023 | 23174 | 进气冷却A变6kV侧开关异常跳闸 |  | digital
N1DCS.EALM024 | 23175 | #1机组保安段备自投装置故障 |  | digital
N1DCS.EALM025 | 23176 | #1机组保安段母线异常 |  | digital
N1DCS.EALM026 | 23177 | 柴油发电机异常 |  | digital
N1DCS.EALM027 | 23178 | 110V直流母线电压低 |  | digital
N1DCS.EALM028 | 23179 | 110V直流蓄电池故障 |  | digital
N1DCS.EALM029 | 23180 | 220V直流母线电压低 |  | digital
N1DCS.EALM030 | 23181 | 220V直流蓄电池故障 |  | digital
N1DCS.EALM031 | 23182 | UPS主控柜故障 |  | digital
N1DCS.EALM032 | 23183 | 发电机漏水 |  | digital
N1DCS.EALM32 | 23184 | 发电机漏水 |  | digital
N1DCS.EALMALL | 23185 | #1机电气光字牌报警汇总1 |  | digital
N1DCS.EALMUNACK | 23186 | #1机电气光字牌报警手动确认指令 |  | digital
N1DCS.LCALARM | 23187 | #1机励磁故障总信号 |  | digital
N1DCS.ON10 | 23188 | 开关量1 |  | digital
N1DCS.QJBW_SEQSTACKOK | 23189 | #1机并网前各刀闸在正确位置 |  | digital
N1DCS.QJBW_SEQSTFINISH | 23190 | #1机并网顺控控已完成 |  | digital
N1DCS.QJTQYX1 | 23191 | #1机并网允许条件 |  | digital
N1DCS.ZERO10 | 23192 | 开关量0 |  | digital
N1DCS.10BBA00EH201 | 23193 | 6KV IA段备用分支PT异常 |  | digital
N1DCS.10BBA00EH202 | 23194 | 6KV IA段备用分支PT保护小车位置 |  | digital
N1DCS.10BBA00GS002PF | 23195 | 6KV开关61A02保护装置异常总信号 |  | digital
N1DCS.10BBA00GS002RC | 23196 | 6KV IA段备用进线开关远方控制 |  | digital
N1DCS.10BBA00GS002RD | 23197 | 6KV IA段备用电源进线开关合闸 |  | digital
N1DCS.10BBA00GS002RP | 23198 | 6KV IA段备用进线开关合闸位置 |  | digital
N1DCS.10BBA00GS002SW | 23199 | 6KV IA段备用进线开关试验位置 |  | digital
N1DCS.10BBA00GS002TD | 23200 | 6KV IA段备用电源进线开关分闸 |  | digital
N1DCS.10BBA00GS002TP | 23201 | 6KV IA段备用进线开关分闸位置 |  | digital
N1DCS.10BBA00GS002YW | 23202 | 6KV IA段备用进线开关工作位置 |  | digital
N1DCS.10BBB00EH001 | 23203 | 6KV IB段母线PT保护装置故障 |  | digital
N1DCS.10BBB00EH002 | 23204 | 6KV IB段母线过压报警 |  | digital
N1DCS.10BBB00EH003 | 23205 | 6KV IB段母线低压报警 |  | digital
N1DCS.10BBB00EH004 | 23206 | 6KV IB段母线失压报警 |  | digital
N1DCS.10BBB00EH005 | 23207 | 6KV IB段母线接地报警 |  | digital
N1DCS.10BBB00EH006 | 23208 | 6KV IB段母线谐振报警 |  | digital
N1DCS.10BBB00EH101 | 23209 | 6kV IB段工作分支PT异常 |  | digital
N1DCS.10BBB00EH102 | 23210 | 6kV IB段工作分支PT保护小车位置 |  | digital
N1DCS.10BBB00GS001PF | 23211 | 6KV开关61B01保护装置异常总信号 |  | digital
N1DCS.10BBB00GS001PF1 | 23212 | 6KV开关61B01弧光保护装置故障 |  | digital
N1DCS.10BBB00GS001PS1 | 23213 | 6KV开关61B01弧光保护动作 |  | digital
N1DCS.10BBB00GS001RC | 23214 | 6KV IB段工作进线开关远方控制 |  | digital
N1DCS.10BBB00GS001RD | 23215 | 6KV IB段工作电源进线开关合闸 |  | digital
N1DCS.10BBB00GS001RP | 23216 | 6KV IB段工作进线开关合闸位置 |  | digital
N1DCS.10BBB00GS001SW | 23217 | 6KV IB段工作进线开关试验位置 |  | digital
N1DCS.10BBB00GS001TD | 23218 | 6KV IB段工作电源进线开关分闸 |  | digital
N1DCS.10BBB00GS001TP | 23219 | 6KV IB段工作进线开关分闸位置 |  | digital
N1DCS.10BBB00GS001YW | 23220 | 6KV IB段工作进线开关工作位置 |  | digital
N1DCS.10BBT01_DPMT | 23221 | #1高厂变有载调压降压允许 |  | digital
N1DCS.10BBT01_UPMT | 23222 | #1高厂变有载调压升压允许 |  | digital
N1DCS.10BBT01EH901 | 23223 | 高厂变有载调压开关分接头位置1 |  | digital
N1DCS.10BBT01EH902 | 23224 | 高厂变有载调压开关分接头位置2 |  | digital
N1DCS.10BBT01EH903 | 23225 | 高厂变有载调压开关分接头位置3 |  | digital
N1DCS.10BBT01EH904 | 23226 | 高厂变有载调压开关分接头位置4 |  | digital
N1DCS.10BBT01EH905 | 23227 | 高厂变有载调压开关分接头位置5 |  | digital
N1DCS.10BBT01EH906 | 23228 | 高厂变有载调压开关分接头位置6 |  | digital
N1DCS.10BBT01EH907 | 23229 | 高厂变有载调压开关分接头位置7 |  | digital
N1DCS.10BBT01EH908 | 23230 | 高厂变有载调压开关分接头位置8 |  | digital
N1DCS.10BBT01EH909A | 23231 | 高厂变有载调压开关分接头位置9A |  | digital
N1DCS.10BBT01EH909B | 23232 | 高厂变有载调压开关分接头位置9B |  | digital
N1DCS.10BBT01EH909C | 23233 | 高厂变有载调压开关分接头位置9C |  | digital
N1DCS.10BBT01EH910 | 23234 | 高厂变有载调压开关分接头位置10 |  | digital
N1DCS.10BBT01EH911 | 23235 | 高厂变有载调压开关分接头位置11 |  | digital
N1DCS.10BBT01EH912 | 23236 | 高厂变有载调压开关分接头位置12 |  | digital
N1DCS.10BBT01EH913 | 23237 | 高厂变有载调压开关分接头位置13 |  | digital
N1DCS.10BBT01EH914 | 23238 | 高厂变有载调压开关分接头位置14 |  | digital
N1DCS.10BBT01EH915 | 23239 | 高厂变有载调压开关分接头位置15 |  | digital
N1DCS.10BBT01EH916 | 23240 | 高厂变有载调压开关分接头位置16 |  | digital
N1DCS.10BBT01EH917 | 23241 | 高厂变有载调压开关分接头位置17 |  | digital
N1DCS.10BBT01GS001PF | 23242 | #1高厂变有载调压故障 |  | digital
N1DCS.10BBT01GS001PS | 23243 | #1高厂变有载调压切换操作未完成 |  | digital
N1DCS.10BBT01GS001RC | 23244 | #1高厂变有载调压远方控制 |  | digital
N1DCS.10BBT01GS001RD1 | 23245 | #1高厂变有载调压开关升压 |  | digital
N1DCS.10BBT01GS001RD2 | 23246 | #1高厂变有载调压开关降压 |  | digital
N1DCS.10BBT01GS001RP | 23247 | #1高厂变有载调压开关正在调压 |  | digital
N1DCS.10BBT01GS001TD | 23248 | #1高厂变有载调压开关停止调压 |  | digital
N1DCS.10BFB00EH201 | 23249 | 380V机组工作PC IB段母线电压低 |  | digital
N1DCS.10BFB00EH202 | 23250 | 380V工作PC IB段PT保护装置故障 |  | digital
N1DCS.10BFB00EH203 | 23251 | 380V工作PC IB段PT刀熔开关分位 |  | digital
N1DCS.10BFB00GS201PF | 23252 | 工作PC IB至保安段开关综合故障 |  | digital
N1DCS.10BFB00GS201RC | 23253 | 工作PC IB至保安段开关在远控 |  | digital
N1DCS.10BFB00GS201RD | 23254 | 工作PC IB至保安段开关合闸指令 |  | digital
N1DCS.10BFB00GS201RP | 23255 | 工作PC IB至保安段开关合闸位置 |  | digital
N1DCS.10BFB00GS201TD | 23256 | 工作PC IB至保安段开关分闸指令 |  | digital
N1DCS.10BFB00GS201TP | 23257 | 工作PC IB至保安段开关分闸位置 |  | digital
N1DCS.10BFT20GS101PF | 23258 | 6KV开关61B10保护装置异常总信号 |  | digital
N1DCS.10BFT20GS101PS | 23259 | 工作IB变6kV侧开关保护动作 |  | digital
N1DCS.10BFT20GS101RC | 23260 | 工作IB变6kV侧开关远方控制 |  | digital
N1DCS.10BFT20GS101RD | 23261 | 工作IB变6kV侧开关合闸指令 |  | digital
N1DCS.10BFT20GS101RP | 23262 | 工作IB变6kV侧开关合闸位置 |  | digital
N1DCS.10BFT20GS101SW | 23263 | 工作IB变6kV侧开关试验位置 |  | digital
N1DCS.10BFT20GS101TD | 23264 | 工作IB变6kV侧开关分闸指令 |  | digital
N1DCS.10BFT20GS101TP | 23265 | 工作IB变6kV侧开关分闸位置 |  | digital
N1DCS.10BFT20GS101YW | 23266 | 工作IB变6kV侧开关工作位置 |  | digital
N1DCS.10BFT20GS102PF | 23267 | 工作IB变380V侧开关综合故障 |  | digital
N1DCS.10BFT20GS102RC | 23268 | 工作IB变380V侧开关远方控制 |  | digital
N1DCS.10BFT20GS102RD | 23269 | 工作IB变380V侧开关合闸指令 |  | digital
N1DCS.10BFT20GS102RP | 23270 | 工作IB变380V侧开关合闸位置 |  | digital
N1DCS.10BFT20GS102TD | 23271 | 工作IB变380V侧开关分闸指令 |  | digital
N1DCS.10BFT20GS102TP | 23272 | 工作IB变380V侧开关分闸位置 |  | digital
N1DCS.10BJA00GS202RP | 23273 | 工作PCIB至#1机MCCA开关合闸位置 |  | digital
N1DCS.10BJA00GS202TP | 23274 | 工作PCIB至#1机MCCA开关分闸位置 |  | digital
N1DCS.10BJB00GS202RP | 23275 | 工作PCIB至#1机MCCB开关合闸位置 |  | digital
N1DCS.10BJB00GS202TP | 23276 | 工作PCIB至#1机MCCB开关分闸位置 |  | digital
N1DCS.10BJC00GS202RP | 23277 | 工作PC IB至余炉MCC开关合闸位置 |  | digital
N1DCS.10BJC00GS202TP | 23278 | 工作PC IB至余炉MCC开关分闸位置 |  | digital
N1DCS.10BJD00GS202PF | 23279 | 工作PCIB至#2机MCCA开关综合故障 |  | digital
N1DCS.10BJD00GS202RC | 23280 | 工作PCIB至#2机MCCA开关远方控制 |  | digital
N1DCS.10BJD00GS202RD | 23281 | 工作PC IB至#2机MCC A开关合指令 |  | digital
N1DCS.10BJD00GS202RP | 23282 | 工作PCIB至#2机MCCA开关合闸位置 |  | digital
N1DCS.10BJD00GS202TD | 23283 | 工作PC IB至#2机MCC A开关分指令 |  | digital
N1DCS.10BJD00GS202TP | 23284 | 工作PCIB至#2机MCCA开关分闸位置 |  | digital
N1DCS.10BJE00GS202PF | 23285 | 工作PCIB至#2机MCCB开关综合故障 |  | digital
N1DCS.10BJE00GS202RC | 23286 | 工作PCIB至#2机MCCB开关远方控制 |  | digital
N1DCS.10BJE00GS202RD | 23287 | 工作PCIB至#2机MCC B开关合指令 |  | digital
N1DCS.10BJE00GS202RP | 23288 | 工作PCIB至#2机MCCB开关合闸位置 |  | digital
N1DCS.10BJE00GS202TD | 23289 | 工作PCIB至#2机MCC B开关分指令 |  | digital
N1DCS.10BJE00GS202TP | 23290 | 工作PCIB至#2机MCCB开关分闸位置 |  | digital
N1DCS.10BMA00EH201 | 23291 | 380V保安段母线电压低 |  | digital
N1DCS.10BMA00EH202 | 23292 | 380V保安段PT保护装置故障 |  | digital
N1DCS.10BMA00GS001_PUT | 23293 | 保安段备自投装置已投入 |  | digital
N1DCS.10BMA00GS001PF | 23294 | 保安段柴油机进线K11开关故障 |  | digital
N1DCS.10BMA00GS001RC | 23295 | 保安段柴油机进线K11开关在远控 |  | digital
N1DCS.10BMA00GS001RD | 23296 | 保安段柴油机进线K11开关合闸令 |  | digital
N1DCS.10BMA00GS001RP | 23297 | 保安段柴油机进线K11开关合闸位 |  | digital
N1DCS.10BMA00GS001TD | 23298 | 保安段柴油机进线K11开关分闸令 |  | digital
N1DCS.10BMA00GS001TP | 23299 | 保安段柴油机进线K11开关分闸位 |  | digital
N1DCS.10BMA00GS002_PUT | 23300 | 保安段备自投装置已投入 |  | digital
N1DCS.10BMA00GS002PF | 23301 | 保安段工作进线K12开关综合故障 |  | digital
N1DCS.10BMA00GS002RC | 23302 | 保安段工作进线K12开关远方控制 |  | digital
N1DCS.10BMA00GS002RD | 23303 | 保安段工作进线K12开关合闸指令 |  | digital
N1DCS.10BMA00GS002RP | 23304 | 保安段工作进线K12开关合闸位置 |  | digital
N1DCS.10BMA00GS002TD | 23305 | 保安段工作进线K12开关分闸指令 |  | digital
N1DCS.10BMA00GS002TP | 23306 | 保安段工作进线K12开关分闸位置 |  | digital
N1DCS.10BMA00GS003_PUT | 23307 | 保安段备自投装置已投入 |  | digital
N1DCS.10BMA00GS003PF | 23308 | 保安段工作进线K13开关综合故障 |  | digital
N1DCS.10BMA00GS003RC | 23309 | 保安段工作进线K13开关远方控制 |  | digital
N1DCS.10BMA00GS003RD | 23310 | 保安段工作进线K13开关合闸指令 |  | digital
N1DCS.10BMA00GS003RP | 23311 | 保安段工作进线K13开关合闸位置 |  | digital
N1DCS.10BMA00GS003TD | 23312 | 保安段工作进线K13开关分闸指令 |  | digital
N1DCS.10BMA00GS003TP | 23313 | 保安段工作进线K13开关分闸位置 |  | digital
N1DCS.10BNA00GS202PF | 23314 | 工作PCIB至#2机EMCC开关综合故障 |  | digital
N1DCS.10BNA00GS202RC | 23315 | 工作PCIB至#2机EMCC开关远方控制 |  | digital
N1DCS.10BNA00GS202RD | 23316 | 工作PCIB至#2机EMCC开关合闸指令 |  | digital
N1DCS.10BNA00GS202RP | 23317 | 工作PCIB至#2机EMCC开关合闸位置 |  | digital
N1DCS.10BNA00GS202TD | 23318 | 工作PCIB至#2机EMCC开关分闸指令 |  | digital
N1DCS.10BNA00GS202TP | 23319 | 工作PCIB至#2机EMCC开关分闸位置 |  | digital
N1DCS.10BRU01EH001 | 23320 | #1机组UPS系统主机柜1综合报警 |  | digital
N1DCS.10BRU01EH003 | 23321 | #1机组UPS系统主机柜2综合报警 |  | digital
N1DCS.10BRU02EH002 | 23322 | #1机组UPS系统配电开关报警 |  | digital
N1DCS.10BTB01EH001 | 23323 | #1机110V直流#1电池组熔断 |  | digital
N1DCS.10BTB02EH001 | 23324 | #1机110V直流#2电池组熔断 |  | digital
N1DCS.10BTL01EH001 | 23325 | #1机220V直流系统交流电源告警 |  | digital
N1DCS.10BTL01EH002 | 23326 | #1机220V直流系统整流模块告警 |  | digital
N1DCS.10BTL01EH003 | 23327 | #1机220V直流系统蓄电池组告警 |  | digital
N1DCS.10BTL01EH004 | 23328 | #1机220V直流系统直流母线告警 |  | digital
N1DCS.10BTL01EH005 | 23329 | #1机220V直流系统直流配电告警 |  | digital
N1DCS.10BTL01EH006 | 23330 | #1机220V直流系统通信中断告警 |  | digital
N1DCS.10BTL01EH007 | 23331 | #1机220V直流系统微机监控故障 |  | digital
N1DCS.10BTL01EH008 | 23332 | #1机220V直流联络开关合闸报警 |  | digital
N1DCS.10BTM01EH001 | 23333 | #1机110V直流A段交流电源告警 |  | digital
N1DCS.10BTM01EH002 | 23334 | #1机110V直流A段整流模块告警 |  | digital
N1DCS.10BTM01EH003 | 23335 | #1机110V直流#1蓄电池组告警 |  | digital
N1DCS.10BTM01EH004 | 23336 | #1机110V直流A段直流母线告警 |  | digital
N1DCS.10BTM01EH005 | 23337 | #1机110V直流A段直流配电告警 |  | digital
N1DCS.10BTM01EH006 | 23338 | #1机110V直流A段通信中断告警 |  | digital
N1DCS.10BTM01EH007 | 23339 | #1机110V直流A段微机监控故障 |  | digital
N1DCS.10BTM02EH001 | 23340 | #1机110V直流B段交流电源告警 |  | digital
N1DCS.10BTM02EH002 | 23341 | #1机110V直流B段整流模块告警 |  | digital
N1DCS.10BTM02EH003 | 23342 | #1机110V直流#2蓄电池组告警 |  | digital
N1DCS.10BTM02EH004 | 23343 | #1机110V直流B段直流母线告警 |  | digital
N1DCS.10BTM02EH005 | 23344 | #1机110V直流B段直流配电告警 |  | digital
N1DCS.10BTM02EH006 | 23345 | #1机110V直流B段通信中断告警 |  | digital
N1DCS.10BTM02EH007 | 23346 | #1机110V直流B段微机监控故障 |  | digital
N1DCS.10CBQ01EH2_FL | 23347 | 6kV IB段快切装置故障 |  | digital
N1DCS.10CBQ01EH201 | 23348 | 6kV IB段快切装置启动正常切换 |  | digital
N1DCS.10CBQ01EH202 | 23349 | 6kV IB段快切装置手动闭锁 |  | digital
N1DCS.10CBQ01EH203 | 23350 | 6kV IB段快切装置远方复归 |  | digital
N1DCS.10CBQ01EH204 | 23351 | 6kV IB段快切装置合工作 |  | digital
N1DCS.10CBQ01EH205 | 23352 | 6kV IB段快切装置合备用 |  | digital
N1DCS.10CBQ01EH206 | 23353 | 6kV IB段快切装置总告警 |  | digital
N1DCS.10CBQ01EH207 | 23354 | 6kV IB段快切装置切换完毕 |  | digital
N1DCS.10CBQ01EH208 | 23355 | 6kV IB段快切装置电源失压 |  | digital
N1DCS.10CBQ01EH209 | 23356 | 6kV IB段快切装置切换失败 |  | digital
N1DCS.10CBQ01EH210 | 23357 | 6kV IB段快切装置切换闭锁 |  | digital
N1DCS.10CBQ01EH211 | 23358 | 6kV IB段快切装置自动允许 |  | digital
N1DCS.10CBQ01EH212 | 23359 | 6kV IB段快切装置手动允许 |  | digital
N1DCS.10CBQ01EH213 | 23360 | 6kV IB段快切装置单操 |  | digital
N1DCS.10CBQ02EH101 | 23361 | #1机保安段备自投远方手动切换 |  | digital
N1DCS.10CBQ02EH102 | 23362 | #1机保安段备自投信号复归 |  | digital
N1DCS.10CBQ02EH103 | 23363 | #1机保安段备自投远方闭锁 |  | digital
N1DCS.10CBQ02EH104 | 23364 | #1机保安段备自投动作 |  | digital
N1DCS.10CBQ02EH105 | 23365 | #1机保安段备自投装置故障报警 |  | digital
N1DCS.10CBQ02EH106 | 23366 | #1机保安段备自投装置已闭锁 |  | digital
N1DCS.10CBQ02EH107 | 23367 | #1机保安段备自投装置失电告警 |  | digital
N1DCS.10MJA01EH001 | 23368 | #1机柴油发电机水温故障 |  | digital
N1DCS.10MJA01EH002 | 23369 | #1机柴油发电机低油压故障 |  | digital
N1DCS.10MJA01EH003 | 23370 | #1机柴油发电机超速故障 |  | digital
N1DCS.10MJA01EH004 | 23371 | #1机柴油发电机三次启动失败 |  | digital
N1DCS.10MJA01EH005 | 23372 | #1机柴油发电机运行正常 |  | digital
N1DCS.10MJA01EH006 | 23373 | #1机柴油发电机系统处于自动 |  | digital
N1DCS.10MJA01EH007 | 23374 | #1机柴油发电机蓄电池电压低报警 |  | digital
N1DCS.10MJA01EH008 | 23375 | #1机柴油发电机公共预报警 |  | digital
N1DCS.10MJA01EH009 | 23376 | #1机柴油发电机公共报警 |  | digital
N1DCS.10MJA01EH010 | 23377 | #1机柴油发电机差动保护 |  | digital
N1DCS.10MJA01EH011 | 23378 | #1机柴油发电机DC 24V电源丢失 |  | digital
N1DCS.10MJA01EH012 | 23379 | #1机柴油发电机DC 110V电源丢失 |  | digital
N1DCS.10MJA01GS001RP | 23380 | #1机柴油发电机K0开关合闸状态 |  | digital
N1DCS.10MJA01GS001TP | 23381 | #1机柴油发电机K0开关分闸状态 |  | digital
N1DCS.11BAC01GS101RP | 23382 | #2发电机出口GCB开关合闸位置 |  | digital
N1DCS.11BAC01GS101TP | 23383 | #2发电机出口GCB开关分闸位置 |  | digital
N1DCS.11BAC01GS201RP | 23384 | #2发电机出口隔离开关8020合位置 |  | digital
N1DCS.11BAC01GS201TP | 23385 | #2发电机出口隔离开关8020分位置 |  | digital
N1DCS.11BAC01GS202RP | 23386 | #2发电机SFC启动开关8021合位置 |  | digital
N1DCS.11BAC01GS202TP | 23387 | #2发电机SFC启动开关8021分位置 |  | digital
N1DCS.11BAC01GS301RP | 23388 | #2发电机出口接地开关GS301合位 |  | digital
N1DCS.11BAC01GS301TP | 23389 | #2发电机出口接地开关82000分位 |  | digital
N1DCS.11BAC01GS302RP | 23390 | #2发电机出口接地开关GS303合位 |  | digital
N1DCS.11BAC01GS302TP | 23391 | #2发电机出口接地开关GS303分位 |  | digital
N1DCS.11BAT01EH001 | 23392 | #2主变冷却器Ⅰ段电源运行 |  | digital
N1DCS.11BAT01EH002 | 23393 | #2主变冷却器II段电源运行 |  | digital
N1DCS.11BAT01EH003 | 23394 | #2主变冷却器Ⅰ段电源故障 |  | digital
N1DCS.11BAT01EH004 | 23395 | #2主变冷却器II段电源故障 |  | digital
N1DCS.11BAT01EH005 | 23396 | #2主变冷却器控制电源故障 |  | digital
N1DCS.11BAT01EH006 | 23397 | #2主变工作冷却器故障 |  | digital
N1DCS.11BAT01EH007 | 23398 | #2主变备用冷却器故障 |  | digital
N1DCS.11BAT01EH008 | 23399 | #2主变风冷全停 |  | digital
N1DCS.11BAT01EH009 | 23400 | #2主变辅助投入 |  | digital
N1DCS.11BAW10GS201RP | 23401 | #2发电机中性点地刀82000合闸位 |  | digital
N1DCS.11BAW10GS201TP | 23402 | #2发电机中性点地刀82000分闸位 |  | digital
N1DCS.11CEQ01EH001 | 23403 | #2发变组故障录波装置故障 |  | digital
N1DCS.11CEQ01EH002 | 23404 | #2发变组故障录波装置启动 |  | digital
N1DCS.11CEQ01EH003 | 23405 | #2发变组故障录波装置失电报警 |  | digital
N1DCS.11CHA01EH101 | 23406 | #2发电机A套差动跳闸 |  | digital
N1DCS.11CHA01EH102 | 23407 | #2发电机A套定子接地跳闸 |  | digital
N1DCS.11CHA01EH103 | 23408 | #2发电机A套匝间跳闸 |  | digital
N1DCS.11CHA01EH104 | 23409 | #2发电机A套过负荷跳闸 |  | digital
N1DCS.11CHA01EH105 | 23410 | #2发电机A套电压异常保护跳闸 |  | digital
N1DCS.11CHA01EH106 | 23411 | #2发电机A套失磁保护跳闸 |  | digital
N1DCS.11CHA01EH107 | 23412 | #2发电机A套失步保护跳闸 |  | digital
N1DCS.11CHA01EH108 | 23413 | #2发电机A套负序过负荷跳闸 |  | digital
N1DCS.11CHA01EH109 | 23414 | #2发电机A套过励磁跳闸 |  | digital
N1DCS.11CHA01EH110 | 23415 | #2发电机A套过频保护跳闸 |  | digital
N1DCS.11CHA01EH111 | 23416 | #2发电机A套相间后备跳闸 |  | digital
N1DCS.11CHA01EH112 | 23417 | #2发电机A套误上电跳闸 |  | digital
N1DCS.11CHA01EH113 | 23418 | #2发电机A套逆功率跳闸 |  | digital
N1DCS.11CHA01EH114 | 23419 | #2发电机A套低功率跳闸 |  | digital
N1DCS.11CHA01EH115 | 23420 | #2发电机A套启停机跳闸 |  | digital
N1DCS.11CHA01EH116 | 23421 | #2发电机A套GCB失灵保护跳闸 |  | digital
N1DCS.11CHA01EH117 | 23422 | #2发电机A套低频保护跳闸 |  | digital
N1DCS.11CHA01EH118 | 23423 | #2发电机A套励磁后备保护跳闸 |  | digital
N1DCS.11CHA01EH119 | 23424 | #2发电机A套逆功率报警 |  | digital
N1DCS.11CHA01EH120 | 23425 | #2发电机A套过励磁报警 |  | digital
N1DCS.11CHA01EH121 | 23426 | #2发电机A套定子过负荷报警 |  | digital
N1DCS.11CHA01EH122 | 23427 | #2发电机A套负序过负荷报警 |  | digital
N1DCS.11CHA01EH123 | 23428 | #2发电机A套励磁过负荷报警 |  | digital
N1DCS.11CHA01EH124 | 23429 | #2发电机A套定子接地报警 |  | digital
N1DCS.11CHA01EH125 | 23430 | #2发电机A套失磁报警 |  | digital
N1DCS.11CHA01EH126 | 23431 | #2发电机A套失步报警 |  | digital
N1DCS.11CHA01EH127 | 23432 | #2发电机A套频率保护报警 |  | digital
N1DCS.11CHA01EH128 | 23433 | #2发电机A套保护TA回路断线 |  | digital
N1DCS.11CHA01EH129 | 23434 | #2发电机A套保护TV回路断线 |  | digital
N1DCS.11CHA01EH130 | 23435 | #2发电机A套保护装置闭锁 |  | digital
N1DCS.11CHA01EH131 | 23436 | #2发电机A套保护装置报警 |  | digital
N1DCS.11CHA01EH132 | 23437 | #2发电机A套SFC系统故障联跳 |  | digital
N1DCS.11CHA02EH101 | 23438 | #2发电机B套差动跳闸 |  | digital
N1DCS.11CHA02EH102 | 23439 | #2发电机B套匝间保护跳闸 |  | digital
N1DCS.11CHA02EH103 | 23440 | #2发电机B套起停机接地保护跳闸 |  | digital
N1DCS.11CHA02EH104 | 23441 | #2发电机B套对称过负荷保护跳闸 |  | digital
N1DCS.11CHA02EH105 | 23442 | #2发电机B套负荷过负荷保护跳闸 |  | digital
N1DCS.11CHA02EH106 | 23443 | #2发电机B套失磁保护跳闸 |  | digital
N1DCS.11CHA02EH107 | 23444 | #2发电机B套失步保护跳闸 |  | digital
N1DCS.11CHA02EH108 | 23445 | #2发电机B套电压异常跳闸 |  | digital
N1DCS.11CHA02EH109 | 23446 | #2发电机B套过励磁保护跳闸 |  | digital
N1DCS.11CHA02EH110 | 23447 | #2发电机B套逆功率保护跳闸 |  | digital
N1DCS.11CHA02EH111 | 23448 | #2机B套机端开关失灵启动动作 |  | digital
N1DCS.11CHA02EH112 | 23449 | #2机B套发电机相间后备保护跳 |  | digital
N1DCS.11CHA02EH113 | 23450 | #2机B套发电机频率异常保护跳 |  | digital
N1DCS.11CHA02EH114 | 23451 | #2发电机B套误上电保护跳闸 |  | digital
N1DCS.11CHA02EH115 | 23452 | #2发电机B套励磁变保护跳闸 |  | digital
N1DCS.11CHA02EH116 | 23453 | #2机B套燃机控制系统保护联跳 |  | digital
N1DCS.11CHA02EH117 | 23454 | #2发电机B套差流越限告警 |  | digital
N1DCS.11CHA02EH118 | 23455 | #2发电机B套定时限过负荷告警 |  | digital
N1DCS.11CHA02EH119 | 23456 | #2机B套三次谐波定子接地告警 |  | digital
N1DCS.11CHA02EH120 | 23457 | #2发电机B套TA异常告警 |  | digital
N1DCS.11CHA02EH121 | 23458 | #2发电机B套TV异常告警 |  | digital
N1DCS.11CHA02EH122 | 23459 | #2发电机B套装置故障告警 |  | digital
N1DCS.11CHA02EH123 | 23460 | #2发电机B套失电告警 |  | digital
N1DCS.11CHA02EH124 | 23461 | #2发电机B套SFC系统故障联跳 |  | digital
N1DCS.11CHA03EH101 | 23462 | #2主变A套差动跳闸 |  | digital
N1DCS.11CHA03EH102 | 23463 | #2主变A套相间后备跳闸 |  | digital
N1DCS.11CHA03EH103 | 23464 | #2主变A套接地零序跳闸 |  | digital
N1DCS.11CHA03EH104 | 23465 | #2主变A套间隙零序跳闸 |  | digital
N1DCS.11CHA03EH105 | 23466 | #2主变A套过励磁保护跳闸 |  | digital
N1DCS.11CHA03EH106 | 23467 | #2主变A套开关断口闪络保护跳 |  | digital
N1DCS.11CHA03EH107 | 23468 | #2主变A套非全相跳闸 |  | digital
N1DCS.11CHA03EH108 | 23469 | #1高厂变A套差动跳闸 |  | digital
N1DCS.11CHA03EH109 | 23470 | #1高厂变A套高压侧后备跳闸 |  | digital
N1DCS.11CHA03EH110 | 23471 | #1高厂变A套A分支后备跳闸 |  | digital
N1DCS.11CHA03EH111 | 23472 | #1高厂变A套A分支接地后备跳闸 |  | digital
N1DCS.11CHA03EH112 | 23473 | #1高厂变A套B分支后备跳闸 |  | digital
N1DCS.11CHA03EH113 | 23474 | #1高厂变A套B分支接地后备跳闸 |  | digital
N1DCS.11CHA03EH114 | 23475 | #2主变A套保护装置闭锁 |  | digital
N1DCS.11CHA03EH115 | 23476 | #2主变A套保护装置报警 |  | digital
N1DCS.11CHA03EH116 | 23477 | #2主变A套保护TA断线 |  | digital
N1DCS.11CHA03EH117 | 23478 | #2主变A套保护TV断线 |  | digital
N1DCS.11CHA03EH118 | 23479 | #2主变A套保护失灵启动报警 |  | digital
N1DCS.11CHA03EH119 | 23480 | #2主变A套过激磁报警 |  | digital
N1DCS.11CHA03EH120 | 23481 | #2主变A套过负荷报警 |  | digital
N1DCS.11CHA03EH121 | 23482 | #1高厂变A套过负荷报警 |  | digital
N1DCS.11CHA03EH122 | 23483 | #2主变A套低压侧零序电压报警 |  | digital
N1DCS.11CHA03EH123 | 23484 | #2主变A套保护切换继电器动作 |  | digital
N1DCS.11CHA03EH124 | 23485 | #2主变A套保护切换继电器失电 |  | digital
N1DCS.11CHA04EH101 | 23486 | #2主变B套差动跳闸 |  | digital
N1DCS.11CHA04EH102 | 23487 | #2主变B套相间后备跳闸 |  | digital
N1DCS.11CHA04EH103 | 23488 | #2主变B套接地后备跳闸 |  | digital
N1DCS.11CHA04EH104 | 23489 | #2主变B套间隙后备跳闸 |  | digital
N1DCS.11CHA04EH105 | 23490 | #2主变B套高压侧失灵启动动 |  | digital
N1DCS.11CHA04EH106 | 23491 | #2主变B套高压侧非全相动作 |  | digital
N1DCS.11CHA04EH107 | 23492 | #2主变B套高压侧断口闪络动 |  | digital
N1DCS.11CHA04EH108 | 23493 | #2主变B套过励磁动作 |  | digital
N1DCS.11CHA04EH109 | 23494 | #1高厂变B套主保护动作 |  | digital
N1DCS.11CHA04EH110 | 23495 | #1高厂变B套后备保护动作 |  | digital
N1DCS.11CHA04EH111 | 23496 | #1高厂变B套A分支后备动作 |  | digital
N1DCS.11CHA04EH112 | 23497 | #1高厂变B套B分支后备动作 |  | digital
N1DCS.11CHA04EH113 | 23498 | #1高厂变B套低压侧接地动作 |  | digital
N1DCS.11CHA04EH114 | 23499 | #2机B套差流越限告警 |  | digital
N1DCS.11CHA04EH115 | 23500 | #2机B套定时限过负荷报警 |  | digital
N1DCS.11CHA04EH117 | 23501 | #2机B套启动厂变通风告警 |  | digital
N1DCS.11CHA04EH118 | 23502 | #2机B套TA异常告警 |  | digital
N1DCS.11CHA04EH119 | 23503 | #2机B套TV异常告警 |  | digital
N1DCS.11CHA04EH120 | 23504 | #2主变B套低压侧接地告警 |  | digital
N1DCS.11CHA04EH121 | 23505 | #2机B套装置故障告警 |  | digital
N1DCS.11CHA04EH122 | 23506 | #2机B套失电告警 |  | digital
N1DCS.11CHA04EH123 | 23507 | #2主变B套保护切换继电器动作 |  | digital
N1DCS.11CHA04EH124 | 23508 | #2主变B套保护切换继电器失电 |  | digital
N1DCS.11CHA05EH101 | 23509 | #2主变保护装置闭锁 |  | digital
N1DCS.11CHA05EH102 | 23510 | #2主变保护装置报警 |  | digital
N1DCS.11CHA05EH103 | 23511 | #2主变非电量电源监视 |  | digital
N1DCS.11CHA05EH104 | 23512 | #2主变冷控失电延时跳闸 |  | digital
N1DCS.11CHA05EH105 | 23513 | #2主变本体重瓦斯跳闸 |  | digital
N1DCS.11CHA05EH106 | 23514 | #2主变绕组温度高跳闸 |  | digital
N1DCS.11CHA05EH107 | 23515 | #2主变压力突变跳闸 |  | digital
N1DCS.11CHA05EH108 | 23516 | #2主变油温高跳闸 |  | digital
N1DCS.11CHA05EH109 | 23517 | #2机母差及失灵联跳 |  | digital
N1DCS.11CHA05EH110 | 23518 | #2机安稳切机跳闸 |  | digital
N1DCS.11CHA05EH111 | 23519 | #2机转子一点接地保护跳闸 |  | digital
N1DCS.11CHA05EH112 | 23520 | #2主变本体轻瓦斯信号 |  | digital
N1DCS.11CHA05EH113 | 23521 | #2主变绕组温度高信号 |  | digital
N1DCS.11CHA05EH114 | 23522 | #2主变油位异常信号 |  | digital
N1DCS.11CHA05EH115 | 23523 | #2主变压力释放信号 |  | digital
N1DCS.11CHA05EH128 | 23524 | #2发变组非电量保护控制回路断线 |  | digital
N1DCS.11CHA05EH129 | 23525 | #2发变组非电量保护控制回路断线 |  | digital
N1DCS.11CHA05EH130 | 23526 | #2发变组非电量保护第一出口跳闸 |  | digital
N1DCS.11CHA05EH131 | 23527 | #2发变组非电量保护第二出口跳闸 |  | digital
N1DCS.11CHA05EH132 | 23528 | #2主变断路器位置不一致 |  | digital
N1DCS.11CHA05EH133 | 23529 | #2机失步解列跳闸 |  | digital
N1DCS.10CBQ01EH213A | 23530 | 6KV IB段快切装置切换启允许 |  | digital
N1DCS.AGCOFFFVFRPOFF | 23531 | Ovation Control Builder |  | digital
N1DCS.APSAUTOMODE | 23532 | APS自动模式已投入 |  | digital
N1DCS.APSMODEOFF | 23533 | APS模式已退出 |  | digital
N1DCS.APSMODEON | 23534 | APS模式已投入 |  | digital
N1DCS.APSMODEPMT | 23535 | APS模式投入允许 |  | digital
N1DCS.APSSPBP1_BYPASS | 23536 | 降负荷断点旁路 |  | digital
N1DCS.APSSPBP1_TIMINGPMT | 23537 | 降负荷断点同步条件 |  | digital
N1DCS.APSSPBP1FINISH | 23538 | 降负荷断点完成 |  | digital
N1DCS.APSSPBP1FINISH1 | 23539 | 降负荷断点完成1 |  | digital
N1DCS.APSSPBP1PMTACK | 23540 | APS停机相关系统检查卡确认 |  | digital
N1DCS.APSSPBP2_BYPASS | 23541 | #2机打闸断点旁路 |  | digital
N1DCS.APSSPBP2_TIMINGPMT | 23542 | #2机打闸断点同步条件 |  | digital
N1DCS.APSSPBP2FINISH | 23543 | #2机打闸断点完成 |  | digital
N1DCS.APSSPBP3_BYPASS | 23544 | #1余热锅炉停止断点旁路 |  | digital
N1DCS.APSSPBP3_TIMINGPMT | 23545 | #1余热锅炉停止断点同步条件 |  | digital
N1DCS.APSSPBP3FINISH | 23546 | #1余热锅炉停止断点完成 |  | digital
N1DCS.APSSPBP3FINISH1 | 23547 | #1余热锅炉停止断点完成1 |  | digital
N1DCS.APSSPBP4_BYPASS | 23548 | #1机组停运断点旁路 |  | digital
N1DCS.APSSPBP4_TIMINGPMT | 23549 | #1机组停运断点同步条件 |  | digital
N1DCS.APSSPBP4FINISH | 23550 | #1机组停运断点完成 |  | digital
N1DCS.APSSPBP4FINISH1 | 23551 | #1机组停运断点完成1 |  | digital
N1DCS.APSSPRUNNING | 23552 | APS停止进行中 |  | digital
N1DCS.APSSTARTMODE | 23553 | APS启机模式已投入 |  | digital
N1DCS.APSSTBP1_BYPASS | 23554 | 系统准备断点旁路 |  | digital
N1DCS.APSSTBP1_TIMINGPMT | 23555 | 系统准备断点同步条件 |  | digital
N1DCS.APSSTBP1FINISH1 | 23556 | 系统准备断点完成1 |  | digital
N1DCS.APSSTBP1PMTACK | 23557 | APS启机相关系统检查卡确认 |  | digital
N1DCS.APSSTBP2_BYPASS | 23558 | #1机组上水断点旁路 |  | digital
N1DCS.APSSTBP2_TIMINGPMT | 23559 | #1机组上水断点同步条件 |  | digital
N1DCS.APSSTBP2FINISH | 23560 | #1机组上水断点完成 |  | digital
N1DCS.APSSTBP2FINISH1 | 23561 | #1机组上水断点完成1 |  | digital
N1DCS.APSSTBP3_BYPASS | 23562 | #2机启动断点旁路 |  | digital
N1DCS.APSSTBP3_TIMINGPMT | 23563 | #2机启动断点同步条件 |  | digital
N1DCS.APSSTBP3FINISH | 23564 | #2机点火断点完成 |  | digital
N1DCS.APSSTBP3FINISH1 | 23565 | #2机点火断点完成1 |  | digital
N1DCS.APSSTBP4_BYPASS | 23566 | #1机并网断点旁路 |  | digital
N1DCS.APSSTBP4_TIMINGPMT | 23567 | #1机并网断点同步条件 |  | digital
N1DCS.APSSTBP4FINISH | 23568 | #1机并网断点已完成 |  | digital
N1DCS.APSSTBP4FINISH1 | 23569 | #1机并网断点已完成 |  | digital
N1DCS.APSSTBP5_BYPASS | 23570 | 升负荷断点旁路 |  | digital
N1DCS.APSSTBP5_TIMINGPMT | 23571 | 升负荷断点同步条件 |  | digital
N1DCS.APSSTBP5FINISH | 23572 | 升负荷断点已完成 |  | digital
N1DCS.APSSTOPMODE | 23573 | APS停机模式已投入 |  | digital
N1DCS.APSSTRUNNING | 23574 | APS启机进行中 |  | digital
N1DCS.BOTHCNDCPSTOP | 23575 | 余热锅炉停止断点已完成 |  | digital
N1DCS.BOTHHPWFSTOP | 23576 | #1炉高压给水泵全停 |  | digital
N1DCS.BOTHIPWFSTOP | 23577 | #1炉中压给水泵全停 |  | digital
N1DCS.CCSMODE | 23578 | Ovation Control Builder |  | digital
N1DCS.GTALR | 23579 | Ovation Control Builder |  | digital
N1DCS.GTBRONACKOK | 23580 | #2机并网状态确认 |  | digital
N1DCS.GTBRONDMD | 23581 | #2机并网指令 |  | digital
N1DCS.GTCBON | 23582 | #2机负荷>7MW |  | digital
N1DCS.GTCCSOFF | 23583 | CCS已退出 |  | digital
N1DCS.GTCCSONDMDPMT | 23584 | Ovation Control Builder |  | digital
N1DCS.GTCCSPMT | 23585 | CCS投入允许条件1 |  | digital
N1DCS.GTLOADL155 | 23586 | #2机负荷<155MW |  | digital
N1DCS.GTRUN | 23587 | #2机在运行 |  | digital
N1DCS.GTSTACKOK | 23588 | 手动确认#2机可以启动 |  | digital
N1DCS.HILBPVAUTO | 23589 | 高中低压旁路调阀均在自动模式 |  | digital
N1DCS.SEQ134101 | 23590 | Ovation Control Builder |  | digital
N1DCS.SEQ134105 | 23591 | Ovation Control Builder |  | digital
N1DCS.STMODESEL | 23592 | #1机启动模式已选(冷、温、热、? |  | digital
N1DCS.TURBBRONACKOK | 23593 | 手动确认#1机准备并网指令 |  | digital
N1DCS.TURBBRONDMD | 23594 | APS顺控#1机并网指令 |  | digital
N1DCS.TURBDRNVLVCLS | 23595 | 疏水阀均在全关位 |  | digital
N1DCS.TURBDRNVLVOPN | 23596 | 疏水阀均在全开位 |  | digital
N1DCS.TURBSTACKOK | 23597 | 手动确认#1机准备启动指令 |  | digital
N1DCS.TURBSTACKPMT | 23598 | #1机启动允许 |  | digital
N1DCS.TURBSTACKPMT1 | 23599 | #1机启动允许 |  | digital
N1DCS.TURBTRIPACKOK | 23600 | #1机手动打闸指令 |  | digital
N1DCS.TURBWARMFINISH | 23601 | #1机暖机完成 |  | digital
N1DCS.UNIT_START | 23602 | 机组启动（APS模式） |  | digital
N1DCS.10DCSFA002 | 23603 | #1机冲转并网断点第1步已完成 |  | digital
N1DCS.10DCSFA003 | 23604 | Ovation Control Builder |  | digital
N1DCS.10DCSFA009 | 23605 | Ovation Control Builder |  | digital
N1DCS.10DCSFA013 | 23606 | #1炉停止断点已完成 |  | digital
N1DCS.10DCSFA014 | 23607 | #1炉停止断点已完成 |  | digital
N1DCS.10DCSFA015 | 23608 | #1炉停止断点已完成 |  | digital
N1DCS.10DEHCLDSTUP | 23609 | #1机DEH为冷态启动 |  | digital
N1DCS.10DEHHOTSTUP | 23610 | #1机DEH为热态启动 |  | digital
N1DCS.10DEHWAMSTUP | 23611 | #1机DEH为温态启动 |  | digital
N1DCS.10LBA10CPNORMAL | 23612 | Ovation Control Builder |  | digital
N1DCS.10LBA30AA402OCP | 23613 | Ovation Control Builder |  | digital
N1DCS.10LBA30AA404OCP | 23614 | Ovation Control Builder |  | digital
N1DCS.10LBA30CPNORMAL | 23615 | Ovation Control Builder |  | digital
N1DCS.10LBB20AA402CP | 23616 | Ovation Control Builder |  | digital
N1DCS.10LBC10AA402CP | 23617 | Ovation Control Builder |  | digital
N1DCS.10LBD20AA403CP | 23618 | Ovation Control Builder |  | digital
N1DCS.10LBD30AA402CP | 23619 | Ovation Control Builder |  | digital
N1DCS.10LBD30AA404CP | 23620 | Ovation Control Builder |  | digital
N1DCS.10LBD30AA406CP | 23621 | Ovation Control Builder |  | digital
N1DCS.10LBD30AA408CP | 23622 | Ovation Control Builder |  | digital
N1DCS.10LBD30AA409CP | 23623 | Ovation Control Builder |  | digital
N1DCS.10LBD50AA402CP | 23624 | Ovation Control Builder |  | digital
N1DCS.10LBD50AA404CP | 23625 | Ovation Control Builder |  | digital
N1DCS.10LBD50AA406CP | 23626 | Ovation Control Builder |  | digital
N1DCS.10MAA10AA402CP | 23627 | Ovation Control Builder |  | digital
N1DCS.10MAA10AA404CP | 23628 | Ovation Control Builder |  | digital
N1DCS.10MAB10AA402CP | 23629 | Ovation Control Builder |  | digital
N1DCS.10MAB10AA404CP | 23630 | Ovation Control Builder |  | digital
N1DCS.10MAB20AA402CP | 23631 | Ovation Control Builder |  | digital
N1DCS.10MAC10AA402CP | 23632 | Ovation Control Builder |  | digital
N1DCS.10MAC10AA404CP | 23633 | Ovation Control Builder |  | digital
N1DCS.10MAC10AA406CP | 23634 | Ovation Control Builder |  | digital
N1DCS.10MAN20AA001AUTO | 23635 | Ovation Control Builder |  | digital
N1DCS.10MAN20AA402CP | 23636 | Ovation Control Builder |  | digital
N1DCS.10MAW17AA002AUTO | 23637 | Ovation Control Builder |  | digital
N1DCS.10MBK01AE301PF | 23638 | Ovation Control Builder |  | digital
N1DCS.10TCSAI04LL | 23639 | Ovation Control Builder |  | digital
N1DCS.10TCSDO01 | 23640 | Ovation Control Builder |  | digital
N1DCS.10TCSDO03 | 23641 | Ovation Control Builder |  | digital
N1DCS.10TCSDO04 | 23642 | Ovation Control Builder |  | digital
N1DCS.10TCSDO06 | 23643 | Ovation Control Builder |  | digital
N1DCS.10TCSDO08 | 23644 | Ovation Control Builder |  | digital
N1DCS.10TCSDO09 | 23645 | Ovation Control Builder |  | digital
N1DCS.11AGCFVFRP | 23646 | AGC在投入状态 |  | digital
N1DCS.12AVCAUTOOFF | 23647 | AVC在退出状态 |  | digital
N1DCS.12AVCAUTORG | 23648 | AVC在投入状态 |  | digital
N1DCS.12CBP01EJ_TQPMT | 23649 | Ovation Control Builder |  | digital
N1DCS.AGCPMT | 23650 | AGC投入允许 |  | digital
N1DCS.APSIN | 23651 | Ovation Control Builder |  | digital
N1DCS.APSMODEOFF_PLUSE | 23652 | APS模式已退出(脉冲) |  | digital
N1DCS.APSSPBP2FINISHNO | 23653 | Ovation Control Builder |  | digital
N1DCS.APSSTBP1FINISH1NO | 23654 | 系统准备断点未完成1 |  | digital
N1DCS.APSSTBP3_SEQAUX1 | 23655 | Ovation Control Builder |  | digital
N1DCS.APSSTBP4_SEQAUX1 | 23656 | Ovation Control Builder |  | digital
N1DCS.APSSTBP4_SEQAUX2 | 23657 | Ovation Control Builder |  | digital
N1DCS.APSSTBP5FINISH1 | 23658 | 升负荷断点已完成 |  | digital
N1DCS.BOTHCIRPMP_SEQSTOK | 23659 | #1机低压蒸汽压力控制模式 |  | digital
N1DCS.BOTHCNDPMPSTOP | 23660 | 凝结水泵全停 |  | digital
N1DCS.CIRWTR_SEQSTFINISH | 23661 | 开式水系统启顺控已完成 |  | digital
N1DCS.CNDPMPSEQSTOPNO1 | 23662 | Ovation Control Builder |  | digital
N1DCS.CNDWTR_SEQSTFINISH | 23663 | Ovation Control Builder |  | digital
N1DCS.CNDWTRFILLACKOK | 23664 | 凝泵密封及系统注水完成确认指令 |  | digital
N1DCS.CNSRCIRVLVOP | 23665 | 凝汽器循环水出水电动门均已全开 |  | digital
N1DCS.COLD | 23666 | Ovation Control Builder |  | digital
N1DCS.COLDORWARMON | 23667 | 汽机冷态/温态模式 |  | digital
N1DCS.D01P331_KBGB | 23668 | Ovation Control Builder |  | digital
N1DCS.D01P334 | 23669 | Ovation Control Builder |  | digital
N1DCS.DCS_DEH_DO1 | 23670 | #2机打闸断点第1步指令（至DEH |  | digital
N1DCS.DCS_DEH_DO2 | 23671 | #2机打闸断点第2步指令（至DEH |  | digital
N1DCS.DCS_DEH_DO3 | 23672 | #2机打闸断点第3步指令（至DEH |  | digital
N1DCS.DEH_DCS_DI1 | 23673 | #1机低压调阀已关 |  | digital
N1DCS.ELC_OKGB | 23674 | 电气检查正常手动确认指令 |  | digital
N1DCS.EXHOT | 23675 | #1炉极热态模式启动 |  | digital
N1DCS.GLDSYS_SEQSPFINISH | 23676 | 轴封系统停顺控已完成 |  | digital
N1DCS.GTBRONOK | 23677 | #2机已并网 |  | digital
N1DCS.GTCBOFF | 23678 | #2机已解列 |  | digital
N1DCS.GTCCS | 23679 | CCS已投入 |  | digital
N1DCS.GTH2SYSOK | 23680 | #2发电机氢气系统压力正常确认 |  | digital
N1DCS.GTLOAD15 | 23681 | #2机负荷>15MW |  | digital
N1DCS.GTOILSYSOK | 23682 | #2机滑油、密封油系统运行正常 |  | digital
N1DCS.GTREADYCTL | 23683 | Ovation Control Builder |  | digital
N1DCS.GTSPEED3000 | 23684 | #2机转速3000rpm |  | digital
N1DCS.GTSTOP | 23685 | #2机已停止 |  | digital
N1DCS.HILVLVHZERO | 23686 | Ovation Control Builder |  | digital
N1DCS.HOT | 23687 | Ovation Control Builder |  | digital
N1DCS.HPCTL | 23688 | Ovation Control Builder |  | digital
N1DCS.HPFWPASTOP | 23689 | #1高压给水泵已停止 |  | digital
N1DCS.HPFWPBSTOP | 23690 | #2高压给水泵已停止 |  | digital
N1DCS.HPSTMHTGRPOK | 23691 | Ovation Control Builder |  | digital
N1DCS.HRSGTRIPNONO | 23692 | Ovation Control Builder |  | digital
N1DCS.HXZSSYSOK | 23693 | 化水制水系统正常确认指令 |  | digital
N1DCS.IPCTL | 23694 | Ovation Control Builder |  | digital
N1DCS.IPIN | 23695 | #1机中压蒸汽压力控制模式 |  | digital
N1DCS.JYPMPACK | 23696 | 凝结水加压系统正常投运确认指令 |  | digital
N1DCS.LATCHED | 23697 | Ovation Control Builder |  | digital
N1DCS.LPCTLIN | 23698 | #1机低压蒸汽压力控制模式 |  | digital
N1DCS.MAINSTEAMPANDUAN | 23699 | 高压主蒸汽温度>最佳主蒸汽温度 |  | digital
N1DCS.MPSTMHTGRPOK | 23700 | Ovation Control Builder |  | digital
N1DCS.QJSKJX | 23701 | #1机启顺控进行中 |  | digital
N1DCS.SEQ135101 | 23702 | Ovation Control Builder |  | digital
N1DCS.SEQ135102 | 23703 | Ovation Control Builder |  | digital
N1DCS.SEQ135103 | 23704 | Ovation Control Builder |  | digital
N1DCS.SEQ135104 | 23705 | Ovation Control Builder |  | digital
N1DCS.STCBOFF | 23706 | #1机已并网 |  | digital
N1DCS.STCBON | 23707 | #1机已解列 |  | digital
N1DCS.STHIGORV2 | 23708 | Ovation Control Builder |  | digital
N1DCS.STLOADLOW100 | 23709 | #1机负荷<100MW |  | digital
N1DCS.STLOADLOW5 | 23710 | #1机负荷<5MW |  | digital
N1DCS.STLOWORV2 | 23711 | Ovation Control Builder |  | digital
N1DCS.STMONORV2 | 23712 | Ovation Control Builder |  | digital
N1DCS.TBEHOILSYSOK | 23713 | #1机润滑油系统运行正常确认 |  | digital
N1DCS.TPIN | 23714 | #1机高压蒸汽压力控制模式 |  | digital
N1DCS.TURBLATCHED | 23715 | #1机无跳闸信号 |  | digital
N1DCS.TURBTRIP | 23716 | #1机已遮断信号 |  | digital
N1DCS.VACM_SEQSPFINISH | 23717 | 抽真空系统停顺控已完成 |  | digital
N1DCS.VACM_SEQSTFINISH | 23718 | 抽真空系统启顺控已完成 |  | digital
N1DCS.WARM | 23719 | Ovation Control Builder |  | digital
N1DCS.Y0AEA12GS101OK | 23720 | Ovation Control Builder |  | digital
N1DCS.10QUA01CT301H | 23721 | #1机凝结水泵出口样水温度高 |  | digital
N1DCS.10QUA02CT301H | 23722 | #1机凝结水泵加药后样水温度高 |  | digital
N1DCS.10QUA03CT301H | 23723 | #1机中压省煤器入口样水温度高 |  | digital
N1DCS.10QUA04CT301H | 23724 | #1机高压省煤器入口样水温度高 |  | digital
N1DCS.10QUA05CT301H | 23725 | #1机低压汽包炉水样水温度高 |  | digital
N1DCS.10QUA06CT301H | 23726 | #1机中压汽包炉水样水温度高 |  | digital
N1DCS.10QUA07CT301H | 23727 | #1机高压汽包炉水样水温度高 |  | digital
N1DCS.10QUA08CT301H | 23728 | #1机低压饱和蒸汽样水温度高 |  | digital
N1DCS.10QUA09CT301H | 23729 | #1机中压饱和蒸汽样水温度高 |  | digital
N1DCS.10QUA10CT301H | 23730 | #1机高压饱和蒸汽样水温度高 |  | digital
N1DCS.10QUA11CT301H | 23731 | #1机低压过热蒸汽样水温度高 |  | digital
N1DCS.10QUA12CT301H | 23732 | #1机中压过热蒸汽样水温度高 |  | digital
N1DCS.10QUA13CT301H | 23733 | #1机高压过热蒸汽样水温度高 |  | digital
N1DCS.10QUA14CT301H | 23734 | #1机再热蒸汽样水温度高 |  | digital
N1DCS.10QUA15CT301H | 23735 | #1机闭式水出口母管样水温度高 |  | digital
N1DCS.10QUA16CT301H | 23736 | #2机发电机内冷水样水温度高 |  | digital
N1DCS.10QUA20CF001L | 23737 | #1机高温架冷却水进口流量低 |  | digital
N1DCS.10QUA20CP001L | 23738 | #1机高温架冷却水进口压力低 |  | digital
N1DCS.20QUA01CT301H | 23739 | #3机凝结水泵出口样水温度高 |  | digital
N1DCS.20QUA02CT301H | 23740 | #3机凝结水泵加药后样水温度高 |  | digital
N1DCS.20QUA03CT301H | 23741 | #3机中压省煤器入口样水温度高 |  | digital
N1DCS.20QUA04CT301H | 23742 | #3机高压省煤器入口样水温度高 |  | digital
N1DCS.20QUA05CT301H | 23743 | #3机低压汽包炉水样水温度高 |  | digital
N1DCS.20QUA06CT301H | 23744 | #3机中压汽包炉水样水温度高 |  | digital
N1DCS.20QUA07CT301H | 23745 | #3机高压汽包炉水样水温度高 |  | digital
N1DCS.20QUA08CT301H | 23746 | #3机低压饱和蒸汽样水温度高 |  | digital
N1DCS.20QUA09CT301H | 23747 | #3机中压饱和蒸汽样水温度高 |  | digital
N1DCS.20QUA10CT301H | 23748 | #3机高压饱和蒸汽样水温度高 |  | digital
N1DCS.20QUA11CT301H | 23749 | #3机低压过热蒸汽样水温度高 |  | digital
N1DCS.20QUA12CT301H | 23750 | #3机中压过热蒸汽样水温度高 |  | digital
N1DCS.20QUA13CT301H | 23751 | #3机高压过热蒸汽样水温度高 |  | digital
N1DCS.20QUA14CT301H | 23752 | #3机再热蒸汽样水温度高 |  | digital
N1DCS.20QUA15CT301H | 23753 | #3机闭式水出口母管样水温度高 |  | digital
N1DCS.20QUA16CT301H | 23754 | #4机发电机内冷水样水温度高 |  | digital
N1DCS.20QUA20CF001L | 23755 | #3机高温架冷却水进口流量低 |  | digital
N1DCS.20QUA20CP001L | 23756 | #3机高温架冷却水进口压力低 |  | digital
N1DCS.J0CSD31PF1 | 23757 | 公用UPS电源盘电源消失 |  | digital
N1DCS.J0CSD31PF2 | 23758 | 公用APS电源盘电源消失 |  | digital
N1DCS.J0DCSRUNSB | 23759 | DCS启动指令(启动-启动锅炉） |  | digital
N1DCS.J0DCSTOPSB | 23760 | DCS停运指令(启动-启动锅炉） |  | digital
N1DCS.J0LBD20AA001CD | 23761 | 供热计量站母管流量计前门关指令 |  | digital
N1DCS.J0LBD20AA001CP | 23762 | 供热计量站母管流量计前门全关位 |  | digital
N1DCS.J0LBD20AA001CPDO | 23763 | 供热计量站母管流量计前门全关位 |  | digital
N1DCS.J0LBD20AA001F | 23764 | 供热计量站母管流量计前门故障 |  | digital
N1DCS.J0LBD20AA001OD | 23765 | 供热计量站母管流量计前门开指令 |  | digital
N1DCS.J0LBD20AA001OP | 23766 | 供热计量站母管流量计前门全开位 |  | digital
N1DCS.J0LBD20AA001OPDO | 23767 | 供热计量站母管流量计前门全开位 |  | digital
N1DCS.J0LBD20AA001RC | 23768 | 供热计量站母管流量计前门在远控 |  | digital
N1DCS.J0LBD20AA002CD | 23769 | 供热计量站母管流量计后门关指令 |  | digital
N1DCS.J0LBD20AA002CP | 23770 | 供热计量站母管流量计后门全关位 |  | digital
N1DCS.J0LBD20AA002CPDO | 23771 | 供热计量站母管流量计后门全关位 |  | digital
N1DCS.J0LBD20AA002F | 23772 | 供热计量站母管流量计后门故障 |  | digital
N1DCS.J0LBD20AA002OD | 23773 | 供热计量站母管流量计后门开指令 |  | digital
N1DCS.J0LBD20AA002OP | 23774 | 供热计量站母管流量计后门全开位 |  | digital
N1DCS.J0LBD20AA002OPDO | 23775 | 供热计量站母管流量计后门全开位 |  | digital
N1DCS.J0LBD20AA002RC | 23776 | 供热计量站母管流量计后门在远控 |  | digital
N1DCS.J0LBD20AA003CD | 23777 | 供热计量站旁路流量计前门关指令 |  | digital
N1DCS.J0LBD20AA003CP | 23778 | 供热计量站旁路流量计前门全关位 |  | digital
N1DCS.J0LBD20AA003CPDO | 23779 | 供热计量站旁路流量计前门全关位 |  | digital
N1DCS.J0LBD20AA003F | 23780 | 供热计量站旁路流量计前门故障 |  | digital
N1DCS.J0LBD20AA003OD | 23781 | 供热计量站旁路流量计前门开指令 |  | digital
N1DCS.J0LBD20AA003OP | 23782 | 供热计量站旁路流量计前门全开位 |  | digital
N1DCS.J0LBD20AA003OPDO | 23783 | 供热计量站旁路流量计前门全开位 |  | digital
N1DCS.J0LBD20AA003RC | 23784 | 供热计量站旁路流量计前门在远控 |  | digital
N1DCS.J0LBD20AA004CD | 23785 | 供热计量站旁路流量计后门关指令 |  | digital
N1DCS.J0LBD20AA004CP | 23786 | 供热计量站旁路流量计后门全关位 |  | digital
N1DCS.J0LBD20AA004CPDO | 23787 | 供热计量站旁路流量计后门全关位 |  | digital
N1DCS.J0LBD20AA004F | 23788 | 供热计量站旁路流量计后门故障 |  | digital
N1DCS.J0LBD20AA004OD | 23789 | 供热计量站旁路流量计后门开指令 |  | digital
N1DCS.J0LBD20AA004OP | 23790 | 供热计量站旁路流量计后门全开位 |  | digital
N1DCS.J0LBD20AA004OPDO | 23791 | 供热计量站旁路流量计后门全开位 |  | digital
N1DCS.J0LBD20AA004RC | 23792 | 供热计量站旁路流量计后门在远控 |  | digital
N1DCS.J0LBG10AA003CD | 23793 | 辅汽母管#1机侧电动门关指令 |  | digital
N1DCS.J0LBG10AA003CP | 23794 | 辅汽母管#1机侧电动门全关位 |  | digital
N1DCS.J0LBG10AA003F | 23795 | 辅汽母管#1机侧电动门综合故障 |  | digital
N1DCS.J0LBG10AA003OD | 23796 | 辅汽母管#1机侧电动门开指令 |  | digital
N1DCS.J0LBG10AA003OP | 23797 | 辅汽母管#1机侧电动门全开位 |  | digital
N1DCS.J0LBG10AA003RC | 23798 | 辅汽母管#1机侧电动门在远控 |  | digital
N1DCS.J0LBG10AA004CD | 23799 | 辅汽母管#3机侧电动门关指令 |  | digital
N1DCS.J0LBG10AA004CP | 23800 | 辅汽母管#3机侧电动门全关位 |  | digital
N1DCS.J0LBG10AA004F | 23801 | 辅汽母管#3机侧电动门综合故障 |  | digital
N1DCS.J0LBG10AA004OD | 23802 | 辅汽母管#3机侧电动门开指令 |  | digital
N1DCS.J0LBG10AA004OP | 23803 | 辅汽母管#3机侧电动门全开位 |  | digital
N1DCS.J0LBG10AA004RC | 23804 | 辅汽母管#3机侧电动门在远控 |  | digital
N1DCS.J0LBG10AA005CD | 23805 | 一、二期辅汽母管联络电门关指令 |  | digital
N1DCS.J0LBG10AA005CP | 23806 | 一、二期辅汽母管联络电门全关位 |  | digital
N1DCS.J0LBG10AA005F | 23807 | 一、二期辅汽母管联络电动门综故 |  | digital
N1DCS.J0LBG10AA005OD | 23808 | 一、二期辅汽母管联络电门开指令 |  | digital
N1DCS.J0LBG10AA005OP | 23809 | 一、二期辅汽母管联络电门全开位 |  | digital
N1DCS.J0LBG10AA005RC | 23810 | 一、二期辅汽母管联络电门在远控 |  | digital
N1DCS.J0LBG22AA001CD | 23811 | 启动锅炉供辅汽母管电动门关指令 |  | digital
N1DCS.J0LBG22AA001CP | 23812 | 启动锅炉供辅汽母管电动门全关位 |  | digital
N1DCS.J0LBG22AA001F | 23813 | 启动锅炉供辅汽母管电动门综故 |  | digital
N1DCS.J0LBG22AA001OD | 23814 | 启动锅炉供辅汽母管电动门开指令 |  | digital
N1DCS.J0LBG22AA001OP | 23815 | 启动锅炉供辅汽母管电动门全开位 |  | digital
N1DCS.J0LBG22AA001RC | 23816 | 启动锅炉供辅汽母管电动门在远控 |  | digital
N1DCS.J0PGA41AA011CD | 23817 | #1机闭式水至空压机房电门关指令 |  | digital
N1DCS.J0PGA41AA011CP | 23818 | #1机闭式水至空压机房电门全关位 |  | digital
N1DCS.J0PGA41AA011F | 23819 | #1机闭式水至空压机房电门故障 |  | digital
N1DCS.J0PGA41AA011OD | 23820 | #1机闭式水至空压机房电门开指令 |  | digital
N1DCS.J0PGA41AA011OP | 23821 | #1机闭式水至空压机房电门全开位 |  | digital
N1DCS.J0PGA41AA011RC | 23822 | #1机闭式水至空压机房电门在远控 |  | digital
N1DCS.J0PGA41AA012CD | 23823 | #3机闭式水至空压机房电门关指令 |  | digital
N1DCS.J0PGA41AA012CP | 23824 | #3机闭式水至空压机房电门全关位 |  | digital
N1DCS.J0PGA41AA012F | 23825 | #3机闭式水至空压机房电门故障 |  | digital
N1DCS.J0PGA41AA012OD | 23826 | #3机闭式水至空压机房电门开指令 |  | digital
N1DCS.J0PGA41AA012OP | 23827 | #3机闭式水至空压机房电门全开位 |  | digital
N1DCS.J0PGA41AA012RC | 23828 | #3机闭式水至空压机房电门在远控 |  | digital
N1DCS.J0PGA41AA021CD | 23829 | 空压机房至#1机闭式水电门关指令 |  | digital
N1DCS.J0PGA41AA021CP | 23830 | 空压机房至#1机闭式水电门全关位 |  | digital
N1DCS.J0PGA41AA021F | 23831 | 空压机房至#1机闭式水电门故障 |  | digital
N1DCS.J0PGA41AA021OD | 23832 | 空压机房至#1机闭式水电门开指令 |  | digital
N1DCS.J0PGA41AA021OP | 23833 | 空压机房至#1机闭式水电门全开位 |  | digital
N1DCS.J0PGA41AA021RC | 23834 | 空压机房至#1机闭式水电门在远控 |  | digital
N1DCS.J0PGA41AA022CD | 23835 | 空压机房至#3机闭式水电门关指令 |  | digital
N1DCS.J0PGA41AA022CP | 23836 | 空压机房至#3机闭式水电门全关位 |  | digital
N1DCS.J0PGA41AA022F | 23837 | 空压机房至#3机闭式水电门故障 |  | digital
N1DCS.J0PGA41AA022OD | 23838 | 空压机房至#3机闭式水电门开指令 |  | digital
N1DCS.J0PGA41AA022OP | 23839 | 空压机房至#3机闭式水电门全开位 |  | digital
N1DCS.J0PGA41AA022RC | 23840 | 空压机房至#3机闭式水电门在远控 |  | digital
N1DCS.J0PLCPF | 23841 | 启动锅炉LCB控制系统故障 |  | digital
N1DCS.J0QCA21AA001CD | 23842 | #1氨溶液箱进氨电动门关闭指令 |  | digital
N1DCS.J0QCA21AA001CP | 23843 | #1氨溶液箱进氨电动门全关位置 |  | digital
N1DCS.J0QCA21AA001OD | 23844 | #1氨溶液箱进氨电动门打开指令 |  | digital
N1DCS.J0QCA21AA001OP | 23845 | #1氨溶液箱进氨电动门全开位置 |  | digital
N1DCS.J0QCA21AA002CD | 23846 | #1氨溶液箱进水电动门关闭指令 |  | digital
N1DCS.J0QCA21AA002CP | 23847 | #1氨溶液箱进水电动门全关位置 |  | digital
N1DCS.J0QCA21AA002OD | 23848 | #1氨溶液箱进水电动门打开指令 |  | digital
N1DCS.J0QCA21AA002OP | 23849 | #1氨溶液箱进水电动门全开位置 |  | digital
N1DCS.J0QCA21AA003CD | 23850 | #1氨溶液箱出口电动门关闭指令 |  | digital
N1DCS.J0QCA21AA003CP | 23851 | #1氨溶液箱出口电动门全关位置 |  | digital
N1DCS.J0QCA21AA003OD | 23852 | #1氨溶液箱出口电动门打开指令 |  | digital
N1DCS.J0QCA21AA003OP | 23853 | #1氨溶液箱出口电动门全开位置 |  | digital
N1DCS.J0QCA21AM001F | 23854 | #1氨溶液箱电动搅拌器故障 |  | digital
N1DCS.J0QCA21AM001RC | 23855 | #1氨溶液箱电动搅拌器在远控 |  | digital
N1DCS.J0QCA21AM001RD | 23856 | #1氨溶液箱电动搅拌器启动指令 |  | digital
N1DCS.J0QCA21AM001RP | 23857 | #1氨溶液箱电动搅拌器在运行 |  | digital
N1DCS.J0QCA21AM001TD | 23858 | #1氨溶液箱电动搅拌器停止指令 |  | digital
N1DCS.J0QCA22AA001CD | 23859 | #2氨溶液箱进氨电动门关闭指令 |  | digital
N1DCS.J0QCA22AA001CP | 23860 | #2氨溶液箱进氨电动门全关位置 |  | digital
N1DCS.J0QCA22AA001OD | 23861 | #2氨溶液箱进氨电动门打开指令 |  | digital
N1DCS.J0QCA22AA001OP | 23862 | #2氨溶液箱进氨电动门全开位置 |  | digital
N1DCS.J0QCA22AA002CD | 23863 | #2氨溶液箱进水电动门关闭指令 |  | digital
N1DCS.J0QCA22AA002CP | 23864 | #2氨溶液箱进水电动门全关位置 |  | digital
N1DCS.J0QCA22AA002OD | 23865 | #2氨溶液箱进水电动门打开指令 |  | digital
N1DCS.J0QCA22AA002OP | 23866 | #2氨溶液箱进水电动门全开位置 |  | digital
N1DCS.J0QCA22AA003CD | 23867 | #2氨溶液箱出口电动门关闭指令 |  | digital
N1DCS.J0QCA22AA003CP | 23868 | #2氨溶液箱出口电动门全关位置 |  | digital
N1DCS.J0QCA22AA003OD | 23869 | #2氨溶液箱出口电动门打开指令 |  | digital
N1DCS.J0QCA22AA003OP | 23870 | #2氨溶液箱出口电动门全开位置 |  | digital
N1DCS.J0QCA22AM001F | 23871 | #2氨溶液箱电动搅拌器故障 |  | digital
N1DCS.J0QCA22AM001RC | 23872 | #2氨溶液箱电动搅拌器在远控 |  | digital
N1DCS.J0QCA22AM001RD | 23873 | #2氨溶液箱电动搅拌器启动指令 |  | digital
N1DCS.J0QCA22AM001RP | 23874 | #2氨溶液箱电动搅拌器在运行 |  | digital
N1DCS.J0QCA22AM001TD | 23875 | #2氨溶液箱电动搅拌器停止指令 |  | digital
N1DCS.J0QCA31AP001F | 23876 | #1中压给水加氨计量泵故障 |  | digital
N1DCS.J0QCA31AP001RC | 23877 | #1中压给水加氨计量泵在远控 |  | digital
N1DCS.J0QCA31AP001RD | 23878 | #1中压给水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA31AP001RP | 23879 | #1中压给水加氨计量泵在运行 |  | digital
N1DCS.J0QCA31AP001TD | 23880 | #1中压给水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA31GH001RC | 23881 | 给水、凝结水加氨装置球阀在远控 |  | digital
N1DCS.J0QCA32AP001F | 23882 | #2中压给水加氨计量泵故障 |  | digital
N1DCS.J0QCA32AP001RC | 23883 | #2中压给水加氨计量泵在远控 |  | digital
N1DCS.J0QCA32AP001RD | 23884 | #2中压给水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA32AP001RP | 23885 | #2中压给水加氨计量泵在运行 |  | digital
N1DCS.J0QCA32AP001TD | 23886 | #2中压给水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA33AP001F | 23887 | #3中压给水加氨计量泵故障 |  | digital
N1DCS.J0QCA33AP001RC | 23888 | #3中压给水加氨计量泵在远控 |  | digital
N1DCS.J0QCA33AP001RD | 23889 | #3中压给水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA33AP001RP | 23890 | #3中压给水加氨计量泵在运行 |  | digital
N1DCS.J0QCA33AP001TD | 23891 | #3中压给水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA34AP001F | 23892 | #1高压给水加氨计量泵故障 |  | digital
N1DCS.J0QCA34AP001RC | 23893 | #1高压给水加氨计量泵在远控 |  | digital
N1DCS.J0QCA34AP001RD | 23894 | #1高压给水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA34AP001RP | 23895 | #1高压给水加氨计量泵在运行 |  | digital
N1DCS.J0QCA34AP001TD | 23896 | #1高压给水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA35AP001F | 23897 | #2高压给水加氨计量泵故障 |  | digital
N1DCS.J0QCA35AP001RC | 23898 | #2高压给水加氨计量泵在远控 |  | digital
N1DCS.J0QCA35AP001RD | 23899 | #2高压给水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA35AP001RP | 23900 | #2高压给水加氨计量泵在运行 |  | digital
N1DCS.J0QCA35AP001TD | 23901 | #2高压给水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA36AP001F | 23902 | #3高压给水加氨计量泵故障 |  | digital
N1DCS.J0QCA36AP001RC | 23903 | #3高压给水加氨计量泵在远控 |  | digital
N1DCS.J0QCA36AP001RD | 23904 | #3高压给水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA36AP001RP | 23905 | #3高压给水加氨计量泵在运行 |  | digital
N1DCS.J0QCA36AP001TD | 23906 | #3高压给水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA37AP001F | 23907 | #1凝结水加氨计量泵故障 |  | digital
N1DCS.J0QCA37AP001RC | 23908 | #1凝结水加氨计量泵在远控 |  | digital
N1DCS.J0QCA37AP001RD | 23909 | #1凝结水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA37AP001RP | 23910 | #1凝结水加氨计量泵在运行 |  | digital
N1DCS.J0QCA37AP001TD | 23911 | #1凝结水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA38AP001F | 23912 | #2凝结水加氨计量泵故障 |  | digital
N1DCS.J0QCA38AP001RC | 23913 | #2凝结水加氨计量泵在远控 |  | digital
N1DCS.J0QCA38AP001RD | 23914 | #2凝结水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA38AP001RP | 23915 | #2凝结水加氨计量泵在运行 |  | digital
N1DCS.J0QCA38AP001TD | 23916 | #2凝结水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA39AP001F | 23917 | #3凝结水加氨计量泵故障 |  | digital
N1DCS.J0QCA39AP001RC | 23918 | #3凝结水加氨计量泵在远控 |  | digital
N1DCS.J0QCA39AP001RD | 23919 | #3凝结水加氨计量泵启动指令 |  | digital
N1DCS.J0QCA39AP001RP | 23920 | #3凝结水加氨计量泵在运行 |  | digital
N1DCS.J0QCA39AP001TD | 23921 | #3凝结水加氨计量泵停止指令 |  | digital
N1DCS.J0QCA40AA001CD | 23922 | #1#2中压给水加氨泵出口门关指令 |  | digital
N1DCS.J0QCA40AA001CP | 23923 | #1#2中压给水加氨泵出口门全关位 |  | digital
N1DCS.J0QCA40AA001OD | 23924 | #1#2中压给水加氨泵出口门开指令 |  | digital
N1DCS.J0QCA40AA001OP | 23925 | #1#2中压给水加氨泵出口门全开位 |  | digital
N1DCS.J0QCA40AA002CD | 23926 | #2#3中压给水加氨泵出口门关指令 |  | digital
N1DCS.J0QCA40AA002CP | 23927 | #2#3中压给水加氨泵出口门全关位 |  | digital
N1DCS.J0QCA40AA002OD | 23928 | #2#3中压给水加氨泵出口门开指令 |  | digital
N1DCS.J0QCA40AA002OP | 23929 | #2#3中压给水加氨泵出口门全开位 |  | digital
N1DCS.J0QCA40AA003CD | 23930 | #1#2高压给水加氨泵出口门关指令 |  | digital
N1DCS.J0QCA40AA003CP | 23931 | #1#2高压给水加氨泵出口门全关位 |  | digital
N1DCS.J0QCA40AA003OD | 23932 | #1#2高压给水加氨泵出口门开指令 |  | digital
N1DCS.J0QCA40AA003OP | 23933 | #1#2高压给水加氨泵出口门全开位 |  | digital
N1DCS.J0QCA40AA004CD | 23934 | #2#3高压给水加氨泵出口门关指令 |  | digital
N1DCS.J0QCA40AA004CP | 23935 | #2#3高压给水加氨泵出口门全关位 |  | digital
N1DCS.J0QCA40AA004OD | 23936 | #2#3高压给水加氨泵出口门开指令 |  | digital
N1DCS.J0QCA40AA004OP | 23937 | #2#3高压给水加氨泵出口门全开位 |  | digital
N1DCS.J0QCA40AA005CD | 23938 | #1#2凝结水加氨泵出口门关指令 |  | digital
N1DCS.J0QCA40AA005CP | 23939 | #1#2凝结水加氨泵出口门全关位 |  | digital
N1DCS.J0QCA40AA005OD | 23940 | #1#2凝结水加氨泵出口门开指令 |  | digital
N1DCS.J0QCA40AA005OP | 23941 | #1#2凝结水加氨泵出口门全开位 |  | digital
N1DCS.J0QCA40AA006CD | 23942 | #2#3凝结水加氨泵出口门关指令 |  | digital
N1DCS.J0QCA40AA006CP | 23943 | #2#3凝结水加氨泵出口门全关位 |  | digital
N1DCS.J0QCA40AA006OD | 23944 | #2#3凝结水加氨泵出口门开指令 |  | digital
N1DCS.J0QCA40AA006OP | 23945 | #2#3凝结水加氨泵出口门全开位 |  | digital
N1DCS.J0QCB21AA004CD | 23946 | #1联氨溶液箱出口电动门关闭指令 |  | digital
N1DCS.J0QCB21AA004CP | 23947 | #1联氨溶液箱出口电动门全关位置 |  | digital
N1DCS.J0QCB21AA004OD | 23948 | #1联氨溶液箱出口电动门打开指令 |  | digital
N1DCS.J0QCB21AA004OP | 23949 | #1联氨溶液箱出口电动门全开位置 |  | digital
N1DCS.J0QCB21AM001F | 23950 | #1联氨溶液箱电动搅拌器故障 |  | digital
N1DCS.J0QCB21AM001RC | 23951 | #1联氨溶液箱电动搅拌器在远控 |  | digital
N1DCS.J0QCB21AM001RD | 23952 | #1联氨溶液箱电动搅拌器启动指令 |  | digital
N1DCS.J0QCB21AM001RP | 23953 | #1联氨溶液箱电动搅拌器在运行 |  | digital
N1DCS.J0QCB21AM001TD | 23954 | #1联氨溶液箱电动搅拌器停止指令 |  | digital
N1DCS.J0QCB22AA004CD | 23955 | #2联氨溶液箱出口电动门关闭指令 |  | digital
N1DCS.J0QCB22AA004CP | 23956 | #2联氨溶液箱出口电动门全关位置 |  | digital
N1DCS.J0QCB22AA004OD | 23957 | #2联氨溶液箱出口电动门打开指令 |  | digital
N1DCS.J0QCB22AA004OP | 23958 | #2联氨溶液箱出口电动门全开位置 |  | digital
N1DCS.J0QCB22AM001F | 23959 | #2联氨溶液箱电动搅拌器故障 |  | digital
N1DCS.J0QCB22AM001RC | 23960 | #2联氨溶液箱电动搅拌器在远控 |  | digital
N1DCS.J0QCB22AM001RD | 23961 | #2联氨溶液箱电动搅拌器启动指令 |  | digital
N1DCS.J0QCB22AM001RP | 23962 | #2联氨溶液箱电动搅拌器在运行 |  | digital
N1DCS.J0QCB22AM001TD | 23963 | #2联氨溶液箱电动搅拌器停止指令 |  | digital
N1DCS.J0QCB31AP001F | 23964 | #1联氨加药泵故障 |  | digital
N1DCS.J0QCB31AP001RC | 23965 | #1联氨加药泵在远控 |  | digital
N1DCS.J0QCB31AP001RD | 23966 | #1联氨加药泵启动指令 |  | digital
N1DCS.J0QCB31AP001RP | 23967 | #1联氨加药泵在运行 |  | digital
N1DCS.J0QCB31AP001TD | 23968 | #1联氨加药泵停止指令 |  | digital
N1DCS.J0QCB31GH001RC | 23969 | 加联氨装置球阀在远控状态 |  | digital
N1DCS.J0QCB32AP001F | 23970 | #2联氨加药泵故障 |  | digital
N1DCS.J0QCB32AP001RC | 23971 | #2联氨加药泵在远控 |  | digital
N1DCS.J0QCB32AP001RD | 23972 | #2联氨加药泵启动指令 |  | digital
N1DCS.J0QCB32AP001RP | 23973 | #2联氨加药泵在运行 |  | digital
N1DCS.J0QCB32AP001TD | 23974 | #2联氨加药泵停止指令 |  | digital
N1DCS.J0QCB33AP001F | 23975 | #3联氨加药泵故障 |  | digital
N1DCS.J0QCB33AP001RC | 23976 | #3联氨加药泵在远控 |  | digital
N1DCS.J0QCB33AP001RD | 23977 | #3联氨加药泵启动指令 |  | digital
N1DCS.J0QCB33AP001RP | 23978 | #3联氨加药泵在运行 |  | digital
N1DCS.J0QCB33AP001TD | 23979 | #3联氨加药泵停止指令 |  | digital
N1DCS.J0QCB34AP001F | 23980 | #4联氨加药泵故障 |  | digital
N1DCS.J0QCB34AP001RC | 23981 | #4联氨加药泵在远控 |  | digital
N1DCS.J0QCB34AP001RD | 23982 | #4联氨加药泵启动指令 |  | digital
N1DCS.J0QCB34AP001RP | 23983 | #4联氨加药泵在运行 |  | digital
N1DCS.J0QCB34AP001TD | 23984 | #4联氨加药泵停止指令 |  | digital
N1DCS.J0QCB35AP001F | 23985 | #5联氨加药泵故障 |  | digital
N1DCS.J0QCB35AP001RC | 23986 | #5联氨加药泵在远控 |  | digital
N1DCS.J0QCB35AP001RD | 23987 | #5联氨加药泵启动指令 |  | digital
N1DCS.J0QCB35AP001RP | 23988 | #5联氨加药泵在运行 |  | digital
N1DCS.J0QCB35AP001TD | 23989 | #5联氨加药泵停止指令 |  | digital
N1DCS.J0QCB36AP001F | 23990 | #6联氨加药泵故障 |  | digital
N1DCS.J0QCB36AP001RC | 23991 | #6联氨加药泵在远控 |  | digital
N1DCS.J0QCB36AP001RD | 23992 | #6联氨加药泵启动指令 |  | digital
N1DCS.J0QCB36AP001RP | 23993 | #6联氨加药泵在运行 |  | digital
N1DCS.J0QCB36AP001TD | 23994 | #6联氨加药泵停止指令 |  | digital
N1DCS.J0QCB40AA001CD | 23995 | #1#2联胺加药泵出口电动门关指令 |  | digital
N1DCS.J0QCB40AA001CP | 23996 | #1#2联胺加药泵出口电动门全关位 |  | digital
N1DCS.J0QCB40AA001OD | 23997 | #1#2联胺加药泵出口电动门开指令 |  | digital
N1DCS.J0QCB40AA001OP | 23998 | #1#2联胺加药泵出口电动门全开位 |  | digital
N1DCS.J0QCB40AA002CD | 23999 | #2#3联胺加药泵出口电动门关指令 |  | digital
N1DCS.J0QCB40AA002CP | 24000 | #2#3联胺加药泵出口电动门全关位 |  | digital
N1DCS.J0QCB40AA002OD | 24001 | #2#3联胺加药泵出口电动门开指令 |  | digital
N1DCS.J0QCB40AA002OP | 24002 | #2#3联胺加药泵出口电动门全开位 |  | digital
N1DCS.J0QCB40AA003CD | 24003 | #4#5联胺加药泵出口电动门关指令 |  | digital
N1DCS.J0QCB40AA003CP | 24004 | #4#5联胺加药泵出口电动门全关位 |  | digital
N1DCS.J0QCB40AA003OD | 24005 | #4#5联胺加药泵出口电动门开指令 |  | digital
N1DCS.J0QCB40AA003OP | 24006 | #4#5联胺加药泵出口电动门全开位 |  | digital
N1DCS.J0QCB40AA004CD | 24007 | #5#6联胺加药泵出口电动门关指令 |  | digital
N1DCS.J0QCB40AA004CP | 24008 | #5#6联胺加药泵出口电动门全关位 |  | digital
N1DCS.J0QCB40AA004OD | 24009 | #5#6联胺加药泵出口电动门开指令 |  | digital
N1DCS.J0QCB40AA004OP | 24010 | #5#6联胺加药泵出口电动门全开位 |  | digital
N1DCS.J0QCC21AM001F | 24011 | #1磷酸盐溶液箱电动搅拌器故障 |  | digital
N1DCS.J0QCC21AM001RC | 24012 | #1磷酸盐溶液箱电动搅拌器在远控 |  | digital
N1DCS.J0QCC21AM001RD | 24013 | #1磷酸盐溶液箱电搅拌器启动指令 |  | digital
N1DCS.J0QCC21AM001RP | 24014 | #1磷酸盐溶液箱电动搅拌器在运行 |  | digital
N1DCS.J0QCC21AM001TD | 24015 | #1磷酸盐溶液箱电动搅拌器停止 |  | digital
N1DCS.J0QCC22AM001F | 24016 | #2磷酸盐溶液箱电动搅拌器故障 |  | digital
N1DCS.J0QCC22AM001RC | 24017 | #2磷酸盐溶液箱电动搅拌器在远控 |  | digital
N1DCS.J0QCC22AM001RD | 24018 | #2磷酸盐溶液箱动搅拌器启动指令 |  | digital
N1DCS.J0QCC22AM001RP | 24019 | #2磷酸盐溶液箱电动搅拌器在运行 |  | digital
N1DCS.J0QCC22AM001TD | 24020 | #2磷酸盐溶液箱电动搅拌器停止 |  | digital
N1DCS.J0QCC31AP001F | 24021 | #1磷酸盐加药泵故障 |  | digital
N1DCS.J0QCC31AP001RC | 24022 | #1磷酸盐加药泵在远控 |  | digital
N1DCS.J0QCC31AP001RD | 24023 | #1磷酸盐加药泵启动指令 |  | digital
N1DCS.J0QCC31AP001RP | 24024 | #1磷酸盐加药泵在运行 |  | digital
N1DCS.J0QCC31AP001TD | 24025 | #1磷酸盐加药泵停止指令 |  | digital
N1DCS.J0QCC32AP001F | 24026 | #2磷酸盐加药泵故障 |  | digital
N1DCS.J0QCC32AP001RC | 24027 | #2磷酸盐加药泵在远控 |  | digital
N1DCS.J0QCC32AP001RD | 24028 | #2磷酸盐加药泵启动指令 |  | digital
N1DCS.J0QCC32AP001RP | 24029 | #2磷酸盐加药泵在运行 |  | digital
N1DCS.J0QCC32AP001TD | 24030 | #2磷酸盐加药泵停止指令 |  | digital
N1DCS.J0QCC33AP001F | 24031 | #3磷酸盐加药泵故障 |  | digital
N1DCS.J0QCC33AP001RC | 24032 | #3磷酸盐加药泵在远控 |  | digital
N1DCS.J0QCC33AP001RD | 24033 | #3磷酸盐加药泵启动指令 |  | digital
N1DCS.J0QCC33AP001RP | 24034 | #3磷酸盐加药泵在运行 |  | digital
N1DCS.J0QCC33AP001TD | 24035 | #3磷酸盐加药泵停止指令 |  | digital
N1DCS.J0QCC34AP001F | 24036 | #4磷酸盐加药泵故障 |  | digital
N1DCS.J0QCC34AP001RC | 24037 | #4磷酸盐加药泵在远控 |  | digital
N1DCS.J0QCC34AP001RD | 24038 | #4磷酸盐加药泵启动指令 |  | digital
N1DCS.J0QCC34AP001RP | 24039 | #4磷酸盐加药泵在运行 |  | digital
N1DCS.J0QCC34AP001TD | 24040 | #4磷酸盐加药泵停止指令 |  | digital
N1DCS.J0QCC35AP001F | 24041 | #5磷酸盐加药泵故障 |  | digital
N1DCS.J0QCC35AP001RC | 24042 | #5磷酸盐加药泵在远控 |  | digital
N1DCS.J0QCC35AP001RD | 24043 | #5磷酸盐加药泵启动指令 |  | digital
N1DCS.J0QCC35AP001RP | 24044 | #5磷酸盐加药泵在运行 |  | digital
N1DCS.J0QCC35AP001TD | 24045 | #5磷酸盐加药泵停止指令 |  | digital
N1DCS.J0QCC36AP001F | 24046 | #6磷酸盐加药泵故障 |  | digital
N1DCS.J0QCC36AP001RC | 24047 | #6磷酸盐加药泵在远控 |  | digital
N1DCS.J0QCC36AP001RD | 24048 | #6磷酸盐加药泵启动指令 |  | digital
N1DCS.J0QCC36AP001RP | 24049 | #6磷酸盐加药泵在运行 |  | digital
N1DCS.J0QCC36AP001TD | 24050 | #6磷酸盐加药泵停止指令 |  | digital
N1DCS.J0SBRRC | 24051 | 启动锅炉接受远方控制 |  | digital
N1DCS.J0SBRUN | 24052 | 启动锅炉在运行 |  | digital
N1DCS.J0SBSTOP | 24053 | 启动锅炉已停运 |  | digital
N1DCS.ONE31 | 24054 | 开关量1 |  | digital
N1DCS.ZERO31 | 24055 | 开关量0 |  | digital
N1DCS.E1_LC | 24056 | 启动锅炉LC卡通讯信号1（冗余） |  | digital
N1DCS.F1_LC | 24057 | 启动锅炉LC卡通讯信号2（冗余） |  | digital
N1DCS.J0QCA21AA001AUTO | 24058 | #1氨溶液箱进氨电动门在自动 |  | digital
N1DCS.J0QCA21AA001AUTOCL | 24059 | #1氨溶液箱进氨电动门自动关指令 |  | digital
N1DCS.J0QCA21AA001AUTOOP | 24060 | #1氨溶液箱进氨电动门自动开指令 |  | digital
N1DCS.J0QCA21AA001MANUL | 24061 | #1氨溶液箱进氨电动门在手动 |  | digital
N1DCS.J0QCA21AA002AUTO | 24062 | #1氨溶液箱进水电动门在自动 |  | digital
N1DCS.J0QCA21AA002AUTOCL | 24063 | #1氨溶液箱进水电动门自动关指令 |  | digital
N1DCS.J0QCA21AA002AUTOOP | 24064 | #1氨溶液箱进水电动门自动开指令 |  | digital
N1DCS.J0QCA21AA002MANUL | 24065 | #1氨溶液箱进水电动门在手动 |  | digital
N1DCS.J0QCA22AA001AUTO | 24066 | #2氨溶液箱进氨电动门在自动 |  | digital
N1DCS.J0QCA22AA001AUTOCL | 24067 | #2氨溶液箱进氨电动门自动关指令 |  | digital
N1DCS.J0QCA22AA001AUTOOP | 24068 | #2氨溶液箱进氨电动门自动开指令 |  | digital
N1DCS.J0QCA22AA001MANUL | 24069 | #2氨溶液箱进氨电动门在手动 |  | digital
N1DCS.J0QCA22AA002AUTO | 24070 | #2氨溶液箱进水电动门在自动 |  | digital
N1DCS.J0QCA22AA002AUTOCL | 24071 | #2氨溶液箱进水电动门自动关指令 |  | digital
N1DCS.J0QCA22AA002AUTOOP | 24072 | #2氨溶液箱进水电动门自动开指令 |  | digital
N1DCS.J0QCA22AA002MANUL | 24073 | #2氨溶液箱进水电动门在手动 |  | digital
N1DCS.J0QCA31AP001AUTO | 24074 | #1中压给水加氨计量泵变频器自动 |  | digital
N1DCS.J0QCA32AP001AUTO | 24075 | #2中压给水加氨计量泵变频器自动 |  | digital
N1DCS.J0QCA33AP001AUTO | 24076 | #3中压给水加氨计量泵变频器自动 |  | digital
N1DCS.J0QCA34AP001AUTO | 24077 | #1高压给水加氨计量泵变频器自动 |  | digital
N1DCS.J0QCA35AP001AUTO | 24078 | #2高压给水加氨计量泵变频器自动 |  | digital
N1DCS.J0QCA36AP001AUTO | 24079 | #3高压给水加氨计量泵变频器自动 |  | digital
N1DCS.J0QCA37AP001AUTO | 24080 | #1凝结水加氨计量泵变频器在自动 |  | digital
N1DCS.J0QCA38AP001AUTO | 24081 | #2凝结水加氨计量泵变频器在自动 |  | digital
N1DCS.J0QCA39AP001AUTO | 24082 | #3凝结水加氨计量泵变频器在自动 |  | digital
N1DCS.J0QCB31AP001AUTO | 24083 | #1联氨加药泵变频器在自动 |  | digital
N1DCS.J0QCB32AP001AUTO | 24084 | #2联氨加药泵变频器在自动 |  | digital
N1DCS.J0QCB33AP001AUTO | 24085 | #3联氨加药泵变频器在自动 |  | digital
N1DCS.J0QCB34AP001AUTO | 24086 | #4联氨加药泵变频器在自动 |  | digital
N1DCS.J0QCB35AP001AUTO | 24087 | #5联氨加药泵变频器在自动 |  | digital
N1DCS.J0QCB36AP001AUTO | 24088 | #6联氨加药泵变频器在自动 |  | digital
N1DCS.J0QCC31AP001AUTO | 24089 | #1磷酸盐加药泵变频器在自动 |  | digital
N1DCS.J0QCC32AP001AUTO | 24090 | #2磷酸盐加药泵变频器在自动 |  | digital
N1DCS.J0QCC33AP001AUTO | 24091 | #3磷酸盐加药泵变频器在自动 |  | digital
N1DCS.J0QCC34AP001AUTO | 24092 | #4磷酸盐加药泵变频器在自动 |  | digital
N1DCS.J0QCC35AP001AUTO | 24093 | #5磷酸盐加药泵变频器在自动 |  | digital
N1DCS.J0QCC36AP001AUTO | 24094 | #6磷酸盐加药泵变频器在自动 |  | digital
N1DCS.QDGL00001 | 24095 | 启动锅炉鼓风机在运行 |  | digital
N1DCS.QDGL00002 | 24096 | 启动锅炉鼓风机故障 |  | digital
N1DCS.QDGL00003 | 24097 | 启动锅炉#1给水泵在运行 |  | digital
N1DCS.QDGL00004 | 24098 | 启动锅炉#1给水泵故障 |  | digital
N1DCS.QDGL00005 | 24099 | 启动锅炉#2给水泵在运行 |  | digital
N1DCS.QDGL00006 | 24100 | 启动锅炉#2给水泵故障 |  | digital
N1DCS.QDGL00007 | 24101 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00008 | 24102 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00009 | 24103 | 启动锅炉过热蒸汽出口门开到位 |  | digital
N1DCS.QDGL00010 | 24104 | 启动锅炉过热蒸汽出口门关到位 |  | digital
N1DCS.QDGL00011 | 24105 | 启动锅炉蒸汽点火排汽门开到位 |  | digital
N1DCS.QDGL00012 | 24106 | 启动锅炉蒸汽点火排汽门关到位 |  | digital
N1DCS.QDGL00013 | 24107 | 启动锅炉本体表面排污门开到位 |  | digital
N1DCS.QDGL00014 | 24108 | 启动锅炉本体表面排污门关到位 |  | digital
N1DCS.QDGL00015 | 24109 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00016 | 24110 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00017 | 24111 | 启动锅炉本体#1排污电动门开到位 |  | digital
N1DCS.QDGL00018 | 24112 | 启动锅炉本体#1排污电动门关到位 |  | digital
N1DCS.QDGL00019 | 24113 | 启动锅炉本体#2排污电动门开到位 |  | digital
N1DCS.QDGL00020 | 24114 | 启动锅炉本体#2排污电动门关到位 |  | digital
N1DCS.QDGL00021 | 24115 | 启动锅炉给水电动门开到位 |  | digital
N1DCS.QDGL00022 | 24116 | 启动锅炉给水电动门关到位 |  | digital
N1DCS.QDGL00023 | 24117 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00024 | 24118 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00025 | 24119 | 启动锅炉给水再循环电动门开到位 |  | digital
N1DCS.QDGL00026 | 24120 | 启动锅炉给水再循环电动门关到位 |  | digital
N1DCS.QDGL00027 | 24121 | 启动锅炉减温水调阀前电门开到位 |  | digital
N1DCS.QDGL00028 | 24122 | 启动锅炉减温水调阀前电门关到位 |  | digital
N1DCS.QDGL00029 | 24123 | 启动锅炉排污扩容器冷水门开到位 |  | digital
N1DCS.QDGL00030 | 24124 | 启动锅炉排污扩容器冷水门关到位 |  | digital
N1DCS.QDGL00031 | 24125 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00032 | 24126 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00033 | 24127 | 启动锅炉锅筒液位高高（左侧） |  | digital
N1DCS.QDGL00034 | 24128 | 启动锅炉锅筒液位低（左侧开关1 |  | digital
N1DCS.QDGL00034L | 24129 | 启动锅炉锅筒液位低（左侧开关1 |  | digital
N1DCS.QDGL00035 | 24130 | 启动锅炉锅筒液位低低（左侧） |  | digital
N1DCS.QDGL00036 | 24131 | 启动锅炉锅筒液位高高（右侧） |  | digital
N1DCS.QDGL00037 | 24132 | 启动锅炉锅筒液位低（右侧开关2 |  | digital
N1DCS.QDGL00037L | 24133 | 启动锅炉锅筒液位低（右侧开关2 |  | digital
N1DCS.QDGL00038 | 24134 | 启动锅炉锅筒液位低低（右侧） |  | digital
N1DCS.QDGL00039 | 24135 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00040 | 24136 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00041 | 24137 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00042 | 24138 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00043 | 24139 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00044 | 24140 | 启动锅炉给水箱液位>1900mm |  | digital
N1DCS.QDGL00045 | 24141 | 启动锅炉给水箱液位>1000mm |  | digital
N1DCS.QDGL00046 | 24142 | 启动锅炉给水箱液位<200mm |  | digital
N1DCS.QDGL00047 | 24143 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00048 | 24144 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00049 | 24145 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00050 | 24146 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00051 | 24147 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00052 | 24148 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00053 | 24149 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00054 | 24150 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00055 | 24151 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00056 | 24152 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00057 | 24153 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00058 | 24154 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00059 | 24155 | 启动锅炉燃烧器点火阀已打开 |  | digital
N1DCS.QDGL00060 | 24156 | 启动锅炉燃烧器主气阀1已打开 |  | digital
N1DCS.QDGL00061 | 24157 | 启动锅炉燃烧器主气阀2已打开 |  | digital
N1DCS.QDGL00062 | 24158 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00063 | 24159 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00064 | 24160 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00065 | 24161 | 启动锅炉启顺控步骤1：启动点火 |  | digital
N1DCS.QDGL00066 | 24162 | 启动锅炉启顺控步骤2：正常燃烧 |  | digital
N1DCS.QDGL00067 | 24163 | 启动锅炉停顺控步骤2：初始状态 |  | digital
N1DCS.QDGL00068 | 24164 | 启动锅炉停顺控步骤1：停机过程 |  | digital
N1DCS.QDGL00069 | 24165 | 启动锅炉在运行 |  | digital
N1DCS.QDGL00070 | 24166 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00071 | 24167 | 启动锅炉火检检测到有火焰 |  | digital
N1DCS.QDGL00072 | 24168 | 启动锅炉处于DCS控制 |  | digital
N1DCS.QDGL00073 | 24169 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00074 | 24170 | 启动锅炉锅筒超压MFT(1.45MPa） |  | digital
N1DCS.QDGL00075 | 24171 | 启动锅炉燃烧器故障MFT |  | digital
N1DCS.QDGL00076 | 24172 | 启动锅炉锅筒夜位低低MFT(-100mm |  | digital
N1DCS.QDGL00077 | 24173 | 启动锅炉鼓风机故障MFT |  | digital
N1DCS.QDGL00078 | 24174 | 启动锅炉燃气压力低MFT(13KPa) |  | digital
N1DCS.QDGL00079 | 24175 | 启动锅炉燃气压力高MFT(18KPa) |  | digital
N1DCS.QDGL00080 | 24176 | 启动锅炉火检无火MFT |  | digital
N1DCS.QDGL00081 | 24177 | 启动锅炉燃气泄漏MFT |  | digital
N1DCS.QDGL00082 | 24178 | 启动锅炉给水箱液位高报警(190mm |  | digital
N1DCS.QDGL00083 | 24179 | 启动锅炉房手动停机MFT |  | digital
N1DCS.QDGL00084 | 24180 | 启动锅炉锅筒液位超高报警(100mm |  | digital
N1DCS.QDGL00085 | 24181 | 启动锅炉锅筒液位低报警(-50mm |  | digital
N1DCS.QDGL00086 | 24182 | 启动锅炉#1给水泵故障报警 |  | digital
N1DCS.QDGL00087 | 24183 | 启动锅炉#2给水泵故障报警 |  | digital
N1DCS.QDGL00088 | 24184 | 启动锅炉给水箱液位低报警(20mm |  | digital
N1DCS.QDGL00089 | 24185 | 启动锅炉MFT停机指令 |  | digital
N1DCS.QDGL00090 | 24186 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00091 | 24187 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00092 | 24188 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00093 | 24189 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00094 | 24190 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00095 | 24191 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL00096 | 24192 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10001 | 24193 | 启动锅炉一键启动指令 |  | digital
N1DCS.QDGL10002 | 24194 | 启动锅炉一键停止指令 |  | digital
N1DCS.QDGL10003 | 24195 | 启动锅炉MFT条件复位指令 |  | digital
N1DCS.QDGL10004 | 24196 | 启动锅炉报警消音指令 |  | digital
N1DCS.QDGL10005 | 24197 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10006 | 24198 | 启动锅炉鼓风机在手/自动 |  | digital
N1DCS.QDGL10007 | 24199 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10008 | 24200 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10009 | 24201 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10010 | 24202 | 启动锅炉鼓风机在手动 |  | digital
N1DCS.QDGL10011 | 24203 | 启动锅炉排污扩容器冷水门在手动 |  | digital
N1DCS.QDGL10012 | 24204 | 启动锅炉减温水调节阀在手动 |  | digital
N1DCS.QDGL10013 | 24205 | 启动锅炉减温水调阀前电门在手动 |  | digital
N1DCS.QDGL10014 | 24206 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10015 | 24207 | 启动锅炉给水再循环电动门在手动 |  | digital
N1DCS.QDGL10016 | 24208 | 启动锅炉给水电动门在手动 |  | digital
N1DCS.QDGL10017 | 24209 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10018 | 24210 | 启动锅炉燃烧器故障复位指令 |  | digital
N1DCS.QDGL10019 | 24211 | 启动锅炉燃烧器检漏故障复位指令 |  | digital
N1DCS.QDGL10020 | 24212 | 启动锅炉负荷调节在手动 |  | digital
N1DCS.QDGL10021 | 24213 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10022 | 24214 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10023 | 24215 | 启动锅炉#1排污电动门中停指令 |  | digital
N1DCS.QDGL10024 | 24216 | 启动锅炉#2排污电动门中停指令 |  | digital
N1DCS.QDGL10025 | 24217 | 启动锅炉过热蒸汽出口门打开指令 |  | digital
N1DCS.QDGL10026 | 24218 | 启动锅炉过热蒸汽出口门关闭指令 |  | digital
N1DCS.QDGL10027 | 24219 | 启动锅炉过热蒸汽出口门中停指令 |  | digital
N1DCS.QDGL10028 | 24220 | 启动锅炉蒸汽点火排汽门打开指令 |  | digital
N1DCS.QDGL10029 | 24221 | 启动锅炉蒸汽点火排汽门关闭指令 |  | digital
N1DCS.QDGL10030 | 24222 | 启动锅炉蒸汽点火排汽门中停指令 |  | digital
N1DCS.QDGL10031 | 24223 | 启动锅炉本体表面排污门打开指令 |  | digital
N1DCS.QDGL10032 | 24224 | 启动锅炉本体表面排污门关闭指令 |  | digital
N1DCS.QDGL10033 | 24225 | 启动锅炉#1排污电动门手动开指令 |  | digital
N1DCS.QDGL10034 | 24226 | 启动锅炉#1排污电动门手动关指令 |  | digital
N1DCS.QDGL10035 | 24227 | 启动锅炉#2排污电动门手动开指令 |  | digital
N1DCS.QDGL10036 | 24228 | 启动锅炉#2排污电动门手动关指令 |  | digital
N1DCS.QDGL10037 | 24229 | 启动锅炉给水电动门打开指令 |  | digital
N1DCS.QDGL10038 | 24230 | 启动锅炉给水电动门关闭指令 |  | digital
N1DCS.QDGL10039 | 24231 | 启动锅炉给水再循环电动门开指令 |  | digital
N1DCS.QDGL10040 | 24232 | 启动锅炉给水再循环电动门关指令 |  | digital
N1DCS.QDGL10041 | 24233 | 启动锅炉减温水电动门手动开指令 |  | digital
N1DCS.QDGL10042 | 24234 | 启动锅炉减温水电动门手动关指令 |  | digital
N1DCS.QDGL10043 | 24235 | 启动炉排污器冷水门手动开指令 |  | digital
N1DCS.QDGL10044 | 24236 | 启动炉排污器冷水门手动关指令 |  | digital
N1DCS.QDGL10045 | 24237 | 启动炉排污器冷水门手动中停指令 |  | digital
N1DCS.QDGL10046 | 24238 | 启动锅炉#1排污电动门在手动 |  | digital
N1DCS.QDGL10047 | 24239 | 启动锅炉#2排污电动门在手动 |  | digital
N1DCS.QDGL10048 | 24240 | 启动炉给水再循环电动门中停指令 |  | digital
N1DCS.QDGL10049 | 24241 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10050 | 24242 | 启动锅炉鼓风机手动启动指令 |  | digital
N1DCS.QDGL10051 | 24243 | 启动锅炉鼓风机手动停止指令 |  | digital
N1DCS.QDGL10052 | 24244 | 启动锅炉#1给水泵启动指令 |  | digital
N1DCS.QDGL10053 | 24245 | 启动锅炉#1给水泵停止指令 |  | digital
N1DCS.QDGL10054 | 24246 | 启动锅炉#2给水泵启动指令 |  | digital
N1DCS.QDGL10055 | 24247 | 启动锅炉#2给水泵停止指令 |  | digital
N1DCS.QDGL10056 | 24248 | 启动锅炉给水泵连锁已投入 |  | digital
N1DCS.QDGL10057 | 24249 | 启动锅炉手动减负荷指令 |  | digital
N1DCS.QDGL10058 | 24250 | 启动锅炉手动加负荷指令 |  | digital
N1DCS.QDGL10059 | 24251 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10060 | 24252 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10061 | 24253 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10062 | 24254 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10063 | 24255 | 启动锅炉备用通道 |  | digital
N1DCS.QDGL10064 | 24256 | 启动锅炉备用通道 |  | digital
N1DCS.10SAC01AH101F | 24257 | #1机MCC间空调1故障 |  | digital
N1DCS.10SAC01AH101RP | 24258 | #1机MCC间空调1在运行 |  | digital
N1DCS.10SAC01AH102F | 24259 | #1机6KV配电间空调2故障 |  | digital
N1DCS.10SAC01AH102RP | 24260 | #1机6KV配电间空调2在运行 |  | digital
N1DCS.10SAC01AH103F | 24261 | #1机6KV配电间空调3故障 |  | digital
N1DCS.10SAC01AH103RP | 24262 | #1机6KV配电间空调3在运行 |  | digital
N1DCS.10SAC01AH201F | 24263 | #1励磁小室空调4故障 |  | digital
N1DCS.10SAC01AH201RP | 24264 | #1励磁小室空调4在运行 |  | digital
N1DCS.10SAC01AH202F | 24265 | #1励磁小室空调5故障 |  | digital
N1DCS.10SAC01AH202RP | 24266 | #1励磁小室空调5在运行 |  | digital
N1DCS.10SAC01AH203F | 24267 | #2机电子间空调6故障 |  | digital
N1DCS.10SAC01AH203RP | 24268 | #2机电子间空调6在运行 |  | digital
N1DCS.10SAC01AH204F | 24269 | #2机电子间空调7故障 |  | digital
N1DCS.10SAC01AH204RP | 24270 | #2机电子间空调7在运行 |  | digital
N1DCS.10SAC01AH205F | 24271 | #2机配电间空调8故障 |  | digital
N1DCS.10SAC01AH205RP | 24272 | #2机配电间空调8在运行 |  | digital
N1DCS.10SAC01AH206F | 24273 | #1励磁及变频室空调9故障 |  | digital
N1DCS.10SAC01AH206RP | 24274 | #1励磁及变频室空调9在运行 |  | digital
N1DCS.10SAC01AH207F | 24275 | #1励磁及变频室空调10故障 |  | digital
N1DCS.10SAC01AH207RP | 24276 | #1励磁及变频室空调10在运行 |  | digital
N1DCS.20PAAINTERLOCK1DI | 24277 | 旋转滤网冲洗水泵连锁条件1 |  | digital
N1DCS.20PAAINTERLOCK2DI | 24278 | 旋转滤网冲洗水泵连锁条件2 |  | digital
N1DCS.ANYWASHPMPRUN | 24279 | 任一台旋转滤网冲洗水泵在运行 |  | digital
N1DCS.COMPRESSOR_STBYPMT | 24280 | 至少2台空压机在运行 |  | digital
N1DCS.CPRESSAIR_SEQSPOK | 24281 | 空压机系统停顺控已完成 |  | digital
N1DCS.CPRESSAIR_SEQSTOK | 24282 | 空压机系统启顺控已完成 |  | digital
N1DCS.J0JQLQF | 24283 | 进气冷却装置故障 |  | digital
N1DCS.J0JQLQRD | 24284 | 启动进气冷却装置 |  | digital
N1DCS.J0JQLQRP | 24285 | 进气冷却装置在运行 |  | digital
N1DCS.J0JQLQTD | 24286 | 停止进气冷却装置 |  | digital
N1DCS.J0JQLQTP | 24287 | 进气冷却装置已停止 |  | digital
N1DCS.J0LBG10AA003CD_DI | 24288 | #3机自动关辅汽母管#1机侧电动门 |  | digital
N1DCS.J0LBG10AA003CP_DO | 24289 | 辅汽管#1机侧电动门全关(至#3机 |  | digital
N1DCS.J0LBG22AA001CD_DI | 24290 | #3机自动关启动炉至辅汽母管电门 |  | digital
N1DCS.J0LBG22AA001CP_DO | 24291 | 启动炉至辅汽母管门全关(至#3机 |  | digital
N1DCS.J0LBG22AA001OD_DI | 24292 | #3机自动开启动炉至辅汽母管电门 |  | digital
N1DCS.J0LBG22AA001OP_DO | 24293 | 启动炉至辅汽母管门全开(至#3机 |  | digital
N1DCS.J0PAA11AA003CD | 24294 | #1旋转滤网冲洗水泵出口门关指令 |  | digital
N1DCS.J0PAA11AA003CP | 24295 | #1旋转滤网冲洗水泵出口门全关位 |  | digital
N1DCS.J0PAA11AA003F | 24296 | #1旋转滤网冲洗水泵出口门故障 |  | digital
N1DCS.J0PAA11AA003OD | 24297 | #1旋转滤网冲洗水泵出口门开指令 |  | digital
N1DCS.J0PAA11AA003OP | 24298 | #1旋转滤网冲洗水泵出口门全开位 |  | digital
N1DCS.J0PAA11AA003RC | 24299 | #1旋转滤网冲洗水泵出口门在远控 |  | digital
N1DCS.J0PAA11AP001PF | 24300 | #1旋转滤网冲洗水泵综合故障 |  | digital
N1DCS.J0PAA11AP001PS | 24301 | #1旋转滤网冲洗水泵保护动作 |  | digital
N1DCS.J0PAA11AP001RC | 24302 | #1旋转滤网冲洗水泵远方控制 |  | digital
N1DCS.J0PAA11AP001RD | 24303 | #1旋转滤网冲洗水泵启动指令 |  | digital
N1DCS.J0PAA11AP001RP | 24304 | #1旋转滤网冲洗水泵在运行 |  | digital
N1DCS.J0PAA11AP001TD | 24305 | #1旋转滤网冲洗水泵停止指令 |  | digital
N1DCS.J0PAA11AP001TP | 24306 | #1旋转滤网冲洗水泵已停止 |  | digital
N1DCS.J0PAA11GH501CD | 24307 | #1全自动滤水器停止反冲洗指令 |  | digital
N1DCS.J0PAA11GH501CP | 24308 | #1全自动滤水器排污阀门全关位置 |  | digital
N1DCS.J0PAA11GH501F | 24309 | #1全自动滤水器滤水器电机故障 |  | digital
N1DCS.J0PAA11GH501OD | 24310 | #1全自动滤水器启动反冲洗指令 |  | digital
N1DCS.J0PAA11GH501OP | 24311 | #1全自动滤水器排污阀全开位置 |  | digital
N1DCS.J0PAA11GH501PF | 24312 | #1全自动滤水器电源消失 |  | digital
N1DCS.J0PAA11GH501RC | 24313 | #1全自动滤水器在远控 |  | digital
N1DCS.J0PAA11GH501W | 24314 | #1全自动滤水器反冲洗进行中 |  | digital
N1DCS.J0PAA12AA003CD | 24315 | #2旋转滤网冲洗水泵出口门关指令 |  | digital
N1DCS.J0PAA12AA003CP | 24316 | #2旋转滤网冲洗水泵出口门全关位 |  | digital
N1DCS.J0PAA12AA003F | 24317 | #2旋转滤网冲洗水泵出口门故障 |  | digital
N1DCS.J0PAA12AA003OD | 24318 | #2旋转滤网冲洗水泵出口门开指令 |  | digital
N1DCS.J0PAA12AA003OP | 24319 | #2旋转滤网冲洗水泵出口门全开位 |  | digital
N1DCS.J0PAA12AA003RC | 24320 | #2旋转滤网冲洗水泵出口门在远控 |  | digital
N1DCS.J0PAA12AP001PF | 24321 | #2旋转滤网冲洗水泵综合故障 |  | digital
N1DCS.J0PAA12AP001PS | 24322 | #2旋转滤网冲洗水泵保护动作 |  | digital
N1DCS.J0PAA12AP001RC | 24323 | #2旋转滤网冲洗水泵远方控制 |  | digital
N1DCS.J0PAA12AP001RD | 24324 | #2旋转滤网冲洗水泵启动指令 |  | digital
N1DCS.J0PAA12AP001RP | 24325 | #2旋转滤网冲洗水泵在运行 |  | digital
N1DCS.J0PAA12AP001TD | 24326 | #2旋转滤网冲洗水泵停止指令 |  | digital
N1DCS.J0PAA12AP001TP | 24327 | #2旋转滤网冲洗水泵已停止 |  | digital
N1DCS.J0PAA12GH501CD | 24328 | #2全自动滤水器停止反冲洗指令 |  | digital
N1DCS.J0PAA12GH501CP | 24329 | #2全自动滤水器排污阀门全关位置 |  | digital
N1DCS.J0PAA12GH501F | 24330 | #2全自动滤水器滤水器电机故障 |  | digital
N1DCS.J0PAA12GH501OD | 24331 | #2全自动滤水器启动反冲洗指令 |  | digital
N1DCS.J0PAA12GH501OP | 24332 | #2全自动滤水器排污阀全开位置 |  | digital
N1DCS.J0PAA12GH501PF | 24333 | #2全自动滤水器电源消失 |  | digital
N1DCS.J0PAA12GH501RC | 24334 | #2全自动滤水器在远控 |  | digital
N1DCS.J0PAA12GH501W | 24335 | #2全自动滤水器反冲洗进行中 |  | digital
N1DCS.J0PAA21AA001CP | 24336 | 旋转滤网冲洗水至排污槽门全关位 |  | digital
N1DCS.J0PAA21AA001F | 24337 | 旋转滤网冲洗水至排污槽门故障 |  | digital
N1DCS.J0PAA21AA001OP | 24338 | 旋转滤网冲洗水至排污槽门全开位 |  | digital
N1DCS.J0PAB60AA004CD | 24339 | 生活水至循泵冷却水电动门关指令 |  | digital
N1DCS.J0PAB60AA004CD_DI | 24340 | #3机自动关生活水至循泵冷却水门 |  | digital
N1DCS.J0PAB60AA004CP | 24341 | 生活水至循泵冷却水电动门全关位 |  | digital
N1DCS.J0PAB60AA004CP_DO | 24342 | 生活水至循泵冷水门全关(至#3机 |  | digital
N1DCS.J0PAB60AA004F | 24343 | 生活水至循泵冷却水电动门故障 |  | digital
N1DCS.J0PAB60AA004OD | 24344 | 生活水至循泵冷却水电动门开指令 |  | digital
N1DCS.J0PAB60AA004OD_DI | 24345 | #3机自动开生活水至循泵冷却水门 |  | digital
N1DCS.J0PAB60AA004OP | 24346 | 生活水至循泵冷却水电动门全开位 |  | digital
N1DCS.J0PAB60AA004OP_DI | 24347 | 生活水至循泵冷水门全开(至#3机 |  | digital
N1DCS.J0PAB60AA004RC | 24348 | 生活水至循泵冷却水电动门在远控 |  | digital
N1DCS.J0QEB50AA002+CD | 24349 | 杂用储气罐出口母管电动门关指令 |  | digital
N1DCS.J0QEB50AA002+CP | 24350 | 杂用储气罐出口母管电动门全关位 |  | digital
N1DCS.J0QEB50AA002+F | 24351 | 杂用储气罐出口母管电动门故障 |  | digital
N1DCS.J0QEB50AA002+OD | 24352 | 杂用储气罐出口母管电动门开指令 |  | digital
N1DCS.J0QEB50AA002+OP | 24353 | 杂用储气罐出口母管电动门全开位 |  | digital
N1DCS.J0QEB50AA002+RC | 24354 | 杂用储气罐出口母管电动门在远控 |  | digital
N1DCS.J0QFA11AA002CD | 24355 | #1空压机出口电动门关闭指令 |  | digital
N1DCS.J0QFA11AA002CP | 24356 | #1空压机出口电动门全关位置 |  | digital
N1DCS.J0QFA11AA002F | 24357 | #1空压机出口电动门综合故障 |  | digital
N1DCS.J0QFA11AA002OD | 24358 | #1空压机出口电动门打开指令 |  | digital
N1DCS.J0QFA11AA002OP | 24359 | #1空压机出口电动门全开位置 |  | digital
N1DCS.J0QFA11AA002RC | 24360 | #1空压机出口电动门在远控 |  | digital
N1DCS.J0QFA11AN001_STBY | 24361 | #1空压机备用已投入 |  | digital
N1DCS.J0QFA11AN001PF | 24362 | #1空压机综合故障 |  | digital
N1DCS.J0QFA11AN001RC | 24363 | #1空压机远方控制 |  | digital
N1DCS.J0QFA11AN001RD | 24364 | #1空压机启动指令 |  | digital
N1DCS.J0QFA11AN001RP | 24365 | #1空压机在运行 |  | digital
N1DCS.J0QFA11AN001TD | 24366 | #1空压机停止指令 |  | digital
N1DCS.J0QFA11AN001TP | 24367 | #1空压机已停止 |  | digital
N1DCS.J0QFA12AA002CD | 24368 | #2空压机出口电动门关闭指令 |  | digital
N1DCS.J0QFA12AA002CP | 24369 | #2空压机出口电动门全关位置 |  | digital
N1DCS.J0QFA12AA002F | 24370 | #2空压机出口电动门综合故障 |  | digital
N1DCS.J0QFA12AA002OD | 24371 | #2空压机出口电动门打开指令 |  | digital
N1DCS.J0QFA12AA002OP | 24372 | #2空压机出口电动门全开位置 |  | digital
N1DCS.J0QFA12AA002RC | 24373 | #2空压机出口电动门在远控 |  | digital
N1DCS.J0QFA12AN001_STBY | 24374 | #2空压机备用已投入 |  | digital
N1DCS.J0QFA12AN001PF | 24375 | #2空压机综合故障 |  | digital
N1DCS.J0QFA12AN001RC | 24376 | #2空压机远方控制 |  | digital
N1DCS.J0QFA12AN001RD | 24377 | #2空压机启动指令 |  | digital
N1DCS.J0QFA12AN001RP | 24378 | #2空压机在运行 |  | digital
N1DCS.J0QFA12AN001TD | 24379 | #2空压机停止指令 |  | digital
N1DCS.J0QFA12AN001TP | 24380 | #2空压机已停止 |  | digital
N1DCS.J0QFA13AN001_STBY | 24381 | #3空压机备用已投入 |  | digital
N1DCS.J0QFA14AN001_STBY | 24382 | #4空压机备用已投入 |  | digital
N1DCS.J0QFA21AA001CD | 24383 | #1压缩空气干燥机进口门关指令 |  | digital
N1DCS.J0QFA21AA001CP | 24384 | #1压缩空气干燥机进口门全关位 |  | digital
N1DCS.J0QFA21AA001F | 24385 | #1压缩空气干燥机进口门故障 |  | digital
N1DCS.J0QFA21AA001OD | 24386 | #1压缩空气干燥机进口门开指令 |  | digital
N1DCS.J0QFA21AA001OP | 24387 | #1压缩空气干燥机进口门全开位 |  | digital
N1DCS.J0QFA21AA001RC | 24388 | #1压缩空气干燥机进口门在远控 |  | digital
N1DCS.J0QFA21AT001PF | 24389 | #1组合式压缩空气干燥机故障报警 |  | digital
N1DCS.J0QFA21AT001RD | 24390 | #1组合式压缩空气干燥机启动指令 |  | digital
N1DCS.J0QFA21AT001RP | 24391 | #1组合式压缩空气干燥机在运行 |  | digital
N1DCS.J0QFA21AT001TD | 24392 | #1组合式压缩空气干燥机停止指令 |  | digital
N1DCS.J0QFA21AT001TP | 24393 | #1组合式压缩空气干燥机已停止 |  | digital
N1DCS.J0QFA22AA001CD | 24394 | #2压缩空气干燥机进口门关指令 |  | digital
N1DCS.J0QFA22AA001CP | 24395 | #2压缩空气干燥机进口门全关位 |  | digital
N1DCS.J0QFA22AA001F | 24396 | #2压缩空气干燥机进口门故障 |  | digital
N1DCS.J0QFA22AA001OD | 24397 | #2压缩空气干燥机进口门开指令 |  | digital
N1DCS.J0QFA22AA001OP | 24398 | #2压缩空气干燥机进口门全开位 |  | digital
N1DCS.J0QFA22AA001RC | 24399 | #2压缩空气干燥机进口门在远控 |  | digital
N1DCS.J0QFA22AT001PF | 24400 | #2组合式压缩空气干燥机故障报警 |  | digital
N1DCS.J0QFA22AT001RD | 24401 | #2组合式压缩空气干燥机启动指令 |  | digital
N1DCS.J0QFA22AT001RP | 24402 | #2组合式压缩空气干燥机在运行 |  | digital
N1DCS.J0QFA22AT001TD | 24403 | #2组合式压缩空气干燥机停止指令 |  | digital
N1DCS.J0QFA22AT001TP | 24404 | #2组合式压缩空气干燥机已停止 |  | digital
N1DCS.J0QFB50AP001RD_DI | 24405 | #3机自动启动空压机系统顺控 |  | digital
N1DCS.J0QFB50CP101DO | 24406 | 空压机系统启顺控已完成(至#3机 |  | digital
N1DCS.J0SAC02AH101F | 24407 | 集控楼电子设备间空调21故障 |  | digital
N1DCS.J0SAC02AH101RP | 24408 | 集控楼电子设备间空调21在运行 |  | digital
N1DCS.J0SAC02AH103F | 24409 | 集控楼配电室空调23故障 |  | digital
N1DCS.J0SAC02AH103RP | 24410 | 集控楼配电室空调23在运行 |  | digital
N1DCS.J0SAC02AH301F | 24411 | 集控楼集控室空调25故障 |  | digital
N1DCS.J0SAC02AH301RP | 24412 | 集控楼集控室空调25在运行 |  | digital
N1DCS.J0SAC02AH303F | 24413 | 集控楼继电器室空调27故障 |  | digital
N1DCS.J0SAC02AH303RP | 24414 | 集控楼继电器室空调27在运行 |  | digital
N1DCS.J0SAC02AH305F | 24415 | 集控楼蓄电池室空调29故障 |  | digital
N1DCS.J0SAC02AH305RP | 24416 | 集控楼蓄电池室空调29在运行 |  | digital
N1DCS.J0SAQ01AH101F | 24417 | 联合车间电子设备间空调30故障 |  | digital
N1DCS.J0SAQ01AH101RP | 24418 | 联合车间电子设备间空调30在运行 |  | digital
N1DCS.J0SAQ01AH103F | 24419 | 联合车间配电室空调32故障 |  | digital
N1DCS.J0SAQ01AH103RP | 24420 | 联合车间配电室空调32在运行 |  | digital
N1DCS.J0SAQ01AH301F | 24421 | 联合车间继电器室空调34故障 |  | digital
N1DCS.J0SAQ01AH301RP | 24422 | 联合车间继电器室空调34在运行 |  | digital
N1DCS.J0SAQ01AH303F | 24423 | 联合车间蓄电池室空调36故障 |  | digital
N1DCS.J0SAQ01AH303RP | 24424 | 联合车间蓄电池室空调36在运行 |  | digital
N1DCS.J0SAQ01AH304F | 24425 | 联合车间公用段配电间空调37故障 |  | digital
N1DCS.J0SAQ01AH304RP | 24426 | 联合车间公用段配电间空调37运行 |  | digital
N1DCS.NEEDWASHPMPRUN | 24427 | 需求旋转滤网冲洗水泵运行 |  | digital
N1DCS.ONE32 | 24428 | 开关量1 |  | digital
N1DCS.ZERO32 | 24429 | 开关量0 |  | digital
N1DCS.20PAAINTERLOCK1_DI | 24430 | #3、#4任一旋转滤网在运行 |  | digital
N1DCS.20PAAINTERLOCK2_DI | 24431 | #1、#2旋转滤网冲洗水门均已全关 |  | digital
N1DCS.10SAC01AH210F | 24432 | #4机电子间空调11故障 |  | digital
N1DCS.10SAC01AH210RP | 24433 | #4机电子间空调11在运行 |  | digital
N1DCS.10SAC01AH211F | 24434 | #4机电子间空调12故障 |  | digital
N1DCS.10SAC01AH211RP | 24435 | #4机电子间空调12在运行 |  | digital
N1DCS.20SAC01AH104F | 24436 | #3机MCC间空调13故障 |  | digital
N1DCS.20SAC01AH104RP | 24437 | #3机MCC间空调13在运行 |  | digital
N1DCS.20SAC01AH105F | 24438 | #3机6KV配电间空调14故障 |  | digital
N1DCS.20SAC01AH105RP | 24439 | #3机6KV配电间空调14在运行 |  | digital
N1DCS.20SAC01AH106F | 24440 | #3机6KV配电间空调15故障 |  | digital
N1DCS.20SAC01AH106RP | 24441 | #3机6KV配电间空调15在运行 |  | digital
N1DCS.20SAC01AH208F | 24442 | #3励磁小室空调机组16故障 |  | digital
N1DCS.20SAC01AH208RP | 24443 | #3励磁小室空调机组16在运行 |  | digital
N1DCS.20SAC01AH209F | 24444 | #3励磁小室空调机组17故障 |  | digital
N1DCS.20SAC01AH209RP | 24445 | #3励磁小室空调机组17在运行 |  | digital
N1DCS.20SAC01AH212F | 24446 | #4机配电间空调18故障 |  | digital
N1DCS.20SAC01AH212RP | 24447 | #4机配电间空调18在运行 |  | digital
N1DCS.20SAC01AH213F | 24448 | #3励磁及变频室空调19故障 |  | digital
N1DCS.20SAC01AH213RP | 24449 | #3励磁及变频室空调19在运行 |  | digital
N1DCS.20SAC01AH214F | 24450 | #3励磁及变频室空调20故障 |  | digital
N1DCS.20SAC01AH214RP | 24451 | #3励磁及变频室空调20在运行 |  | digital
N1DCS.J0QFA13AA002CD | 24452 | #3空压机出口电动门关闭指令 |  | digital
N1DCS.J0QFA13AA002CP | 24453 | #3空压机出口电动门全关位置 |  | digital
N1DCS.J0QFA13AA002F | 24454 | #3空压机出口电动门综合故障 |  | digital
N1DCS.J0QFA13AA002OD | 24455 | #3空压机出口电动门打开指令 |  | digital
N1DCS.J0QFA13AA002OP | 24456 | #3空压机出口电动门全开位置 |  | digital
N1DCS.J0QFA13AA002RC | 24457 | #3空压机出口电动门在远控 |  | digital
N1DCS.J0QFA13AN001PF | 24458 | #3空压机综合故障 |  | digital
N1DCS.J0QFA13AN001RC | 24459 | #3空压机远方控制 |  | digital
N1DCS.J0QFA13AN001RD | 24460 | #3空压机启动指令 |  | digital
N1DCS.J0QFA13AN001RP | 24461 | #3空压机在运行 |  | digital
N1DCS.J0QFA13AN001TD | 24462 | #3空压机停止指令 |  | digital
N1DCS.J0QFA13AN001TP | 24463 | #3空压机已停止 |  | digital
N1DCS.J0QFA14AA002CD | 24464 | #4空压机出口电动门关闭指令 |  | digital
N1DCS.J0QFA14AA002CP | 24465 | #4空压机出口电动门全关位置 |  | digital
N1DCS.J0QFA14AA002F | 24466 | #4空压机出口电动门综合故障 |  | digital
N1DCS.J0QFA14AA002OD | 24467 | #4空压机出口电动门打开指令 |  | digital
N1DCS.J0QFA14AA002OP | 24468 | #4空压机出口电动门全开位置 |  | digital
N1DCS.J0QFA14AA002RC | 24469 | #4空压机出口电动门在远控 |  | digital
N1DCS.J0QFA14AN001PF | 24470 | #4空压机综合故障 |  | digital
N1DCS.J0QFA14AN001RC | 24471 | #4空压机远方控制 |  | digital
N1DCS.J0QFA14AN001RD | 24472 | #4空压机启动指令 |  | digital
N1DCS.J0QFA14AN001RP | 24473 | #4空压机在运行 |  | digital
N1DCS.J0QFA14AN001TD | 24474 | #4空压机停止指令 |  | digital
N1DCS.J0QFA14AN001TP | 24475 | #4空压机已停止 |  | digital
N1DCS.J0QFA21AT001_STBY | 24476 | #1组合式压缩空气干燥机在备用 |  | digital
N1DCS.J0QFA22AT001_STBY | 24477 | #2组合式压缩空气干燥机在备用 |  | digital
N1DCS.J0QFA23AA001CD | 24478 | #3压缩空气干燥机进口门关指令 |  | digital
N1DCS.J0QFA23AA001CP | 24479 | #3压缩空气干燥机进口门全关位 |  | digital
N1DCS.J0QFA23AA001F | 24480 | #3压缩空气干燥机进口门故障 |  | digital
N1DCS.J0QFA23AA001OD | 24481 | #3压缩空气干燥机进口门开指令 |  | digital
N1DCS.J0QFA23AA001OP | 24482 | #3压缩空气干燥机进口门全开位 |  | digital
N1DCS.J0QFA23AA001RC | 24483 | #3压缩空气干燥机进口门在远控 |  | digital
N1DCS.J0QFA23AT001_STBY | 24484 | #3组合式压缩空气干燥机在备用 |  | digital
N1DCS.J0QFA23AT001PF | 24485 | #3组合式压缩空气干燥机故障报警 |  | digital
N1DCS.J0QFA23AT001RD | 24486 | #3组合式压缩空气干燥机启动指令 |  | digital
N1DCS.J0QFA23AT001RP | 24487 | #3组合式压缩空气干燥机在运行 |  | digital
N1DCS.J0QFA23AT001TD | 24488 | #3组合式压缩空气干燥机停止指令 |  | digital
N1DCS.J0QFA23AT001TP | 24489 | #3组合式压缩空气干燥机已停止 |  | digital
N1DCS.J0SAC02AH102F | 24490 | 集控楼电子设备间空调22故障 |  | digital
N1DCS.J0SAC02AH102RP | 24491 | 集控楼电子设备间空调22在运行 |  | digital
N1DCS.J0SAC02AH104F | 24492 | 集控楼配电室空调24故障 |  | digital
N1DCS.J0SAC02AH104RP | 24493 | 集控楼配电室空调24在运行 |  | digital
N1DCS.J0SAC02AH302F | 24494 | 集控楼集控室空调26故障 |  | digital
N1DCS.J0SAC02AH302RP | 24495 | 集控楼集控室空调26在运行 |  | digital
N1DCS.J0SAC02AH304F | 24496 | 集控楼继电器室空调28故障 |  | digital
N1DCS.J0SAC02AH304RP | 24497 | 集控楼继电器室空调28在运行 |  | digital
N1DCS.J0SAQ01AH102F | 24498 | 联合车间电子设备间空调31故障 |  | digital
N1DCS.J0SAQ01AH102RP | 24499 | 联合车间电子设备间空调31在运行 |  | digital
N1DCS.J0SAQ01AH104F | 24500 | 联合车间配电室空调33故障 |  | digital
N1DCS.J0SAQ01AH104RP | 24501 | 联合车间配电室空调33在运行 |  | digital
N1DCS.J0SAQ01AH302F | 24502 | 联合车间继电器室空调35故障 |  | digital
N1DCS.J0SAQ01AH302RP | 24503 | 联合车间继电器室空调35在运行 |  | digital
N1DCS.J0SAQ01AH305F | 24504 | 联合车间公用段配电间空调38故障 |  | digital
N1DCS.J0SAQ01AH305RP | 24505 | 联合车间公用段配电间空调38运行 |  | digital
N1DCS.C1_LC | 24506 | Ovation Control Builder |  | digital
N1DCS.D1_LC | 24507 | Ovation Control Builder |  | digital
N1DCS.KYJ1LOADING | 24508 | #1空压机加载中 |  | digital
N1DCS.KYJ1PRS_MRE | 24509 | #1空压机出口压力坏点 |  | digital
N1DCS.KYJ1RUN | 24510 | #1空压机在运行 |  | digital
N1DCS.KYJ1STAND | 24511 | #1空压机已停止 |  | digital
N1DCS.KYJ1STANDBY | 24512 | #1空压机待机中 |  | digital
N1DCS.KYJ1UNLOADING | 24513 | #1空压机卸载中 |  | digital
N1DCS.KYJ2LOADING | 24514 | #2空压机加载中 |  | digital
N1DCS.KYJ2PRS_MRE | 24515 | #2空压机出口压力坏点 |  | digital
N1DCS.KYJ2RUN | 24516 | #2空压机在运行 |  | digital
N1DCS.KYJ2STAND | 24517 | #2空压机已停止 |  | digital
N1DCS.KYJ2STANDBY | 24518 | #2空压机待机中 |  | digital
N1DCS.KYJ2UNLOADING | 24519 | #2空压机卸载中 |  | digital
N1DCS.KYJ3LOADING | 24520 | #3空压机加载中 |  | digital
N1DCS.KYJ3PRS_MRE | 24521 | #3空压机出口压力坏点 |  | digital
N1DCS.KYJ3RUN | 24522 | #3空压机在运行 |  | digital
N1DCS.KYJ3STAND | 24523 | #3空压机已停止 |  | digital
N1DCS.KYJ3STANDBY | 24524 | #3空压机待机中 |  | digital
N1DCS.KYJ3UNLOADING | 24525 | #3空压机卸载中 |  | digital
N1DCS.KYJ4LOADING | 24526 | #4空压机加载中 |  | digital
N1DCS.KYJ4PRS_MRE | 24527 | #4空压机出口压力坏点 |  | digital
N1DCS.KYJ4RUN | 24528 | #4空压机在运行 |  | digital
N1DCS.KYJ4STAND | 24529 | #4空压机已停止 |  | digital
N1DCS.KYJ4STANDBY | 24530 | #4空压机待机中 |  | digital
N1DCS.KYJ4UNLOADING | 24531 | #4空压机卸载中 |  | digital
N1DCS.RSTA00001 | 24532 | 调压站仪用空气罐压力低(0.5MPa |  | digital
N1DCS.RSTA00002 | 24533 | 调压站火警阀开到位 |  | digital
N1DCS.RSTA00003 | 24534 | 调压站火警阀关到位 |  | digital
N1DCS.RSTA00004 | 24535 | 调压站火警阀故障 |  | digital
N1DCS.RSTA00005 | 24536 | 绝缘火警模块可燃气体浓度高 |  | digital
N1DCS.RSTA00006 | 24537 | 绝缘火警模块可燃气体浓度高高 |  | digital
N1DCS.RSTA00007 | 24538 | 调压站计量模块联络手动门全开位 |  | digital
N1DCS.RSTA00008 | 24539 | 调压站计量模块联络手动门全关位 |  | digital
N1DCS.RSTA00009 | 24540 | 调压站计量模块联络手动门故障 |  | digital
N1DCS.RSTA00010 | 24541 | #1超声波流量计进口手动门开到位 |  | digital
N1DCS.RSTA00011 | 24542 | #1超声波流量计进口手动门关到位 |  | digital
N1DCS.RSTA00012 | 24543 | #1超声波流量计进口手动门故障 |  | digital
N1DCS.RSTA00013 | 24544 | #1超声波流量计出口手动门开到位 |  | digital
N1DCS.RSTA00014 | 24545 | #1超声波流量计出口手动门关到位 |  | digital
N1DCS.RSTA00015 | 24546 | #1超声波流量计出口手动门故障 |  | digital
N1DCS.RSTA00016 | 24547 | #2超声波流量计进口手动门开到位 |  | digital
N1DCS.RSTA00017 | 24548 | #2超声波流量计进口手动门关到位 |  | digital
N1DCS.RSTA00018 | 24549 | #2超声波流量计进口手动门故障 |  | digital
N1DCS.RSTA00019 | 24550 | #2超声波流量计出口手动门开到位 |  | digital
N1DCS.RSTA00020 | 24551 | #2超声波流量计出口手动门关到位 |  | digital
N1DCS.RSTA00021 | 24552 | #2超声波流量计出口手动门故障 |  | digital
N1DCS.RSTA00022 | 24553 | 调压站计量模块可燃气体浓度高 |  | digital
N1DCS.RSTA00023 | 24554 | 调压站计量模块可燃气体浓度高高 |  | digital
N1DCS.RSTA00024 | 24555 | #1精过滤器差压高 |  | digital
N1DCS.RSTA00025 | 24556 | #1精过滤器低位液位高 |  | digital
N1DCS.RSTA00026 | 24557 | #1精过滤器低位液位低 |  | digital
N1DCS.RSTA00027 | 24558 | #1精过滤器高位液位高 |  | digital
N1DCS.RSTA00028 | 24559 | #1精过滤器高位液位低 |  | digital
N1DCS.RSTA00029 | 24560 | 精过滤模块可燃气体浓度高 |  | digital
N1DCS.RSTA00030 | 24561 | 精过滤模块可燃气体浓度高高 |  | digital
N1DCS.RSTA00031 | 24562 | #2精过滤器差压高 |  | digital
N1DCS.RSTA00032 | 24563 | #2精过滤器低位液位高 |  | digital
N1DCS.RSTA00033 | 24564 | #2精过滤器低位液位低 |  | digital
N1DCS.RSTA00034 | 24565 | #2精过滤器高位液位高 |  | digital
N1DCS.RSTA00035 | 24566 | #2精过滤器高位液位低 |  | digital
N1DCS.RSTA00036 | 24567 | #1精过滤器底部排污气动门开到位 |  | digital
N1DCS.RSTA00037 | 24568 | #1精过滤器底部排污气动门关到位 |  | digital
N1DCS.RSTA00038 | 24569 | #1精过滤器底部排污气动门故障 |  | digital
N1DCS.RSTA00039 | 24570 | #1精过滤器低位排污气动门开到位 |  | digital
N1DCS.RSTA00040 | 24571 | #1精过滤器低位排污气动门关到位 |  | digital
N1DCS.RSTA00041 | 24572 | #1精过滤器低位排污气动门故障 |  | digital
N1DCS.RSTA00042 | 24573 | #1精过滤器进口手动门开到位 |  | digital
N1DCS.RSTA00043 | 24574 | #1精过滤器进口手动门关到位 |  | digital
N1DCS.RSTA00044 | 24575 | #1精过滤器进口手动门故障 |  | digital
N1DCS.RSTA00045 | 24576 | #2精过滤器底部排污气动门开到位 |  | digital
N1DCS.RSTA00046 | 24577 | #2精过滤器底部排污气动门关到位 |  | digital
N1DCS.RSTA00047 | 24578 | #2精过滤器底部排污气动门故障 |  | digital
N1DCS.RSTA00048 | 24579 | #2精过滤器低位排污气动门开到位 |  | digital
N1DCS.RSTA00049 | 24580 | #2精过滤器低位排污气动门关到位 |  | digital
N1DCS.RSTA00050 | 24581 | #2精过滤器低位排污气动门故障 |  | digital
N1DCS.RSTA00051 | 24582 | #2精过滤器进口手动门开到位 |  | digital
N1DCS.RSTA00052 | 24583 | #2精过滤器进口手动门关到位 |  | digital
N1DCS.RSTA00053 | 24584 | #2精过滤器进口手动门故障 |  | digital
N1DCS.RSTA00054 | 24585 | #1精过滤器出口手动门开到位 |  | digital
N1DCS.RSTA00055 | 24586 | #1精过滤器出口手动门关到位 |  | digital
N1DCS.RSTA00056 | 24587 | #1精过滤器出口手动门故障 |  | digital
N1DCS.RSTA00057 | 24588 | #2精过滤器出口手动门开到位 |  | digital
N1DCS.RSTA00058 | 24589 | #2精过滤器出口手动门关到位 |  | digital
N1DCS.RSTA00059 | 24590 | #2精过滤器出口手动门故障 |  | digital
N1DCS.RSTA00060 | 24591 | #1热水加热器气侧进口门开到位 |  | digital
N1DCS.RSTA00061 | 24592 | #1热水加热器气侧进口门关到位 |  | digital
N1DCS.RSTA00062 | 24593 | #1热水加热器气侧进口门故障 |  | digital
N1DCS.RSTA00063 | 24594 | #2热水加热器气侧进口门开到位 |  | digital
N1DCS.RSTA00064 | 24595 | #2热水加热器气侧进口门关到位 |  | digital
N1DCS.RSTA00065 | 24596 | #2热水加热器气侧进口门故障 |  | digital
N1DCS.RSTA00066 | 24597 | 热水加热模块可燃气体浓度高 |  | digital
N1DCS.RSTA00067 | 24598 | 热水加热模块可燃气体浓度高高 |  | digital
N1DCS.RSTA00068 | 24599 | #1热水加热器水侧液位低 |  | digital
N1DCS.RSTA00069 | 24600 | #2热水加热器水侧液位低 |  | digital
N1DCS.RSTA00070 | 24601 | #1热水加热器气侧出口门开到位 |  | digital
N1DCS.RSTA00071 | 24602 | #1热水加热器气侧出口门关到位 |  | digital
N1DCS.RSTA00072 | 24603 | #1热水加热器气侧出口门故障 |  | digital
N1DCS.RSTA00073 | 24604 | #2热水加热器气侧出口门开到位 |  | digital
N1DCS.RSTA00074 | 24605 | #2热水加热器气侧出口门关到位 |  | digital
N1DCS.RSTA00075 | 24606 | #2热水加热器气侧出口门故障 |  | digital
N1DCS.RSTA00076 | 24607 | 色谱分析仪小室可燃气体浓度高 |  | digital
N1DCS.RSTA00077 | 24608 | 色谱分析仪小室可燃气体浓度高高 |  | digital
N1DCS.RSTA00078 | 24609 | #4机调压进口手动门开到位 |  | digital
N1DCS.RSTA00079 | 24610 | #4机调压进口手动门关到位 |  | digital
N1DCS.RSTA00080 | 24611 | #4机调压进口手动门故障 |  | digital
N1DCS.RSTA00081 | 24612 | 备用调压进口手动门开到位 |  | digital
N1DCS.RSTA00082 | 24613 | 备用调压进口手动门关到位 |  | digital
N1DCS.RSTA00083 | 24614 | 备用调压进口手动门故障 |  | digital
N1DCS.RSTA00084 | 24615 | 调压模块#1可燃气体浓度高 |  | digital
N1DCS.RSTA00085 | 24616 | 调压模块#1可燃气体浓度高高 |  | digital
N1DCS.RSTA00086 | 24617 | #4机调压出口手动门开到位 |  | digital
N1DCS.RSTA00087 | 24618 | #4机调压出口手动门关到位 |  | digital
N1DCS.RSTA00088 | 24619 | #4机调压出口手动门故障 |  | digital
N1DCS.RSTA00089 | 24620 | 备用调压段出口手动门开到位 |  | digital
N1DCS.RSTA00090 | 24621 | 备用调压段出口手动门关到位 |  | digital
N1DCS.RSTA00091 | 24622 | 备用调压段出口手动门故障 |  | digital
N1DCS.RSTA00092 | 24623 | 调压出口至#4机放散二次门开到位 |  | digital
N1DCS.RSTA00093 | 24624 | 调压出口至#4机放散二次门关到位 |  | digital
N1DCS.RSTA00094 | 24625 | 调压出口至#4机放散二次门故障 |  | digital
N1DCS.RSTA00095 | 24626 | #2机调压进口手动门开到位 |  | digital
N1DCS.RSTA00096 | 24627 | #2机调压进口手动门关到位 |  | digital
N1DCS.RSTA00097 | 24628 | #2机调压进口手动门故障 |  | digital
N1DCS.RSTA00098 | 24629 | 调压模块#2可燃气体浓度高 |  | digital
N1DCS.RSTA00099 | 24630 | 调压模块#2可燃气体浓度高高 |  | digital
N1DCS.RSTA00100 | 24631 | #2机调压出口手动门开到位 |  | digital
N1DCS.RSTA00101 | 24632 | #2机调压出口手动门关到位 |  | digital
N1DCS.RSTA00102 | 24633 | #2机调压出口手动门故障 |  | digital
N1DCS.RSTA00103 | 24634 | 调压出口至#2机放散二次门开到位 |  | digital
N1DCS.RSTA00104 | 24635 | 调压出口至#2机放散二次门关到位 |  | digital
N1DCS.RSTA00105 | 24636 | 调压出口至#2机放散二次门故障 |  | digital
N1DCS.RSTA00106 | 24637 | 电加热模块可燃气体浓度高 |  | digital
N1DCS.RSTA00107 | 24638 | 电加热模块可燃气体浓度高高 |  | digital
N1DCS.RSTA00108 | 24639 | 调压站排污罐液位高 |  | digital
N1DCS.RSTA00109 | 24640 | 调压站排污罐液位低 |  | digital
N1DCS.RSTA00110 | 24641 | 调压站排污罐排污泵在运行 |  | digital
N1DCS.RSTA00111 | 24642 | 调压站排污罐排污泵故障 |  | digital
N1DCS.RSTA00112 | 24643 | 调压站排污罐排污泵就地控制 |  | digital
N1DCS.RSTA00113 | 24644 | 调压站#1热水锅炉在运行 |  | digital
N1DCS.RSTA00114 | 24645 | 调压站#1热水锅炉故障 |  | digital
N1DCS.RSTA00115 | 24646 | 调压站#2热水锅炉在运行 |  | digital
N1DCS.RSTA00116 | 24647 | 调压站#2热水锅炉故障 |  | digital
N1DCS.RSTA00117 | 24648 | 调压站#3热水锅炉在运行 |  | digital
N1DCS.RSTA00118 | 24649 | 调压站#3热水锅炉故障 |  | digital
N1DCS.RSTA00119 | 24650 | #1热水锅炉可燃气体浓度高 |  | digital
N1DCS.RSTA00120 | 24651 | #1热水锅炉可燃气体浓度高高 |  | digital
N1DCS.RSTA00121 | 24652 | #2热水锅炉可燃气体浓度高 |  | digital
N1DCS.RSTA00122 | 24653 | #2热水锅炉可燃气体浓度高高 |  | digital
N1DCS.RSTA00123 | 24654 | #3热水锅炉可燃气体浓度高 |  | digital
N1DCS.RSTA00124 | 24655 | #3热水锅炉可燃气体浓度高高 |  | digital
N1DCS.RSTA00125 | 24656 | 调压站电加热器在运行 |  | digital
N1DCS.RSTA00126 | 24657 | 调压站电加热器允许远方启动 |  | digital
N1DCS.RSTA00127 | 24658 | 调压站电加热器超温 |  | digital
N1DCS.RSTA00128 | 24659 | #1热水加热器温度控制偏差大 |  | digital
N1DCS.RSTA00129 | 24660 | #1热水加热器温度控制手动 |  | digital
N1DCS.RSTA00130 | 24661 | #2热水加热器温度控制偏差大 |  | digital
N1DCS.RSTA00131 | 24662 | #2热水加热器温度控制手动 |  | digital
N1DCS.RSTA00132 | 24663 | 调压站出口至#2机燃气压力高(3.8 |  | digital
N1DCS.RSTA00133 | 24664 | 调压站出口至#4机燃气压力高(3.8 |  | digital
N1DCS.RSTA00134 | 24665 | 调压站系统报警信号 |  | digital
N1DCS.RSTA00135 | 24666 | 调压站备用通道 |  | digital
N1DCS.RSTA00136 | 24667 | 调压站备用通道 |  | digital
N1DCS.RSTA00137 | 24668 | 调压站火警阀后燃气压力高(7MPa |  | digital
N1DCS.RSTA00138 | 24669 | 热水加热器水侧进口母管压力低 |  | digital
N1DCS.RSTA00139 | 24670 | 热水加热器水侧进口母管温度低 |  | digital
N1DCS.RSTA00140 | 24671 | #1热水加热器气侧出口温度低 |  | digital
N1DCS.RSTA00141 | 24672 | #2热水加热器气侧出口温度低 |  | digital
N1DCS.RSTA00142 | 24673 | 调压站在DCS控制方式 |  | digital
N1DCS.RSTA00143 | 24674 | 调压站#1热水加压泵在运行 |  | digital
N1DCS.RSTA00144 | 24675 | 调压站#2热水加压泵在运行 |  | digital
N1DCS.RSTA00145 | 24676 | 调压站#1热水锅炉小火运行 |  | digital
N1DCS.RSTA00146 | 24677 | 调压站#1热水锅炉大火运行 |  | digital
N1DCS.RSTA00147 | 24678 | 调压站#2热水锅炉小火运行 |  | digital
N1DCS.RSTA00148 | 24679 | 调压站#2热水锅炉大火运行 |  | digital
N1DCS.RSTA00149 | 24680 | 调压站#3热水锅炉小火运行 |  | digital
N1DCS.RSTA00150 | 24681 | 调压站#3热水锅炉大火运行 |  | digital
N1DCS.RSTA00151 | 24682 | 热水锅炉调压出口电磁阀开指令 |  | digital
N1DCS.RSTA00152 | 24683 | 调压站备用通道 |  | digital
N1DCS.RSTA00153 | 24684 | #1精过滤器底部排污门在手动控制 |  | digital
N1DCS.RSTA00154 | 24685 | #1精过滤器低位排污门在手动控制 |  | digital
N1DCS.RSTA00155 | 24686 | #2精过滤器底部排污门在手动控制 |  | digital
N1DCS.RSTA00156 | 24687 | #2精过滤器低位排污门在手动控制 |  | digital
N1DCS.RSTA00157 | 24688 | 调压站出口至#4机放散门在手动 |  | digital
N1DCS.RSTA00158 | 24689 | 调压站出口至#2机放散门在手动 |  | digital
N1DCS.RSTA00159 | 24690 | 调压站备用通道 |  | digital
N1DCS.RSTA00160 | 24691 | 调压站备用通道 |  | digital
N1DCS.RSTA00161 | 24692 | 调压站备用通道 |  | digital
N1DCS.RSTA00162 | 24693 | 调压站备用通道 |  | digital
N1DCS.RSTA00163 | 24694 | 调压站备用通道 |  | digital
N1DCS.RSTA00164 | 24695 | 调压站备用通道 |  | digital
N1DCS.RSTA00165 | 24696 | 调压站备用通道 |  | digital
N1DCS.RSTA00166 | 24697 | 调压站备用通道 |  | digital
N1DCS.RSTA00167 | 24698 | 调压站备用通道 |  | digital
N1DCS.RSTA00168 | 24699 | 调压站备用通道 |  | digital
N1DCS.RSTA00169 | 24700 | 调压站备用通道 |  | digital
N1DCS.RSTA00170 | 24701 | 调压站备用通道 |  | digital
N1DCS.RSTA00171 | 24702 | 调压站备用通道 |  | digital
N1DCS.RSTA00172 | 24703 | 调压站备用通道 |  | digital
N1DCS.RSTA00173 | 24704 | 调压站备用通道 |  | digital
N1DCS.RSTA00174 | 24705 | 调压站备用通道 |  | digital
N1DCS.RSTA00175 | 24706 | 调压站备用通道 |  | digital
N1DCS.RSTA00176 | 24707 | 调压站备用通道 |  | digital
N1DCS.RSTA00177 | 24708 | 调压站备用通道 |  | digital
N1DCS.RSTA00178 | 24709 | 调压站备用通道 |  | digital
N1DCS.RSTA00179 | 24710 | 调压站备用通道 |  | digital
N1DCS.RSTA00180 | 24711 | 调压站备用通道 |  | digital
N1DCS.RSTA00181 | 24712 | 调压站备用通道 |  | digital
N1DCS.RSTA00182 | 24713 | 调压站备用通道 |  | digital
N1DCS.RSTA00183 | 24714 | 调压站备用通道 |  | digital
N1DCS.RSTA00184 | 24715 | 调压站备用通道 |  | digital
N1DCS.RSTA00185 | 24716 | 调压站备用通道 |  | digital
N1DCS.RSTA00186 | 24717 | 调压站备用通道 |  | digital
N1DCS.RSTA00187 | 24718 | 调压站备用通道 |  | digital
N1DCS.RSTA00188 | 24719 | 调压站备用通道 |  | digital
N1DCS.RSTA00189 | 24720 | 调压站备用通道 |  | digital
N1DCS.RSTA00190 | 24721 | 调压站备用通道 |  | digital
N1DCS.RSTA00191 | 24722 | 调压站备用通道 |  | digital
N1DCS.RSTA00192 | 24723 | 调压站备用通道 |  | digital
N1DCS.RSTA00193 | 24724 | 调压站备用通道 |  | digital
N1DCS.RSTA00194 | 24725 | 调压站备用通道 |  | digital
N1DCS.RSTA00195 | 24726 | 调压站备用通道 |  | digital
N1DCS.RSTA00196 | 24727 | 调压站备用通道 |  | digital
N1DCS.RSTA00197 | 24728 | 调压站备用通道 |  | digital
N1DCS.RSTA00198 | 24729 | 调压站备用通道 |  | digital
N1DCS.RSTA00199 | 24730 | 调压站备用通道 |  | digital
N1DCS.RSTA00200 | 24731 | 调压站备用通道 |  | digital
N1DCS.RSTA00201 | 24732 | 调压站备用通道 |  | digital
N1DCS.RSTA00202 | 24733 | 调压站备用通道 |  | digital
N1DCS.RSTA00203 | 24734 | 调压站备用通道 |  | digital
N1DCS.RSTA00204 | 24735 | 调压站备用通道 |  | digital
N1DCS.RSTA00205 | 24736 | 调压站备用通道 |  | digital
N1DCS.RSTA00206 | 24737 | 调压站备用通道 |  | digital
N1DCS.RSTA00207 | 24738 | 调压站备用通道 |  | digital
N1DCS.RSTA00208 | 24739 | 调压站备用通道 |  | digital
N1DCS.RSTA00209 | 24740 | 调压站备用通道 |  | digital
N1DCS.RSTA00210 | 24741 | 调压站备用通道 |  | digital
N1DCS.RSTA00211 | 24742 | 调压站备用通道 |  | digital
N1DCS.RSTA00212 | 24743 | 调压站备用通道 |  | digital
N1DCS.RSTA00213 | 24744 | 调压站备用通道 |  | digital
N1DCS.RSTA00214 | 24745 | 调压站备用通道 |  | digital
N1DCS.RSTA00215 | 24746 | 调压站备用通道 |  | digital
N1DCS.RSTA00216 | 24747 | 调压站备用通道 |  | digital
N1DCS.RSTA00217 | 24748 | 调压站备用通道 |  | digital
N1DCS.RSTA00218 | 24749 | 调压站备用通道 |  | digital
N1DCS.RSTA00219 | 24750 | 调压站备用通道 |  | digital
N1DCS.RSTA00220 | 24751 | 调压站备用通道 |  | digital
N1DCS.RSTA00221 | 24752 | 调压站备用通道 |  | digital
N1DCS.RSTA00222 | 24753 | 调压站备用通道 |  | digital
N1DCS.RSTA00223 | 24754 | 调压站备用通道 |  | digital
N1DCS.RSTA00224 | 24755 | 调压站备用通道 |  | digital
N1DCS.RSTA00225 | 24756 | #1精过滤器底部排污门切手动指令 |  | digital
N1DCS.RSTA00226 | 24757 | #1精过滤器低位排污门切手动指令 |  | digital
N1DCS.RSTA00227 | 24758 | #2精过滤器底部排污门切手动指令 |  | digital
N1DCS.RSTA00228 | 24759 | #2精过滤器低位排污门切手动指令 |  | digital
N1DCS.RSTA00229 | 24760 | 调压出口至#2机放散阀切手动指令 |  | digital
N1DCS.RSTA00230 | 24761 | 调压出口至#4机放散阀切手动指令 |  | digital
N1DCS.RSTA00231 | 24762 | 调压站#1热水加热器切成手动指令 |  | digital
N1DCS.RSTA00232 | 24763 | 调压站#2热水加热器切成手动指令 |  | digital
N1DCS.RSTA00233 | 24764 | #1精过滤器底部排污门切自动指令 |  | digital
N1DCS.RSTA00234 | 24765 | #1精过滤器低位排污门切自动指令 |  | digital
N1DCS.RSTA00235 | 24766 | #2精过滤器底部排污门切自动指令 |  | digital
N1DCS.RSTA00236 | 24767 | #2精过滤器低位排污门切自动指令 |  | digital
N1DCS.RSTA00237 | 24768 | 调压出口至#2机放散门切自动指令 |  | digital
N1DCS.RSTA00238 | 24769 | 调压出口至#4机放散门切自动指令 |  | digital
N1DCS.RSTA00239 | 24770 | #1热水加热器水侧调阀切自动指令 |  | digital
N1DCS.RSTA00240 | 24771 | #2热水加热器水侧调阀切自动指令 |  | digital
N1DCS.RSTA00241 | 24772 | DCS_调压站报警确认指令 |  | digital
N1DCS.RSTA00242 | 24773 | DCS_报警复位调压站系统报警 |  | digital
N1DCS.RSTA00243 | 24774 | DCS_调压站火警阀开指令 |  | digital
N1DCS.RSTA00244 | 24775 | DCS_调压站火警阀关指令 |  | digital
N1DCS.RSTA00245 | 24776 | #1精过滤器底部排污气动门开指令 |  | digital
N1DCS.RSTA00246 | 24777 | #1精过滤器底部排污气动门关指令 |  | digital
N1DCS.RSTA00247 | 24778 | #1精过滤器低位排污气动门开指令 |  | digital
N1DCS.RSTA00248 | 24779 | #1精过滤器低位排污气动门关指令 |  | digital
N1DCS.RSTA00249 | 24780 | #2精过滤器底部排污气动门开指令 |  | digital
N1DCS.RSTA00250 | 24781 | #2精过滤器底部排污气动门关指令 |  | digital
N1DCS.RSTA00251 | 24782 | #2精过滤器低位排污气动门开指令 |  | digital
N1DCS.RSTA00252 | 24783 | #2精过滤器低位排污气动门关指令 |  | digital
N1DCS.RSTA00253 | 24784 | 调压站出口至#4机放散阀开指令 |  | digital
N1DCS.RSTA00254 | 24785 | 调压站出口至#4机放散阀关指令 |  | digital
N1DCS.RSTA00255 | 24786 | 调压站出口至#2机放散阀开指令 |  | digital
N1DCS.RSTA00256 | 24787 | 调压站出口至#2机放散阀关指令 |  | digital
N1DCS.RSTA00257 | 24788 | DCS_调压站排污罐排污泵启动指令 |  | digital
N1DCS.RSTA00258 | 24789 | DCS_调压站排污罐排污泵停止指令 |  | digital
N1DCS.RSTA00259 | 24790 | DCS_调压站电加热器启动指令 |  | digital
N1DCS.RSTA00260 | 24791 | DCS_调压站电加热器停止指令 |  | digital
N1DCS.RSTA00261 | 24792 | DCS_调压站#1热水锅炉启动指令 |  | digital
N1DCS.RSTA00262 | 24793 | DCS_调压站#1热水锅炉停止指令 |  | digital
N1DCS.RSTA00263 | 24794 | DCS_调压站#2热水锅炉启动指令 |  | digital
N1DCS.RSTA00264 | 24795 | DCS_调压站#2热水锅炉停止指令 |  | digital
N1DCS.RSTA00265 | 24796 | DCS_调压站#3热水锅炉启动指令 |  | digital
N1DCS.RSTA00266 | 24797 | DCS_调压站#3热水锅炉停止指令 |  | digital
N1DCS.RSTA30052FAULT | 24798 | 调压站#1超声波流量计声道故障 |  | digital
N1DCS.RSTA40034FAULT | 24799 | 调压站#2超声波流量计声道故障 |  | digital
N1DCS.10MKE01D1 | 24800 | #1SFC隔离变保护动作 |  | digital
N1DCS.10MKE01D2 | 24801 | #1SFC隔离变绕组超温跳闸 |  | digital
N1DCS.10MKE01D3 | 24802 | #1SFC隔离变保护装置闭锁/报警 |  | digital
N1DCS.10MKE01D5 | 24803 | #1SFC隔离变CT/PT断线 |  | digital
N1DCS.10MKE01D7 | 24804 | #1SFC隔离变过负荷报警 |  | digital
N1DCS.10MKE01XM01 | 24805 | #1SFC隔离变绕组或铁心超温报警 |  | digital
N1DCS.10MKE01XM02 | 24806 | #1SFC隔离变温控器故障或失电 |  | digital
N1DCS.10MKE01XM03 | 24807 | #1SFC隔离变风机故障 |  | digital
N1DCS.J0AVC0027 | 24808 | AVC上位机交流220V电源消失 |  | digital
N1DCS.J0AVC0028 | 24809 | AVC上位机直流110V电源消失 |  | digital
N1DCS.J0BFA00EH201 | 24810 | 380V机组公用A段母线电压低 |  | digital
N1DCS.J0BFA00EH202 | 24811 | 380V机组公用A段PT保护装置故障 |  | digital
N1DCS.J0BFA00EH203 | 24812 | 380V机组公用A段PT刀熔开关分位 |  | digital
N1DCS.J0BFA00GS001K_PUT | 24813 | 380V机组公用段开关允许并联运行 |  | digital
N1DCS.J0BFA00GS001L_PUT | 24814 | 380V机组公用段分段开关连锁已投 |  | digital
N1DCS.J0BFA00GS001PF | 24815 | 380V机组公用段分段开关综合故障 |  | digital
N1DCS.J0BFA00GS001RC | 24816 | 380V机组公用段分段开关远方控制 |  | digital
N1DCS.J0BFA00GS001RD | 24817 | 380V机组公用段分段开关合闸指令 |  | digital
N1DCS.J0BFA00GS001RP | 24818 | 380V机组公用段分段开关合闸位置 |  | digital
N1DCS.J0BFA00GS001TD | 24819 | 380V机组公用段分段开关分闸指令 |  | digital
N1DCS.J0BFA00GS001TP | 24820 | 380V机组公用段分段开关分闸位置 |  | digital
N1DCS.J0BFA08EGS101RD | 24821 | #1检修和材料库电源一45A085合闸 |  | digital
N1DCS.J0BFA08EGS101RP | 24822 | #1检修和材料库电源一45A085合位 |  | digital
N1DCS.J0BFA08EGS101TD | 24823 | #1检修和材料库电源一45A085分闸 |  | digital
N1DCS.J0BFA08EGS101TP | 24824 | #1检修和材料库电源一45A085分位 |  | digital
N1DCS.J0BFB08EGS101RD | 24825 | #1检修和材料库电源二45B085合闸 |  | digital
N1DCS.J0BFB08EGS101RP | 24826 | #1检修和材料库电源二45B085合位 |  | digital
N1DCS.J0BFB08EGS101TD | 24827 | #1检修和材料库电源二45B085分闸 |  | digital
N1DCS.J0BFB08EGS101TP | 24828 | #1检修和材料库电源二45B085分位 |  | digital
N1DCS.J0BFT10GS001PF | 24829 | 机组公用A变6kV开关保护装置异常 |  | digital
N1DCS.J0BFT10GS001PS | 24830 | 机组公用A变6kV侧开关保护动作 |  | digital
N1DCS.J0BFT10GS001RC | 24831 | 机组公用A变6kV侧开关远方控制 |  | digital
N1DCS.J0BFT10GS001RD | 24832 | 机组公用A变6kV侧开关合闸指令 |  | digital
N1DCS.J0BFT10GS001RP | 24833 | 机组公用A变6kV侧开关合闸位置 |  | digital
N1DCS.J0BFT10GS001SW | 24834 | 机组公用A变6kV侧开关试验位置 |  | digital
N1DCS.J0BFT10GS001TD | 24835 | 机组公用A变6kV侧开关分闸指令 |  | digital
N1DCS.J0BFT10GS001TP | 24836 | 机组公用A变6kV侧开关分闸位置 |  | digital
N1DCS.J0BFT10GS001YW | 24837 | 机组公用A变6kV侧开关工作位置 |  | digital
N1DCS.J0BFT10GS002_PUT | 24838 | 380V机组公用段分段开关连锁已投 |  | digital
N1DCS.J0BFT10GS002PF | 24839 | 机组公用A变380V侧开关综合故障 |  | digital
N1DCS.J0BFT10GS002RC | 24840 | 机组公用A变380V侧开关远方控制 |  | digital
N1DCS.J0BFT10GS002RD | 24841 | 机组公用A变380V侧开关合闸指令 |  | digital
N1DCS.J0BFT10GS002RP | 24842 | 机组公用A变380V侧开关合闸位置 |  | digital
N1DCS.J0BFT10GS002TD | 24843 | 机组公用A变380V侧开关分闸指令 |  | digital
N1DCS.J0BFT10GS002TP | 24844 | 机组公用A变380V侧开关分闸位置 |  | digital
N1DCS.J0BHT30GS001PF | 24845 | 厂区公用A变6kV开关保护装置异常 |  | digital
N1DCS.J0BHT30GS001PS | 24846 | 厂区公用A变6kV侧开关保护动作 |  | digital
N1DCS.J0BHT30GS001RC | 24847 | 厂区公用A变6kV侧开关远方控制 |  | digital
N1DCS.J0BHT30GS001RD | 24848 | 厂区公用A变6kV侧开关合闸指令 |  | digital
N1DCS.J0BHT30GS001RP | 24849 | 厂区公用A变6kV侧开关合闸位置 |  | digital
N1DCS.J0BHT30GS001SW | 24850 | 厂区公用A变6kV侧开关试验位置 |  | digital
N1DCS.J0BHT30GS001TD | 24851 | 厂区公用A变6kV侧开关分闸指令 |  | digital
N1DCS.J0BHT30GS001TP | 24852 | 厂区公用A变6kV侧开关分闸位置 |  | digital
N1DCS.J0BHT30GS001YW | 24853 | 厂区公用A变6kV侧开关工作位置 |  | digital
N1DCS.J0BHT50GS001PF | 24854 | 补给水A变6kV开关保护装置异常 |  | digital
N1DCS.J0BHT50GS001PS | 24855 | 补给水A变6kV侧开关保护动作 |  | digital
N1DCS.J0BHT50GS001RC | 24856 | 补给水A变6kV侧开关远方控制 |  | digital
N1DCS.J0BHT50GS001RD | 24857 | 补给水A变6kV侧开关合闸指令 |  | digital
N1DCS.J0BHT50GS001RP | 24858 | 补给水A变6kV侧开关合闸位置 |  | digital
N1DCS.J0BHT50GS001SW | 24859 | 补给水A变6kV侧开关试验位置 |  | digital
N1DCS.J0BHT50GS001TD | 24860 | 补给水A变6kV侧开关分闸指令 |  | digital
N1DCS.J0BHT50GS001TP | 24861 | 补给水A变6kV侧开关分闸位置 |  | digital
N1DCS.J0BHT50GS001YW | 24862 | 补给水A变6kV侧开关工作位置 |  | digital
N1DCS.J0BHT70GS001PF | 24863 | #1进气冷却变6kV开关保护异常 |  | digital
N1DCS.J0BHT70GS001PS | 24864 | #1进气冷却变6kV侧开关保护动作 |  | digital
N1DCS.J0BHT70GS001RC | 24865 | #1进气冷却变6kV侧开关远方控制 |  | digital
N1DCS.J0BHT70GS001RD | 24866 | #1进气冷却变6kV侧开关合闸指令 |  | digital
N1DCS.J0BHT70GS001RP | 24867 | #1进气冷却变6kV侧开关合闸位置 |  | digital
N1DCS.J0BHT70GS001SW | 24868 | #1进气冷却变6kV侧开关试验位置 |  | digital
N1DCS.J0BHT70GS001TD | 24869 | #1进气冷却变6kV侧开关分闸指令 |  | digital
N1DCS.J0BHT70GS001TP | 24870 | #1进气冷却变6kV侧开关分闸位置 |  | digital
N1DCS.J0BHT70GS001YW | 24871 | #1进气冷却变6kV侧开关工作位置 |  | digital
N1DCS.J0BLA00GS201PF | 24872 | 机组公用A段至#1照明MCC保护异常 |  | digital
N1DCS.J0BLA00GS201RC | 24873 | 机组公用A段至#1照明MCC段在远控 |  | digital
N1DCS.J0BLA00GS201RD | 24874 | 机组公用A段至#1照明MCC段合指令 |  | digital
N1DCS.J0BLA00GS201RP | 24875 | 机组公用A段至#1照明MCC段合闸位 |  | digital
N1DCS.J0BLA00GS201TD | 24876 | 机组公用A段至#1照明MCC段分指令 |  | digital
N1DCS.J0BLA00GS201TP | 24877 | 机组公用A段至#1照明MCC段分闸位 |  | digital
N1DCS.J0BLA00GS202PF | 24878 | 机组公用B段至#1照明MCC保护异常 |  | digital
N1DCS.J0BLA00GS202RC | 24879 | 机组公用B段至#1照明MCC段在远控 |  | digital
N1DCS.J0BLA00GS202RD | 24880 | 机组公用B段至#1照明MCC段合指令 |  | digital
N1DCS.J0BLA00GS202RP | 24881 | 机组公用B段至#1照明MCC段合闸位 |  | digital
N1DCS.J0BLA00GS202TD | 24882 | 机组公用B段至#1照明MCC段分指令 |  | digital
N1DCS.J0BLA00GS202TP | 24883 | 机组公用B段至#1照明MCC段分闸位 |  | digital
N1DCS.J0BLC00GS201PF | 24884 | 机组公用A段至#1检修MCC保护异常 |  | digital
N1DCS.J0BLC00GS201RC | 24885 | 机组公用A段至#1检修MCC段在远控 |  | digital
N1DCS.J0BLC00GS201RD | 24886 | 机组公用A段至#1检修MCC段合指令 |  | digital
N1DCS.J0BLC00GS201RP | 24887 | 机组公用A段至#1检修MCC段合闸位 |  | digital
N1DCS.J0BLC00GS201TD | 24888 | 机组公用A段至#1检修MCC段分指令 |  | digital
N1DCS.J0BLC00GS201TP | 24889 | 机组公用A段至#1检修MCC段分闸位 |  | digital
N1DCS.J0BLC00GS202PF | 24890 | 机组公用B段至#1检修MCC保护异常 |  | digital
N1DCS.J0BLC00GS202RC | 24891 | 机组公用B段至#1检修MCC段在远控 |  | digital
N1DCS.J0BLC00GS202RD | 24892 | 机组公用B段至#1检修MCC段合指令 |  | digital
N1DCS.J0BLC00GS202RP | 24893 | 机组公用B段至#1检修MCC段合闸位 |  | digital
N1DCS.J0BLC00GS202TD | 24894 | 机组公用B段至#1检修MCC段分指令 |  | digital
N1DCS.J0BLC00GS202TP | 24895 | 机组公用B段至#1检修MCC段分闸位 |  | digital
N1DCS.J0BLE00GS201PF | 24896 | 机组公用A至集控楼MCC保护异常 |  | digital
N1DCS.J0BLE00GS201RC | 24897 | 机组公用A至集控楼MCC开关远控 |  | digital
N1DCS.J0BLE00GS201RD | 24898 | 机组公用A至集控楼MCC开关合指令 |  | digital
N1DCS.J0BLE00GS201RP | 24899 | 机组公用A至集控楼MCC开关合闸位 |  | digital
N1DCS.J0BLE00GS201TD | 24900 | 机组公用A至集控楼MCC开关分指令 |  | digital
N1DCS.J0BLE00GS201TP | 24901 | 机组公用A至集控楼MCC开关分闸位 |  | digital
N1DCS.J0BLF00GS201PF | 24902 | 机组公用A至联合间MCC保护异常 |  | digital
N1DCS.J0BLF00GS201RC | 24903 | 机组公用A至联合间MCC开关远控 |  | digital
N1DCS.J0BLF00GS201RD | 24904 | 机组公用A至联合间MCC开关合指令 |  | digital
N1DCS.J0BLF00GS201RP | 24905 | 机组公用A至联合间MCC开关合闸位 |  | digital
N1DCS.J0BLF00GS201TD | 24906 | 机组公用A至联合间MCC开关分指令 |  | digital
N1DCS.J0BLF00GS201TP | 24907 | 机组公用A至联合间MCC开关分闸位 |  | digital
N1DCS.J0BLG00GS201PF | 24908 | 机组公用A至GIS楼MCC段保护异常 |  | digital
N1DCS.J0BLG00GS201RC | 24909 | 机组公用A至GIS楼MCC开关在远控 |  | digital
N1DCS.J0BLG00GS201RD | 24910 | 机组公用A至GIS楼MCC开关合指令 |  | digital
N1DCS.J0BLG00GS201RP | 24911 | 机组公用A至GIS楼MCC开关合闸位 |  | digital
N1DCS.J0BLG00GS201TD | 24912 | 机组公用A至GIS楼MCC开关分指令 |  | digital
N1DCS.J0BLG00GS201TP | 24913 | 机组公用A至GIS楼MCC开关分闸位 |  | digital
N1DCS.J0BLH00GS201RP | 24914 | 机组公用A至启动炉MCC开关合闸位 |  | digital
N1DCS.J0BLH00GS201TP | 24915 | 机组公用A至启动炉MCC开关分闸位 |  | digital
N1DCS.Y0AEA11GS101RP | 24916 | #2主变开关2202合位置 |  | digital
N1DCS.Y0AEA11GS101TP | 24917 | #2主变开关2202分位置 |  | digital
N1DCS.Y0AEA12GS101RP | 24918 | #1主变开关2201合位置 |  | digital
N1DCS.Y0AEA12GS101TD | 24919 | #1主变开关2201分闸指令 |  | digital
N1DCS.Y0AEA12GS101TP | 24920 | #1主变开关2201分位置 |  | digital
N1DCS.Y0AEA15GS101RP | 24921 | #1高备变220kV开关2209合闸位置 |  | digital
N1DCS.Y0AEA15GS101TP | 24922 | #1高备变220kV开关2209分闸位置 |  | digital
N1DCS.Y0BAY01EH101 | 24923 | #2主变涌流抑制器装置失电 |  | digital
N1DCS.Y0BAY01EH102 | 24924 | #2主变涌流抑制器装置故障 |  | digital
N1DCS.Y0BAY01EH103 | 24925 | #2主变涌流抑制器故障总信号 |  | digital
N1DCS.Y0BAY01EH301 | 24926 | #1高备变涌流抑制器装置失电 |  | digital
N1DCS.Y0BAY01EH302 | 24927 | #1高备变涌流抑制器装置故障 |  | digital
N1DCS.Y0BAY01EH303 | 24928 | #1高备变涌流抑制器故障总信号 |  | digital
N1DCS.Y0BCT01_DOWNCPMT | 24929 | #1高备变有载调压减速允许 |  | digital
N1DCS.Y0BCT01_UPCPMT | 24930 | #1高备变有载调压升速允许 |  | digital
N1DCS.Y0BCT01EH021 | 24931 | #1高备变有载调压电机回路信号 |  | digital
N1DCS.Y0BCT01EH022 | 24932 | #1高备变有载调压开关操作中 |  | digital
N1DCS.Y0BCT01EH023 | 24933 | #1高备变有载调压切换操作未完成 |  | digital
N1DCS.Y0BCT01EH024 | 24934 | #1高备变有载调压器远方控制 |  | digital
N1DCS.Y0BCT01EH901 | 24935 | 高备变有载调压开关分接头位置1 |  | digital
N1DCS.Y0BCT01EH902 | 24936 | 高备变有载调压开关分接头位置2 |  | digital
N1DCS.Y0BCT01EH903 | 24937 | 高备变有载调压开关分接头位置3 |  | digital
N1DCS.Y0BCT01EH904 | 24938 | 高备变有载调压开关分接头位置4 |  | digital
N1DCS.Y0BCT01EH905 | 24939 | 高备变有载调压开关分接头位置5 |  | digital
N1DCS.Y0BCT01EH906 | 24940 | 高备变有载调压开关分接头位置6 |  | digital
N1DCS.Y0BCT01EH907 | 24941 | 高备变有载调压开关分接头位置7 |  | digital
N1DCS.Y0BCT01EH908 | 24942 | 高备变有载调压开关分接头位置8 |  | digital
N1DCS.Y0BCT01EH909A | 24943 | 高备变有载调压开关分接头位置9A |  | digital
N1DCS.Y0BCT01EH909B | 24944 | 高备变有载调压开关分接头位置9B |  | digital
N1DCS.Y0BCT01EH909C | 24945 | 高备变有载调压开关分接头位置9C |  | digital
N1DCS.Y0BCT01EH910 | 24946 | 高备变有载调压开关分接头位置10 |  | digital
N1DCS.Y0BCT01EH911 | 24947 | 高备变有载调压开关分接头位置11 |  | digital
N1DCS.Y0BCT01EH912 | 24948 | 高备变有载调压开关分接头位置12 |  | digital
N1DCS.Y0BCT01EH913 | 24949 | 高备变有载调压开关分接头位置13 |  | digital
N1DCS.Y0BCT01EH914 | 24950 | 高备变有载调压开关分接头位置14 |  | digital
N1DCS.Y0BCT01EH915 | 24951 | 高备变有载调压开关分接头位置15 |  | digital
N1DCS.Y0BCT01EH916 | 24952 | 高备变有载调压开关分接头位置16 |  | digital
N1DCS.Y0BCT01EH917 | 24953 | 高备变有载调压开关分接头位置17 |  | digital
N1DCS.Y0BCT01EJ001 | 24954 | #1高备变有载调压回路K2降压指令 |  | digital
N1DCS.Y0BCT01EJ002 | 24955 | #1高备变有载调压回路K1升压指令 |  | digital
N1DCS.Y0BCT01EJ003 | 24956 | 高备变有载调压开关Q1紧急分闸令 |  | digital
N1DCS.Y0BCT01GS304RP | 24957 | 高备变中性点接地开关GS304合位 |  | digital
N1DCS.Y0BCT01GS304TP | 24958 | 高备变中性点接地开关GS304分位 |  | digital
N1DCS.Y0BHT10GS001PF | 24959 | 生产办公楼A变6KV开关保护异常 |  | digital
N1DCS.Y0BHT10GS001PS | 24960 | 生产办公楼A变6kV开关保护动作 |  | digital
N1DCS.Y0BHT10GS001RC | 24961 | 生产办公楼A变6kV开关远方控制 |  | digital
N1DCS.Y0BHT10GS001RD | 24962 | 生产办公楼A变6kV开关合闸指令 |  | digital
N1DCS.Y0BHT10GS001RP | 24963 | 生产办公楼A变6kV开关合闸位置 |  | digital
N1DCS.Y0BHT10GS001SW | 24964 | 生产办公楼A变6kV开关试验位置 |  | digital
N1DCS.Y0BHT10GS001TD | 24965 | 生产办公楼A变6kV开关分闸指令 |  | digital
N1DCS.Y0BHT10GS001TP | 24966 | 生产办公楼A变6kV开关分闸位置 |  | digital
N1DCS.Y0BHT10GS001YW | 24967 | 生产办公楼A变6kV开关合闸位置 |  | digital
N1DCS.Y0CHA01EH101 | 24968 | #1高备变A套差动动作 |  | digital
N1DCS.Y0CHA01EH102 | 24969 | #1高备变A套相间后备保护动作 |  | digital
N1DCS.Y0CHA01EH103 | 24970 | #1高备变A套高压侧接地保护跳闸 |  | digital
N1DCS.Y0CHA01EH104 | 24971 | #1高备变A套高压侧间隙接地跳闸 |  | digital
N1DCS.Y0CHA01EH105 | 24972 | #1高备变A套A1分支相间后备跳闸 |  | digital
N1DCS.Y0CHA01EH106 | 24973 | #1高备变A套A2分支相间后备跳闸 |  | digital
N1DCS.Y0CHA01EH107 | 24974 | #1高备变A套B1分支相间后备跳闸 |  | digital
N1DCS.Y0CHA01EH108 | 24975 | #1高备变A套B2分支相间后备跳闸 |  | digital
N1DCS.Y0CHA01EH109 | 24976 | #1高备变A套装置闭锁 |  | digital
N1DCS.Y0CHA01EH110 | 24977 | #1高备变A套装置报警 |  | digital
N1DCS.Y0CHA01EH111 | 24978 | #1高备变A套保护CT断线 |  | digital
N1DCS.Y0CHA01EH112 | 24979 | #1高备变A套保护PT断线 |  | digital
N1DCS.Y0CHA01EH113 | 24980 | #1高备变A套过负荷报警 |  | digital
N1DCS.Y0CHA01EH114 | 24981 | #1高备变A套保护切换继电器动作 |  | digital
N1DCS.Y0CHA01EH115 | 24982 | #1高备变A套保护切换继电器失电 |  | digital
N1DCS.Y0CHB01EH101 | 24983 | #1高备变B套差动动作 |  | digital
N1DCS.Y0CHB01EH102 | 24984 | #1高备变B套高压侧相间后备跳闸 |  | digital
N1DCS.Y0CHB01EH103 | 24985 | #1高备变B套高压侧零序过流 |  | digital
N1DCS.Y0CHB01EH104 | 24986 | #1高备变B套高压侧间隙零序 |  | digital
N1DCS.Y0CHB01EH105 | 24987 | #1高备变B套失灵启动 |  | digital
N1DCS.Y0CHB01EH106 | 24988 | #1高备变B套高压侧非全相动作 |  | digital
N1DCS.Y0CHB01EH107 | 24989 | #1高备变B套A1分支相间后备跳闸 |  | digital
N1DCS.Y0CHB01EH108 | 24990 | #1高备变B套A2分支相间后备跳闸 |  | digital
N1DCS.Y0CHB01EH109 | 24991 | #1高备变B套B1分支相间后备跳闸 |  | digital
N1DCS.Y0CHB01EH110 | 24992 | #1高备变B套B2分支相间后备跳闸 |  | digital
N1DCS.Y0CHB01EH111 | 24993 | #1高备变B套低压侧零序过流 |  | digital
N1DCS.Y0CHB01EH112 | 24994 | #1高备变B套差流越限告警 |  | digital
N1DCS.Y0CHB01EH113 | 24995 | #1高备变B套定时限过负荷告警 |  | digital
N1DCS.Y0CHB01EH114 | 24996 | #1高备变B套CT异常告警 |  | digital
N1DCS.Y0CHB01EH115 | 24997 | #1高备变B套PT异常告警 |  | digital
N1DCS.Y0CHB01EH116 | 24998 | #1高备变B套装置故障告警 |  | digital
N1DCS.Y0CHB01EH117 | 24999 | #1高备变B套失电告警 |  | digital
N1DCS.Y0CHB01EH118 | 25000 | #1高备变B套保护切换继电器动作 |  | digital
N1DCS.Y0CHB01EH119 | 25001 | #1高备变B套切换继电器失压 |  | digital
N1DCS.Y0CHC01EH101 | 25002 | #1高备变保护装置闭锁 |  | digital
N1DCS.Y0CHC01EH102 | 25003 | #1高备变保护装置报警 |  | digital
N1DCS.Y0CHC01EH103 | 25004 | #1高备变冷控失电延时跳闸 |  | digital
N1DCS.Y0CHC01EH104 | 25005 | #1高备变重瓦斯 |  | digital
N1DCS.Y0CHC01EH105 | 25006 | #1高备变油面温度过高跳闸 |  | digital
N1DCS.Y0CHC01EH106 | 25007 | #1高备变绕组温度过高跳闸 |  | digital
N1DCS.Y0CHC01EH107 | 25008 | #1高备变调压开关重瓦斯 |  | digital
N1DCS.Y0CHC01EH108 | 25009 | #1高备变突发压力 |  | digital
N1DCS.Y0CHC01EH109 | 25010 | #1高备变轻瓦斯 |  | digital
N1DCS.Y0CHC01EH110 | 25011 | #1高备变油面温度高报警 |  | digital
N1DCS.Y0CHC01EH111 | 25012 | #1高备变绕组温度高报警 |  | digital
N1DCS.Y0CHC01EH112 | 25013 | #1高备变调压开关轻瓦斯 |  | digital
N1DCS.Y0CHC01EH113 | 25014 | #1高备变本体油位异常 |  | digital
N1DCS.Y0CHC01EH114 | 25015 | #1高备变有载开关油位异常 |  | digital
N1DCS.Y0CHC01EH115 | 25016 | #1高备变压力释放 |  | digital
N1DCS.Y0CHC01EH116 | 25017 | #1高备变调压开关压力释放 |  | digital
N1DCS.Y0CHC01EH117 | 25018 | #1高备变断路器位置不一致 |  | digital
N1DCS.Y0CHC01EH118 | 25019 | #1高备变非电量保护第一组断线 |  | digital
N1DCS.Y0CHC01EH119 | 25020 | #1高备变非电量保护第二组断线 |  | digital
N1DCS.Y0CHC01EH120 | 25021 | #1高备变非电量保护第一出口跳闸 |  | digital
N1DCS.Y0CHC01EH121 | 25022 | #1高备变非电量保护第二出口跳闸 |  | digital
N1DCS.Y0CHC01EH122 | 25023 | #1高备变非全相跳闸信号 |  | digital
N1DCS.Y0AEA12GS101RPN | 25024 | #1主变开关2201分闸位置 |  | digital
N1DCS.20MKE01D1 | 25025 | #2SFC隔离变保护动作 |  | digital
N1DCS.20MKE01D2 | 25026 | #2SFC隔离变绕温超高跳闸 |  | digital
N1DCS.20MKE01D3 | 25027 | #2SFC隔离变保护装置闭锁/报警 |  | digital
N1DCS.20MKE01D5 | 25028 | #2SFC隔离变CT/PT断线 |  | digital
N1DCS.20MKE01D7 | 25029 | #2SFC隔离变过负荷报警 |  | digital
N1DCS.20MKE01XM01 | 25030 | #2SFC隔离变绕组或铁心超温报警 |  | digital
N1DCS.20MKE01XM02 | 25031 | #2SFC隔离变温控器故障或失电 |  | digital
N1DCS.20MKE01XM03 | 25032 | #2SFC隔离变风机故障 |  | digital
N1DCS.J0BFA09EGS101RD | 25033 | #2检修和材料库电源一45A095合闸 |  | digital
N1DCS.J0BFA09EGS101RP | 25034 | #2检修和材料库电源一45A095合位 |  | digital
N1DCS.J0BFA09EGS101TD | 25035 | #2检修和材料库电源一45A095分闸 |  | digital
N1DCS.J0BFA09EGS101TP | 25036 | #2检修和材料库电源一45A095分位 |  | digital
N1DCS.J0BFB00EH201 | 25037 | 380V机组公用B段母线电压低 |  | digital
N1DCS.J0BFB00EH202 | 25038 | 380V机组公用B段PT保护装置故障 |  | digital
N1DCS.J0BFB00EH203 | 25039 | 380V机组公用B段PT刀熔开关分位 |  | digital
N1DCS.J0BFB09EGS101RD | 25040 | #2检修和材料库电源二45B095合闸 |  | digital
N1DCS.J0BFB09EGS101RP | 25041 | #2检修和材料库电源二45B095合位 |  | digital
N1DCS.J0BFB09EGS101TD | 25042 | #2检修和材料库电源二45B095分闸 |  | digital
N1DCS.J0BFB09EGS101TP | 25043 | #2检修和材料库电源二45B095分位 |  | digital
N1DCS.J0BFT20GS001PF | 25044 | 机组公用B变6kV侧开关保护异常 |  | digital
N1DCS.J0BFT20GS001PS | 25045 | 机组公用B变6kV侧开关保护动作 |  | digital
N1DCS.J0BFT20GS001RC | 25046 | 机组公用B变6kV侧开关远方控制 |  | digital
N1DCS.J0BFT20GS001RD | 25047 | 机组公用B变6kV侧开关合闸指令 |  | digital
N1DCS.J0BFT20GS001RP | 25048 | 机组公用B变6kV侧开关合闸位置 |  | digital
N1DCS.J0BFT20GS001TD | 25049 | 机组公用B变6kV侧开关分闸指令 |  | digital
N1DCS.J0BFT20GS001TP | 25050 | 机组公用B变6kV侧开关分闸位置 |  | digital
N1DCS.J0BFT20GS001YW | 25051 | 机组公用B变6kV侧开关工作位置 |  | digital
N1DCS.J0BFT20GS002_PUT | 25052 | 380V机组公用段分段开关连锁已投 |  | digital
N1DCS.J0BFT20GS002PF | 25053 | 机组公用B变380V侧开关保护异常 |  | digital
N1DCS.J0BFT20GS002RC | 25054 | 机组公用B变380V侧开关远方控制 |  | digital
N1DCS.J0BFT20GS002RD | 25055 | 机组公用B变380V侧开关合闸指令 |  | digital
N1DCS.J0BFT20GS002RP | 25056 | 机组公用B变380V侧开关合闸位置 |  | digital
N1DCS.J0BFT20GS002TD | 25057 | 机组公用B变380V侧开关分闸指令 |  | digital
N1DCS.J0BFT20GS002TP | 25058 | 机组公用B变380V侧开关分闸位置 |  | digital
N1DCS.J0BFT2GS001SW | 25059 | 机组公用B变6kV侧开关试验位置 |  | digital
N1DCS.J0BHT40GS001PF | 25060 | 厂区公用B变6kV侧开关保护异常 |  | digital
N1DCS.J0BHT40GS001PS | 25061 | 厂区公用B变6kV侧开关保护动作 |  | digital
N1DCS.J0BHT40GS001RC | 25062 | 厂区公用B变6kV侧开关远方控制 |  | digital
N1DCS.J0BHT40GS001RD | 25063 | 厂区公用B变6kV侧开关合闸指令 |  | digital
N1DCS.J0BHT40GS001RP | 25064 | 厂区公用B变6kV侧开关合闸位置 |  | digital
N1DCS.J0BHT40GS001SW | 25065 | 厂区公用B变6kV侧开关试验位置 |  | digital
N1DCS.J0BHT40GS001TD | 25066 | 厂区公用B变6kV侧开关分闸指令 |  | digital
N1DCS.J0BHT40GS001TP | 25067 | 厂区公用B变6kV侧开关分闸位置 |  | digital
N1DCS.J0BHT40GS001YW | 25068 | 厂区公用B变6kV侧开关工作位置 |  | digital
N1DCS.J0BHT60GS001PF | 25069 | 补给水B变6kV侧开关保护异常 |  | digital
N1DCS.J0BHT60GS001PS | 25070 | 补给水B变6kV侧开关保护动作 |  | digital
N1DCS.J0BHT60GS001RC | 25071 | 补给水B变6kV侧开关远方控制 |  | digital
N1DCS.J0BHT60GS001RD | 25072 | 补给水B变6kV侧开关合闸指令 |  | digital
N1DCS.J0BHT60GS001RP | 25073 | 补给水B变6kV侧开关合闸位置 |  | digital
N1DCS.J0BHT60GS001TD | 25074 | 补给水B变6kV侧开关分闸指令 |  | digital
N1DCS.J0BHT60GS001TP | 25075 | 补给水B变6kV侧开关分闸位置 |  | digital
N1DCS.J0BHT60SW | 25076 | 补给水B变6kV侧开关试验位置 |  | digital
N1DCS.J0BHT60YW | 25077 | 补给水B变6kV侧开关工作位置 |  | digital
N1DCS.J0BHT80GS001PF | 25078 | #2进气冷却变6kV侧开关保护异常 |  | digital
N1DCS.J0BHT80GS001PS | 25079 | #2进气冷却变6kV侧开关保护动作 |  | digital
N1DCS.J0BHT80GS001RC | 25080 | #2进气冷却变6kV侧开关远方控制 |  | digital
N1DCS.J0BHT80GS001RD | 25081 | #2进气冷却变6kV侧开关合闸指令 |  | digital
N1DCS.J0BHT80GS001RP | 25082 | #2进气冷却变6kV侧开关合闸位置 |  | digital
N1DCS.J0BHT80GS001SW | 25083 | #2进气冷却变6kV侧开关试验位置 |  | digital
N1DCS.J0BHT80GS001TD | 25084 | #2进气冷却变6kV侧开关分闸指令 |  | digital
N1DCS.J0BHT80GS001TP | 25085 | #2进气冷却变6kV侧开关分闸位置 |  | digital
N1DCS.J0BHT80GS001YW | 25086 | #2进气冷却变6kV侧开关工作位置 |  | digital
N1DCS.J0BLB00GS201PF | 25087 | 机组公用A至#2照明MCC段保护异常 |  | digital
N1DCS.J0BLB00GS201RC | 25088 | 机组公用A至#2照明MCC段在远控 |  | digital
N1DCS.J0BLB00GS201RD | 25089 | 机组公用A至#2照明MCC段合指令 |  | digital
N1DCS.J0BLB00GS201RP | 25090 | 机组公用A至#2照明MCC段合闸位 |  | digital
N1DCS.J0BLB00GS201TD | 25091 | 机组公用A至#2照明MCC段分指令 |  | digital
N1DCS.J0BLB00GS201TP | 25092 | 机组公用A至#2照明MCC段分闸位 |  | digital
N1DCS.J0BLB00GS202PF | 25093 | 机组公用B至#2照明MCC段保护异常 |  | digital
N1DCS.J0BLB00GS202RC | 25094 | 机组公用B至#2照明MCC段在远控 |  | digital
N1DCS.J0BLB00GS202RD | 25095 | 机组公用B至#2照明MCC段合指令 |  | digital
N1DCS.J0BLB00GS202RP | 25096 | 机组公用B至#2照明MCC段合闸位 |  | digital
N1DCS.J0BLB00GS202TD | 25097 | 机组公用B至#2照明MCC段分指令 |  | digital
N1DCS.J0BLB00GS202TP | 25098 | 机组公用B至#2照明MCC段分闸位 |  | digital
N1DCS.J0BLD00GS201PF | 25099 | 机组公用A至#2检修MCC段保护异常 |  | digital
N1DCS.J0BLD00GS201RC | 25100 | 机组公用A至#2检修MCC段在远控 |  | digital
N1DCS.J0BLD00GS201RD | 25101 | 机组公用A至#2检修MCC段合指令 |  | digital
N1DCS.J0BLD00GS201RP | 25102 | 机组公用A至#2检修MCC段合闸位 |  | digital
N1DCS.J0BLD00GS201TD | 25103 | 机组公用A至#2检修MCC段分指令 |  | digital
N1DCS.J0BLD00GS201TP | 25104 | 机组公用A至#2检修MCC段分闸位 |  | digital
N1DCS.J0BLD00GS202PF | 25105 | 机组公用B至#2检修MCC段保护异常 |  | digital
N1DCS.J0BLD00GS202RC | 25106 | 机组公用B至#2检修MCC段在远控 |  | digital
N1DCS.J0BLD00GS202RD | 25107 | 机组公用B至#2检修MCC段合指令 |  | digital
N1DCS.J0BLD00GS202RP | 25108 | 机组公用B至#2检修MCC段合闸位 |  | digital
N1DCS.J0BLD00GS202TD | 25109 | 机组公用B至#2检修MCC段分指令 |  | digital
N1DCS.J0BLD00GS202TP | 25110 | 机组公用B至#2检修MCC段分闸位 |  | digital
N1DCS.J0BLE00GS202PF | 25111 | 机组公用B至集控楼MCC保护异常 |  | digital
N1DCS.J0BLE00GS202RC | 25112 | 机组公用B至集控楼MCC开关远控 |  | digital
N1DCS.J0BLE00GS202RD | 25113 | 机组公用B至集控楼MCC开关合指令 |  | digital
N1DCS.J0BLE00GS202RP | 25114 | 机组公用B至集控楼MCC开关合闸位 |  | digital
N1DCS.J0BLE00GS202TD | 25115 | 机组公用B至集控楼MCC开关分指令 |  | digital
N1DCS.J0BLE00GS202TP | 25116 | 机组公用B至集控楼MCC开关分闸位 |  | digital
N1DCS.J0BLF00GS202PF | 25117 | 机组公用B至联合间MCC保护异常 |  | digital
N1DCS.J0BLF00GS202RC | 25118 | 机组公用B至联合间MCC开关远控 |  | digital
N1DCS.J0BLF00GS202RD | 25119 | 机组公用B至联合间MCC开关合指令 |  | digital
N1DCS.J0BLF00GS202RP | 25120 | 机组公用B至联合间MCC开关合闸位 |  | digital
N1DCS.J0BLF00GS202TD | 25121 | 机组公用B至联合间MCC开关分指令 |  | digital
N1DCS.J0BLF00GS202TP | 25122 | 机组公用B至联合间MCC开关分闸位 |  | digital
N1DCS.J0BLG00GS202PF | 25123 | 机组公用B至GIS楼MCC段保护异常 |  | digital
N1DCS.J0BLG00GS202RC | 25124 | 机组公用B至GIS楼MCC开关在远控 |  | digital
N1DCS.J0BLG00GS202RD | 25125 | 机组公用B至GIS楼MCC开关合指令 |  | digital
N1DCS.J0BLG00GS202RP | 25126 | 机组公用B至GIS楼MCC开关合闸位 |  | digital
N1DCS.J0BLG00GS202TD | 25127 | 机组公用B至GIS楼MCC开关分指令 |  | digital
N1DCS.J0BLG00GS202TP | 25128 | 机组公用B至GIS楼MCC开关分闸位 |  | digital
N1DCS.J0BLH00GS202RP | 25129 | 机组公用B至启动炉MCC开关合闸位 |  | digital
N1DCS.J0BLH00GS202TP | 25130 | 机组公用B至启动炉MCC开关分闸位 |  | digital
N1DCS.Y0AEA13GS101RP | 25131 | #4主变开关2204合位置 |  | digital
N1DCS.Y0AEA13GS101TP | 25132 | #4主变开关2204分位置 |  | digital
N1DCS.Y0AEA14GS101RP | 25133 | #3主变开关2203合位置 |  | digital
N1DCS.Y0AEA14GS101TD | 25134 | #3主变开关2203分闸指令 |  | digital
N1DCS.Y0AEA14GS101TP | 25135 | #3主变开关2203分位置 |  | digital
N1DCS.Y0BAY01EH201 | 25136 | #4主变涌流抑制器装置失电 |  | digital
N1DCS.Y0BAY01EH202 | 25137 | #4主变涌流抑制器装置故障 |  | digital
N1DCS.Y0BAY01EH203 | 25138 | #4主变涌流抑制器故障总信号 |  | digital
N1DCS.Y0BHT20GS001PF | 25139 | 生产办公楼B变6KV开关保护异常 |  | digital
N1DCS.Y0BHT20GS001PS | 25140 | 生产办公楼B变6kV开关保护动作 |  | digital
N1DCS.Y0BHT20GS001RC | 25141 | 生产办公楼B变6kV开关远方控制 |  | digital
N1DCS.Y0BHT20GS001RD | 25142 | 生产办公楼B变6kV开关合闸指令 |  | digital
N1DCS.Y0BHT20GS001RP | 25143 | 生产办公楼B变6kV开关合闸位置 |  | digital
N1DCS.Y0BHT20GS001SW | 25144 | 生产办公楼B变6kV开关试验位置 |  | digital
N1DCS.Y0BHT20GS001TD | 25145 | 生产办公楼B变6kV开关分闸指令 |  | digital
N1DCS.Y0BHT20GS001TP | 25146 | 生产办公楼B变6kV开关分闸位置 |  | digital
N1DCS.Y0BHT20GS001YW | 25147 | 生产办公楼B变6kV开关合闸位置 |  | digital
N1DCS.10CHA00EZ100_XK96 | 25148 | 汽机发电机跳闸 |  | digital
N1DCS.10CHA00EZ100_XV01 | 25149 | Ovation Control Builder |  | digital
N1DCS.10CHA00EZ100A_XK01 | 25150 | 发电机保护停机 1# |  | digital
N1DCS.10CHA00EZ100B_XK01 | 25151 | 发电机保护停机 2# |  | digital
N1DCS.10CHA00EZ100C_XK01 | 25152 | 发电机保护停机 3# |  | digital
N1DCS.10DROP41GW001_XM09 | 25153 | 机柜空开正常 |  | digital
N1DCS.10DROP41GW001_XM10 | 25154 | 机柜电源正常 |  | digital
N1DCS.10HYY01EY001_XK96 | 25155 | Ovation Control Builder |  | digital
N1DCS.10HYY01EY001_XV01 | 25156 | Ovation Control Builder |  | digital
N1DCS.10HYY01EY001A_XV10 | 25157 | 锅炉停机1 |  | digital
N1DCS.10HYY01EY001B_XV10 | 25158 | 锅炉停机2 |  | digital
N1DCS.10HYY01EY001C_XV10 | 25159 | 锅炉停机3 |  | digital
N1DCS.10LBA20EZ007_XV01 | 25160 | Ovation Control Builder |  | digital
N1DCS.10LBB50EZ007_XV01 | 25161 | Ovation Control Builder |  | digital
N1DCS.10LBD20AA001_XG04 | 25162 | 高压抽汽快关调节阀控制电源故障 |  | digital
N1DCS.10LBD40AA001_XG04 | 25163 | 中压抽汽快关调节阀控制电源故障 |  | digital
N1DCS.10LBS45AA001_XB01 | 25164 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_XB02 | 25165 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_XG05A | 25166 | 热再抽汽调阀关闭电磁阀得电指令 |  | digital
N1DCS.10LBS45AA001_XG05B | 25167 | 热再抽汽调阀关闭电磁阀得电指令 |  | digital
N1DCS.10LBS46AA001_XB01 | 25168 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_XB02 | 25169 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_XG05A | 25170 | 冷再抽汽调阀关闭电磁阀得电指令 |  | digital
N1DCS.10LBS46AA001_XG05B | 25171 | 冷再抽汽调阀关闭电磁阀得电指令 |  | digital
N1DCS.10MAA11AA011 | 25172 | 主汽门开启电磁阀 |  | digital
N1DCS.10MAA11AA013_XB01 | 25173 | Ovation Control Builder |  | digital
N1DCS.10MAA11AA013_XB02 | 25174 | Ovation Control Builder |  | digital
N1DCS.10MAA11AA013_ZB21A | 25175 | 主汽门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAA11AA013_ZB21AP | 25176 | 主汽门油动机关闭电磁阀#1监视（ |  | digital
N1DCS.10MAA11AA013_ZB21B | 25177 | 主汽门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAA11AA014_XB01 | 25178 | Ovation Control Builder |  | digital
N1DCS.10MAA11AA014_XB02 | 25179 | Ovation Control Builder |  | digital
N1DCS.10MAA11AA014_ZB21A | 25180 | 主汽门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAA11AA014_ZB21AP | 25181 | 主汽门油动机关闭电磁阀#2监视（ |  | digital
N1DCS.10MAA11AA014_ZB21B | 25182 | 主汽门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAA12AA013_XB01 | 25183 | Ovation Control Builder |  | digital
N1DCS.10MAA12AA013_XB02 | 25184 | Ovation Control Builder |  | digital
N1DCS.10MAA12AA013_ZB21A | 25185 | 高压调门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAA12AA013_ZB21AP | 25186 | 高压调门油动机关闭电磁阀#1监视 |  | digital
N1DCS.10MAA12AA013_ZB21B | 25187 | 高压调门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAA12AA014_XB01 | 25188 | Ovation Control Builder |  | digital
N1DCS.10MAA12AA014_XB02 | 25189 | Ovation Control Builder |  | digital
N1DCS.10MAA12AA014_ZB21A | 25190 | 高压调门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAA12AA014_ZB21AP | 25191 | 高压调门油动机关闭电磁阀#2监视 |  | digital
N1DCS.10MAA12AA014_ZB21B | 25192 | 高压调门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAA22SGFD1 | 25193 | 快关高调阀 |  | digital
N1DCS.10MAA50CT151A_XM20 | 25194 | 高压缸上中壁温A坏点 |  | digital
N1DCS.10MAA50CT152A_XM20 | 25195 | 高压缸下中壁温A坏点 |  | digital
N1DCS.10MAA50CT621A_XH01 | 25196 | #1高压排汽蒸汽温度>412℃ |  | digital
N1DCS.10MAA50CT621A_XH03 | 25197 | #1高压排汽蒸汽温度>384℃ |  | digital
N1DCS.10MAA50CT621A_XH52 | 25198 | Ovation Control Builder |  | digital
N1DCS.10MAA50CT621A_XH54 | 25199 | Ovation Control Builder |  | digital
N1DCS.10MAA50CT621A_XM20 | 25200 | #1高压排汽蒸汽温度坏点 |  | digital
N1DCS.10MAA50CT622A_XH01 | 25201 | #2高压排汽蒸汽温度>412℃ |  | digital
N1DCS.10MAA50CT622A_XH03 | 25202 | #2高压排汽蒸汽温度>384℃ |  | digital
N1DCS.10MAA50CT622A_XH52 | 25203 | Ovation Control Builder |  | digital
N1DCS.10MAA50CT622A_XH54 | 25204 | Ovation Control Builder |  | digital
N1DCS.10MAA50CT622A_XM20 | 25205 | #2高压排汽蒸汽温度坏点 |  | digital
N1DCS.10MAA50CT623A_XH01 | 25206 | #3高压排汽蒸汽温度>412℃ |  | digital
N1DCS.10MAA50CT623A_XH03 | 25207 | #3高压排汽蒸汽温度>384℃ |  | digital
N1DCS.10MAA50CT623A_XH52 | 25208 | Ovation Control Builder |  | digital
N1DCS.10MAA50CT623A_XH54 | 25209 | Ovation Control Builder |  | digital
N1DCS.10MAA50CT623A_XM20 | 25210 | #3高压排汽蒸汽温度坏点 |  | digital
N1DCS.10MAA50EZ111_XV01 | 25211 | Ovation Control Builder |  | digital
N1DCS.10MAA50EZ251_XK93 | 25212 | ＜4HZ时/中压外缸上下温差＞55K |  | digital
N1DCS.10MAA50EZ251_XK94 | 25213 | 中压外缸上下温差＞30K |  | digital
N1DCS.10MAA50EZ251_XK95 | 25214 | 并网120s后中压外缸上下温差>45K |  | digital
N1DCS.10MAA50EZ251_XK96 | 25215 | 高压缸或中压缸上下缸温差保护 |  | digital
N1DCS.10MAA50EZ251_XV01 | 25216 | Ovation Control Builder |  | digital
N1DCS.10MAA50EZ621_XK93 | 25217 | 高排温度测量存在故障 |  | digital
N1DCS.10MAA50EZ621_XK94 | 25218 | 高排温度大于计算报警值 |  | digital
N1DCS.10MAA50EZ621_XK96 | 25219 | 高排温度保护 |  | digital
N1DCS.10MAA50EZ621_XM70 | 25220 | 高压排汽蒸汽温度测点全故障 |  | digital
N1DCS.10MAA50EZ621_XV01 | 25221 | Ovation Control Builder |  | digital
N1DCS.10MAA50EZ621E_XK93 | 25222 | Ovation Control Builder |  | digital
N1DCS.10MAA50EZ621E_XK94 | 25223 | 高排温度＞384℃ |  | digital
N1DCS.10MAA50EZ621E_XK96 | 25224 | 高排温度保护（抽汽模式） |  | digital
N1DCS.10MAA50EZ621E_XM70 | 25225 | Ovation Control Builder |  | digital
N1DCS.10MAA50EZ621E_XS96 | 25226 | 高排温度高高报警 |  | digital
N1DCS.10MAA50FT251_XH02 | 25227 | 高压或中压缸上下壁温差>55℃ |  | digital
N1DCS.10MAA50FT251_XH04 | 25228 | 高压或中压缸上下壁温差>45℃ |  | digital
N1DCS.10MAA50FT251_XH05 | 25229 | 高压或中压缸上下壁温差>30℃ |  | digital
N1DCS.10MAA50FT621_XH01 | 25230 | 高压排汽蒸汽温度>450℃ |  | digital
N1DCS.10MAA50FT621A_DL12 | 25231 | 高压排汽蒸汽温度1/2偏差大 |  | digital
N1DCS.10MAA50FT621A_DL13 | 25232 | 高压排汽蒸汽温度1/3偏差大 |  | digital
N1DCS.10MAA50FT621A_DL23 | 25233 | 高压排汽蒸汽温度2/3偏差大 |  | digital
N1DCS.10MAA50FT621A_XM97 | 25234 | #1高压排汽蒸汽温度测点故障 |  | digital
N1DCS.10MAA50FT621A_XM98 | 25235 | #2高压排汽蒸汽温度测点故障 |  | digital
N1DCS.10MAA50FT621A_XM99 | 25236 | #3高压排汽蒸汽温度测点故障 |  | digital
N1DCS.10MAB11AA011 | 25237 | 中主门开启电磁阀 |  | digital
N1DCS.10MAB11AA013_XB01 | 25238 | Ovation Control Builder |  | digital
N1DCS.10MAB11AA013_XB02 | 25239 | Ovation Control Builder |  | digital
N1DCS.10MAB11AA013_ZB21A | 25240 | 再热主汽门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAB11AA013_ZB21AP | 25241 | 再热主汽门油动机关闭电磁阀#1监 |  | digital
N1DCS.10MAB11AA013_ZB21B | 25242 | 再热主汽门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAB11AA014_XB01 | 25243 | Ovation Control Builder |  | digital
N1DCS.10MAB11AA014_XB02 | 25244 | Ovation Control Builder |  | digital
N1DCS.10MAB11AA014_ZB21A | 25245 | 再热主汽门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAB11AA014_ZB21AP | 25246 | 再热主汽门油动机关闭电磁阀#2监 |  | digital
N1DCS.10MAB11AA014_ZB21B | 25247 | 再热主汽门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAB12AA013_XB01 | 25248 | Ovation Control Builder |  | digital
N1DCS.10MAB12AA013_XB02 | 25249 | Ovation Control Builder |  | digital
N1DCS.10MAB12AA013_ZB21A | 25250 | 中压调门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAB12AA013_ZB21AP | 25251 | 中压调门油动机关闭电磁阀#1监视 |  | digital
N1DCS.10MAB12AA013_ZB21B | 25252 | 中压调门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAB12AA014_XB01 | 25253 | Ovation Control Builder |  | digital
N1DCS.10MAB12AA014_XB02 | 25254 | Ovation Control Builder |  | digital
N1DCS.10MAB12AA014_ZB21A | 25255 | 中压调门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAB12AA014_ZB21AP | 25256 | 中压调门油动机关闭电磁阀#2监视 |  | digital
N1DCS.10MAB12AA014_ZB21B | 25257 | 中压调门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAB22SGAF1 | 25258 | 快关中调阀1# |  | digital
N1DCS.10MAB50CT151A_XM20 | 25259 | Ovation Control Builder |  | digital
N1DCS.10MAB50CT152A_XM20 | 25260 | Ovation Control Builder |  | digital
N1DCS.10MAB50FT621_XH01 | 25261 | 中排温度＞305℃ |  | digital
N1DCS.10MAB50FT621_XH03 | 25262 | 中排温度＞323℃ |  | digital
N1DCS.10MAB50FT621_XK20 | 25263 | Ovation Control Builder |  | digital
N1DCS.10MAC10CT671_XH01 | 25264 | #1低压排汽支架温度>90℃ |  | digital
N1DCS.10MAC10CT671_XH03 | 25265 | #1低压排汽支架温度>70℃ |  | digital
N1DCS.10MAC10CT671_XM20 | 25266 | #1低压排汽支架温度坏点 |  | digital
N1DCS.10MAC10CT672_XH01 | 25267 | #2低压排汽支架温度>90℃ |  | digital
N1DCS.10MAC10CT672_XH03 | 25268 | #2低压排汽支架温度>70℃ |  | digital
N1DCS.10MAC10CT672_XM20 | 25269 | #2低压排汽支架温度坏点 |  | digital
N1DCS.10MAC10CT673_XH01 | 25270 | #3低压排汽支架温度>90℃ |  | digital
N1DCS.10MAC10CT673_XH03 | 25271 | #3低压排汽支架温度>70℃ |  | digital
N1DCS.10MAC10CT673_XM20 | 25272 | #3低压排汽支架温度坏点 |  | digital
N1DCS.10MAC10EZ671_XK93 | 25273 | 低排温度测量存在故障 |  | digital
N1DCS.10MAC10EZ671_XK94 | 25274 | 低排温度＞70℃ |  | digital
N1DCS.10MAC10EZ671_XK96 | 25275 | 低排温度保护 |  | digital
N1DCS.10MAC10EZ671_XV01 | 25276 | Ovation Control Builder |  | digital
N1DCS.10MAC10FT611A_XH01 | 25277 | 低压缸末级叶片温度＞120℃ |  | digital
N1DCS.10MAC10FT611A_XH03 | 25278 | 低压缸末级叶片温度＞180℃ |  | digital
N1DCS.10MAC10FT611A_XH05 | 25279 | 低压缸末级叶片温度＞230℃ |  | digital
N1DCS.10MAC10FT611A_XH52 | 25280 | 低压缸末级叶片温度<100℃ |  | digital
N1DCS.10MAC10FT671_DL12 | 25281 | Ovation Control Builder |  | digital
N1DCS.10MAC10FT671_DL13 | 25282 | Ovation Control Builder |  | digital
N1DCS.10MAC10FT671_DL23 | 25283 | Ovation Control Builder |  | digital
N1DCS.10MAC10FT671_XH01 | 25284 | Ovation Control Builder |  | digital
N1DCS.10MAC10FT671_XH52 | 25285 | Ovation Control Builder |  | digital
N1DCS.10MAC10FT671A_XM97 | 25286 | Ovation Control Builder |  | digital
N1DCS.10MAC10FT671A_XM98 | 25287 | Ovation Control Builder |  | digital
N1DCS.10MAC10FT671A_XM99 | 25288 | Ovation Control Builder |  | digital
N1DCS.10MAC45AA001_XB01 | 25289 | Ovation Control Builder |  | digital
N1DCS.10MAC45AA001_XB02 | 25290 | Ovation Control Builder |  | digital
N1DCS.10MAC45AA001_XG04 | 25291 | 低压补汽主门油动机控制电源故障 |  | digital
N1DCS.10MAC45AA001_XG05A | 25292 | 低压补汽主门油动机关闭电磁阀输 |  | digital
N1DCS.10MAC45AA001_XG05B | 25293 | 低压补汽主门油动机关闭电磁阀输 |  | digital
N1DCS.10MAC45AA001_XG06 | 25294 | 低压主汽门活动性试验 |  | digital
N1DCS.10MAC46AA001_XB01 | 25295 | Ovation Control Builder |  | digital
N1DCS.10MAC46AA001_XB02 | 25296 | Ovation Control Builder |  | digital
N1DCS.10MAC46AA001_XG04 | 25297 | 低压补汽调阀油动机控制电源故障 |  | digital
N1DCS.10MAC46AA001_XG05A | 25298 | 低压补汽调门油动机关闭电磁阀输 |  | digital
N1DCS.10MAC46AA001_XG05B | 25299 | 低压补汽调门油动机关闭电磁阀输 |  | digital
N1DCS.10MAD00EZ111_XK96 | 25300 | 轴承温度保护 |  | digital
N1DCS.10MAD00EZ111_XV01 | 25301 | Ovation Control Builder |  | digital
N1DCS.10MAD01EZ111_XK96 | 25302 | 轴承振动保护 |  | digital
N1DCS.10MAD01EZ111_XV01 | 25303 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114A_XH01 | 25304 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114A_XH03 | 25305 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114A_XM20 | 25306 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114B_XH01 | 25307 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114B_XH03 | 25308 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114B_XM20 | 25309 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114C_XH01 | 25310 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114C_XH03 | 25311 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT114C_XM20 | 25312 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118A_XH01 | 25313 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118A_XH03 | 25314 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118A_XM20 | 25315 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118B_XH01 | 25316 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118B_XH03 | 25317 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118B_XM20 | 25318 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118C_XH01 | 25319 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118C_XH03 | 25320 | Ovation Control Builder |  | digital
N1DCS.10MAD11CT118C_XM20 | 25321 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY021_XM71 | 25322 | #1径向轴承壳振1正常 |  | digital
N1DCS.10MAD11CY022_XM71 | 25323 | #1径向轴承壳振2正常 |  | digital
N1DCS.10MAD11CY121_MAX1 | 25324 | #1径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MAD11CY121_MAX2 | 25325 | #1径向轴承壳振1>11.8mm/s |  | digital
N1DCS.10MAD11CY121_XH01 | 25326 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY121_XH03 | 25327 | #1径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MAD11CY121_XM71 | 25328 | #1径向轴承壳振1正常 |  | digital
N1DCS.10MAD11CY121_XM72 | 25329 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY121_XV20 | 25330 | #1轴瓦振动通道故障1 |  | digital
N1DCS.10MAD11CY122_MAX1 | 25331 | #1径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MAD11CY122_MAX2 | 25332 | #1径向轴承壳振2>11.8mm/s |  | digital
N1DCS.10MAD11CY122_XH01 | 25333 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY122_XH03 | 25334 | #1径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MAD11CY122_XM71 | 25335 | #1径向轴承壳振2正常 |  | digital
N1DCS.10MAD11CY122_XM72 | 25336 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY122_XV20 | 25337 | #1轴瓦振动通道故障2 |  | digital
N1DCS.10MAD11EZ121_XK93 | 25338 | #1轴承座振动存在故障 |  | digital
N1DCS.10MAD11EZ121_XK94 | 25339 | #1轴承座振动＞9.3mm/s |  | digital
N1DCS.10MAD11EZ121_XK96 | 25340 | #1径向轴承壳振大 |  | digital
N1DCS.10MAD11EZ214_XK93 | 25341 | #1轴承径向轴瓦金属测点1故障 |  | digital
N1DCS.10MAD11EZ214_XK94 | 25342 | #1轴承径向轴瓦金属温度1＞90℃ |  | digital
N1DCS.10MAD11EZ214_XK96 | 25343 | Ovation Control Builder |  | digital
N1DCS.10MAD11EZ218_XK93 | 25344 | #1轴承径向轴瓦金属测点2故障 |  | digital
N1DCS.10MAD11EZ218_XK94 | 25345 | #1轴承径向轴瓦金属温度2＞90℃ |  | digital
N1DCS.10MAD11EZ218_XK96 | 25346 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT114A_XM97 | 25347 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT114B_XM98 | 25348 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT114C_XM99 | 25349 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT118A_XM97 | 25350 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT118B_XM98 | 25351 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT118C_XM99 | 25352 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT214A_DL12 | 25353 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT214A_DL13 | 25354 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT214A_DL23 | 25355 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT218A_DL12 | 25356 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT218A_DL13 | 25357 | Ovation Control Builder |  | digital
N1DCS.10MAD11FT218A_DL23 | 25358 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111A_XH01 | 25359 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111A_XH03 | 25360 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111A_XM20 | 25361 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111B_XH01 | 25362 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111B_XH03 | 25363 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111B_XM20 | 25364 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111C_XH01 | 25365 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111C_XH03 | 25366 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT111C_XM20 | 25367 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112A_XH01 | 25368 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112A_XH03 | 25369 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112A_XM20 | 25370 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112B_XH01 | 25371 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112B_XH03 | 25372 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112B_XM20 | 25373 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112C_XH01 | 25374 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112C_XH03 | 25375 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT112C_XM20 | 25376 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113A_XH01 | 25377 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113A_XH03 | 25378 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113A_XM20 | 25379 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113B_XH01 | 25380 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113B_XH03 | 25381 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113B_XM20 | 25382 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113C_XH01 | 25383 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113C_XH03 | 25384 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT113C_XM20 | 25385 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114A_XH01 | 25386 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114A_XH03 | 25387 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114A_XM20 | 25388 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114B_XH01 | 25389 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114B_XH03 | 25390 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114B_XM20 | 25391 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114C_XH01 | 25392 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114C_XH03 | 25393 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT114C_XM20 | 25394 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131A_XH01 | 25395 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131A_XH03 | 25396 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131A_XM20 | 25397 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131B_XH01 | 25398 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131B_XH03 | 25399 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131B_XM20 | 25400 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131C_XH01 | 25401 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131C_XH03 | 25402 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT131C_XM20 | 25403 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132A_XH01 | 25404 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132A_XH03 | 25405 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132A_XM20 | 25406 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132B_XH01 | 25407 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132B_XH03 | 25408 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132B_XM20 | 25409 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132C_XH01 | 25410 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132C_XH03 | 25411 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT132C_XM20 | 25412 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133A_XH01 | 25413 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133A_XH03 | 25414 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133A_XM20 | 25415 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133B_XH01 | 25416 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133B_XH03 | 25417 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133B_XM20 | 25418 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133C_XH01 | 25419 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133C_XH03 | 25420 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT133C_XM20 | 25421 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134A_XH01 | 25422 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134A_XH03 | 25423 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134A_XM20 | 25424 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134B_XH01 | 25425 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134B_XH03 | 25426 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134B_XM20 | 25427 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134C_XH01 | 25428 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134C_XH03 | 25429 | Ovation Control Builder |  | digital
N1DCS.10MAD12CT134C_XM20 | 25430 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY011_XM71 | 25431 | 轴位移1#正常 |  | digital
N1DCS.10MAD12CY012_XM71 | 25432 | 轴位移2#正常 |  | digital
N1DCS.10MAD12CY013_XM71 | 25433 | 轴向位移3#OK |  | digital
N1DCS.10MAD12CY021_XM71 | 25434 | #2径向轴承壳振1正常 |  | digital
N1DCS.10MAD12CY022_XM71 | 25435 | #2径向轴承壳振2正常 |  | digital
N1DCS.10MAD12CY111_XH01 | 25436 | #1轴向位移>1mm |  | digital
N1DCS.10MAD12CY111_XH03 | 25437 | #1轴向位移>0.5mm |  | digital
N1DCS.10MAD12CY111_XH52 | 25438 | #1轴向位移<-1mm |  | digital
N1DCS.10MAD12CY111_XH54 | 25439 | #1轴向位移<-0.5mm |  | digital
N1DCS.10MAD12CY111_XM20 | 25440 | #1轴向位移坏点 |  | digital
N1DCS.10MAD12CY111_XM71 | 25441 | 轴位移1#正常 |  | digital
N1DCS.10MAD12CY111_XM72 | 25442 | 轴位移通道故障1 |  | digital
N1DCS.10MAD12CY112_XH01 | 25443 | #2轴向位移>1mm |  | digital
N1DCS.10MAD12CY112_XH03 | 25444 | #2轴向位移>0.5mm |  | digital
N1DCS.10MAD12CY112_XH52 | 25445 | #2轴向位移<-1mm |  | digital
N1DCS.10MAD12CY112_XH54 | 25446 | #2轴向位移<-0.5mm |  | digital
N1DCS.10MAD12CY112_XM20 | 25447 | #2轴向位移坏点 |  | digital
N1DCS.10MAD12CY112_XM71 | 25448 | 轴位移2#正常 |  | digital
N1DCS.10MAD12CY112_XM72 | 25449 | 轴位移通道故障2 |  | digital
N1DCS.10MAD12CY113_XH01 | 25450 | #3轴向位移>1mm |  | digital
N1DCS.10MAD12CY113_XH03 | 25451 | #3轴向位移>0.5mm |  | digital
N1DCS.10MAD12CY113_XH52 | 25452 | #3轴向位移<-1mm |  | digital
N1DCS.10MAD12CY113_XH54 | 25453 | #3轴向位移<-0.5mm |  | digital
N1DCS.10MAD12CY113_XM20 | 25454 | #3轴向位移坏点 |  | digital
N1DCS.10MAD12CY113_XM71 | 25455 | 轴向位移3#OK |  | digital
N1DCS.10MAD12CY113_XM72 | 25456 | 轴位移通道故障3 |  | digital
N1DCS.10MAD12CY121_MAX1 | 25457 | #2径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MAD12CY121_MAX2 | 25458 | #2径向轴承壳振1>11.8mm/s |  | digital
N1DCS.10MAD12CY121_XH01 | 25459 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY121_XH03 | 25460 | #2径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MAD12CY121_XM71 | 25461 | #2径向轴承壳振1正常 |  | digital
N1DCS.10MAD12CY121_XM72 | 25462 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY121_XV20 | 25463 | #2轴瓦振动通道故障1 |  | digital
N1DCS.10MAD12CY122_MAX1 | 25464 | #2径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MAD12CY122_MAX2 | 25465 | #2径向轴承壳振2>11.8mm/s |  | digital
N1DCS.10MAD12CY122_XH01 | 25466 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY122_XH03 | 25467 | #2径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MAD12CY122_XM71 | 25468 | #2径向轴承壳振2正常 |  | digital
N1DCS.10MAD12CY122_XM72 | 25469 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY122_XV20 | 25470 | #2轴瓦振动通道故障2 |  | digital
N1DCS.10MAD12EZ111_XK93 | 25471 | 轴向位移测量存在故障 |  | digital
N1DCS.10MAD12EZ111_XK94 | 25472 | 轴向位移＜-0.5mm |  | digital
N1DCS.10MAD12EZ111_XK95 | 25473 | 轴向位移＞0.5mm |  | digital
N1DCS.10MAD12EZ111_XK96 | 25474 | 高压缸轴向位移保护 |  | digital
N1DCS.10MAD12EZ111_XV01 | 25475 | Ovation Control Builder |  | digital
N1DCS.10MAD12EZ121_XK93 | 25476 | #2轴承座振动存在故障 |  | digital
N1DCS.10MAD12EZ121_XK94 | 25477 | #2轴承座振动＞9.3mm/s |  | digital
N1DCS.10MAD12EZ121_XK96 | 25478 | #2径向轴承壳振大 |  | digital
N1DCS.10MAD12EZ211_XK93 | 25479 | #2轴承径向轴瓦金属测点1故障 |  | digital
N1DCS.10MAD12EZ211_XK94 | 25480 | #2轴承径向轴瓦金属温度1＞90℃ |  | digital
N1DCS.10MAD12EZ211_XK96 | 25481 | Ovation Control Builder |  | digital
N1DCS.10MAD12EZ212_XK93 | 25482 | #2轴承径向轴瓦金属测点2故障 |  | digital
N1DCS.10MAD12EZ212_XK94 | 25483 | #2轴承径向轴瓦金属温度2＞90℃ |  | digital
N1DCS.10MAD12EZ212_XK96 | 25484 | Ovation Control Builder |  | digital
N1DCS.10MAD12EZ213_XK93 | 25485 | #2轴承径向轴瓦金属测点3故障 |  | digital
N1DCS.10MAD12EZ213_XK94 | 25486 | #2轴承径向轴瓦金属温度3＞90℃ |  | digital
N1DCS.10MAD12EZ213_XK96 | 25487 | Ovation Control Builder |  | digital
N1DCS.10MAD12EZ214_XK93 | 25488 | #2轴承径向轴瓦金属测点4故障 |  | digital
N1DCS.10MAD12EZ214_XK94 | 25489 | #2轴承径向轴瓦金属温度4＞90℃ |  | digital
N1DCS.10MAD12EZ214_XK96 | 25490 | Ovation Control Builder |  | digital
N1DCS.10MAD12EZ231_XK93 | 25491 | #2轴承推力轴瓦金属测点1故障 |  | digital
N1DCS.10MAD12EZ231_XK94 | 25492 | #2轴承推力轴瓦金属温度1＞90℃ |  | digital
N1DCS.10MAD12EZ231_XK96 | 25493 | Ovation Control Builder |  | digital
N1DCS.10MAD12EZ232_XK93 | 25494 | #2轴承推力轴瓦金属温度2故障 |  | digital
N1DCS.10MAD12EZ232_XK94 | 25495 | #2轴承推力轴瓦金属温度2＞90℃ |  | digital
N1DCS.10MAD12EZ232_XK96 | 25496 | Ovation Control Builder |  | digital
N1DCS.10MAD12EZ233_XK93 | 25497 | #2轴承推力轴瓦金属温度3故障 |  | digital
N1DCS.10MAD12EZ233_XK94 | 25498 | #2轴承推力轴瓦金属温度3＞90℃ |  | digital
N1DCS.10MAD12EZ233_XK96 | 25499 | Ovation Control Builder |  | digital
N1DCS.10MAD12EZ234_XK93 | 25500 | #2轴承推力轴瓦金属温度4故障 |  | digital
N1DCS.10MAD12EZ234_XK94 | 25501 | #2轴承推力轴瓦金属温度4＞90℃ |  | digital
N1DCS.10MAD12EZ234_XK96 | 25502 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT111A_DL12 | 25503 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT111A_DL13 | 25504 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT111A_DL23 | 25505 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT111A_XM97 | 25506 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT111B_XM98 | 25507 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT111C_XM99 | 25508 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT112A_DL12 | 25509 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT112A_DL13 | 25510 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT112A_DL23 | 25511 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT112A_XM97 | 25512 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT112B_XM98 | 25513 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT112C_XM99 | 25514 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT113A_DL12 | 25515 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT113A_DL13 | 25516 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT113A_DL23 | 25517 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT113A_XM97 | 25518 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT113B_XM98 | 25519 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT113C_XM99 | 25520 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT114A_DL12 | 25521 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT114A_DL13 | 25522 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT114A_DL23 | 25523 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT114A_XM97 | 25524 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT114B_XM98 | 25525 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT114C_XM99 | 25526 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT131A_DL12 | 25527 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT131A_DL13 | 25528 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT131A_DL23 | 25529 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT131A_XM97 | 25530 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT131B_XM98 | 25531 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT131C_XM99 | 25532 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT132A_DL12 | 25533 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT132A_DL13 | 25534 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT132A_DL23 | 25535 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT132A_XM97 | 25536 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT132B_XM98 | 25537 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT132C_XM99 | 25538 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT133A_DL12 | 25539 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT133A_DL13 | 25540 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT133A_DL23 | 25541 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT133A_XM97 | 25542 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT133B_XM98 | 25543 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT133C_XM99 | 25544 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT134A_DL12 | 25545 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT134A_DL13 | 25546 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT134A_DL23 | 25547 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT134A_XM97 | 25548 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT134B_XM98 | 25549 | Ovation Control Builder |  | digital
N1DCS.10MAD12FT134C_XM99 | 25550 | Ovation Control Builder |  | digital
N1DCS.10MAD12FY111A_DL12 | 25551 | Ovation Control Builder |  | digital
N1DCS.10MAD12FY111A_DL13 | 25552 | Ovation Control Builder |  | digital
N1DCS.10MAD12FY111A_DL23 | 25553 | Ovation Control Builder |  | digital
N1DCS.10MAD12FY111A_XM97 | 25554 | Ovation Control Builder |  | digital
N1DCS.10MAD12FY111A_XM98 | 25555 | Ovation Control Builder |  | digital
N1DCS.10MAD12FY111A_XM99 | 25556 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111A_XH01 | 25557 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111A_XH03 | 25558 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111A_XM20 | 25559 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111B_XH01 | 25560 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111B_XH03 | 25561 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111B_XM20 | 25562 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111C_XH01 | 25563 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111C_XH03 | 25564 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT111C_XM20 | 25565 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112A_XH01 | 25566 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112A_XH03 | 25567 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112A_XM20 | 25568 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112B_XH01 | 25569 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112B_XH03 | 25570 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112B_XM20 | 25571 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112C_XH01 | 25572 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112C_XH03 | 25573 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT112C_XM20 | 25574 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113A_XH01 | 25575 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113A_XH03 | 25576 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113A_XM20 | 25577 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113B_XH01 | 25578 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113B_XH03 | 25579 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113B_XM20 | 25580 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113C_XH01 | 25581 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113C_XH03 | 25582 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT113C_XM20 | 25583 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114A_XH01 | 25584 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114A_XH03 | 25585 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114A_XM20 | 25586 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114B_XH01 | 25587 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114B_XH03 | 25588 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114B_XM20 | 25589 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114C_XH01 | 25590 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114C_XH03 | 25591 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT114C_XM20 | 25592 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115A_XH01 | 25593 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115A_XH03 | 25594 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115A_XM20 | 25595 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115B_XH01 | 25596 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115B_XH03 | 25597 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115B_XM20 | 25598 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115C_XH01 | 25599 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115C_XH03 | 25600 | Ovation Control Builder |  | digital
N1DCS.10MAD13CT115C_XM20 | 25601 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY021_XM71 | 25602 | #3径向轴承壳振1正常 |  | digital
N1DCS.10MAD13CY022_XM71 | 25603 | #3径向轴承壳振2正常 |  | digital
N1DCS.10MAD13CY121_MAX1 | 25604 | #3径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MAD13CY121_MAX2 | 25605 | #3径向轴承壳振1>11.8mm/s |  | digital
N1DCS.10MAD13CY121_XH01 | 25606 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY121_XH03 | 25607 | #3径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MAD13CY121_XM71 | 25608 | #3径向轴承壳振1正常 |  | digital
N1DCS.10MAD13CY121_XM72 | 25609 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY121_XV20 | 25610 | #3轴瓦振动通道故障1 |  | digital
N1DCS.10MAD13CY122_MAX1 | 25611 | #3径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MAD13CY122_MAX2 | 25612 | #3径向轴承壳振2>11.8mm/s |  | digital
N1DCS.10MAD13CY122_XH01 | 25613 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY122_XH03 | 25614 | #3径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MAD13CY122_XM71 | 25615 | #3径向轴承壳振2正常 |  | digital
N1DCS.10MAD13CY122_XM72 | 25616 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY122_XV20 | 25617 | #3轴瓦振动通道故障2 |  | digital
N1DCS.10MAD13EZ121_XK93 | 25618 | #3轴承座振动存在故障 |  | digital
N1DCS.10MAD13EZ121_XK94 | 25619 | #3轴承座振动＞9.3mm/s |  | digital
N1DCS.10MAD13EZ121_XK96 | 25620 | #3径向轴承壳振大 |  | digital
N1DCS.10MAD13EZ211_XK93 | 25621 | #3轴承径向轴瓦金属测点1故障 |  | digital
N1DCS.10MAD13EZ211_XK94 | 25622 | #3轴承径向轴瓦金属温度1＞90℃ |  | digital
N1DCS.10MAD13EZ211_XK96 | 25623 | Ovation Control Builder |  | digital
N1DCS.10MAD13EZ212_XK93 | 25624 | #3轴承径向轴瓦金属测点2故障 |  | digital
N1DCS.10MAD13EZ212_XK94 | 25625 | #3轴承径向轴瓦金属温度2＞90℃ |  | digital
N1DCS.10MAD13EZ212_XK96 | 25626 | Ovation Control Builder |  | digital
N1DCS.10MAD13EZ213_XK93 | 25627 | #3轴承径向轴瓦金属测点3故障 |  | digital
N1DCS.10MAD13EZ213_XK94 | 25628 | #3轴承径向轴瓦金属温度3＞90℃ |  | digital
N1DCS.10MAD13EZ213_XK96 | 25629 | Ovation Control Builder |  | digital
N1DCS.10MAD13EZ214_XK93 | 25630 | #3轴承径向轴瓦金属测点4故障 |  | digital
N1DCS.10MAD13EZ214_XK94 | 25631 | #3轴承径向轴瓦金属温度4＞90℃ |  | digital
N1DCS.10MAD13EZ214_XK96 | 25632 | Ovation Control Builder |  | digital
N1DCS.10MAD13EZ215_XK93 | 25633 | #3轴承径向轴瓦金属测点5故障 |  | digital
N1DCS.10MAD13EZ215_XK94 | 25634 | #3轴承径向轴瓦金属温度5＞90℃ |  | digital
N1DCS.10MAD13EZ215_XK96 | 25635 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT111A_DL12 | 25636 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT111A_DL13 | 25637 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT111A_DL23 | 25638 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT111A_XM97 | 25639 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT111B_XM98 | 25640 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT111C_XM99 | 25641 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT112A_DL12 | 25642 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT112A_DL13 | 25643 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT112A_DL23 | 25644 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT112A_XM97 | 25645 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT112B_XM98 | 25646 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT112C_XM99 | 25647 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT113A_DL12 | 25648 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT113A_DL13 | 25649 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT113A_DL23 | 25650 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT113A_XM97 | 25651 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT113B_XM98 | 25652 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT113C_XM99 | 25653 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT114A_DL12 | 25654 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT114A_DL13 | 25655 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT114A_DL23 | 25656 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT114A_XM97 | 25657 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT114B_XM98 | 25658 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT114C_XM99 | 25659 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT115A_DL12 | 25660 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT115A_DL13 | 25661 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT115A_DL23 | 25662 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT115A_XM97 | 25663 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT115B_XM98 | 25664 | Ovation Control Builder |  | digital
N1DCS.10MAD13FT115C_XM99 | 25665 | Ovation Control Builder |  | digital
N1DCS.10MAG01CP101_XH01 | 25666 | #1凝汽器真空>30kPa |  | digital
N1DCS.10MAG01CP101_XH03 | 25667 | #1凝汽器真空>20kPa |  | digital
N1DCS.10MAG01CP101_XH07 | 25668 | Ovation Control Builder |  | digital
N1DCS.10MAG01CP101_XM20 | 25669 | #1凝汽器真空坏点 |  | digital
N1DCS.10MAG01CP102_XH01 | 25670 | #2凝汽器真空>30kPa |  | digital
N1DCS.10MAG01CP102_XH03 | 25671 | #2凝汽器真空>20kPa |  | digital
N1DCS.10MAG01CP102_XH07 | 25672 | Ovation Control Builder |  | digital
N1DCS.10MAG01CP102_XM20 | 25673 | #2凝汽器真空坏点 |  | digital
N1DCS.10MAG01CP103_XH01 | 25674 | #3凝汽器真空>30kPa |  | digital
N1DCS.10MAG01CP103_XH03 | 25675 | #3凝汽器真空>20kPa |  | digital
N1DCS.10MAG01CP103_XH07 | 25676 | Ovation Control Builder |  | digital
N1DCS.10MAG01CP103_XM20 | 25677 | #3凝汽器真空坏点 |  | digital
N1DCS.10MAG01EZ101_VRA | 25678 | Ovation Control Builder |  | digital
N1DCS.10MAG01EZ101_XK20 | 25679 | Ovation Control Builder |  | digital
N1DCS.10MAG01EZ101_XK93 | 25680 | 真空保护相关探头存在故障 |  | digital
N1DCS.10MAG01EZ101_XK94 | 25681 | 真空大于计算报警值 |  | digital
N1DCS.10MAG01EZ101_XK96 | 25682 | 凝汽器真空保护 |  | digital
N1DCS.10MAG01EZ101_XV01 | 25683 | Ovation Control Builder |  | digital
N1DCS.10MAG01FP101A_DL12 | 25684 | #1/#2凝汽器真空偏差大 |  | digital
N1DCS.10MAG01FP101A_DL13 | 25685 | #1/#3凝汽器真空偏差大 |  | digital
N1DCS.10MAG01FP101A_DL23 | 25686 | #2/#3凝汽器真空偏差大 |  | digital
N1DCS.10MAG01FP101A_XM97 | 25687 | #1凝汽器真空测点故障 |  | digital
N1DCS.10MAG01FP101A_XM98 | 25688 | #2凝汽器真空测点故障 |  | digital
N1DCS.10MAG01FP101A_XM99 | 25689 | #3凝汽器真空测点故障 |  | digital
N1DCS.10MAG10FP101_XH51 | 25690 | 凝汽器真空>80kPa |  | digital
N1DCS.10MAG10FP101_XH52 | 25691 | 凝汽器真空<20kPa |  | digital
N1DCS.10MAG10FP101_XH53 | 25692 | 凝汽器真空>7kPa |  | digital
N1DCS.10MAG10FP101_XH58 | 25693 | 凝汽器真空<13kPa |  | digital
N1DCS.10MAV10CL121_XH01 | 25694 | #1润滑油箱液位>1050mm |  | digital
N1DCS.10MAV10CL121_XH03 | 25695 | #1润滑油箱液位>1000mm |  | digital
N1DCS.10MAV10CL121_XH52 | 25696 | #1润滑油箱液位<850mm |  | digital
N1DCS.10MAV10CL121_XH54 | 25697 | #1润滑油箱液位<900mm |  | digital
N1DCS.10MAV10CL121_XM20 | 25698 | #1润滑油箱液位坏点 |  | digital
N1DCS.10MAV10CL122_XH01 | 25699 | #2润滑油箱液位>1050mm |  | digital
N1DCS.10MAV10CL122_XH03 | 25700 | #2润滑油箱液位>1000mm |  | digital
N1DCS.10MAV10CL122_XH52 | 25701 | #2润滑油箱液位<850mm |  | digital
N1DCS.10MAV10CL122_XH54 | 25702 | #2润滑油箱液位<900mm |  | digital
N1DCS.10MAV10CL122_XM20 | 25703 | Ovation Control Builder |  | digital
N1DCS.10MAV10CL123_XH01 | 25704 | #3润滑油箱液位>1050mm |  | digital
N1DCS.10MAV10CL123_XH03 | 25705 | #3润滑油箱液位>1000mm |  | digital
N1DCS.10MAV10CL123_XH52 | 25706 | #3润滑油箱液位<850mm |  | digital
N1DCS.10MAV10CL123_XH54 | 25707 | #3润滑油箱液位<900mm |  | digital
N1DCS.10MAV10CL123_XM20 | 25708 | Ovation Control Builder |  | digital
N1DCS.10MAV10EZ121_XK93 | 25709 | 润滑油液位测量存在故障 |  | digital
N1DCS.10MAV10EZ121_XK94 | 25710 | 润滑油液位＜900mm |  | digital
N1DCS.10MAV10EZ121_XK95 | 25711 | 润滑油液位＞1000mm |  | digital
N1DCS.10MAV10EZ121_XK96 | 25712 | 润滑油油箱液位保护 |  | digital
N1DCS.10MAV10EZ121_XV01 | 25713 | Ovation Control Builder |  | digital
N1DCS.10MAV10FL121A_DL12 | 25714 | Ovation Control Builder |  | digital
N1DCS.10MAV10FL121A_DL13 | 25715 | Ovation Control Builder |  | digital
N1DCS.10MAV10FL121A_DL23 | 25716 | Ovation Control Builder |  | digital
N1DCS.10MAV10FL121A_XM97 | 25717 | Ovation Control Builder |  | digital
N1DCS.10MAV10FL121A_XM98 | 25718 | Ovation Control Builder |  | digital
N1DCS.10MAV10FL121A_XM99 | 25719 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP116_XH52 | 25720 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP116_XH54 | 25721 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP116_XM20 | 25722 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP117_XH52 | 25723 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP117_XH54 | 25724 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP117_XM20 | 25725 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP118_XH52 | 25726 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP118_XH54 | 25727 | Ovation Control Builder |  | digital
N1DCS.10MAV42CP118_XM20 | 25728 | Ovation Control Builder |  | digital
N1DCS.10MAV42EZ116_XK93 | 25729 | 润滑油压力测量存在故障 |  | digital
N1DCS.10MAV42EZ116_XK94 | 25730 | 润滑油压力＜0.25MPa |  | digital
N1DCS.10MAV42EZ116_XK96 | 25731 | Ovation Control Builder |  | digital
N1DCS.10MAV42EZ116_XV01 | 25732 | Ovation Control Builder |  | digital
N1DCS.10MAV42FP116_XH01 | 25733 | Ovation Control Builder |  | digital
N1DCS.10MAV42FP116_XH03 | 25734 | Ovation Control Builder |  | digital
N1DCS.10MAV42FP116A_DL12 | 25735 | Ovation Control Builder |  | digital
N1DCS.10MAV42FP116A_DL13 | 25736 | Ovation Control Builder |  | digital
N1DCS.10MAV42FP116A_DL23 | 25737 | Ovation Control Builder |  | digital
N1DCS.10MAV42FP116A_XM97 | 25738 | Ovation Control Builder |  | digital
N1DCS.10MAV42FP116A_XM98 | 25739 | Ovation Control Builder |  | digital
N1DCS.10MAV42FP116A_XM99 | 25740 | Ovation Control Builder |  | digital
N1DCS.10MAX01CP101_XH52 | 25741 | 控制油泵出口压力1#<10.5MPa |  | digital
N1DCS.10MAX01CP101_XH54 | 25742 | 控制油泵出口压力1#<12MPa |  | digital
N1DCS.10MAX01CP101_XM20 | 25743 | 控制油泵出口压力1#坏点 |  | digital
N1DCS.10MAX01CP102_XH52 | 25744 | 控制油泵出口压力2#<10.5MPa |  | digital
N1DCS.10MAX01CP102_XH54 | 25745 | 控制油泵出口压力2#<12MPa |  | digital
N1DCS.10MAX01CP102_XM20 | 25746 | 控制油泵出口压力2#坏点 |  | digital
N1DCS.10MAX01CP103_XH52 | 25747 | 控制油泵出口压力3#<10.5MPa |  | digital
N1DCS.10MAX01CP103_XH54 | 25748 | 控制油泵出口压力3#<12MPa |  | digital
N1DCS.10MAX01CP103_XM20 | 25749 | 控制油泵出口压力3#坏点 |  | digital
N1DCS.10MAX01EZ103_XK93 | 25750 | 控制油压力测量存在故障 |  | digital
N1DCS.10MAX01EZ103_XK94 | 25751 | 控制油压力＜12MPa |  | digital
N1DCS.10MAX01EZ103_XK96 | 25752 | 抗燃油压力保护 |  | digital
N1DCS.10MAX01EZ103_XV01 | 25753 | Ovation Control Builder |  | digital
N1DCS.10MAX01FP103_XH01 | 25754 | Ovation Control Builder |  | digital
N1DCS.10MAX01FP103A_DL12 | 25755 | Ovation Control Builder |  | digital
N1DCS.10MAX01FP103A_DL13 | 25756 | Ovation Control Builder |  | digital
N1DCS.10MAX01FP103A_DL23 | 25757 | Ovation Control Builder |  | digital
N1DCS.10MAX01FP103A_XM97 | 25758 | Ovation Control Builder |  | digital
N1DCS.10MAX01FP103A_XM98 | 25759 | Ovation Control Builder |  | digital
N1DCS.10MAX01FP103A_XM99 | 25760 | Ovation Control Builder |  | digital
N1DCS.10MAY01EU001_XK96 | 25761 | 电磁阀失电保护 |  | digital
N1DCS.10MAY01EU001_XV01 | 25762 | Ovation Control Builder |  | digital
N1DCS.10MAY01EZ001_XK01 | 25763 | Ovation Control Builder |  | digital
N1DCS.10MAY01EZ001F_XK46 | 25764 | ETS首出信号未来 |  | digital
N1DCS.10MAY01EZ001F_XK96 | 25765 | ETS首出 |  | digital
N1DCS.10MAY01EZ003_RESET | 25766 | 复位跳闸首出(5S脉冲) |  | digital
N1DCS.10MAY01EZ003_XA01 | 25767 | Ovation Control Builder |  | digital
N1DCS.10MAY01EZ011_XK461 | 25768 | 汽机遮断系统已遮断1 |  | digital
N1DCS.10MAY01EZ011_XK4610 | 25769 | 汽机遮断系统已遮断10 |  | digital
N1DCS.10MAY01EZ011_XK4611 | 25770 | 汽机遮断系统已遮断11 |  | digital
N1DCS.10MAY01EZ011_XK4612 | 25771 | 汽机遮断系统已遮断12 |  | digital
N1DCS.10MAY01EZ011_XK4613 | 25772 | 汽机遮断系统已遮断13 |  | digital
N1DCS.10MAY01EZ011_XK4614 | 25773 | 汽机遮断系统已遮断14 |  | digital
N1DCS.10MAY01EZ011_XK4615 | 25774 | 汽机遮断系统已遮断15 |  | digital
N1DCS.10MAY01EZ011_XK4616 | 25775 | 汽机遮断系统已遮断16 |  | digital
N1DCS.10MAY01EZ011_XK4617 | 25776 | 汽机遮断系统已遮断17 |  | digital
N1DCS.10MAY01EZ011_XK4618 | 25777 | 汽机遮断系统已遮断18 |  | digital
N1DCS.10MAY01EZ011_XK462 | 25778 | 汽机遮断系统已遮断2 |  | digital
N1DCS.10MAY01EZ011_XK463_DEH | 25779 | 汽机遮断系统已遮断3 |  | digital
N1DCS.10MAY01EZ011_XK464_DEH | 25780 | 汽机遮断系统已遮断4 |  | digital
N1DCS.10MAY01EZ011_XK465_DEH | 25781 | 汽机遮断系统已遮断5 |  | digital
N1DCS.10MAY01EZ011_XK466_DEH | 25782 | 汽机遮断系统已遮断6 |  | digital
N1DCS.10MAY01EZ011_XK467_DEH | 25783 | 汽机遮断系统已遮断7 |  | digital
N1DCS.10MAY01EZ011_XK468_DEH | 25784 | 汽机遮断系统已遮断8 |  | digital
N1DCS.10MAY01EZ011_XK469_DEH | 25785 | 汽机遮断系统已遮断9 |  | digital
N1DCS.10MAY01EZ020_XK96 | 25786 | 手动遮断按钮 |  | digital
N1DCS.10MAY01EZ020_XV01 | 25787 | Ovation Control Builder |  | digital
N1DCS.10MAY01EZ020_XG51 | 25788 | 汽轮机遮断按钮STRING1# |  | digital
N1DCS.10MAY01EZ020_XG52 | 25789 | 汽轮机遮断按钮STRING2# |  | digital
N1DCS.10MAY01EZ020_XG53 | 25790 | 汽轮机遮断按钮STRING3# |  | digital
N1DCS.10MAY01GS001_XG02 | 25791 | 汽轮机遮断按钮控制室（常开接点 |  | digital
N1DCS.10MAY01GS002_XG02 | 25792 | 汽轮机遮断按钮控制室（常开接点 |  | digital
N1DCS.10MAY01GS003_XG02 | 25793 | 汽轮机遮断按钮（常开接点） |  | digital
N1DCS.10MKD11CT113A_XH01 | 25794 | Ovation Control Builder |  | digital
N1DCS.10MKD11CT113A_XH03 | 25795 | Ovation Control Builder |  | digital
N1DCS.10MKD11CT113A_XM20 | 25796 | Ovation Control Builder |  | digital
N1DCS.10MKD11CT113B_XH01 | 25797 | Ovation Control Builder |  | digital
N1DCS.10MKD11CT113B_XH03 | 25798 | Ovation Control Builder |  | digital
N1DCS.10MKD11CT113B_XM20 | 25799 | Ovation Control Builder |  | digital
N1DCS.10MKD11CT114B_XH01 | 25800 | Ovation Control Builder |  | digital
N1DCS.10MKD11CT114B_XH03 | 25801 | Ovation Control Builder |  | digital
N1DCS.10MKD11CT114B_XM20 | 25802 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY021_XM71 | 25803 | #1汽轮发电机轴承壳振1正常 |  | digital
N1DCS.10MKD11CY022_XM71 | 25804 | #1汽轮发电机轴承壳振2正常 |  | digital
N1DCS.10MKD11CY121_MAX1 | 25805 | #4径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MKD11CY121_MAX2 | 25806 | #4径向轴承壳振1>11.8mm/s |  | digital
N1DCS.10MKD11CY121_XH01 | 25807 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY121_XH03 | 25808 | #4径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MKD11CY121_XM71 | 25809 | #1汽轮发电机轴承壳振1正常 |  | digital
N1DCS.10MKD11CY121_XM72 | 25810 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY121_XV20 | 25811 | #4轴瓦振动通道故障1 |  | digital
N1DCS.10MKD11CY122_MAX1 | 25812 | #4径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MKD11CY122_MAX2 | 25813 | #4径向轴承壳振2>11.8mm/s |  | digital
N1DCS.10MKD11CY122_XH01 | 25814 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY122_XH03 | 25815 | #4径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MKD11CY122_XM71 | 25816 | #1汽轮发电机轴承壳振2正常 |  | digital
N1DCS.10MKD11CY122_XM72 | 25817 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY122_XV20 | 25818 | #4轴瓦振动通道故障2 |  | digital
N1DCS.10MKD11EZ121_XK93 | 25819 | Ovation Control Builder |  | digital
N1DCS.10MKD11EZ121_XK94 | 25820 | Ovation Control Builder |  | digital
N1DCS.10MKD11EZ121_XK96 | 25821 | #4径向轴承壳振大 |  | digital
N1DCS.10MKD11EZ201_XK93 | 25822 | 汽端发电机轴瓦温度测量存在故障 |  | digital
N1DCS.10MKD11EZ201_XK94 | 25823 | 汽端发电机轴瓦温度＞99℃ |  | digital
N1DCS.10MKD11EZ201_XK96 | 25824 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT113A_XH01 | 25825 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT113A_XH03 | 25826 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT113A_XM20 | 25827 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT113B_XH01 | 25828 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT113B_XH03 | 25829 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT113B_XM20 | 25830 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT114B_XH01 | 25831 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT114B_XH03 | 25832 | Ovation Control Builder |  | digital
N1DCS.10MKD12CT114B_XM20 | 25833 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY021_XM71 | 25834 | #2汽轮发电机轴承壳振1正常 |  | digital
N1DCS.10MKD12CY022_XM71 | 25835 | #2汽轮发电机轴承壳振2正常 |  | digital
N1DCS.10MKD12CY121_MAX1 | 25836 | #5径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MKD12CY121_MAX2 | 25837 | #5径向轴承壳振1>11.8mm/s |  | digital
N1DCS.10MKD12CY121_XH01 | 25838 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY121_XH03 | 25839 | #5径向轴承壳振1>9.3mm/s |  | digital
N1DCS.10MKD12CY121_XM71 | 25840 | #2汽轮发电机轴承壳振1正常 |  | digital
N1DCS.10MKD12CY121_XM72 | 25841 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY121_XV20 | 25842 | #5轴瓦振动通道故障1 |  | digital
N1DCS.10MKD12CY122_MAX1 | 25843 | #5径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MKD12CY122_MAX2 | 25844 | #5径向轴承壳振2>11.8mm/s |  | digital
N1DCS.10MKD12CY122_XH01 | 25845 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY122_XH03 | 25846 | #5径向轴承壳振2>9.3mm/s |  | digital
N1DCS.10MKD12CY122_XM71 | 25847 | #2汽轮发电机轴承壳振2正常 |  | digital
N1DCS.10MKD12CY122_XM72 | 25848 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY122_XV20 | 25849 | #5轴瓦振动通道故障2 |  | digital
N1DCS.10MKD12EZ121_XK93 | 25850 | Ovation Control Builder |  | digital
N1DCS.10MKD12EZ121_XK94 | 25851 | Ovation Control Builder |  | digital
N1DCS.10MKD12EZ121_XK96 | 25852 | #5径向轴承壳振大 |  | digital
N1DCS.10MKD12EZ201_XK93 | 25853 | 励端发电机轴瓦温度测量存在故障 |  | digital
N1DCS.10MKD12EZ201_XK94 | 25854 | 励端发电机轴瓦温度＞99℃ |  | digital
N1DCS.10MKD12EZ201_XK96 | 25855 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG010_XT10 | 25856 | ENABLE CSI6300 #1 TRIP TEST |  | digital
N1DCS.10MYA01DG010_XT11 | 25857 | RESET CSI6300 #1 TRIP LATCHED |  | digital
N1DCS.10MYA01DG010_XT20 | 25858 | CSI6300 #1 TRIP MODULE A TEST |  | digital
N1DCS.10MYA01DG010_XT30 | 25859 | CSI6300 #1 TRIP MODULE B TEST |  | digital
N1DCS.10MYA01DG010_XT40 | 25860 | CSI6300 #1 TRIP MODULE C TEST |  | digital
N1DCS.10MYA01DG020_XT10 | 25861 | ENABLE CSI6300 #2 TRIP TEST |  | digital
N1DCS.10MYA01DG020_XT11 | 25862 | RESET CSI6300 #2 TRIP LATCHED |  | digital
N1DCS.10MYA01DG020_XT20 | 25863 | CSI6300 #2 TRIP MODULE A TEST |  | digital
N1DCS.10MYA01DG020_XT30 | 25864 | CSI6300 #2 TRIP MODULE B TEST |  | digital
N1DCS.10MYA01DG020_XT40 | 25865 | CSI6300 #2 TRIP MODULE C TEST |  | digital
N1DCS.10MYA01DG030_AFTEST | 25866 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG030_FDTEST | 25867 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG030_TESTAFS | 25868 | 中压主汽门活动性试验 |  | digital
N1DCS.10MYA01DG030_TESTFDS | 25869 | 高压主汽门活动性试验 |  | digital
N1DCS.10MYA01DG030_TESTON | 25870 | Ovation Control Builder |  | digital
N1DCS.10MYA01EZ011_XK96 | 25871 | 汽轮机超速保护1 |  | digital
N1DCS.10MYA01EZ011_XT22 | 25872 | Ovation Control Builder |  | digital
N1DCS.10MYA01EZ011_XV01 | 25873 | Ovation Control Builder |  | digital
N1DCS.10MYA01EZ011_XK61 | 25874 | 超速保护 CSI6300 1# A OUT2 |  | digital
N1DCS.10MYA01EZ011_XK62 | 25875 | 超速保护 CSI6300 1# B OUT2 |  | digital
N1DCS.10MYA01EZ011_XK63 | 25876 | 超速保护 CSI6300 1# C OUT2 |  | digital
N1DCS.10MYA01EZ011_XT12 | 25877 | 超速保护 CSI6300 1# MODULE A O |  | digital
N1DCS.10MYA01EZ011_XT14 | 25878 | 超速保护 CSI6300 1# MODULE B O |  | digital
N1DCS.10MYA01EZ011_XT16 | 25879 | 超速保护 CSI6300 1# MODULE C O |  | digital
N1DCS.10MYA01EZ011_XT21 | 25880 | CSI6300 1# System OK |  | digital
N1DCS.10MYA01EZ021_XK96 | 25881 | 汽轮机超速保护2 |  | digital
N1DCS.10MYA01EZ021_XT22 | 25882 | Ovation Control Builder |  | digital
N1DCS.10MYA01EZ021_XV01 | 25883 | Ovation Control Builder |  | digital
N1DCS.10MYA01EZ021_XK61 | 25884 | 超速保护 CSI6300 2# A OUT2 |  | digital
N1DCS.10MYA01EZ021_XK62 | 25885 | 超速保护 CSI6300 2# B OUT2 |  | digital
N1DCS.10MYA01EZ021_XK63 | 25886 | 超速保护 CSI6300 2# C OUT2 |  | digital
N1DCS.10MYA01EZ021_XT21 | 25887 | CSI6300 2# System OK |  | digital
N1DCS.10MYA02EZ011_XT12 | 25888 | 超速保护 CSI6300 2# MODULE A O |  | digital
N1DCS.10MYA02EZ011_XT14 | 25889 | 超速保护 CSI6300 2# MODULE B O |  | digital
N1DCS.10MYA02EZ011_XT16 | 25890 | 超速保护 CSI6300 2# MODULE C O |  | digital
N1DCS.10LBC40FP101_XV01 | 25891 | Ovation Control Builder |  | digital
N1DCS.10MAA50EZ621E_XV01 | 25892 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY145_XM72 | 25893 | 膨胀通道故障 |  | digital
N1DCS.10MAY01DU100_1TO2 | 25894 | Ovation Control Builder |  | digital
N1DCS.10MAY01DU100_XK96 | 25895 | COMMUNICATION TRIP |  | digital
N1DCS.10BAC01GS001H1 | 25896 | 发电机出口开关闭合(NO 接点1) |  | digital
N1DCS.10BAC01GS001H2 | 25897 | 发电机出口开关闭合(NO 接点2) |  | digital
N1DCS.10BAC01GS001H3 | 25898 | 发电机出口开关闭合(NO 接点3) |  | digital
N1DCS.10CBA00FU002_DEH | 25899 | 负荷遥控模式 |  | digital
N1DCS.10CBA00FU019 | 25900 | 自动同步控制（请求同期） |  | digital
N1DCS.10CJA06DU001_XT01 | 25901 | 负荷控制协调方式请求 |  | digital
N1DCS.10CJJ01EE001_XT09 | 25902 | 汽机疏水投自动 |  | digital
N1DCS.10LBA10CF001_XH10 | 25903 | 高压蒸汽流量>10% |  | digital
N1DCS.10LBA10CF001_XH15 | 25904 | 高压蒸汽流量>15% |  | digital
N1DCS.10LBA10CF001_XH20 | 25905 | Ovation Control Builder |  | digital
N1DCS.10LBA10CP901_ST1 | 25906 | 高压主汽门前蒸汽压力测点全坏 |  | digital
N1DCS.10LBA10CP901_XH01 | 25907 | 高压主汽门前蒸汽压力>2Mpa |  | digital
N1DCS.10LBA10CP901_XH02 | 25908 | 高压主汽门前蒸汽压力>0.5MPa |  | digital
N1DCS.10LBA10CP901_XH03 | 25909 | 高压主汽门前蒸汽压力>3Mpa |  | digital
N1DCS.10LBA10CP901_XM01 | 25910 | 高压主汽门前蒸汽压力测点全坏 |  | digital
N1DCS.10LBA90CP901_ST1 | 25911 | 低压主汽门前蒸汽压力测点全坏 |  | digital
N1DCS.10LBA90CP901_XH01 | 25912 | 低压主汽门前蒸汽压力>0.2MPa |  | digital
N1DCS.10LBA90CP901_XH02 | 25913 | 低压主汽门前蒸汽压力>0 |  | digital
N1DCS.10LBA90CP901_XH03 | 25914 | 低压主汽门前蒸汽压力>0 |  | digital
N1DCS.10LBA90CP901_XM01 | 25915 | 低压主汽门前蒸汽压力测点全坏 |  | digital
N1DCS.10LBB10CP901_ST1 | 25916 | 中压主汽门前蒸汽压力测点全坏 |  | digital
N1DCS.10LBB10CP901_XH03 | 25917 | 中压主汽门前蒸汽压力<0.1MPa |  | digital
N1DCS.10LBB10CP901_XH09 | 25918 | 中压主汽门前蒸汽压力>0.5MPa |  | digital
N1DCS.10LBC10AA001_XB01 | 25919 | 高排逆止阀关 |  | digital
N1DCS.10LBC10AA001_XB02 | 25920 | 高排逆止阀开 |  | digital
N1DCS.10LBC10AA001_XM20 | 25921 | 高排逆止门故障(全开全关均为1) |  | digital
N1DCS.10LBC40CP101_XM20 | 25922 | #1高压排汽蒸汽压力坏点 |  | digital
N1DCS.10LBC40CP102_XM20 | 25923 | #2高压排汽蒸汽压力坏点 |  | digital
N1DCS.10LBC40CP103_XM20 | 25924 | #3高压排汽蒸汽压力坏点 |  | digital
N1DCS.10LBC40FP101_XH01 | 25925 | 高排压力高高-抽汽解裂 |  | digital
N1DCS.10LBC40FP101_XH02 | 25926 | 高排压力低低-抽汽解裂 |  | digital
N1DCS.10LBC40FP101_XH03 | 25927 | 高压排汽蒸汽压力<0 |  | digital
N1DCS.10LBC40FP101_XH04 | 25928 | 高排低-抽汽报警 |  | digital
N1DCS.10LBC40FP101_XH05 | 25929 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP101_XH52 | 25930 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP101_XH54 | 25931 | Ovation Control Builder |  | digital
N1DCS.10LBC41AA001_XM20 | 25932 | 高排通风阀故障(全开全关均为1) |  | digital
N1DCS.10LBC41CG051B | 25933 | 高排通风阀开 |  | digital
N1DCS.10LBC41CG051C | 25934 | 高排通风阀关 |  | digital
N1DCS.10LBS44AA001_XG01 | 25935 | Ovation Control Builder |  | digital
N1DCS.10LBS44AA001_XG03 | 25936 | Ovation Control Builder |  | digital
N1DCS.10LBS44AA001_XM20 | 25937 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_IPEGO | 25938 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_IPEIN | 25939 | 热再抽汽控制投入 |  | digital
N1DCS.10LBS45AA001_IPEQSP | 25940 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_IPETM | 25941 | 热再抽汽控制手动 |  | digital
N1DCS.10LBS45AA001_LOWER | 25942 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_RAISE | 25943 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_TRACK | 25944 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_XG01 | 25945 | 中压抽汽快关调节阀就地控制允许 |  | digital
N1DCS.10LBS45CG001 | 25946 | 中压抽汽快关调节阀开反馈 |  | digital
N1DCS.10LBS45CG003 | 25947 | 中压抽汽快关调节阀关反馈 |  | digital
N1DCS.10LBS45CG151_XH01 | 25948 | Ovation Control Builder |  | digital
N1DCS.10LBS45CG151_XH51 | 25949 | Ovation Control Builder |  | digital
N1DCS.10LBS45CG151_XM20 | 25950 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_HPEGO | 25951 | 高排抽汽设定运行 |  | digital
N1DCS.10LBS46AA001_HPEIN | 25952 | 冷再抽汽控制投入 |  | digital
N1DCS.10LBS46AA001_HPEQSP | 25953 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_HPETM | 25954 | 高排抽汽控制手动 |  | digital
N1DCS.10LBS46AA001_LOWER | 25955 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_RAISE | 25956 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_TRACK | 25957 |  |  | digital
N1DCS.10LBS46AA001_XG01 | 25958 | 高压抽汽快关调节阀就地控制允许 |  | digital
N1DCS.10LBS46CG001 | 25959 | 高压抽汽快关调节阀开反馈 |  | digital
N1DCS.10LBS46CG003 | 25960 | 高压抽汽快关调节阀关反馈 |  | digital
N1DCS.10LBS46CG151_XH01 | 25961 | Ovation Control Builder |  | digital
N1DCS.10LBS46CG151_XH51 | 25962 | Ovation Control Builder |  | digital
N1DCS.10LBS46CG151_XM20 | 25963 | Ovation Control Builder |  | digital
N1DCS.10MAA11CG051_XG01 | 25964 | 主汽门已全开 |  | digital
N1DCS.10MAA11CG051_XG11 | 25965 | 主汽门关闭 |  | digital
N1DCS.10MAA11CG151_XH01 | 25966 | 高压主汽门全开反馈 |  | digital
N1DCS.10MAA11CG151_XH52 | 25967 | 高压主汽门全关位 |  | digital
N1DCS.10MAA11CG151_XM20 | 25968 | 高压主气门反馈坏点 |  | digital
N1DCS.10MAA12CG051_XG01 | 25969 | 高压调门开启状态 |  | digital
N1DCS.10MAA12CG051_XG11 | 25970 | 高调门关闭 |  | digital
N1DCS.10MAA12CG151_SBFD | 25971 | 高压调门阀位坏点 |  | digital
N1DCS.10MAA12CG151_XH02 | 25972 | 高压调门阀位反馈>3% |  | digital
N1DCS.10MAA12CG151_XH52 | 25973 | 高调门已关闭 |  | digital
N1DCS.10MAA12DG010_BFDNA | 25974 | 汽机未遮断(脉冲) |  | digital
N1DCS.10MAA12DG010_BFDZU | 25975 | 汽机已遮断(脉冲) |  | digital
N1DCS.10MAA12DG010_SPBFD | 25976 | Ovation Control Builder |  | digital
N1DCS.10MAA12DG010_TRACK | 25977 | Ovation Control Builder |  | digital
N1DCS.10MAA12DG010_TRACKN | 25978 | Ovation Control Builder |  | digital
N1DCS.10MAA12DG010_VLVTE | 25979 | 汽机未遮断 |  | digital
N1DCS.10MAA12DG010_XH01 | 25980 | 高调门阀限>104.5 |  | digital
N1DCS.10MAA12SGAF1 | 25981 | 快关中调阀 |  | digital
N1DCS.10MAA12SGAF2 | 25982 | Ovation Control Builder |  | digital
N1DCS.10MAA12SGFD1 | 25983 | 快关高调阀 |  | digital
N1DCS.10MAA12SGFD2 | 25984 | 高压调门快关激活 |  | digital
N1DCS.10MAA12SGZD2 | 25985 | 低压调阀快关激活 |  | digital
N1DCS.10MAA30EE001_SEALCV | 25986 | Ovation Control Builder |  | digital
N1DCS.10MAA30EE001_SEALESV | 25987 | Ovation Control Builder |  | digital
N1DCS.10MAA30EE001_SEALESVINH | 25988 | Ovation Control Builder |  | digital
N1DCS.10MAA50CP101_XM20 | 25989 | 高调门阀后蒸汽压力1#坏点 |  | digital
N1DCS.10MAA50CP102_XM20 | 25990 | 高调门阀后蒸汽压力2#坏点 |  | digital
N1DCS.10MAA50CP103_XM20 | 25991 | 高调门阀后蒸汽压力3#坏点 |  | digital
N1DCS.10MAA50CP111_XM20 | 25992 | Ovation Control Builder |  | digital
N1DCS.10MAA50CP112_XM20 | 25993 | Ovation Control Builder |  | digital
N1DCS.10MAA50CP113_XM20 | 25994 | Ovation Control Builder |  | digital
N1DCS.10MAA50EZ111_XH52 | 25995 | 高压缸压比＜1.05 |  | digital
N1DCS.10MAA50EZ111_XH54 | 25996 | 高压缸压比＜1.08 |  | digital
N1DCS.10MAA50EZ111_XK20 | 25997 | Ovation Control Builder |  | digital
N1DCS.10MAA50EZ111_XK96 | 25998 | 高压缸压比保护 |  | digital
N1DCS.10MAA50FP011_XH03 | 25999 | 高调门阀后蒸汽压力>7MPa |  | digital
N1DCS.10MAA50FP011_XH05 | 26000 | 高调门阀后蒸汽压力>2.5MPa |  | digital
N1DCS.10MAA50FP011_XM23 | 26001 | 高调门阀后蒸汽压力测点全坏 |  | digital
N1DCS.10MAB11CG051_XG01 | 26002 | 再热主汽门已全开 |  | digital
N1DCS.10MAB11CG051_XG11 | 26003 | 再热主汽门关闭 |  | digital
N1DCS.10MAB11CG151_XH01 | 26004 | 中压主汽门全开反馈 |  | digital
N1DCS.10MAB11CG151_XH52 | 26005 | 中压主汽门全关位 |  | digital
N1DCS.10MAB11CG151_XM20 | 26006 | Ovation Control Builder |  | digital
N1DCS.10MAB12AA001_EGVIN | 26007 | 再热调门抽汽投入 |  | digital
N1DCS.10MAB12AA001_EGVOFF | 26008 | 再热调门抽汽退出 |  | digital
N1DCS.10MAB12CG051_XG01 | 26009 | 中压调门开启状态 |  | digital
N1DCS.10MAB12CG051_XG11 | 26010 | 中压调门关闭 |  | digital
N1DCS.10MAB12CG151_SBAF | 26011 | Ovation Control Builder |  | digital
N1DCS.10MAB12CG151_XH02 | 26012 | 中压调门阀位反馈>3% |  | digital
N1DCS.10MAB12CG151_XH52 | 26013 | 中调门已关闭 |  | digital
N1DCS.10MAB12CG151_XH53 | 26014 | 中压调门阀位>10% |  | digital
N1DCS.10MAB12DG010_XH01 | 26015 | 中调门阀限>104.5 |  | digital
N1DCS.10MAB50CP101_XM20 | 26016 | Ovation Control Builder |  | digital
N1DCS.10MAC10CP101_XM20 | 26017 | Ovation Control Builder |  | digital
N1DCS.10MAC10CP102_XM20 | 26018 | Ovation Control Builder |  | digital
N1DCS.10MAC10CP103_XM20 | 26019 | Ovation Control Builder |  | digital
N1DCS.10MAC10CP901_XH01 | 26020 | Ovation Control Builder |  | digital
N1DCS.10MAC10CP901_XH03 | 26021 | Ovation Control Builder |  | digital
N1DCS.10MAC10CP901_XH05 | 26022 | Ovation Control Builder |  | digital
N1DCS.10MAC10CP901_XH52 | 26023 | Ovation Control Builder |  | digital
N1DCS.10MAC10CP901_XH54 | 26024 | Ovation Control Builder |  | digital
N1DCS.10MAC11FF001_DEH | 26025 | 热网故障 |  | digital
N1DCS.10MAC45AA001_XM20 | 26026 | 补汽主汽门故障 |  | digital
N1DCS.10MAC45AA001_XB11 | 26027 | 开低压补汽主门油动机 |  | digital
N1DCS.10MAC45AA001_XB13 | 26028 | 关低压补汽主门油动机 |  | digital
N1DCS.10MAC45AA001_XG01 | 26029 | 低压补汽主门油动机就地控制允许 |  | digital
N1DCS.10MAC45AA001_XG05 | 26030 | 低压补汽主门油动机试验电磁阀动 |  | digital
N1DCS.10MAC45AA011_XB01 | 26031 | Ovation Control Builder |  | digital
N1DCS.10MAC45AA011_XB02 | 26032 | Ovation Control Builder |  | digital
N1DCS.10MAC45CG001 | 26033 | 补汽主汽门开反馈 |  | digital
N1DCS.10MAC45CG002 | 26034 | 补汽主汽门关反馈 |  | digital
N1DCS.10MAC46AA001_XG01 | 26035 | 低压补汽调门油动机就地控制允许 |  | digital
N1DCS.10MAC46CG001 | 26036 | 补汽调阀开反馈 |  | digital
N1DCS.10MAC46CG003 | 26037 | 补汽调阀关反馈 |  | digital
N1DCS.10MAC46CG151_SBZD | 26038 | 低压补汽调门阀位反馈坏点 |  | digital
N1DCS.10MAC46CG151_XH02 | 26039 | 低压补汽调门开启 |  | digital
N1DCS.10MAC46CG151_XH52 | 26040 | 低压补汽调门关闭 |  | digital
N1DCS.10MAC46DG010_XH01 | 26041 | Ovation Control Builder |  | digital
N1DCS.10MAL11AA051_XM20 | 26042 | 高压调门前疏水阀位反馈质量坏点 |  | digital
N1DCS.10MAL11AA051T_XV02 | 26043 | 高压主门疏水门指令反馈无偏差 |  | digital
N1DCS.10MAL11CG151_XH02 | 26044 | 高压调门前疏水阀位反馈大于98 |  | digital
N1DCS.10MAL11CG151_XH52 | 26045 | 高压调门前疏水阀位反馈<5.5% |  | digital
N1DCS.10MAL23AA051_XM20 | 26046 | 中压主汽门前疏水门故障 |  | digital
N1DCS.10MAL23AA051A_XT01 | 26047 | 中压主汽门前疏水门开指令 |  | digital
N1DCS.10MAL23AA051B_XG01 | 26048 | 中压主汽门前疏水门反馈开 |  | digital
N1DCS.10MAL23AA051C_XG01 | 26049 | 中压主汽门前疏水门反馈关 |  | digital
N1DCS.10MAL23CG051B_XG01 | 26050 | 中压主汽门前疏水门反馈开 |  | digital
N1DCS.10MAL23CG051C_XG01 | 26051 | 中压主汽门前疏水门反馈关 |  | digital
N1DCS.10MAL26AA051_XM20 | 26052 | 中压调节阀前疏水门故障 |  | digital
N1DCS.10MAL26AA051A_XT01 | 26053 | 中压调节阀前疏水门开指令 |  | digital
N1DCS.10MAL26AA051B_XG01 | 26054 | 中压调节阀前疏水门反馈开 |  | digital
N1DCS.10MAL26AA051C_XG01 | 26055 | 中压调节阀前疏水门反馈关 |  | digital
N1DCS.10MAL26CG051B_XG01 | 26056 | 中压调节阀前疏水门反馈开 |  | digital
N1DCS.10MAL26CG051C_XG01 | 26057 | 中压调节阀前疏水门反馈关 |  | digital
N1DCS.10MAV30EU001_XV01 | 26058 | Ovation Control Builder |  | digital
N1DCS.10MAV30EU001_XV04 | 26059 | Ovation Control Builder |  | digital
N1DCS.10MAW10EG003_XV01 | 26060 | Ovation Control Builder |  | digital
N1DCS.10MAY00EE001_XA01 | 26061 | 已释放蒸汽品质 |  | digital
N1DCS.10MAY00EE001_XA02 | 26062 | 未释放蒸汽品质 |  | digital
N1DCS.10MAY00EE002_XA01 | 26063 | 已释放额定转速 |  | digital
N1DCS.10MAY00EE002_XA02 | 26064 | 未释放额定转速 |  | digital
N1DCS.10MAY01CG151_XH51 | 26065 | 所有主汽门已关闭1(去发电机主保 |  | digital
N1DCS.10MAY01CG151_XH52 | 26066 | 所有主汽门已关闭1(去锅炉主保护 |  | digital
N1DCS.10MAY01CG151_XH53 | 26067 | 所有主汽门已关闭2(去发电机主保 |  | digital
N1DCS.10MAY01CG151_XH54 | 26068 | 所有主汽门已关闭2(去锅炉主保护 |  | digital
N1DCS.10MAY01EZ001_XK46 | 26069 | Ovation Control Builder |  | digital
N1DCS.10MAY01EZ001_XK96 | 26070 | 汽机已遮断 |  | digital
N1DCS.10MAY01EZ001A_XK46 | 26071 | 汽机遮断系统已遮断A |  | digital
N1DCS.10MAY01EZ001B_XK46 | 26072 | 汽机遮断系统已遮断B |  | digital
N1DCS.10MAY10EC001_14JT6 | 26073 | 汽轮机启动顺控跳至第6步 |  | digital
N1DCS.10MAY10EC001_AAUS | 26074 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_CLSESV | 26075 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_CVCLSD | 26076 | 高、中、低压调门均全关 |  | digital
N1DCS.10MAY10EC001_DFAIL | 26077 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_DFINISHED | 26078 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_ENOP | 26079 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_ESVCLSD | 26080 | 高、中、低压主门均全关 |  | digital
N1DCS.10MAY10EC001_ESVOPND | 26081 | 高、中、低压主汽门均全开 |  | digital
N1DCS.10MAY10EC001_EVSSVOK | 26082 | 高/中/低压暖管完成 |  | digital
N1DCS.10MAY10EC001_M01 | 26083 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_RELEASE | 26084 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S10OK | 26085 | 汽机顺控启动第十步完成反馈 |  | digital
N1DCS.10MAY10EC001_S11OK | 26086 | 汽机顺控启动第十一步完成反馈 |  | digital
N1DCS.10MAY10EC001_S12OK | 26087 | 汽机顺控启动第十二步完成反馈 |  | digital
N1DCS.10MAY10EC001_S13OK | 26088 | 汽机顺控启动第十三步完成反馈 |  | digital
N1DCS.10MAY10EC001_S14OK | 26089 | 汽机顺控启动第十四步完成反馈 |  | digital
N1DCS.10MAY10EC001_S15OK | 26090 | 汽机顺控第十五步完成反馈 |  | digital
N1DCS.10MAY10EC001_S16OK | 26091 | 汽机顺控第十六步完成反馈 |  | digital
N1DCS.10MAY10EC001_S17OK | 26092 | 汽机顺控第十七步完成反馈 |  | digital
N1DCS.10MAY10EC001_S18OK | 26093 | 汽机顺控第十八步完成反馈 |  | digital
N1DCS.10MAY10EC001_S19OK | 26094 | 汽机顺控第十九步完成反馈 |  | digital
N1DCS.10MAY10EC001_S1OK | 26095 | 汽机顺控启动第一步完成反馈 |  | digital
N1DCS.10MAY10EC001_S20OK | 26096 | 汽机顺控第二十步完成反馈 |  | digital
N1DCS.10MAY10EC001_S21OK | 26097 | 汽机顺控第二十一步完成反馈 |  | digital
N1DCS.10MAY10EC001_S22OK | 26098 | 汽机顺控第二十二步完成反馈 |  | digital
N1DCS.10MAY10EC001_S23OK | 26099 | 汽机顺控第二十三步完成反馈 |  | digital
N1DCS.10MAY10EC001_S24OK | 26100 | 汽机顺控第二十四步完成反馈 |  | digital
N1DCS.10MAY10EC001_S25OK | 26101 | 汽机顺控第二十五步完成反馈 |  | digital
N1DCS.10MAY10EC001_S2OK | 26102 | 汽机顺控启动第二步完成反馈 |  | digital
N1DCS.10MAY10EC001_S3OK | 26103 | 汽机顺控启动第三步完成反馈 |  | digital
N1DCS.10MAY10EC001_S4OK | 26104 | 汽机顺控启动第四步完成反馈 |  | digital
N1DCS.10MAY10EC001_S51OK | 26105 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S52OK | 26106 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S53OK | 26107 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S54OK | 26108 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S55OK | 26109 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S56OK | 26110 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S57OK | 26111 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S58OK | 26112 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S59OK | 26113 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S5OK | 26114 | 汽机顺控启动第五步完成反馈 |  | digital
N1DCS.10MAY10EC001_S60OK | 26115 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S61OK | 26116 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_S6OK | 26117 | 汽机顺控启动第六步完成反馈 |  | digital
N1DCS.10MAY10EC001_S7OK | 26118 | 汽机顺控启动第七步完成反馈 |  | digital
N1DCS.10MAY10EC001_S8OK | 26119 | 汽机顺控启动第八步完成反馈 |  | digital
N1DCS.10MAY10EC001_S9OK | 26120 | 汽机顺控启动第九步完成反馈 |  | digital
N1DCS.10MAY10EC001_SASTILL | 26121 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_UDONE | 26122 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_UFAIL | 26123 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS01 | 26124 | 汽机顺控启动第一步指令 |  | digital
N1DCS.10MAY10EC001_XS02 | 26125 | 汽机顺控启动第二步指令 |  | digital
N1DCS.10MAY10EC001_XS03 | 26126 | 汽机启动顺控第三步指令 |  | digital
N1DCS.10MAY10EC001_XS04 | 26127 | 汽机顺控启动第四步指令 |  | digital
N1DCS.10MAY10EC001_XS05 | 26128 | 汽机顺控启动第五步指令 |  | digital
N1DCS.10MAY10EC001_XS06 | 26129 | 汽机顺控启动第六步指令 |  | digital
N1DCS.10MAY10EC001_XS07 | 26130 | 汽机顺控启动第七步指令 |  | digital
N1DCS.10MAY10EC001_XS08 | 26131 | 汽机顺控启动第八步指令 |  | digital
N1DCS.10MAY10EC001_XS09 | 26132 | 汽机顺控启动第九步指令 |  | digital
N1DCS.10MAY10EC001_XS10 | 26133 | 汽机顺控启动第十步指令 |  | digital
N1DCS.10MAY10EC001_XS11 | 26134 | 汽机顺控启动第十一步指令 |  | digital
N1DCS.10MAY10EC001_XS12 | 26135 | 汽机顺控启动第十二步指令 |  | digital
N1DCS.10MAY10EC001_XS13 | 26136 | 汽机顺控启动第十三步指令 |  | digital
N1DCS.10MAY10EC001_XS14 | 26137 | 汽机顺控启动第十四步指令 |  | digital
N1DCS.10MAY10EC001_XS15 | 26138 | 汽机顺控启动第十五步指令 |  | digital
N1DCS.10MAY10EC001_XS16 | 26139 | 汽机顺控启动第十六步指令 |  | digital
N1DCS.10MAY10EC001_XS17 | 26140 | 汽机顺控启动第十七步指令 |  | digital
N1DCS.10MAY10EC001_XS18 | 26141 | 汽机顺控启动第十八步指令 |  | digital
N1DCS.10MAY10EC001_XS19 | 26142 | 汽机顺控启动第十九步指令 |  | digital
N1DCS.10MAY10EC001_XS20 | 26143 | 汽机顺控启动第二十步指令 |  | digital
N1DCS.10MAY10EC001_XS21 | 26144 | 汽机顺控启动第二十一步指令 |  | digital
N1DCS.10MAY10EC001_XS22 | 26145 | 汽机顺控启动第二十二步指令 |  | digital
N1DCS.10MAY10EC001_XS23 | 26146 | 汽机顺控启动第二十三步指令 |  | digital
N1DCS.10MAY10EC001_XS24 | 26147 | 汽机顺控启动第二十四步指令 |  | digital
N1DCS.10MAY10EC001_XS25 | 26148 | 汽机顺控启动第二十五步指令 |  | digital
N1DCS.10MAY10EC001_XS51 | 26149 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS52 | 26150 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS53 | 26151 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS54 | 26152 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS55 | 26153 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS56 | 26154 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS57 | 26155 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS58 | 26156 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS59 | 26157 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XS60 | 26158 | 汽机顺控启动第六十步指令 |  | digital
N1DCS.10MAY10EC001_XS61 | 26159 | 汽机顺控启动第六十一步指令 |  | digital
N1DCS.10MAY10EC001_XV01 | 26160 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XV03 | 26161 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XV04 | 26162 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC001_XV07 | 26163 | Ovation Control Builder |  | digital
N1DCS.10MAY10EC009_XT01 | 26164 | 润滑油控制油系统正常运行 |  | digital
N1DCS.10MAY10FT910_FINISHED | 26165 | 暖机计时完成 |  | digital
N1DCS.10MAY10FT910_NST | 26166 | Ovation Control Builder |  | digital
N1DCS.10MAY10FT910_SOFAB | 26167 | Ovation Control Builder |  | digital
N1DCS.10MAY10FT910_ST | 26168 | Ovation Control Builder |  | digital
N1DCS.10MKA01CE903_OPC | 26169 | OPC动作至DCS |  | digital
N1DCS.10MKA01CE903_XH01 | 26170 | 发电机功率大于42.21MW |  | digital
N1DCS.10MKA01CE903_XH02 | 26171 | 发电机功率大于14.07MW |  | digital
N1DCS.10MKA01CE903_XH03 | 26172 | 发电机功率大于28.14MW |  | digital
N1DCS.10MKA01CE903_XH52 | 26173 | 发电机功率<98.49MW |  | digital
N1DCS.10MKW11EU001_ZV03 | 26174 | Ovation Control Builder |  | digital
N1DCS.10MKY01DE011A | 26175 | 同步转速允许 |  | digital
N1DCS.10MKY01DE011C | 26176 | 同步转速升 |  | digital
N1DCS.10MKY01DE011D | 26177 | 同步转速降 |  | digital
N1DCS.10MYA01CS901_ANFABR | 26178 | 启动终止 |  | digital
N1DCS.10MYA01CS901_FGNF11 | 26179 | 汽机转速在临界转速区:6~14HZ |  | digital
N1DCS.10MYA01CS901_FGNF21 | 26180 | 汽机转速在临界转速区:16~47.5HZ |  | digital
N1DCS.10MYA01CS901_NTASP | 26181 | 汽机转速不在临界转速 |  | digital
N1DCS.10MYA01CS901_NTGRKL | 26182 | 汽机转速加速度过小 |  | digital
N1DCS.10MYA01CS901_X16C | 26183 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH05 | 26184 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH11 | 26185 | OPC |  | digital
N1DCS.10MYA01CS901_XH15 | 26186 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH19 | 26187 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH21 | 26188 | 汽轮机转速>6.5Hz |  | digital
N1DCS.10MYA01CS901_XH25 | 26189 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH33 | 26190 | 汽轮机转速>33Hz |  | digital
N1DCS.10MYA01CS901_XH37 | 26191 | 汽轮机转速>47.5Hz |  | digital
N1DCS.10MYA01CS901_XH38 | 26192 | 汽机转速>NWART |  | digital
N1DCS.10MYA01CS901_XH54 | 26193 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH63 | 26194 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH71 | 26195 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH87 | 26196 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XT02 | 26197 | 汽轮机已并网 |  | digital
N1DCS.10MYA01CS901_XT03 | 26198 | 汽轮机未并网 |  | digital
N1DCS.10MYA01CS901_ZV23 | 26199 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_ZV71 | 26200 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_ZV83 | 26201 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH02 | 26202 | 汽轮机转速大于2950RPM |  | digital
N1DCS.10MYA01DG010_ANABWT | 26203 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG010_FGSWF | 26204 | 非转速设定跟踪 |  | digital
N1DCS.10MYA01DG010_INTPELIN | 26205 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG010_OSABGL | 26206 | 进汽设定值达到信号 |  | digital
N1DCS.10MYA01DG010_OSK | 26207 | 负荷设定跟踪 |  | digital
N1DCS.10MYA01DG010_OSKN | 26208 | 负荷设定不跟踪 |  | digital
N1DCS.10MYA01DG010_OSNF | 26209 | 进汽设定值跟踪 |  | digital
N1DCS.10MYA01DG010_OSXE | 26210 | 负荷远程控制ON |  | digital
N1DCS.10MYA01DG010_P10 | 26211 | 负荷远程控制投入 |  | digital
N1DCS.10MYA01DG010_SET | 26212 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG010_SPSWF | 26213 | 转速/负荷设定值控制闭锁 |  | digital
N1DCS.10MYA01DG010_STPNS | 26214 | 转速设定值控制停止 |  | digital
N1DCS.10MYA01DG010_STPSWF | 26215 | 转速-负荷控制停止 |  | digital
N1DCS.10MYA01DG010_XH01 | 26216 | 外部负荷设定>98% |  | digital
N1DCS.10MYA01DG010_XT52 | 26217 | 负荷控制投入(协调方式） |  | digital
N1DCS.10MYA01DG011_OSGE | 26218 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_A | 26219 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_AHIGH | 26220 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_ALOW | 26221 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_ASTOP | 26222 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_DOWN | 26223 | TAB下降 |  | digital
N1DCS.10MYA01DG020_RSTCV | 26224 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_RSTESV | 26225 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_SDMAN | 26226 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_SE_EINL | 26227 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_STOP | 26228 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_TIME | 26229 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_TRIP | 26230 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_TRIPCV | 26231 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_TRIPESV | 26232 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_TRIPN | 26233 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_UP | 26234 | TAB上升 |  | digital
N1DCS.10MYA01DG020_XH01 | 26235 | TAB>99% |  | digital
N1DCS.10MYA01DG020_XH03 | 26236 | TAB>62% |  | digital
N1DCS.10MYA01DG020_XH05 | 26237 | TAB>12.5 |  | digital
N1DCS.10MYA01DG020_XH175 | 26238 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XH225 | 26239 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XH275 | 26240 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XH325 | 26241 | TAB>32.5 |  | digital
N1DCS.10MYA01DG020_XH375 | 26242 | TAB<37.5 |  | digital
N1DCS.10MYA01DG020_XH425 | 26243 | TAB>42.5 |  | digital
N1DCS.10MYA01DG020_XH475 | 26244 | TAB<47.5 |  | digital
N1DCS.10MYA01DG020_XH52 | 26245 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XH53 | 26246 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XH75 | 26247 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XT07 | 26248 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XT12 | 26249 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XT17 | 26250 | 主汽门油动机关闭电磁阀失电指令 |  | digital
N1DCS.10MYA01DG020_XT22 | 26251 | 主汽门油动机关闭电磁阀带电指令 |  | digital
N1DCS.10MYA01DG020_XT27 | 26252 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XT32 | 26253 | Ovation Control Builder |  | digital
N1DCS.10MYA01DG020_XT37 | 26254 | TAB主汽门开启电磁阀得电指令 |  | digital
N1DCS.10MYA01DG020_XT42 | 26255 | 高中低主汽门开启电磁阀失电指令 |  | digital
N1DCS.10MYA01DP010_FDSXA | 26256 | 高压压力手动设定投入 |  | digital
N1DCS.10MYA01DP010_FDSXE | 26257 | 高压压力自动设定投入 |  | digital
N1DCS.10MYA01DP011_GDE | 26258 | 限压模式 |  | digital
N1DCS.10MYA01DP011_GDER | 26259 | 限压模式下高压压力激活 |  | digital
N1DCS.10MYA01DP011_OSNF | 26260 | 进汽设定值跟踪 |  | digital
N1DCS.10MYA01DP011_VDE | 26261 | 初压模式 |  | digital
N1DCS.10MYA01DP020_HZSXA | 26262 | 中压压力手动设定投入 |  | digital
N1DCS.10MYA01DP020_HZSXE | 26263 | 中压压力自动设定投入 |  | digital
N1DCS.10MYA01DP030_ZDSXA | 26264 | 低压压力手动设定投入 |  | digital
N1DCS.10MYA01DP030_ZDSXE | 26265 | 低压压力自动设定投入 |  | digital
N1DCS.10MYA01DP050_XT01 | 26266 | Ovation Control Builder |  | digital
N1DCS.10MYA01DP090_HVDRA | 26267 | 高压缸压比控制退出 |  | digital
N1DCS.10MYA01DP090_HVDRE | 26268 | 高压缸压比控制投入 |  | digital
N1DCS.10MYA01DP090_S | 26269 | Ovation Control Builder |  | digital
N1DCS.10MYA01DP090_S20Q | 26270 | TAB或限压模式高压控制激活 |  | digital
N1DCS.10MYA01DS010_C12 | 26271 | 同步转速升/降(匹配电网频率) |  | digital
N1DCS.10MYA01DS010_C15 | 26272 | Ovation Control Builder |  | digital
N1DCS.10MYA01DS010_N60Q | 26273 | 转速不在临界转速区时熱应力故障 |  | digital
N1DCS.10MYA01DS010_N90Q | 26274 | Ovation Control Builder |  | digital
N1DCS.10MYA01DS010_NSABGL | 26275 | 转速设定值达到 |  | digital
N1DCS.10MYA01DS010_NSGPE | 26276 | 超速试验过程中 |  | digital
N1DCS.10MYA01DS010_NSKQ | 26277 | 转速设定跟踪 |  | digital
N1DCS.10MYA01DS010_NSKQN | 26278 | 转速设定不跟踪 |  | digital
N1DCS.10MYA01DS010_NSNF | 26279 | 转速设定跟踪 |  | digital
N1DCS.10MYA01DS010_OPC | 26280 | OPC试验过程中 |  | digital
N1DCS.10MYA01DS010_PSSE | 26281 | 超速测试 |  | digital
N1DCS.10MYA01DS010_PSSEFL | 26282 | Ovation Control Builder |  | digital
N1DCS.10MYA01DS010_RSSE | 26283 | Ovation Control Builder |  | digital
N1DCS.10MYA01DS010_RSSEFL | 26284 | Ovation Control Builder |  | digital
N1DCS.10MYA01DS010_SYHT | 26285 | 同步转速升 |  | digital
N1DCS.10MYA01DS010_SYTT | 26286 | 同步转速降 |  | digital
N1DCS.10MYA01DS010_XH03 | 26287 | Ovation Control Builder |  | digital
N1DCS.10MYA01DS010_XH05 | 26288 | Ovation Control Builder |  | digital
N1DCS.10MYA01DT050_HATRA | 26289 | 高排温度控制退出 |  | digital
N1DCS.10MYA01DT050_HATRE | 26290 | 高排温度控制投入 |  | digital
N1DCS.10MYA01DT050_S | 26291 | Ovation Control Builder |  | digital
N1DCS.10MYA01DT050_S20Q | 26292 | TAB或限压模式高压控制激活 |  | digital
N1DCS.10MYA01DU010_XT02 | 26293 | 负荷控制投入 |  | digital
N1DCS.10MYA01DU011_VWQN | 26294 | 热应力计算退出 |  | digital
N1DCS.10MYA01DU011_W60Q | 26295 | Ovation Control Builder |  | digital
N1DCS.10MYA01DU011_WTE | 26296 | 热应力计算投入 |  | digital
N1DCS.10MYA01DU012_SWFQ | 26297 | 确认设定值控制信号 |  | digital
N1DCS.10MYA01DU012_WTS | 26298 | 热应力故障 |  | digital
N1DCS.10MYA01DU050_FREQE | 26299 | Ovation Control Builder |  | digital
N1DCS.10MYA01DU050_LB | 26300 | 汽轮机已并网 |  | digital
N1DCS.10MYA01DU050_LBQ | 26301 | 汽轮机未并网 |  | digital
N1DCS.10MYA01DU050_LBX | 26302 | 汽机并网且无OPC动作 |  | digital
N1DCS.10MYA01DU050_XH01 | 26303 | 转速/负荷控制器输出值>0.5% |  | digital
N1DCS.10MYA01DU050_XH51 | 26304 | Ovation Control Builder |  | digital
N1DCS.10MYA01DU060_FDPRIE | 26305 | 高压压力控制激活 |  | digital
N1DCS.10MYA01DU060_HATRIE | 26306 | 高排温度控制器激活 |  | digital
N1DCS.10MYA01DU060_HVDRIE | 26307 | 高压压比控制器激活 |  | digital
N1DCS.10MYA01DU060_HZPRIE | 26308 | 再热压力控制器激活 |  | digital
N1DCS.10MYA01DU060_NORIE | 26309 | 转速/负荷控制器激活 |  | digital
N1DCS.10MYA01DU060_NTRIE | 26310 | 转速控制器激活 |  | digital
N1DCS.10MYA01DU060_ORIE | 26311 | 进汽控制器激活 |  | digital
N1DCS.10MYA01DU060_TAB50 | 26312 | TAB>0.62 |  | digital
N1DCS.10MYA01DU060_TABG0 | 26313 | Ovation Control Builder |  | digital
N1DCS.10MYA01DU060_TABGNF | 26314 | Ovation Control Builder |  | digital
N1DCS.10MYA01DU060_TABIE | 26315 | TAB控制器激活 |  | digital
N1DCS.10MYA01DU060_XT01 | 26316 | 转速控制激活 |  | digital
N1DCS.10MYA01DU060_XT02 | 26317 | 负荷控制激活 |  | digital
N1DCS.10MYA01DU060_ZDPRIE | 26318 | 低压进汽压力控制器激活 |  | digital
N1DCS.10MYA01EZ400_XT01 | 26319 | 冷态启动保护 |  | digital
N1DCS.10NAA01FP101_XH01 | 26320 | 冷再抽汽减压阀前压力<0.1MPa |  | digital
N1DCS.10NAA01FP101_XK20 | 26321 | 冷再抽汽减压阀前压力测点全坏 |  | digital
N1DCS.10NAA01FP101_XM20 | 26322 | 冷再抽汽减压阀前压力测点3坏2 |  | digital
N1DCS.10NAA02FP101_XH01 | 26323 | Ovation Control Builder |  | digital
N1DCS.10NAA02FP101_XK20 | 26324 | 热再抽汽减压阀前压力测点全坏 |  | digital
N1DCS.10NAA02FP101_XM20 | 26325 | 热再抽汽减压阀前压力测点3坏2 |  | digital
N1DCS.10SIM01SW001_SIMON | 26326 | 混仿 |  | digital
N1DCS.10SIM01SW002_SIMLB | 26327 | 仿真并网 |  | digital
N1DCS.10SIM01SW002_SIMVLV | 26328 | Ovation Control Builder |  | digital
N1DCS.10SIM01SW002_SIMVP | 26329 | 纯仿 |  | digital
N1DCS.11MAN10AC101ZC2 | 26330 | 锅炉高旁阀关闭 |  | digital
N1DCS.11MAN20AC101ZC2 | 26331 | 锅炉中旁阀关闭 |  | digital
N1DCS.1_1_7_COIL_1_KSERVO_ALM | 26332 | Ovation Control Builder |  | digital
N1DCS.1_1_7_COIL_2_KSERVO_ALM | 26333 | Ovation Control Builder |  | digital
N1DCS.1_1_8_COIL_1_KSERVO_ALM | 26334 | Ovation Control Builder |  | digital
N1DCS.1_1_8_COIL_2_KSERVO_ALM | 26335 | Ovation Control Builder |  | digital
N1DCS.DCS_AUXOK | 26336 | Ovation Control Builder |  | digital
N1DCS.DCS_DRNWTR | 26337 | Ovation Control Builder |  | digital
N1DCS.DCS_GEN_SEAL_OIL_OK | 26338 | Ovation Control Builder |  | digital
N1DCS.DCS_GLANDSTEAMON | 26339 | Ovation Control Builder |  | digital
N1DCS.DCS_LIFTPUMPS_2OF3ON | 26340 | Ovation Control Builder |  | digital
N1DCS.DCS_LIFTPUMPS_ALLOFF | 26341 | Ovation Control Builder |  | digital
N1DCS.DEH_OPNDRN | 26342 | Ovation Control Builder |  | digital
N1DCS.DEH_PASSWORD_IS_SET | 26343 | Ovation Control Builder |  | digital
N1DCS.DNTGR | 26344 | 转速控制偏差大 |  | digital
N1DCS.ENOPC | 26345 | Ovation Control Builder |  | digital
N1DCS.FGNF1 | 26346 | Ovation Control Builder |  | digital
N1DCS.FGNF2 | 26347 | Ovation Control Builder |  | digital
N1DCS.GV_ARE | 26348 | Ovation Control Builder |  | digital
N1DCS.GV_CAL | 26349 | Ovation Control Builder |  | digital
N1DCS.GV_CARD_CNTIGENCY | 26350 | Ovation Control Builder |  | digital
N1DCS.GV_COIL_1_OPEN | 26351 | Ovation Control Builder |  | digital
N1DCS.GV_COIL_1_SHORT | 26352 | Ovation Control Builder |  | digital
N1DCS.GV_COIL_2_OPEN | 26353 | Ovation Control Builder |  | digital
N1DCS.GV_COIL_2_SHORT | 26354 | Ovation Control Builder |  | digital
N1DCS.GV_COIL_3_OPEN | 26355 | Ovation Control Builder |  | digital
N1DCS.GV_COIL_3_SHORT | 26356 | Ovation Control Builder |  | digital
N1DCS.GV_CONTINGENCY | 26357 | Ovation Control Builder |  | digital
N1DCS.GV_FATAL_ERROR | 26358 | Ovation Control Builder |  | digital
N1DCS.GV_LOCAL | 26359 | Ovation Control Builder |  | digital
N1DCS.GV_REDUNDANT_LINK | 26360 | Ovation Control Builder |  | digital
N1DCS.IV_ARE | 26361 | Ovation Control Builder |  | digital
N1DCS.IV_CAL | 26362 | Ovation Control Builder |  | digital
N1DCS.IV_CARD_CNTIGENCY | 26363 | Ovation Control Builder |  | digital
N1DCS.IV_COIL_1_OPEN | 26364 | Ovation Control Builder |  | digital
N1DCS.IV_COIL_1_SHORT | 26365 | Ovation Control Builder |  | digital
N1DCS.IV_COIL_2_OPEN | 26366 | Ovation Control Builder |  | digital
N1DCS.IV_COIL_2_SHORT | 26367 | Ovation Control Builder |  | digital
N1DCS.IV_COIL_3_OPEN | 26368 | Ovation Control Builder |  | digital
N1DCS.IV_COIL_3_SHORT | 26369 | Ovation Control Builder |  | digital
N1DCS.IV_CONTINGENCY | 26370 | Ovation Control Builder |  | digital
N1DCS.IV_FATAL_ERROR | 26371 | Ovation Control Builder |  | digital
N1DCS.IV_LOCAL | 26372 | Ovation Control Builder |  | digital
N1DCS.IV_REDUNDANT_LINK | 26373 | Ovation Control Builder |  | digital
N1DCS.MANUALL_MAL11 | 26374 | 高调门前疏水阀在手动 |  | digital
N1DCS.NT_MRE | 26375 | Ovation Control Builder |  | digital
N1DCS.NT_XALM | 26376 | Ovation Control Builder |  | digital
N1DCS.PEL_MRE | 26377 | Ovation Control Builder |  | digital
N1DCS.PEL_XALM | 26378 | Ovation Control Builder |  | digital
N1DCS.PFD11_MRE | 26379 | Ovation Control Builder |  | digital
N1DCS.PFD11_XALM | 26380 | Ovation Control Builder |  | digital
N1DCS.PZD11_MRE | 26381 | Ovation Control Builder |  | digital
N1DCS.PZD11_XALM | 26382 | Ovation Control Builder |  | digital
N1DCS.SHUTDOWNSGCON | 26383 | Ovation Control Builder |  | digital
N1DCS.STARTSGCON | 26384 | Ovation Control Builder |  | digital
N1DCS.STNT1 | 26385 | #1转速探头故障 |  | digital
N1DCS.STNT2 | 26386 | #2转速探头故障 |  | digital
N1DCS.STNT3 | 26387 | #3转速探头故障 |  | digital
N1DCS.STPEL1 | 26388 | #1功率变送器故障 |  | digital
N1DCS.STPEL2 | 26389 | #2功率变送器故障 |  | digital
N1DCS.STPEL3 | 26390 | #3功率变送器故障 |  | digital
N1DCS.STPFD1 | 26391 | Ovation Control Builder |  | digital
N1DCS.STPFD2 | 26392 | Ovation Control Builder |  | digital
N1DCS.STPFD3 | 26393 | Ovation Control Builder |  | digital
N1DCS.STPHZ1 | 26394 | Ovation Control Builder |  | digital
N1DCS.STPHZ2 | 26395 | Ovation Control Builder |  | digital
N1DCS.STPHZ3 | 26396 | Ovation Control Builder |  | digital
N1DCS.STPZD1 | 26397 | Ovation Control Builder |  | digital
N1DCS.STPZD2 | 26398 | Ovation Control Builder |  | digital
N1DCS.STPZD3 | 26399 | Ovation Control Builder |  | digital
N1DCS.VGBAFALM | 26400 | Ovation Control Builder |  | digital
N1DCS.VGBFDALM | 26401 | Ovation Control Builder |  | digital
N1DCS.VGBZDALM | 26402 | Ovation Control Builder |  | digital
N1DCS.VGFDSALM | 26403 | 高压压力手动设定报警 |  | digital
N1DCS.VGHZSALM | 26404 | Ovation Control Builder |  | digital
N1DCS.VGNSALM | 26405 | 转速设定报警 |  | digital
N1DCS.VGOSALM | 26406 | 负荷设定报警 |  | digital
N1DCS.VGOSGALM | 26407 | Ovation Control Builder |  | digital
N1DCS.VGTABALM | 26408 | Ovation Control Builder |  | digital
N1DCS.VGZDSALM | 26409 | 中压压力手动设定报警 |  | digital
N1DCS.W150Q1 | 26410 | Ovation Control Builder |  | digital
N1DCS.W160Q1 | 26411 | Ovation Control Builder |  | digital
N1DCS.10LBC40CP101_XH01 | 26412 | HP EXH PRS 1>4.23MPa |  | digital
N1DCS.10LBC40CP102_XH01 | 26413 | HP EXH PRS 2>4.23MPa |  | digital
N1DCS.10LBC40CP103_XH01 | 26414 | HP EXH PRS 3>4.23MPa |  | digital
N1DCS.10LBC40FP101_XK96 | 26415 | 高排压力保护 |  | digital
N1DCS.10LBC40FP101A_DL12 | 26416 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP101A_DL13 | 26417 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP101A_DL23 | 26418 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP101A_XM97 | 26419 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP101A_XM98 | 26420 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP101A_XM99 | 26421 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_HPEQSP1 | 26422 | Ovation Control Builder |  | digital
N1DCS.10MAL11AA051T_OPEN | 26423 | TRIP OR LBQ OPEN DRAIN VLV |  | digital
N1DCS.10MAY01DU100_2TO3 | 26424 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH07 | 26425 | ST SPEED >2700rpm |  | digital
N1DCS.10MYA01CS901_XH17 | 26426 | SPEED>49Hz |  | digital
N1DCS.10MYA01CS901_XH53 | 26427 | Ovation Control Builder |  | digital
N1DCS.10MYA01CS901_XH72 | 26428 | 转速小于3030RPM |  | digital
N1DCS.10MYA01CS901_ZV84 | 26429 | 汽机转速<1000RPM |  | digital
N1DCS.10MYA01DG020_SDAUTO | 26430 | 自动状态 |  | digital
N1DCS.10MYA01DG020_XH40 | 26431 | TAB>40 |  | digital
N1DCS.NJWC | 26432 | 暖机完成 |  | digital
N1DCS.10CBA00FU003_DEH | 26433 | 开高压疏水阀（10% LOAD关） |  | digital
N1DCS.10CBA00FU004_DEH | 26434 | 开中压疏水阀（20%LOAD关）24VDC |  | digital
N1DCS.10LBA20CT007_XH01 | 26435 | Ovation Control Builder |  | digital
N1DCS.10LBA20CT007_XH03 | 26436 | 主蒸汽温度过高 |  | digital
N1DCS.10LBA20CT007_XH04 | 26437 | 高压主汽门前蒸汽温度>350℃ |  | digital
N1DCS.10LBA20CT007_XH10 | 26438 | Ovation Control Builder |  | digital
N1DCS.10LBA20CT007_XM20 | 26439 | 高压主汽门前蒸汽温度测点全坏 |  | digital
N1DCS.10LBA20EZ007_XK96 | 26440 | 主蒸汽温度保护 |  | digital
N1DCS.10LBA90CT001_XM20 | 26441 | 低压主汽门前蒸汽温度坏点 |  | digital
N1DCS.10LBB50CT007_XH01 | 26442 | Ovation Control Builder |  | digital
N1DCS.10LBB50CT007_XH03 | 26443 | 再热蒸汽温度过高 |  | digital
N1DCS.10LBB50CT007_XH07 | 26444 | 中压主汽门前蒸汽温度>330℃ |  | digital
N1DCS.10LBB50CT007_XM20 | 26445 | 中压主汽门前蒸汽温度测点全坏 |  | digital
N1DCS.10LBB50EZ007_XK96 | 26446 | 热再热蒸汽温度保护 |  | digital
N1DCS.10LBC40FP001_REL1 | 26447 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP001_REL2 | 26448 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP001_XK20 | 26449 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP001_XK93 | 26450 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP001_XK94 | 26451 | 高排过热度＜20K |  | digital
N1DCS.10LBC40FP001_XK96 | 26452 | 高排过热度＜10K |  | digital
N1DCS.10LBC40FP101_REL1 | 26453 | Ovation Control Builder |  | digital
N1DCS.10LBC40FP101_XK20 | 26454 | Ovation Control Builder |  | digital
N1DCS.10LBC41AA051A | 26455 | 高排通风阀电磁阀1 |  | digital
N1DCS.10LBC41AA051A_A_OFF | 26456 | Ovation Control Builder |  | digital
N1DCS.10LBC41AA051A_A_ON | 26457 | Ovation Control Builder |  | digital
N1DCS.10LBC41AA051B | 26458 | 高排通风阀电磁阀2 |  | digital
N1DCS.10MAA11CL011 | 26459 | 高压主汽门油动机油盘液位 |  | digital
N1DCS.10MAA11CT121A_XM20 | 26460 | 高压主汽门内壁温度A坏点 |  | digital
N1DCS.10MAA11CT122A_XM20 | 26461 | 高压主汽门中壁温度A坏点 |  | digital
N1DCS.10MAA12CL011 | 26462 | 高压调门油动机油盘液位 |  | digital
N1DCS.10MAA12CT121A_XM20 | 26463 | 高压调节汽门内壁温度A坏点 |  | digital
N1DCS.10MAA12CT122A_XH52 | 26464 | 高压调节汽门中壁温度A(50%)<150 |  | digital
N1DCS.10MAA12CT122A_XM20 | 26465 | 高压调门中壁温度A（50%）坏点 |  | digital
N1DCS.10MAA12CT122A_XH54 | 26466 | Ovation Control Builder |  | digital
N1DCS.10MAA50CT131A_XM20 | 26467 | 高压缸内壁温度A（100%）坏点 |  | digital
N1DCS.10MAA50CT132A_XM20 | 26468 | 高压缸内壁温度A（50%）坏点 |  | digital
N1DCS.10MAA50CT141A_XM20 | 26469 | 高压缸外壁温（50%）坏点 |  | digital
N1DCS.10MAA50CT142A_XM20 | 26470 | 高压缸中壁温（50%）坏点 |  | digital
N1DCS.10MAA50CT143A_XM20 | 26471 | 高压缸内壁温（50%）坏点 |  | digital
N1DCS.10MAA50FT004A_DL12 | 26472 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT004A_DL13 | 26473 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT004A_DL23 | 26474 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT004A_XK20 | 26475 | 高压调节门后蒸汽温度测点全坏 |  | digital
N1DCS.10MAA50FT004A_XK93 | 26476 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_S/HTG+5 | 26477 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_S/HTG_20_A | 26478 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_S/HTG_20_B | 26479 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_TEMP_OK | 26480 | 高压缸壁温质量无坏点 |  | digital
N1DCS.10MAA50FT051_TEMPOK | 26481 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_XH02 | 26482 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_XV01 | 26483 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_XV02 | 26484 | 高压调节门后蒸汽温度过热度>0 |  | digital
N1DCS.10MAA50FT051_XV03 | 26485 | 高压缸壁温条件满足 |  | digital
N1DCS.10MAA50FT051_XV06 | 26486 |  |  | digital
N1DCS.10MAA50FT051_XV32 | 26487 | 高压缸内壁温条件满足 |  | digital
N1DCS.10MAA50FT051_XV51 | 26488 | 高压缸上中壁温条件满足 |  | digital
N1DCS.10MAA50FT051_XV52 | 26489 | 高压缸下中壁温条件满足 |  | digital
N1DCS.10MAA50FT051_XV54 | 26490 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV11 | 26491 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV12 | 26492 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV13 | 26493 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV21 | 26494 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV22 | 26495 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV23 | 26496 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV31 | 26497 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV32 | 26498 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV33 | 26499 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV41 | 26500 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV42 | 26501 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV43 | 26502 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_ZV53 | 26503 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT151_CT05_OK | 26504 | 高压缸上/下中壁温测点正常 |  | digital
N1DCS.10MAA50FT151_XM23 | 26505 | 上/下中壁温及调阀后压力测点ok |  | digital
N1DCS.10MAB11CL011 | 26506 | 中压主汽门油动机油盘液位 |  | digital
N1DCS.10MAB12CL011 | 26507 | 中压调门油动机油盘液位 |  | digital
N1DCS.10MAB50FT011A_DL12 | 26508 | Ovation Control Builder |  | digital
N1DCS.10MAB50FT011A_DL13 | 26509 | Ovation Control Builder |  | digital
N1DCS.10MAB50FT011A_DL23 | 26510 | Ovation Control Builder |  | digital
N1DCS.10MAB50FT011A_XK20 | 26511 | 中压内缸进汽口壁温无质量坏点 |  | digital
N1DCS.10MAB50FT011A_XK93 | 26512 | Ovation Control Builder |  | digital
N1DCS.10MAB50FT021_REL1 | 26513 | Ovation Control Builder |  | digital
N1DCS.10MAB50FT021_REL2 | 26514 | Ovation Control Builder |  | digital
N1DCS.10MAB50FT021_XK20 | 26515 | Ovation Control Builder |  | digital
N1DCS.10MAB50FT021_XK94 | 26516 | 中排过热度＜20K |  | digital
N1DCS.10MAB50FT021_XK96 | 26517 | 中排过热度＜10K |  | digital
N1DCS.10MAC01AA001A | 26518 | 低压缸喷水电磁阀1 |  | digital
N1DCS.10MAC01AA001A_ZV01 | 26519 | Ovation Control Builder |  | digital
N1DCS.10MAC01AA001A_ZV02 | 26520 | Ovation Control Builder |  | digital
N1DCS.10MAC01AA001A_ZV03 | 26521 | Ovation Control Builder |  | digital
N1DCS.10MAC01AA001A_ZV04 | 26522 | Ovation Control Builder |  | digital
N1DCS.10MAC01AA002A | 26523 | 低压缸喷水电磁阀2 |  | digital
N1DCS.10MAC10CT181A_XH01 | 26524 | Ovation Control Builder |  | digital
N1DCS.10MAC10CT181A_XH52 | 26525 | Ovation Control Builder |  | digital
N1DCS.10MAC10CT181A_XM20 | 26526 | Ovation Control Builder |  | digital
N1DCS.10MAC10CT182A_XH01 | 26527 | Ovation Control Builder |  | digital
N1DCS.10MAC10CT182A_XH52 | 26528 | Ovation Control Builder |  | digital
N1DCS.10MAC10CT182A_XM20 | 26529 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY041_XM71 | 26530 | #1径向轴承轴振通道X正常 |  | digital
N1DCS.10MAD11CY042_XM71 | 26531 | #1径向轴承轴振通道Y OK |  | digital
N1DCS.10MAD11CY141_MAX1 | 26532 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY141_MAX2 | 26533 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY141_XH01 | 26534 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY141_XH03 | 26535 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY141_XM71 | 26536 | #1径向轴承轴振通道X正常 |  | digital
N1DCS.10MAD11CY141_XM72 | 26537 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY141_XV20 | 26538 | #1轴瓦轴振X通道故障 |  | digital
N1DCS.10MAD11CY142_MAX1 | 26539 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY142_MAX2 | 26540 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY142_XH01 | 26541 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY142_XH03 | 26542 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY142_XM71 | 26543 | #1径向轴承轴振通道Y OK |  | digital
N1DCS.10MAD11CY142_XM72 | 26544 | Ovation Control Builder |  | digital
N1DCS.10MAD11CY142_XV20 | 26545 | #1轴瓦轴振Y通道故障 |  | digital
N1DCS.10MAD11EZ141_XK93 | 26546 | #1轴承转子振动测量存在故障 |  | digital
N1DCS.10MAD11EZ141_XK94 | 26547 | #1轴承转子振动＞83um |  | digital
N1DCS.10MAD11EZ141_XK96 | 26548 | #1轴承转子振动＞130um |  | digital
N1DCS.10MAD12CY041_XM71 | 26549 | #2径向轴承轴振通道X正常 |  | digital
N1DCS.10MAD12CY042_XM71 | 26550 | #2径向轴承轴振通道Y OK |  | digital
N1DCS.10MAD12CY141_MAX1 | 26551 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY141_MAX2 | 26552 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY141_XH01 | 26553 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY141_XH03 | 26554 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY141_XM71 | 26555 | #2径向轴承轴振通道X正常 |  | digital
N1DCS.10MAD12CY141_XM72 | 26556 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY141_XV20 | 26557 | #2轴瓦轴振X通道故障 |  | digital
N1DCS.10MAD12CY142_MAX1 | 26558 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY142_MAX2 | 26559 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY142_XH01 | 26560 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY142_XH03 | 26561 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY142_XM71 | 26562 | #2径向轴承轴振通道Y OK |  | digital
N1DCS.10MAD12CY142_XM72 | 26563 | Ovation Control Builder |  | digital
N1DCS.10MAD12CY142_XV20 | 26564 | #2轴瓦Y向轴振通道故障 |  | digital
N1DCS.10MAD12CY145_XM71 | 26565 | 膨胀通道OK |  | digital
N1DCS.10MAD12EZ141_XK93 | 26566 | #2轴承转子振动测量存在故障 |  | digital
N1DCS.10MAD12EZ141_XK94 | 26567 | #2轴承转子振动＞83um |  | digital
N1DCS.10MAD12EZ141_XK96 | 26568 | #2轴承转子振动＞130um |  | digital
N1DCS.10MAD13CY041_XM71 | 26569 | #3径向轴承轴振通道X正常 |  | digital
N1DCS.10MAD13CY042_XM71 | 26570 | #3径向轴承轴振通道Y OK |  | digital
N1DCS.10MAD13CY141_MAX1 | 26571 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY141_MAX2 | 26572 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY141_XH01 | 26573 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY141_XH03 | 26574 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY141_XM71 | 26575 | #3径向轴承轴振通道X正常 |  | digital
N1DCS.10MAD13CY141_XM72 | 26576 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY141_XV20 | 26577 | #3轴瓦轴振X通道故障 |  | digital
N1DCS.10MAD13CY142_MAX1 | 26578 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY142_MAX2 | 26579 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY142_XH01 | 26580 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY142_XH03 | 26581 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY142_XM71 | 26582 | #3径向轴承轴振通道Y OK |  | digital
N1DCS.10MAD13CY142_XM72 | 26583 | Ovation Control Builder |  | digital
N1DCS.10MAD13CY142_XV20 | 26584 | #3轴瓦轴振Y通道故障 |  | digital
N1DCS.10MAD13EZ141_XK93 | 26585 | #3轴承转子振动测量存在故障 |  | digital
N1DCS.10MAD13EZ141_XK94 | 26586 | #3轴承转子振动＞83um |  | digital
N1DCS.10MAD13EZ141_XK96 | 26587 | #3轴承转子振动＞130um |  | digital
N1DCS.10MAV51AA012VO | 26588 | 盘车三通阀（220VAC） |  | digital
N1DCS.10MAY01EP144_FAST | 26589 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP145_FAST | 26590 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_CV | 26591 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_ESV | 26592 | 高主门上升温度裕度<最小裕度 |  | digital
N1DCS.10MAY01EP150_HPC | 26593 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_HPS | 26594 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_IPS | 26595 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_RSTF | 26596 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_RSTN | 26597 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_RSTS | 26598 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_XH04 | 26599 | 上升温度裕度>20℃ |  | digital
N1DCS.10MAY01EP150_XH06 | 26600 | 上升温度裕度>30℃ |  | digital
N1DCS.10MAY01EP150_XH09 | 26601 | 高主/高调上升温度裕度大于2.5 |  | digital
N1DCS.10MAY01EP150_XH52 | 26602 | 最小上升温度裕度<0 |  | digital
N1DCS.10MAY01EP150_XH54 | 26603 | 最小上升温度裕度<15 |  | digital
N1DCS.10MAY01EP150_XH55 | 26604 | 最小下降温度裕度<2 |  | digital
N1DCS.10MAY01EP150_XH57 | 26605 | 最小下降温度裕度<0 |  | digital
N1DCS.10MAY01EP150_XM01 | 26606 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP150_XT01 | 26607 | 热应力测点异常 |  | digital
N1DCS.10MAY01EP150_XT21 | 26608 | Margin Mode Fast |  | digital
N1DCS.10MAY01EP150_XT22 | 26609 | Margin Mode Normal |  | digital
N1DCS.10MAY01EP150_XT23 | 26610 | Margin Mode Slow |  | digital
N1DCS.10MAY01EP151_XT01 | 26611 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP151_XT06 | 26612 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP151_XT07 | 26613 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP151_XT16 | 26614 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP151_XT17 | 26615 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP151_XT24 | 26616 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP151_XT25 | 26617 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP151_XTOR | 26618 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP152_XT01 | 26619 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP152_XT06 | 26620 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP152_XT07 | 26621 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP152_XT16 | 26622 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP152_XT17 | 26623 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP152_XT24 | 26624 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP152_XT25 | 26625 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP153_XT01 | 26626 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP153_XT06 | 26627 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP153_XT07 | 26628 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP153_XT16 | 26629 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP153_XT17 | 26630 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP153_XT24 | 26631 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP153_XT25 | 26632 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_DPSIM | 26633 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_STSIM | 26634 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_TGFH | 26635 | 高压转子温度3>610℃ |  | digital
N1DCS.10MAY01EP154_TGFL | 26636 | 高压转子温度3<10℃ |  | digital
N1DCS.10MAY01EP154_TSFH | 26637 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_TSFL | 26638 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_TSFTH | 26639 | 高压转子温度2>610℃ |  | digital
N1DCS.10MAY01EP154_TSFTL | 26640 | 高压转子温度2<10℃ |  | digital
N1DCS.10MAY01EP154_XH01 | 26641 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XH05 | 26642 | 高压转子温度3大于200℃ |  | digital
N1DCS.10MAY01EP154_XH07 | 26643 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XH08 | 26644 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XH53 | 26645 | 高压转子温度3<400℃ |  | digital
N1DCS.10MAY01EP154_XK20F | 26646 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XT01 | 26647 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XT02 | 26648 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XT06 | 26649 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XT07 | 26650 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XT16 | 26651 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XT17 | 26652 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XT24 | 26653 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP154_XT25 | 26654 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_DPSIM | 26655 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_STSIM | 26656 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_TGFH | 26657 | 高压转子温度3>610℃ |  | digital
N1DCS.10MAY01EP155_TGFL | 26658 | 高压转子温度3<10℃ |  | digital
N1DCS.10MAY01EP155_TSFH | 26659 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_TSFL | 26660 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_TSFTH | 26661 | 高压转子温度2>610℃ |  | digital
N1DCS.10MAY01EP155_TSFTL | 26662 | 高压转子温度2<10℃ |  | digital
N1DCS.10MAY01EP155_XH02 | 26663 | 中压转子温度2>20℃ |  | digital
N1DCS.10MAY01EP155_XH03 | 26664 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XH05 | 26665 | 中压转子温度3>200℃ |  | digital
N1DCS.10MAY01EP155_XH11 | 26666 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XH57 | 26667 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XK20F | 26668 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XT01 | 26669 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XT02 | 26670 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XT06 | 26671 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XT07 | 26672 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XT16 | 26673 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XT17 | 26674 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XT24 | 26675 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP155_XT25 | 26676 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP181_MINLO | 26677 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP181_S | 26678 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP181_STOP | 26679 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP182_MINLO | 26680 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP182_S | 26681 | Ovation Control Builder |  | digital
N1DCS.10MAY01EP182_STOP | 26682 | Ovation Control Builder |  | digital
N1DCS.10MAY01EZ011_XK46 | 26683 | 汽机遮断系统已遮断1 |  | digital
N1DCS.10MAY01EZ011_XK47 | 26684 | 汽机遮断系统已遮断2 |  | digital
N1DCS.10MAY10FT000_XM20 | 26685 | X准则计算故障 |  | digital
N1DCS.10MAY10FT001_XH02 | 26686 | 满足热应力准则X1 |  | digital
N1DCS.10MAY10FT001_XM20 | 26687 | 热应力准则X1故障 |  | digital
N1DCS.10MAY10FT002_XH51 | 26688 | 满足热应力准则X2 |  | digital
N1DCS.10MAY10FT002_XM20 | 26689 | 热应力准则X2故障 |  | digital
N1DCS.10MAY10FT004_XH02 | 26690 | 满足热应力准则X4 |  | digital
N1DCS.10MAY10FT004_XH52 | 26691 | Ovation Control Builder |  | digital
N1DCS.10MAY10FT004_XM20 | 26692 | 热应力准则X4故障 |  | digital
N1DCS.10MAY10FT005_XH02 | 26693 | 满足热应力准则X5 |  | digital
N1DCS.10MAY10FT005_XM20 | 26694 | 热应力准则X5故障 |  | digital
N1DCS.10MAY10FT006_XH02 | 26695 | 满足热应力准则X6 |  | digital
N1DCS.10MAY10FT006_XM20 | 26696 | 热应力准则X6故障 |  | digital
N1DCS.10MAY10FT007A_XH51 | 26697 | 满足热应力准则X7_A |  | digital
N1DCS.10MAY10FT007A_XM20 | 26698 | 热应力准则X7_A故障 |  | digital
N1DCS.10MAY10FT007B_XH51 | 26699 | 满足热应力准则X7_B |  | digital
N1DCS.10MAY10FT007B_XM20 | 26700 | 热应力准则X7_B故障 |  | digital
N1DCS.10MAY10FT008_XH51 | 26701 | 满足热应力准则X8 |  | digital
N1DCS.10MAY10FT008_XM20 | 26702 | 热应力准则X8故障 |  | digital
N1DCS.10MAY10FT010_XM20 | 26703 | Z准则计算故障 |  | digital
N1DCS.10MAY10FT011_XH02 | 26704 | 满足热应力准则Z1-CRIT |  | digital
N1DCS.10MAY10FT011_XM20 | 26705 | Z1准则计算故障 |  | digital
N1DCS.10MAY10FT012_XH02 | 26706 | 满足热应力准则Z2-CRIT |  | digital
N1DCS.10MAY10FT012_XM20 | 26707 | Z2准则计算故障 |  | digital
N1DCS.10MAY10FT013_XH02 | 26708 | 满足热应力准则Z3-CRIT |  | digital
N1DCS.10MAY10FT013_XH52 | 26709 | 高压主汽门前蒸汽过热度<15 |  | digital
N1DCS.10MAY10FT013_XM20 | 26710 | Z3准则计算故障 |  | digital
N1DCS.10MAY10FT014_XH02 | 26711 | 满足热应力准则Z4-CRIT |  | digital
N1DCS.10MAY10FT014_XH04 | 26712 | 中压主汽门前蒸汽过热度>10℃ |  | digital
N1DCS.10MAY10FT014_XH52 | 26713 | 中压主汽门前蒸汽过热度<20℃ |  | digital
N1DCS.10MAY10FT014_XM20 | 26714 | Z4准则计算故障 |  | digital
N1DCS.10MAY10FT015_XH02 | 26715 | 满足热应力准则Z5-CRIT |  | digital
N1DCS.10MAY10FT015_XM20 | 26716 | Z5准则计算故障 |  | digital
N1DCS.10MKD11CY041_XM71 | 26717 | #1汽轮发电机轴承轴振通道X正常 |  | digital
N1DCS.10MKD11CY042_XM71 | 26718 | #1汽轮发电机轴承轴振通道Y正常 |  | digital
N1DCS.10MKD11CY141_MAX1 | 26719 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY141_MAX2 | 26720 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY141_XH01 | 26721 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY141_XH03 | 26722 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY141_XM71 | 26723 | #1汽轮发电机轴承轴振通道X正常 |  | digital
N1DCS.10MKD11CY141_XM72 | 26724 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY141_XV20 | 26725 | #4轴瓦轴振X通道故障 |  | digital
N1DCS.10MKD11CY142_MAX1 | 26726 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY142_MAX2 | 26727 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY142_XH01 | 26728 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY142_XH03 | 26729 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY142_XM71 | 26730 | #1汽轮发电机轴承轴振通道Y正常 |  | digital
N1DCS.10MKD11CY142_XM72 | 26731 | Ovation Control Builder |  | digital
N1DCS.10MKD11CY142_XV20 | 26732 | #4轴瓦轴振Y通道故障 |  | digital
N1DCS.10MKD11EZ141_XK93 | 26733 | 发电机后轴承转子振动测量故障 |  | digital
N1DCS.10MKD11EZ141_XK94 | 26734 | 发电机后轴承转子振动＞83um |  | digital
N1DCS.10MKD11EZ141_XK96 | 26735 | 发电机后轴承转子振动>130μm |  | digital
N1DCS.10MKD12CY041_XM71 | 26736 | #2汽轮发电机轴承轴振通道X正常 |  | digital
N1DCS.10MKD12CY042_XM71 | 26737 | #2汽轮发电机轴承轴振通道Y正常 |  | digital
N1DCS.10MKD12CY141_MAX1 | 26738 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY141_MAX2 | 26739 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY141_XH01 | 26740 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY141_XH03 | 26741 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY141_XM71 | 26742 | #2汽轮发电机轴承轴振通道X正常 |  | digital
N1DCS.10MKD12CY141_XM72 | 26743 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY141_XV20 | 26744 | #5轴瓦轴振X通道故障 |  | digital
N1DCS.10MKD12CY142_MAX1 | 26745 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY142_MAX2 | 26746 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY142_XH01 | 26747 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY142_XH03 | 26748 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY142_XM71 | 26749 | #2汽轮发电机轴承轴振通道Y正常 |  | digital
N1DCS.10MKD12CY142_XM72 | 26750 | Ovation Control Builder |  | digital
N1DCS.10MKD12CY142_XV20 | 26751 | #5轴瓦轴振Y通道故障 |  | digital
N1DCS.10MKD12EZ141_XK93 | 26752 | 励磁机后轴承转子振动测量故障 |  | digital
N1DCS.10MKD12EZ141_XK94 | 26753 | 励磁机后轴承转子振动＞83um |  | digital
N1DCS.10MKD12EZ141_XK96 | 26754 | 励磁机后轴承转子振动>130μm |  | digital
N1DCS.11CJA00EA001_XS53 | 26755 | DCS启动DEH启动顺控 |  | digital
N1DCS.11CJA00EA001_XS54 | 26756 | DCS启动DEH停机顺控 |  | digital
N1DCS.PK1_NORM | 26757 | Ovation Control Builder |  | digital
N1DCS.PK2_SLOW | 26758 | Ovation Control Builder |  | digital
N1DCS.PK3_FAST | 26759 | Ovation Control Builder |  | digital
N1DCS.10MAA50FT051_S/HTG_5 | 26760 | Ovation Control Builder |  | digital
N1DCS.10MAY01DU100_3TO1 | 26761 | Ovation Control Builder |  | digital
N1DCS.CANCEL160 | 26762 |  |  | digital
N1DCS.CANCEL180 | 26763 |  |  | digital
N1DCS.CANCEL200 | 26764 |  |  | digital
N1DCS.CANCEL201 | 26765 |  |  | digital
N1DCS.CANCEL211 | 26766 |  |  | digital
N1DCS.CANCEL212 | 26767 |  |  | digital
N1DCS.CANCEL213 | 26768 |  |  | digital
N1DCS.10LBA10AA402_LP | 26769 | #1机高压主汽母管疏水气动门1 |  | digital
N1DCS.10LBA10AA404_LP | 26770 | #1机高压主汽母管疏水气动门2 |  | digital
N1DCS.10LBA20AA402_LP | 26771 | #1机低压主汽门前疏水气动门 |  | digital
N1DCS.10LBA20AA406_LP | 26772 | #1机低压主汽母管疏水气动门 |  | digital
N1DCS.10LBA20CP_LP | 26773 | #1机低压蒸汽母管压力 |  | digital
N1DCS.10LBB10AA402_LP | 26774 | #1机高温再热蒸汽母管疏水气动门 |  | digital
N1DCS.10LBB10AA404_LP | 26775 | #1机中旁阀前疏水气动门 |  | digital
N1DCS.10LBB10CP_LP | 26776 | #1机高温再热蒸汽压力 |  | digital
N1DCS.10LBC10AA001_LP | 26777 | #1机高排逆止门 |  | digital
N1DCS.10LBC10AA404_LP | 26778 | #1机高排逆止门后疏水气动门 |  | digital
N1DCS.10LBC10AA406_LP | 26779 | #1机冷再疏水气动门 |  | digital
N1DCS.10LBH10AA402_LP | 26780 | #1机高排通风阀前疏水气动门 |  | digital
N1DCS.10MAL65AA051_LP | 26781 | #1机高排逆止门前疏水气动门 |  | digital
N1DCS.10MAN10AA001_LP | 26782 | #1机高旁减温水气动隔离门 |  | digital
N1DCS.10MAN10AA101_MODE | 26783 | #1机高旁阀 |  | digital
N1DCS.10MAN10AA102_MODE | 26784 | #1机高旁减温水调节阀 |  | digital
N1DCS.10MAN10CP_LP | 26785 | #1机高旁阀后蒸汽压力 |  | digital
N1DCS.10MAN10CT_LP | 26786 | #1机高旁阀后蒸汽温度 |  | digital
N1DCS.10MAN10GH001R1_LP | 26787 | #1机高压旁路油站#1油泵 |  | digital
N1DCS.10MAN10GH001R2_LP | 26788 | #1机高压旁路油站#2油泵 |  | digital
N1DCS.10MAN20AA101_MODE | 26789 | #1机中旁阀 |  | digital
N1DCS.10MAN20CP_LP | 26790 | #1机中旁阀后蒸汽压力 |  | digital
N1DCS.10MAN20CT_LP | 26791 | #1机中旁阀后蒸汽温度 |  | digital
N1DCS.10MAN20GH001R1_LP | 26792 | #1机中低压旁路油站#1油泵 |  | digital
N1DCS.10MAN20GH001R2_LP | 26793 | #1机中低压旁路油站#2油泵 |  | digital
N1DCS.10MAP10AA101_MODE | 26794 | #1机低旁阀 |  | digital
N1DCS.10MAP10AA404_LP | 26795 | #1机低旁阀前疏水气动门 |  | digital
N1DCS.10MAP10CP_LP | 26796 | #1机低旁阀后蒸汽压力 |  | digital
N1DCS.10MAP10CT_LP | 26797 | #1机低旁阀后蒸汽温度 |  | digital
N1DCS.HOILSTNOILP_BYLP | 26798 | #1机高压旁路油站油泵 |  | digital
N1DCS.ILOILSTNOILP_BYLP | 26799 | #1机中低压旁路油站油泵 |  | digital
N1DCS.TURBDRNHPCP_LP1 | 26800 | #1机高压疏水阀组1关闭状态 |  | digital
N1DCS.TURBDRNHPCP_LP2 | 26801 | #1机高压疏水阀组2关闭状态 |  | digital
N1DCS.TURBDRNHPOP_LP1 | 26802 | #1机高压疏水阀组1打开状态 |  | digital
N1DCS.TURBDRNHPOP_LP2 | 26803 | #1机高压疏水阀组2打开状态 |  | digital
N1DCS.TURBDRNIPCP_LP | 26804 | #1机中压疏水阀组关闭状态 |  | digital
N1DCS.TURBDRNIPOP_LP | 26805 | #1机中压疏水阀组打开状态 |  | digital
N1DCS.TURBDRNLPCP_LP | 26806 | #1机低压疏水阀组关闭状态 |  | digital
N1DCS.TURBDRNLPOP_LP | 26807 | #1机低压疏水阀组打开状态 |  | digital
N1DCS.DCSETSTP | 26808 | ETS跳闸条件画面显示 |  | int32
N1DCS.GTLOADMODE1 | 26809 | #2机负荷设定方式 |  | digital
N1DCS.LOADGOHOLD1 | 26810 | 机组总负荷增闭锁信号 |  | digital
N1DCS.LOADSPMODE1 | 26811 | 机组总负荷设定方式 |  | digital
N1DCS.RB_TRIP | 26812 | #2机RB动作 |  | digital
N1DCS.STTRIPLP | 26813 | #1机跳闸信号 |  | digital
N1DCS.STTRIPTAGLP | 26814 | 锅炉联跳汽机保护解除信号 |  | digital
N1DCS.10LBD20AA001_LP | 26815 | #1机冷再供热电动门 |  | digital
N1DCS.10LBD20AA002_LP | 26816 | #1机冷再供热逆止门后电动门 |  | digital
N1DCS.10LBD20AA402_LP | 26817 | #1机冷再供热母管气动疏水门 |  | digital
N1DCS.10LBD20AC001MODE | 26818 | #1机冷再供热减温减压器 |  | digital
N1DCS.10LBD40AA001_LP | 26819 | #1机热再供热电动门 |  | digital
N1DCS.10LBD40AA002_LP | 26820 | #1机热再供热逆止门后电动门 |  | digital
N1DCS.10LBD40AA402_LP | 26821 | #1机热再供热母管气动疏水门 |  | digital
N1DCS.10LBD40AC001MODE | 26822 | #1机热再供热减温减压器 |  | digital
N1DCS.10LBD60AA001_LP | 26823 | #1机供热母管电动门 |  | digital
N1DCS.10LBD80AA001_LP | 26824 | #1机冷再抽汽至预留中压电动门 |  | digital
N1DCS.10LBD80AA402_LP | 26825 | 冷再抽汽至预留中压管道疏水门 |  | digital
N1DCS.10LBG11AA007_LP | 26826 | #1机高排至辅汽母管供汽电动门 |  | digital
N1DCS.10LBG11AC001MODE | 26827 | 高排至辅汽母管供汽减温减压器 |  | digital
N1DCS.10LBG21AA001_LP | 26828 | 辅汽母管至#1机轴封供汽电动门 |  | digital
N1DCS.10LBG22AA001_LP | 26829 | 辅汽至#1机蒸汽喷射装置电动门 |  | digital
N1DCS.10LCE11AA001_LP | 26830 | #1机凝结水至辅汽减温水电动门 |  | digital
N1DCS.10LCE11AA101MODE | 26831 | #1机凝结水至辅汽减温水电动调阀 |  | digital
N1DCS.10LCE12AA001_LP | 26832 | #1机凝结水至低旁减温水气动门 |  | digital
N1DCS.10LCE12AA101_MODE | 26833 | #1机凝结水至低旁减温水调节阀 |  | digital
N1DCS.10LCE13AA001_LP | 26834 | #1机凝结水至热再减温水电动门 |  | digital
N1DCS.10LCE13AA101MODE | 26835 | #1机凝结水至热再减温水电动调阀 |  | digital
N1DCS.10LCE15AA001_LP | 26836 | #1机凝结水至中旁减温水气动门 |  | digital
N1DCS.10LCE15AA101_MODE | 26837 | #1机凝结水至中旁减温水调节阀 |  | digital
N1DCS.10LCE17AA001_LP | 26838 | #1机凝结水至冷再减温水电动门 |  | digital
N1DCS.10LCE17AA101MODE | 26839 | #1机凝结水至冷再减温水电动调阀 |  | digital
N1DCS.10LCE18AA152MODE | 26840 | #1机凝结水至轴封减温水气动调阀 |  | digital
N1DCS.10LCE19AA101_LP | 26841 | 凝结水至凝汽器水幕喷水气动阀 |  | digital
N1DCS.10LCE19AA101MODE | 26842 | 凝结水至凝汽器水幕喷水气动调阀 |  | digital
N1DCS.10LCE20AA101MODE | 26843 | 凝结水至疏水扩容器减温水调节阀 |  | digital
N1DCS.10MAL22AA051_LP | 26844 | #1机高压缸气动疏水门1 |  | digital
N1DCS.10MAL22AA053_LP | 26845 | #1机高压缸气动疏水门2 |  | digital
N1DCS.10MAL22AA054_LP | 26846 | #1机高压缸气动疏水门3 |  | digital
N1DCS.10MAL35AA051_LP | 26847 | 中压缸气动疏水门1 |  | int32
N1DCS.10MAL36AA051_LP | 26848 | 中压缸气动疏水门2 |  | int32
N1DCS.10MAL50AA051_LP | 26849 | 低压缸气动疏水门 |  | int32
N1DCS.10MAW10AA151MODE | 26850 | 辅汽至#1机高、中压轴封气动调阀 |  | digital
N1DCS.10MAW13AA151MODE | 26851 | 辅汽至#1机低压轴封气动调节阀 |  | digital
N1DCS.10MAW50AA151MODE | 26852 | #1机轴封供汽溢流阀 |  | digital
N1DCS.10MAW65AA051_LP | 26853 | 高压缸轴封漏汽至中压缸气动门 |  | digital
N1DCS.10MAW65AA052_LP | 26854 | 高压缸轴封漏汽至低压后缸气动门 |  | digital
N1DCS.10MAW80AN001_LP | 26855 | #1机#1轴封风机 |  | digital
N1DCS.10MAW80AN002_LP | 26856 | #1机#2轴封风机 |  | digital
N1DCS.AUXSTMSYS_SEQST | 26857 | 辅汽系统启顺控 |  | digital
N1DCS.AUXSTMSYS_SEQSTAUX | 26858 | 辅汽系统启顺控辅助点 |  | digital
N1DCS.AUXSTMSYS_SEQSTAUX0 | 26859 | 辅汽系统启顺控启允许条件 |  | digital
N1DCS.AUXSTMSYS_SEQSTAUX1 | 26860 | 辅汽系统启顺控第1步完成条件 |  | digital
N1DCS.AUXSTMSYS_SEQSTAUX2 | 26861 | 辅汽系统启顺控第2步完成条件 |  | digital
N1DCS.AUXSTMSYS_SEQSTAUX3 | 26862 | 辅汽系统启顺控第3步完成条件 |  | digital
N1DCS.AUXSTMSYS_SEQSTLP | 26863 | 辅汽系统启顺控状态 |  | digital
N1DCS.GLDCLREGF_BYLP | 26864 | #1机轴封风机 |  | digital
N1DCS.GLDSTMSYS_SEQSP | 26865 | 轴封系统停顺控 |  | digital
N1DCS.GLDSTMSYS_SEQSPAUX | 26866 | 轴封系统停顺控辅助点 |  | digital
N1DCS.GLDSTMSYS_SEQSPAUX0 | 26867 | 轴封系统停顺控启允许条件 |  | digital
N1DCS.GLDSTMSYS_SEQSPAUX1 | 26868 | 轴封系统停顺控第1步完成条件 |  | digital
N1DCS.GLDSTMSYS_SEQSPAUX2 | 26869 | 轴封系统停顺控第2步完成条件 |  | digital
N1DCS.GLDSTMSYS_SEQSPAUX3 | 26870 | 轴封系统停顺控第3步完成条件 |  | digital
N1DCS.GLDSTMSYS_SEQSPLP | 26871 | 轴封系统停顺控状态 |  | digital
N1DCS.GLDSTMSYS_SEQST | 26872 | 轴封系统启顺控 |  | digital
N1DCS.GLDSTMSYS_SEQSTAUX | 26873 | 轴封系统启顺控辅助点 |  | digital
N1DCS.GLDSTMSYS_SEQSTAUX0 | 26874 | 轴封系统启顺控启允许条件 |  | digital
N1DCS.GLDSTMSYS_SEQSTAUX1 | 26875 | 轴封系统启顺控第1步完成条件 |  | digital
N1DCS.GLDSTMSYS_SEQSTAUX2 | 26876 | 轴封系统启顺控第2步完成条件 |  | digital
N1DCS.GLDSTMSYS_SEQSTAUX3 | 26877 | 轴封系统启顺控第3步完成条件 |  | digital
N1DCS.GLDSTMSYS_SEQSTAUX4 | 26878 | 轴封系统启顺控第4步完成条件 |  | digital
N1DCS.GLDSTMSYS_SEQSTLP | 26879 | 轴封系统启顺控状态 |  | digital
N1DCS.J0LBG10CP_LP | 26880 | 辅汽母管压力 |  | digital
N1DCS.J0LBG10CT_LP | 26881 | 辅汽母管温度 |  | digital
N1DCS.10LCM40AA403_LP | 26882 | #1机#1疏水泵出口真空电动门 |  | digital
N1DCS.10LCM40AA406_LP | 26883 | #1机#2疏水泵出口真空电动门 |  | digital
N1DCS.10LCM40AA407_LP | 26884 | 疏水扩容器放水至凝泵坑电动门 |  | digital
N1DCS.10LCM40AP001_LP | 26885 | #1机#1疏水泵 |  | digital
N1DCS.10LCM40AP002_LP | 26886 | #1机#2疏水泵 |  | digital
N1DCS.GLDSTMSYS_SEQSTAUX5 | 26887 | 轴封系统启顺控第5步完成条件 |  | digital
N1DCS.SHUSHUIPMP_BYLP | 26888 | #1机疏水泵 |  | digital
N1DCS.10LCA11AA001_LP | 26889 | #1机#1凝结水泵进口真空电动门 |  | digital
N1DCS.10LCA11AA003_LP | 26890 | #1机#1凝结水泵出口真空电动门 |  | digital
N1DCS.10LCA30AA101MODE | 26891 | #1机凝结水再循环气动调节阀 |  | digital
N1DCS.10LCA40AA002_LP | 26892 | #1机凝结水无压放水电动门 |  | digital
N1DCS.10LCB11AP001_LP | 26893 | #1机#1凝结水泵 |  | digital
N1DCS.10LCB11GH001_MODE | 26894 | #1机#1凝结水泵永磁控制器 |  | digital
N1DCS.10LCE01AA001_LP | 26895 | #1机凝结水杂用水母管电动门 |  | digital
N1DCS.10LCE16AA101MODE | 26896 | 凝结水至闭式水箱补水电动调节阀 |  | digital
N1DCS.10LCR10AA001_LP | 26897 | 第一套机组除盐水补水电动门 |  | digital
N1DCS.10LCR10AA101MODE | 26898 | #1机凝汽器正常补水电动调节阀 |  | digital
N1DCS.10LCR10AA102MODE | 26899 | #1机凝汽器启动补水电动调节阀 |  | digital
N1DCS.10LCR14AA001_LP | 26900 | 除盐水至#1机闭式水箱注水电动门 |  | digital
N1DCS.10PAB11AA001_LP | 26901 | #1机凝汽器循环水进水#1电动门 |  | digital
N1DCS.10PAB21AA001_LP | 26902 | #1机凝汽器循环水#1出水电动门 |  | digital
N1DCS.10PAH11AA002_LP | 26903 | #1机凝汽器#1胶球泵出口电动门 |  | digital
N1DCS.10PAH11AP001_LP | 26904 | #1机凝汽器#1胶球泵 |  | digital
N1DCS.10PAH11AT001_LP | 26905 | #1机凝汽器#1收球网 |  | digital
N1DCS.10PAH11BB001_LP | 26906 | #1机凝汽器#1装球室 |  | digital
N1DCS.10PCB10AA001_LP | 26907 | #1机开式水电动过滤器进水电动门 |  | digital
N1DCS.10PCB10AA002_LP | 26908 | #1机开式水电动过滤器出水电动门 |  | digital
N1DCS.10PCB10AA003_LP | 26909 | #1机开式水电动过滤器旁路电动门 |  | digital
N1DCS.10PCB10GH501_LP | 26910 | #1机开式水电动过滤器 |  | digital
N1DCS.10PCB11AA001_LP | 26911 | #1机#1开式冷却水泵进口电动门 |  | digital
N1DCS.10PCB11AA002_LP | 26912 | #1机#1开式冷却水泵出口电动门 |  | digital
N1DCS.10PCB11AP001_LP | 26913 | #1机#1开式冷却水泵 |  | digital
N1DCS.10PCB13AA011_LP | 26914 | #1真空泵冷却器开式水进水电动门 |  | digital
N1DCS.10PCB21AA001_LP | 26915 | #1热交换器开式冷却水进水电动门 |  | digital
N1DCS.10PCB23AA011_LP | 26916 | #1真空泵冷却器开式水出水电动门 |  | digital
N1DCS.10PCB31AA001_LP | 26917 | #1热交换器开式冷却水出水电动门 |  | digital
N1DCS.10PGA11AA001_LP | 26918 | #1机#1闭式冷却水泵进口电动门 |  | digital
N1DCS.10PGA11AA003_LP | 26919 | #1机#1闭式冷却水泵出口电动门 |  | digital
N1DCS.10PGA11AP001_LP | 26920 | #1机#1闭式冷却水泵 |  | digital
N1DCS.10PGA21AA001_LP | 26921 | #1热交换器闭式水进口电动门 |  | digital
N1DCS.10PGA21AA002_LP | 26922 | #1热交换器闭式水出口电动门 |  | digital
N1DCS.CIRWTR_SEQST | 26923 | 开式冷却水系统启顺控 |  | digital
N1DCS.CLCLGPMP_BYLP | 26924 | #1机闭式冷却水泵 |  | digital
N1DCS.CLCLGPMPA_PMTLP | 26925 | #1机闭式冷却水泵启允许条件 |  | digital
N1DCS.CLCLGPMPA_SEQSP | 26926 | #1闭式水泵停顺控 |  | digital
N1DCS.CLCLGPMPA_SEQSPAUX | 26927 | #1闭式水泵停顺控辅助点 |  | digital
N1DCS.CLCLGPMPA_SEQSPAUX0 | 26928 | #1闭式水泵停顺控启允许条件 |  | digital
N1DCS.CLCLGPMPA_SEQSPAUX1 | 26929 | #1闭式水泵停顺控第1步完成条件 |  | digital
N1DCS.CLCLGPMPA_SEQSPAUX2 | 26930 | #1闭式水泵停顺控第2步完成条件 |  | digital
N1DCS.CLCLGPMPA_SEQSPLP | 26931 | #1闭式水泵停顺控状态 |  | digital
N1DCS.CLCLGPMPA_SEQST | 26932 | #1闭式水泵启顺控 |  | digital
N1DCS.CLCLGPMPA_SEQSTAUX | 26933 | #1闭式水泵启顺控辅助点 |  | digital
N1DCS.CLCLGPMPA_SEQSTAUX0 | 26934 | #1闭式水泵启顺控启允许条件 |  | digital
N1DCS.CLCLGPMPA_SEQSTAUX1 | 26935 | #1闭式水泵启顺控第1步完成条件 |  | digital
N1DCS.CLCLGPMPA_SEQSTAUX2 | 26936 | #1闭式水泵启顺控第2步完成条件 |  | digital
N1DCS.CLCLGPMPA_SEQSTAUX3 | 26937 | #1闭式水泵启顺控第3步完成条件 |  | digital
N1DCS.CLCLGPMPA_SEQSTLP | 26938 | #1闭式水泵启顺控状态 |  | digital
N1DCS.CLCLGPMPA_TRIP | 26939 | #1闭式水泵跳闸条件 |  | digital
N1DCS.CLCLGPMPA_TRIPTAG | 26940 | #1闭式水泵跳闸条件解除信号 |  | digital
N1DCS.CLCLGWTR_SEQST | 26941 | 闭式水系统启顺控 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX | 26942 | 闭式水系统启顺控辅助点 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX0 | 26943 | 闭式水系统启顺控启允许条件 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX1 | 26944 | 闭式水系统启顺控第1步完成条件 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX2 | 26945 | 闭式水系统启顺控第2步完成条件 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX3 | 26946 | 闭式水系统启顺控第3步完成条件 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX4 | 26947 | 闭式水系统启顺控第4步完成条件 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX5 | 26948 | 闭式水系统启顺控第5步完成条件 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX6 | 26949 | 闭式水系统启顺控第6步完成条件 |  | digital
N1DCS.CLCLGWTR_SEQSTAUX7 | 26950 | 闭式水系统启顺控第7步完成条件 |  | digital
N1DCS.CLCLGWTR_SEQSTLP | 26951 | 闭式水系统启顺控状态 |  | digital
N1DCS.CLCLGWTR_SEQSTOK | 26952 | 闭式水系统启顺控第8步完成条件 |  | digital
N1DCS.CNDHWLVL_LP | 26953 | #1机凝汽器热井液位 |  | digital
N1DCS.CNDPA_SEQSP | 26954 | #1机#1凝结水泵停顺控 |  | digital
N1DCS.CNDPA_SEQSPAUX | 26955 | #1机#1凝结水泵停顺控辅助点 |  | digital
N1DCS.CNDPA_SEQSPAUX1 | 26956 | #1凝结水泵停顺控第1步完成条件 |  | digital
N1DCS.CNDPA_SEQSPAUX2 | 26957 | #1凝结水泵停顺控第2步完成条件 |  | digital
N1DCS.CNDPA_SEQSPAUX3 | 26958 | #1凝结水泵停顺控第3步完成条件 |  | digital
N1DCS.CNDPA_SEQST | 26959 | #1凝结水泵启顺控 |  | int32
N1DCS.CNDPA_SEQSTAUX | 26960 | #1凝结水泵启顺控辅助点 |  | digital
N1DCS.CNDPA_SEQSTAUX0 | 26961 | #1凝结水泵启顺控启允许条件 |  | int32
N1DCS.CNDPA_SEQSTAUX1 | 26962 | #1凝结水泵启顺控第1步完成条件 |  | digital
N1DCS.CNDPA_SEQSTAUX2 | 26963 | #1凝结水泵启顺控第2步完成条件 |  | digital
N1DCS.CNDPA_SEQSTAUX3 | 26964 | #1凝结水泵启顺控第3步完成条件 |  | digital
N1DCS.CNDPAPA_SEQSPLP | 26965 | #1凝结水泵停顺控状态 |  | digital
N1DCS.CNDPAPA_SEQSTLP | 26966 | #1凝结水泵启顺控状态 |  | digital
N1DCS.CNDPMP_BYLP | 26967 | #1机凝结水泵 |  | digital
N1DCS.CNDPMPA_STPMTLP | 26968 | #1机#1凝结水泵启允许条件 |  | digital
N1DCS.CNDPMPA_TRIP | 26969 | #1机#1凝结水泵跳闸条件 |  | digital
N1DCS.CNDPMPA_TRIPTAG | 26970 | #1机#1凝结水泵跳闸条件解除信号 |  | digital
N1DCS.CNDWTRSYS_SEQST | 26971 | 凝结水系统启顺控 |  | digital
N1DCS.CNDWTRSYS_SEQSTAUX | 26972 | 凝结水系统启顺控辅助点 |  | digital
N1DCS.CNDWTRSYS_SEQSTAUX0 | 26973 | 凝结水系统启顺控启允许条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTAUX1 | 26974 | 凝结水系统启顺控第1步完成条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTAUX2 | 26975 | 凝结水系统启顺控第2步完成条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTAUX3 | 26976 | 凝结水系统启顺控第3步完成条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTLP | 26977 | 凝结水系统启顺控状态 |  | digital
N1DCS.CNDWTRSYS_SEQSTREY | 26978 | 凝结水系统准备顺控 |  | digital
N1DCS.CNDWTRSYS_SEQSTREYAUX | 26979 | 凝结水系统准备顺控辅助点 |  | digital
N1DCS.CNDWTRSYS_SEQSTREYAUX0 | 26980 | 凝结水系统准备顺控启允许条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTREYAUX1 | 26981 | 凝结水系统准备顺控1步完成条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTREYAUX2 | 26982 | 凝结水系统准备顺控2步完成条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTREYAUX3 | 26983 | 凝结水系统准备顺控3步完成条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTREYAUX4 | 26984 | 凝结水系统准备顺控4步完成条件 |  | digital
N1DCS.CNDWTRSYS_SEQSTREYLP | 26985 | 凝结水系统准备顺控状态 |  | digital
N1DCS.CNSRLVL_LP | 26986 | #1机凝汽器热井液位 |  | digital
N1DCS.OPNCIRPMPA_PMTLP | 26987 | #1机#1开式水泵启允许条件 |  | digital
N1DCS.OPNCIRPMPA_SEQSP | 26988 | #1机#1开式水泵停顺控 |  | digital
N1DCS.OPNCIRPMPA_SEQSPAUX | 26989 | #1机#1开式水泵停顺控辅助点 |  | digital
N1DCS.OPNCIRPMPA_SEQSPAUX1 | 26990 | #1开式水泵停顺控第1步完成条件 |  | digital
N1DCS.OPNCIRPMPA_SEQSPAUX2 | 26991 | #1开式水泵停顺控第2步完成条件 |  | digital
N1DCS.OPNCIRPMPA_SEQSPLP | 26992 | #1机#1开式水泵停顺控状态 |  | digital
N1DCS.OPNCIRPMPA_SEQST | 26993 | #1机#1开式水泵启顺控 |  | digital
N1DCS.OPNCIRPMPA_SEQSTAUX | 26994 | #1机#1开式水泵启顺控辅助点 |  | digital
N1DCS.OPNCIRPMPA_SEQSTAUX0 | 26995 | #1机#1开式水泵启顺控启允许条件 |  | digital
N1DCS.OPNCIRPMPA_SEQSTAUX1 | 26996 | #1开式水泵启顺控第1步完成条件 |  | digital
N1DCS.OPNCIRPMPA_SEQSTAUX2 | 26997 | #1开式水泵启顺控第2步完成条件 |  | digital
N1DCS.OPNCIRPMPA_SEQSTAUX3 | 26998 | #1开式水泵启顺控第3步完成条件 |  | digital
N1DCS.OPNCIRPMPA_SEQSTLP | 26999 | #1机#1开式水泵启顺控状态 |  | digital
N1DCS.OPNCIRPMPA_TRIP | 27000 | #1机#1开式水泵跳闸条件 |  | digital
N1DCS.OPNCIRPMPA_TRIPTAG | 27001 | #1机#1开式水泵跳闸条件解除信号 |  | digital
N1DCS.OPNCIRWTR_SEQST | 27002 | 开式水系统启顺控 |  | digital
N1DCS.OPNCIRWTR_SEQSTAUX | 27003 | 开式水系统启顺控辅助点 |  | digital
N1DCS.OPNCIRWTR_SEQSTAUX0 | 27004 | 开式水系统启顺控启允许条件 |  | digital
N1DCS.OPNCIRWTR_SEQSTAUX1 | 27005 | 开式水系统启顺控第1步完成条件 |  | digital
N1DCS.OPNCIRWTR_SEQSTAUX2 | 27006 | 开式水系统启顺控第2步完成条件 |  | digital
N1DCS.OPNCIRWTR_SEQSTAUX3 | 27007 | 开式水系统启顺控第3步完成条件 |  | digital
N1DCS.OPNCIRWTR_SEQSTAUX4 | 27008 | 开式水系统启顺控第4步完成条件 |  | digital
N1DCS.OPNCIRWTR_SEQSTLP | 27009 | 开式水系统启顺控状态 |  | digital
N1DCS.OPNCIRWTRPMP_BYLP | 27010 | #1机开式冷却水泵 |  | digital
N1DCS.RBBRBALLA_SEQSP | 27011 | 凝汽器#1胶球收球顺控 |  | digital
N1DCS.RBBRBALLA_SEQSPAUX | 27012 | 凝汽器#1胶球收球顺控辅助点 |  | digital
N1DCS.RBBRBALLA_SEQSPAUX1 | 27013 | #1胶球收球顺控第1步完成条件 |  | digital
N1DCS.RBBRBALLA_SEQSPAUX2 | 27014 | #1胶球收球顺控第2步完成条件 |  | digital
N1DCS.RBBRBALLA_SEQSPAUX3 | 27015 | #1胶球收球顺控第3步完成条件 |  | digital
N1DCS.RBBRBALLA_SEQSPAUX4 | 27016 | #1胶球收球顺控第4步完成条件 |  | digital
N1DCS.RBBRBALLA_SEQSPLP | 27017 | 凝汽器#1胶球收球顺控状态 |  | digital
N1DCS.RBBRBALLA_SEQST | 27018 | 凝汽器#1胶球投球顺控 |  | digital
N1DCS.RBBRBALLA_SEQSTAUX | 27019 | 凝汽器#1胶球投球顺控辅助点 |  | digital
N1DCS.RBBRBALLA_SEQSTAUX0 | 27020 | 凝汽器#1胶球投球顺控启允许条件 |  | digital
N1DCS.RBBRBALLA_SEQSTAUX1 | 27021 | #1胶球投球顺控第1步完成条件 |  | digital
N1DCS.RBBRBALLA_SEQSTAUX2 | 27022 | #1胶球投球顺控第2步完成条件 |  | digital
N1DCS.RBBRBALLA_SEQSTAUX3 | 27023 | #1胶球投球顺控第3步完成条件 |  | digital
N1DCS.RBBRBALLA_SEQSTAUX4 | 27024 | #1胶球投球顺控第4步完成条件 |  | digital
N1DCS.RBBRBALLA_SEQSTLP | 27025 | 凝汽器#1胶球投球顺控状态 |  | digital
N1DCS.10LBG21AA002_LP | 27026 | 轴封电加热器进口电动门 |  | int32
N1DCS.10LBG21AA003_LP | 27027 | 轴封电加热器出口电动门 |  | int32
N1DCS.10LBG21AC001_LP | 27028 | 轴封电加热器 |  | int32
N1DCS.10LDK10AA003_LP | 27029 | #1机除铁过滤器升压气动门 |  | digital
N1DCS.10LDK10AA004_LP | 27030 | #1机除铁过滤器出水电动门 |  | digital
N1DCS.CNDWTRSYS_SEQSTREYAUX5 | 27031 | 凝结水系统准备顺控5步完成条件 |  | digital
N1DCS.10LCA12AA001_LP | 27032 | #1机#2凝结水泵进口真空电动门 |  | digital
N1DCS.10LCA12AA003_LP | 27033 | #1机#2凝结水泵出口真空电动门 |  | digital
N1DCS.10LCB12AP001_LP | 27034 | #1机#2凝结水泵 |  | digital
N1DCS.10LCB12AP002_LP | 27035 | #1机#2凝结水泵 |  | digital
N1DCS.10LCB12GH0012_LP | 27036 | #2凝结水泵#2永磁调速水泵 |  | digital
N1DCS.10PAB12AA001_LP | 27037 | #1机凝汽器循环水进水#2电动门 |  | digital
N1DCS.10PAB22AA001_LP | 27038 | #1机凝汽器循环水#2出水电动门 |  | digital
N1DCS.10PAH12AA002_LP | 27039 | #1机凝汽器#2胶球泵出口电动门 |  | digital
N1DCS.10PAH12AP001_LP | 27040 | #1机凝汽器#2胶球泵 |  | digital
N1DCS.10PAH12AT001_LP | 27041 | #1机凝汽器#2收球网 |  | digital
N1DCS.10PAH12BB001_LP | 27042 | #1机凝汽器#2装球室 |  | digital
N1DCS.10PCB11AA003_LP | 27043 | #1机#2开式冷却水泵进口电动门 |  | digital
N1DCS.10PCB11AA004_LP | 27044 | #1机#2开式冷却水泵出口电动门 |  | digital
N1DCS.10PCB11AP002_LP | 27045 | #1机#2开式冷却水泵 |  | digital
N1DCS.10PCB13AA012_LP | 27046 | #2真空泵冷却器开式水进水电动门 |  | digital
N1DCS.10PCB22AA001_LP | 27047 | #2热交换器开式冷却水进水电动门 |  | digital
N1DCS.10PCB23AA012_LP | 27048 | #2真空泵冷却器开式水出水电动门 |  | digital
N1DCS.10PCB32AA001_LP | 27049 | #2热交换器开式冷却水出水电动门 |  | digital
N1DCS.10PGA12AA001_LP | 27050 | #1机#2闭式冷却水泵进口电动门 |  | digital
N1DCS.10PGA12AA003_LP | 27051 | #1机#2闭式冷却水泵出口电动门 |  | digital
N1DCS.10PGA12AP001_LP | 27052 | #1机#2闭式冷却水泵 |  | digital
N1DCS.10PGA22AA001_LP | 27053 | #2热交换器闭式水进口电动门 |  | digital
N1DCS.10PGA22AA002_LP | 27054 | #2热交换器闭式水出口电动门 |  | digital
N1DCS.10PGA26AA101MODE | 27055 | #2发电机定冷水进水电动调节阀 |  | digital
N1DCS.10PGA26AA102MODE | 27056 | #2发电机氢冷器进水电动调节阀 |  | digital
N1DCS.10PGA26AA103MODE | 27057 | #2机润滑油冷却器进水电动调节阀 |  | digital
N1DCS.10PGA32AA101MODE | 27058 | #1机EH油冷却器进水电动调节阀 |  | digital
N1DCS.10PGA33AA101MODE | 27059 | #1机润滑油冷却器进水电动调节阀 |  | digital
N1DCS.10PGA34AA101MODE | 27060 | #1发电机空冷器进水电动调节阀 |  | digital
N1DCS.CLCLGPMPB_PMTLP | 27061 | #1机闭式冷却水泵启允许条件 |  | digital
N1DCS.CLCLGPMPB_SEQSP | 27062 | #2闭式水泵停顺控 |  | digital
N1DCS.CLCLGPMPB_SEQSPAUX | 27063 | #2闭式水泵停顺控辅助点 |  | digital
N1DCS.CLCLGPMPB_SEQSPAUX0 | 27064 | #2闭式水泵停顺控启允许条件 |  | digital
N1DCS.CLCLGPMPB_SEQSPAUX1 | 27065 | #2闭式水泵停顺控第1步完成条件 |  | digital
N1DCS.CLCLGPMPB_SEQSPAUX2 | 27066 | #2闭式水泵停顺控第2步完成条件 |  | digital
N1DCS.CLCLGPMPB_SEQSPLP | 27067 | #2闭式水泵停顺控状态 |  | digital
N1DCS.CLCLGPMPB_SEQST | 27068 | #2闭式水泵启顺控 |  | digital
N1DCS.CLCLGPMPB_SEQSTAUX | 27069 | #2闭式水泵启顺控辅助点 |  | digital
N1DCS.CLCLGPMPB_SEQSTAUX0 | 27070 | #2闭式水泵启顺控启允许条件 |  | digital
N1DCS.CLCLGPMPB_SEQSTAUX1 | 27071 | #2闭式水泵启顺控第1步完成条件 |  | digital
N1DCS.CLCLGPMPB_SEQSTAUX2 | 27072 | #2闭式水泵启顺控第2步完成条件 |  | digital
N1DCS.CLCLGPMPB_SEQSTAUX3 | 27073 | #2闭式水泵启顺控第3步完成条件 |  | digital
N1DCS.CLCLGPMPB_SEQSTLP | 27074 | #2闭式水泵启顺控状态 |  | digital
N1DCS.CLCLGPMPB_TRIP | 27075 | #2闭式水泵跳闸条件 |  | digital
N1DCS.CLCLGPMPB_TRIPTAG | 27076 | #2闭式水泵跳闸条件解除信号 |  | digital
N1DCS.CNDPAPB_SEQSPLP | 27077 | #2凝结水泵停顺控状态 |  | digital
N1DCS.CNDPAPB_SEQSTLP | 27078 | #2凝结水泵启顺控状态 |  | digital
N1DCS.CNDPB_SEQSP | 27079 | #2凝结水泵停顺控 |  | digital
N1DCS.CNDPB_SEQSPAUX | 27080 | #2凝结水泵停顺控辅助点 |  | digital
N1DCS.CNDPB_SEQSPAUX1 | 27081 | #2凝结水泵停顺控第1步完成条件 |  | digital
N1DCS.CNDPB_SEQSPAUX2 | 27082 | #2凝结水泵停顺控第2步完成条件 |  | digital
N1DCS.CNDPB_SEQST | 27083 | #2凝结水泵启顺控 |  | digital
N1DCS.CNDPB_SEQSTAUX | 27084 | #2凝结水泵启顺控辅助点 |  | digital
N1DCS.CNDPB_SEQSTAUX0 | 27085 | #2凝结水泵启顺控启允许条件 |  | digital
N1DCS.CNDPB_SEQSTAUX1 | 27086 | #2凝结水泵启顺控第1步完成条件 |  | digital
N1DCS.CNDPB_SEQSTAUX2 | 27087 | #2凝结水泵启顺控第2步完成条件 |  | digital
N1DCS.CNDPB_SEQSTAUX3 | 27088 | #2凝结水泵启顺控第3步完成条件 |  | digital
N1DCS.CNDPB_SEQSTAUX4 | 27089 | #2凝结水泵启顺控第4步完成条件 |  | digital
N1DCS.CNDPMPB_STPMTLP | 27090 | #1机#2凝结水泵启允许条件 |  | digital
N1DCS.CNDPMPB_TRIP | 27091 | #1机#2凝结水泵跳闸条件 |  | digital
N1DCS.CNDPMPB_TRIPTAG | 27092 | #1机#2凝结水泵跳闸条件解除信号 |  | digital
N1DCS.OPNCIRPMPB_PMTLP | 27093 | #1机#2开式水泵启允许条件 |  | digital
N1DCS.OPNCIRPMPB_SEQSP | 27094 | #1机#2开式水泵停顺控 |  | digital
N1DCS.OPNCIRPMPB_SEQSPAUX | 27095 | #1机#2开式水泵停顺控辅助点 |  | digital
N1DCS.OPNCIRPMPB_SEQSPAUX1 | 27096 | #2开式水泵停顺控第1步完成条件 |  | digital
N1DCS.OPNCIRPMPB_SEQSPAUX2 | 27097 | #2开式水泵停顺控第2步完成条件 |  | digital
N1DCS.OPNCIRPMPB_SEQSPLP | 27098 | #1机#2开式水泵停顺控状态 |  | digital
N1DCS.OPNCIRPMPB_SEQST | 27099 | #1机#2开式水泵启顺控 |  | digital
N1DCS.OPNCIRPMPB_SEQSTAUX | 27100 | #1机#2开式水泵启顺控辅助点 |  | digital
N1DCS.OPNCIRPMPB_SEQSTAUX0 | 27101 | #1机#2开式水泵启顺控启允许条件 |  | digital
N1DCS.OPNCIRPMPB_SEQSTAUX1 | 27102 | #2开式水泵启顺控第1步完成条件 |  | digital
N1DCS.OPNCIRPMPB_SEQSTAUX2 | 27103 | #2开式水泵启顺控第2步完成条件 |  | digital
N1DCS.OPNCIRPMPB_SEQSTAUX3 | 27104 | #2开式水泵启顺控第3步完成条件 |  | digital
N1DCS.OPNCIRPMPB_SEQSTLP | 27105 | #1机#2开式水泵启顺控状态 |  | digital
N1DCS.OPNCIRPMPB_TRIP | 27106 | #1机#2开式水泵跳闸条件 |  | digital
N1DCS.OPNCIRPMPB_TRIPTAG | 27107 | #1机#2开式水泵跳闸条件解除信号 |  | digital
N1DCS.RBBRBALLB_SEQSP | 27108 | 凝汽器#2胶球收球顺控 |  | digital
N1DCS.RBBRBALLB_SEQSPAUX | 27109 | 凝汽器#2胶球收球顺控辅助点 |  | digital
N1DCS.RBBRBALLB_SEQSPAUX1 | 27110 | #2胶球收球顺控第1步完成条件 |  | digital
N1DCS.RBBRBALLB_SEQSPAUX2 | 27111 | #2胶球收球顺控第2步完成条件 |  | digital
N1DCS.RBBRBALLB_SEQSPAUX3 | 27112 | #2胶球收球顺控第3步完成条件 |  | digital
N1DCS.RBBRBALLB_SEQSPAUX4 | 27113 | #2胶球收球顺控第4步完成条件 |  | digital
N1DCS.RBBRBALLB_SEQSPLP | 27114 | 凝汽器#2胶球收球顺控状态 |  | digital
N1DCS.RBBRBALLB_SEQST | 27115 | 凝汽器#2胶球投球顺控 |  | digital
N1DCS.RBBRBALLB_SEQSTAUX | 27116 | 凝汽器#2胶球投球顺控辅助点 |  | digital
N1DCS.RBBRBALLB_SEQSTAUX0 | 27117 | 凝汽器#2胶球投球顺控启允许条件 |  | digital
N1DCS.RBBRBALLB_SEQSTAUX1 | 27118 | #2胶球投球顺控第1步完成条件 |  | digital
N1DCS.RBBRBALLB_SEQSTAUX2 | 27119 | #2胶球投球顺控第2步完成条件 |  | digital
N1DCS.RBBRBALLB_SEQSTAUX3 | 27120 | #2胶球投球顺控第3步完成条件 |  | digital
N1DCS.RBBRBALLB_SEQSTAUX4 | 27121 | #2胶球投球顺控第4步完成条件 |  | digital
N1DCS.RBBRBALLB_SEQSTLP | 27122 | 凝汽器#2胶球投球顺控状态 |  | digital
N1DCS.10LCB12GH001_LP | 27123 | #2凝结水泵#1永磁调速水泵 |  | digital
N1DCS.10LCB12GH001MODE | 27124 | #2凝结水泵永磁调速控制器 |  | digital
N1DCS.10LDB10AA501_LP | 27125 | 凝结水除铁过滤器#1排气气动门 |  | digital
N1DCS.10LDB10AA502_LP | 27126 | 凝结水除铁过滤器#2排气气动门 |  | digital
N1DCS.10LDK10AA002_LP | 27127 | 凝结水除铁过滤器进口电动门 |  | digital
N1DCS.10LDK20AA002_LP | 27128 | 凝结水除铁过滤器旁路电动门 |  | digital
N1DCS.CNDYCPMP_BYLP | 27129 | #2凝结水泵永磁调速冷却水泵 |  | digital
N1DCS.CTGLQ_BYLP | 27130 | 除铁过滤器主、旁路预选 |  | digital
N1DCS.HXCTQ_SEQSP | 27131 | 除铁过滤器停顺控 |  | digital
N1DCS.HXCTQ_SEQSPAUX | 27132 | 除铁过滤器停顺控辅助点 |  | digital
N1DCS.HXCTQ_SEQSPAUX0 | 27133 | 除铁过滤器停顺控启允许条件 |  | digital
N1DCS.HXCTQ_SEQSPAUX1 | 27134 | 除铁过滤器停顺控第1步完成条件 |  | digital
N1DCS.HXCTQ_SEQSPAUX2 | 27135 | 除铁过滤器停顺控第2步完成条件 |  | digital
N1DCS.HXCTQ_SEQSPAUX3 | 27136 | 除铁过滤器停顺控第3步完成条件 |  | digital
N1DCS.HXCTQ_SEQSPLP | 27137 | 除铁过滤器停顺控状态 |  | digital
N1DCS.HXCTQ_SEQST | 27138 | 除铁过滤器启顺控 |  | digital
N1DCS.HXCTQ_SEQSTAUX | 27139 | 除铁过滤器启顺控辅助点 |  | digital
N1DCS.HXCTQ_SEQSTAUX0 | 27140 | 除铁过滤器启顺控启允许条件 |  | digital
N1DCS.HXCTQ_SEQSTAUX1 | 27141 | 除铁过滤器启顺控第1步完成条件 |  | digital
N1DCS.HXCTQ_SEQSTAUX2 | 27142 | 除铁过滤器启顺控第2步完成条件 |  | digital
N1DCS.HXCTQ_SEQSTAUX3 | 27143 | 除铁过滤器启顺控第3步完成条件 |  | digital
N1DCS.HXCTQ_SEQSTAUX4 | 27144 | 除铁过滤器启顺控第4步完成条件 |  | digital
N1DCS.HXCTQ_SEQSTAUX5 | 27145 | 除铁过滤器启顺控第5步完成条件 |  | digital
N1DCS.HXCTQ_SEQSTLP | 27146 | 除铁过滤器启顺控状态 |  | digital
N1DCS.10MAJ21AA001_LP | 27147 | #1机#1真空泵进口气动门2 |  | digital
N1DCS.10MAJ21AA007_LP | 27148 | #1真空泵汽水分离器补水电磁阀 |  | digital
N1DCS.10MAJ21AA011_LP | 27149 | #1机#1真空泵进口气动门1 |  | digital
N1DCS.10MAJ21AP001_LP | 27150 | #1机#1真空泵 |  | digital
N1DCS.10MAJ23AA009_LP | 27151 | #1机蒸汽喷射装置进口气动门 |  | digital
N1DCS.10MAJ23AA014_LP | 27152 | 蒸汽喷射装置换热器放水气动门 |  | digital
N1DCS.10MAJ23AA016_LP | 27153 | 蒸汽喷射装置换热器汽侧出口气门 |  | int32
N1DCS.10MAJ23AA101_MODE | 27154 | #1机蒸汽喷射装置压力调节阀 |  | digital
N1DCS.10MAJ30AA002_LP | 27155 | #1机凝汽器真空破坏气动门 |  | digital
N1DCS.10MAV10AH001_LP | 27156 | #1机润滑油箱#1电加热器 |  | digital
N1DCS.10MAV10AH002_LP | 27157 | #1机润滑油箱#2电加热器 |  | digital
N1DCS.10MAV21AP021_LP | 27158 | #1机#1润滑油泵 |  | digital
N1DCS.10MAV31AP001_LP | 27159 | #1机#1顶轴油泵 |  | digital
N1DCS.10MAV82AN001_LP | 27160 | #1机#1润滑油风机 |  | digital
N1DCS.10MAX01AP001_LP | 27161 | #1机#1EH油泵 |  | digital
N1DCS.10MAX01AP011_LP | 27162 | #1机#1EH油循环泵 |  | digital
N1DCS.10PAA11AA001_LP | 27163 | #1旋转滤网冲洗水电动门 |  | digital
N1DCS.10PAB11AA002_LP | 27164 | #1循环水泵出口液控蝶阀 |  | digital
N1DCS.10PAB11AT001_LP | 27165 | #1旋转滤网 |  | digital
N1DCS.10PAB41AP001_LP | 27166 | #1循环水泵冷却水#1加压泵 |  | digital
N1DCS.10PAB42AP001_LP | 27167 | #1循环水泵冷却水#2加压泵 |  | digital
N1DCS.10PAB61AA001_LP | 27168 | 生活水至#1循环水泵冷却水电磁阀 |  | digital
N1DCS.10PAC11AP001_LP | 27169 | #1循环水泵 |  | int32
N1DCS.10PAC11AP001H_LP | 27170 | #1循环水泵高速 |  | int32
N1DCS.10PAC11AP001L_LP | 27171 | #1循环水泵低速 |  | int32
N1DCS.10PSA01AP001_LP | 27172 | #1冷却塔排水池#1排污泵 |  | int32
N1DCS.ACLUBOILP_BYLP | 27173 | #1机润滑油泵 |  | digital
N1DCS.CIRPMPA_STPMTLP | 27174 | #1循环水泵启允许条件 |  | digital
N1DCS.CIRPMPA_TRIP | 27175 | #1循环水泵跳闸条件 |  | digital
N1DCS.CIRPMPA_TRIPTAG | 27176 | #1循环水泵跳闸条件解除信号 |  | digital
N1DCS.CIRWTRPMP_BYLP | 27177 | 循环水泵 |  | int32
N1DCS.CIRWTRPMPA_SEQSP | 27178 | #1循环水泵停顺控 |  | digital
N1DCS.CIRWTRPMPA_SEQSPAUX | 27179 | #1循环水泵停顺控辅助点 |  | digital
N1DCS.CIRWTRPMPA_SEQSPAUX1 | 27180 | #1循环水泵停顺控第1步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSPAUX2 | 27181 | #1循环水泵停顺控第2步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSPAUX3 | 27182 | #1循环水泵停顺控第3步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSPAUX4 | 27183 | #1循环水泵停顺控第4步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSPLP | 27184 | #1循环水泵停顺控状态 |  | digital
N1DCS.CIRWTRPMPA_SEQST | 27185 | #1循环水泵启顺控 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX | 27186 | #1循环水泵停顺控辅助点 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX0 | 27187 | #1循环水泵停顺控启允许条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX1 | 27188 | #1循环水泵停顺控第1步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX2 | 27189 | #1循环水泵停顺控第2步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX3 | 27190 | #1循环水泵停顺控第3步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX4 | 27191 | #1循环水泵停顺控第4步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX5 | 27192 | #1循环水泵停顺控第5步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX6 | 27193 | #1循环水泵停顺控第6步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSTAUX7 | 27194 | #1循环水泵停顺控第7步完成条件 |  | digital
N1DCS.CIRWTRPMPA_SEQSTLP | 27195 | #1循环水泵启顺控状态 |  | digital
N1DCS.CIRWTRSYS_SEQST | 27196 | 循环水系统启顺控 |  | int32
N1DCS.CIRWTRSYS_SEQSTAUX | 27197 | 循环水系统启顺控辅助点 |  | digital
N1DCS.CIRWTRSYS_SEQSTAUX0 | 27198 | 循环水系统启顺控启允许条件 |  | int32
N1DCS.CIRWTRSYS_SEQSTAUX1 | 27199 | 循环水系统启顺控第1步完成条件 |  | digital
N1DCS.CIRWTRSYS_SEQSTAUX2 | 27200 | 循环水系统启顺控第2步完成条件 |  | digital
N1DCS.CIRWTRSYS_SEQSTAUX3 | 27201 | 循环水系统启顺控第3步完成条件 |  | digital
N1DCS.CIRWTRSYS_SEQSTAUX4 | 27202 | 循环水系统启顺控第4步完成条件 |  | digital
N1DCS.CIRWTRSYS_SEQSTLP | 27203 | 循环水系统启顺控状态 |  | digital
N1DCS.CNSRVACM_LP | 27204 | #1机凝汽器真空压力 |  | digital
N1DCS.EHMAINOILP_BYLP | 27205 | EH油泵 |  | int32
N1DCS.EHOILCIRP_BYLP | 27206 | EH油循环泵 |  | digital
N1DCS.EHOILSYS_SEQSP | 27207 | EH油系统停顺控 |  | digital
N1DCS.EHOILSYS_SEQSPAUX | 27208 | EH油系统停顺控辅助点 |  | digital
N1DCS.EHOILSYS_SEQSPAUX0 | 27209 | EH油系统停顺控启允许条件 |  | digital
N1DCS.EHOILSYS_SEQSPAUX1 | 27210 | EH油系统停顺控第1步完成条件 |  | digital
N1DCS.EHOILSYS_SEQSPAUX2 | 27211 | EH油系统停顺控第2步完成条件 |  | digital
N1DCS.EHOILSYS_SEQSPLP | 27212 | EH油系统停顺控第3步完成条件 |  | digital
N1DCS.EHOILSYS_SEQST | 27213 | EH油系统启顺控 |  | int32
N1DCS.EHOILSYS_SEQSTAUX | 27214 | EH油系统启顺控辅助点 |  | digital
N1DCS.EHOILSYS_SEQSTAUX0 | 27215 | EH油系统启顺控启允许条件 |  | int32
N1DCS.EHOILSYS_SEQSTAUX1 | 27216 | EH油系统启顺控第1步完成条件 |  | digital
N1DCS.EHOILSYS_SEQSTAUX2 | 27217 | EH油系统启顺控第2步完成条件 |  | digital
N1DCS.EHOILSYS_SEQSTLP | 27218 | EH油系统启顺控状态 |  | digital
N1DCS.EHOILSYS_SEQSTOKLP | 27219 | EH油系统启顺控第3步完成条件 |  | digital
N1DCS.JACKOILP_BYLP | 27220 | 顶轴油泵 |  | int32
N1DCS.LUBOILEGF_BYLP | 27221 | #1机润滑油风机 |  | digital
N1DCS.LUBOILHTR_BYLP | 27222 | #1机润滑油箱电加热器 |  | digital
N1DCS.LUBWTINPREPMPA_BYLP | 27223 | #1循环水泵冷却水加压泵 |  | digital
N1DCS.ROTFLTRA_SEQST | 27224 | #1旋转滤网冲洗顺控 |  | digital
N1DCS.ROTFLTRA_SEQSTAUX | 27225 | #1旋转滤网冲洗顺控辅助点 |  | digital
N1DCS.ROTFLTRA_SEQSTLP | 27226 | #1旋转滤网冲洗顺控状态 |  | digital
N1DCS.TURBDRNALLCP_LP1 | 27227 | #1机本体疏水阀组1关闭状态 |  | digital
N1DCS.TURBDRNALLCP_LP2 | 27228 | #1机本体疏水阀组2关闭状态 |  | digital
N1DCS.TURBDRNALLOP_LP1 | 27229 | #1机本体疏水阀组1打开状态 |  | digital
N1DCS.TURBDRNALLOP_LP2 | 27230 | #1机本体疏水阀组2打开状态 |  | digital
N1DCS.TURBOILSYS_SEQST | 27231 | #1机润滑油系统启顺控 |  | digital
N1DCS.TURBOILSYS_SEQSTAUX | 27232 | #1机润滑油系统启顺控辅助点 |  | digital
N1DCS.TURBOILSYS_SEQSTAUX0 | 27233 | #1机润滑油系统启顺控启允许条件 |  | digital
N1DCS.TURBOILSYS_SEQSTAUX1 | 27234 | 润滑油系统启顺控第1步完成条件 |  | digital
N1DCS.TURBOILSYS_SEQSTAUX2 | 27235 | 润滑油系统启顺控第2步完成条件 |  | digital
N1DCS.TURBOILSYS_SEQSTAUX3 | 27236 | 润滑油系统启顺控第3步完成条件 |  | digital
N1DCS.TURBOILSYS_SEQSTAUX4 | 27237 | 润滑油系统启顺控第4步完成条件 |  | digital
N1DCS.TURBOILSYS_SEQSTAUX5 | 27238 | 润滑油系统启顺控第5步完成条件 |  | digital
N1DCS.TURBOILSYS_SEQSTLP | 27239 | #1机润滑油系统启顺控状态 |  | digital
N1DCS.TURBOILSYS_SEQSTOKLP | 27240 | 润滑油系统启顺控第6步完成条件 |  | digital
N1DCS.VACM_SEQSP | 27241 | Ovation Control Builder |  | int32
N1DCS.VACMPMP_BYLP | 27242 | #1机真空泵 |  | digital
N1DCS.VACMPMPA_PMTLP | 27243 | #1真空泵启允许条件 |  | digital
N1DCS.VACMPMPA_SEQSP | 27244 | #1真空泵停顺控 |  | int32
N1DCS.VACMPMPA_SEQSPAUX | 27245 | #1真空泵停顺控辅助点 |  | digital
N1DCS.VACMPMPA_SEQSPAUX1 | 27246 | #1真空泵停顺控第1步完成条件 |  | digital
N1DCS.VACMPMPA_SEQSPAUX2 | 27247 | #1真空泵停顺控第2步完成条件 |  | digital
N1DCS.VACMPMPA_SEQSPLP | 27248 | #1真空泵停顺控状态 |  | digital
N1DCS.VACMPMPA_SEQST | 27249 | #1真空泵启顺控 |  | int32
N1DCS.VACMPMPA_SEQSTAUX | 27250 | #1真空泵启顺控辅助点 |  | digital
N1DCS.VACMPMPA_SEQSTAUX0 | 27251 | #1真空泵启顺控启允许条件 |  | int32
N1DCS.VACMPMPA_SEQSTAUX1 | 27252 | #1真空泵启顺控第1步完成条件 |  | digital
N1DCS.VACMPMPA_SEQSTAUX2 | 27253 | #1真空泵启顺控第2步完成条件 |  | digital
N1DCS.VACMPMPA_SEQSTAUX3 | 27254 | #1真空泵启顺控第3步完成条件 |  | digital
N1DCS.VACMPMPA_SEQSTLP | 27255 | #1真空泵启顺控状态 |  | digital
N1DCS.VACMPMPA_TRIP | 27256 | #1真空泵跳闸条件 |  | digital
N1DCS.VACMPMPA_TRIPTAG | 27257 | #1真空泵跳闸条件解除信号 |  | digital
N1DCS.VACMSYS_SEQSP | 27258 | 抽真空系统停顺控 |  | int32
N1DCS.VACMSYS_SEQSPAUX | 27259 | 抽真空系统停顺控辅助点 |  | digital
N1DCS.VACMSYS_SEQSPLP | 27260 | 抽真空系统停顺控状态 |  | digital
N1DCS.VACMSYS_SEQST | 27261 | 抽真空系统启顺控 |  | int32
N1DCS.VACMSYS_SEQSTAUX | 27262 | 抽真空系统启顺控辅助点 |  | digital
N1DCS.VACMSYS_SEQSTAUX0 | 27263 | 抽真空系统启顺控启允许条件 |  | int32
N1DCS.VACMSYS_SEQSTAUX1 | 27264 | 抽真空系统启顺控第1步完成条件 |  | digital
N1DCS.VACMSYS_SEQSTAUX2 | 27265 | 抽真空系统启顺控第2步完成条件 |  | digital
N1DCS.VACMSYS_SEQSTAUX3 | 27266 | 抽真空系统启顺控第3步完成条件 |  | digital
N1DCS.VACMSYS_SEQSTAUX4 | 27267 | 抽真空系统启顺控第4步完成条件 |  | digital
N1DCS.VACMSYS_SEQSTAUX5 | 27268 | 抽真空系统启顺控第5步完成条件 |  | digital
N1DCS.VACMSYS_SEQSTLP | 27269 | 抽真空系统启顺控状态 |  | digital
N1DCS.ZQPSSYS_SEQSP | 27270 | 蒸汽喷射装置停顺控 |  | int32
N1DCS.ZQPSSYS_SEQSPAUX | 27271 | 蒸汽喷射装置停顺控辅助点 |  | int32
N1DCS.ZQPSSYS_SEQSPAUX0 | 27272 | 蒸汽喷射装置停顺控启允许条件 |  | int32
N1DCS.ZQPSSYS_SEQSPAUX1 | 27273 | 蒸汽喷射装置停顺控1步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSPAUX2 | 27274 | 蒸汽喷射装置停顺控2步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSPAUX3 | 27275 | 蒸汽喷射装置停顺控3步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSPAUX4 | 27276 | 蒸汽喷射装置停顺控4步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSPAUX5 | 27277 | 蒸汽喷射装置停顺控5步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSPLP | 27278 | 蒸汽喷射装置停顺控状态 |  | int32
N1DCS.ZQPSSYS_SEQST | 27279 | 蒸汽喷射装置启顺控 |  | int32
N1DCS.ZQPSSYS_SEQSTAUX | 27280 | 蒸汽喷射装置启顺控辅助点 |  | int32
N1DCS.ZQPSSYS_SEQSTAUX0 | 27281 | 蒸汽喷射装置启顺控启允许条件 |  | int32
N1DCS.ZQPSSYS_SEQSTAUX1 | 27282 | 蒸汽喷射装置启顺控1步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSTAUX2 | 27283 | 蒸汽喷射装置启顺控2步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSTAUX3 | 27284 | 蒸汽喷射装置启顺控3步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSTAUX4 | 27285 | 蒸汽喷射装置启顺控4步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSTAUX5 | 27286 | 蒸汽喷射装置启顺控5步完成条件 |  | int32
N1DCS.ZQPSSYS_SEQSTLP | 27287 | 蒸汽喷射装置启顺控状态 |  | int32
N1DCS.10MAJ22AA001_LP | 27288 | #1机#2真空泵进口气动门2 |  | digital
N1DCS.10MAJ22AA007_LP | 27289 | #2真空泵汽水分离器补水电磁阀 |  | digital
N1DCS.10MAJ22AA011_LP | 27290 | #1机#2真空泵进口气动门1 |  | digital
N1DCS.10MAJ22AP001_LP | 27291 | #1机#2真空泵 |  | digital
N1DCS.10MAV10AH003_LP | 27292 | #1机润滑油箱#3电加热器 |  | digital
N1DCS.10MAV10AH004_LP | 27293 | #1机润滑油箱#4电加热器 |  | digital
N1DCS.10MAV21AA321_LP | 27294 | #1机润滑油泵出口试验电磁阀 |  | digital
N1DCS.10MAV21AP022_LP | 27295 | #1机#2润滑油泵 |  | digital
N1DCS.10MAV24AP001_LP | 27296 | #1机润滑油应急油泵 |  | digital
N1DCS.10MAV32AP001_LP | 27297 | #1机#2顶轴油泵 |  | digital
N1DCS.10MAV42AA322_LP | 27298 | #1机润滑油母管试验电磁阀1 |  | digital
N1DCS.10MAV42AA329_LP | 27299 | #1机润滑油母管试验电磁阀2 |  | digital
N1DCS.10MAV82AN002_LP | 27300 | #1机#2润滑油风机 |  | digital
N1DCS.10MAX01AP002_LP | 27301 | #1机#2EH油泵 |  | digital
N1DCS.10MAX01AP012_LP | 27302 | #1机#2EH油循环泵 |  | digital
N1DCS.10PAA12AA001_LP | 27303 | #2旋转滤网冲洗水电动门 |  | digital
N1DCS.10PAB10AA001_LP | 27304 | 循环水母管电动联络门 |  | digital
N1DCS.10PAB12AA002_LP | 27305 | #2循环水泵出口液控蝶阀 |  | digital
N1DCS.10PAB12AT001_LP | 27306 | #2旋转滤网 |  | int32
N1DCS.10PAB31AA002_LP | 27307 | 循环水母管至循泵冷却水电动门 |  | digital
N1DCS.10PAB51AP001_LP | 27308 | #2循环水泵冷却水#1加压泵 |  | digital
N1DCS.10PAB52AP001_LP | 27309 | #2循环水泵冷却水#2加压泵 |  | digital
N1DCS.10PAB62AA001_LP | 27310 | 生活水至#2循环水泵冷却水电磁阀 |  | digital
N1DCS.10PAC12AP001_LP | 27311 | #2循环水泵 |  | int32
N1DCS.10PAC12AP001H_LP | 27312 | #2循环水泵高速 |  | int32
N1DCS.10PAC12AP001L_LP | 27313 | #2循环水泵低速 |  | int32
N1DCS.10PAR01AA002MODE | 27314 | #1冷却塔进水流量电动调节阀 |  | digital
N1DCS.10PSA02AP001_LP | 27315 | #1冷却塔排水池#2排污泵 |  | digital
N1DCS.CIRPMPB_STPMTLP | 27316 | #2循环水泵启允许条件 |  | digital
N1DCS.CIRPMPB_TRIP | 27317 | #2循环水泵跳闸条件 |  | digital
N1DCS.CIRPMPB_TRIPTAG | 27318 | #2循环水泵跳闸条件解除信号 |  | digital
N1DCS.CIRWTRPMPB_SEQSP | 27319 | #2循环水泵停顺控 |  | int32
N1DCS.CIRWTRPMPB_SEQSPAUX | 27320 | #2循环水泵停顺控辅助点 |  | digital
N1DCS.CIRWTRPMPB_SEQSPAUX1 | 27321 | #2循环水泵停顺控第1步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSPAUX2 | 27322 | #2循环水泵停顺控第2步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSPAUX3 | 27323 | #2循环水泵停顺控第3步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSPAUX4 | 27324 | #2循环水泵停顺控第4步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSPLP | 27325 | #2循环水泵停顺控状态 |  | digital
N1DCS.CIRWTRPMPB_SEQST | 27326 | #2循环水泵启顺控 |  | int32
N1DCS.CIRWTRPMPB_SEQSTAUX | 27327 | #2循环水泵启顺控辅助点 |  | digital
N1DCS.CIRWTRPMPB_SEQSTAUX0 | 27328 | #2循环水泵启顺控启允许条件 |  | int32
N1DCS.CIRWTRPMPB_SEQSTAUX1 | 27329 | #2循环水泵启顺控第1步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSTAUX2 | 27330 | #2循环水泵启顺控第2步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSTAUX3 | 27331 | #2循环水泵启顺控第3步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSTAUX4 | 27332 | #2循环水泵启顺控第4步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSTAUX5 | 27333 | #2循环水泵启顺控第5步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSTAUX6 | 27334 | #2循环水泵启顺控第6步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSTAUX7 | 27335 | #2循环水泵启顺控第7步完成条件 |  | digital
N1DCS.CIRWTRPMPB_SEQSTLP | 27336 | #2循环水泵启顺控状态 |  | digital
N1DCS.LUBWTINPREPMPB_BYLP | 27337 | #2循环水泵冷却水加压泵 |  | digital
N1DCS.ROTFLTRB_SEQST | 27338 | #2旋转滤网冲洗顺控 |  | digital
N1DCS.ROTFLTRB_SEQSTAUX | 27339 | #2旋转滤网冲洗顺控辅助点 |  | digital
N1DCS.ROTFLTRB_SEQSTLP | 27340 | #2旋转滤网冲洗顺控状态 |  | digital
N1DCS.VACMPMPAB_PMTLP | 27341 | #2真空泵启允许条件 |  | int32
N1DCS.VACMPMPB_SEQSP | 27342 | #2真空泵停顺控 |  | int32
N1DCS.VACMPMPB_SEQSPAUX | 27343 | #2真空泵停顺控辅助点 |  | digital
N1DCS.VACMPMPB_SEQSPAUX1 | 27344 | #2真空泵停顺控第1步完成条件 |  | digital
N1DCS.VACMPMPB_SEQSPAUX2 | 27345 | #2真空泵停顺控第2步完成条件 |  | digital
N1DCS.VACMPMPB_SEQSPLP | 27346 | #2真空泵停顺控状态 |  | digital
N1DCS.VACMPMPB_SEQST | 27347 | #2真空泵启顺控 |  | int32
N1DCS.VACMPMPB_SEQSTAUX | 27348 | #2真空泵启顺控辅助点 |  | digital
N1DCS.VACMPMPB_SEQSTAUX0 | 27349 | #2真空泵启顺控启允许条件 |  | int32
N1DCS.VACMPMPB_SEQSTAUX1 | 27350 | #2真空泵启顺控第1步完成条件 |  | digital
N1DCS.VACMPMPB_SEQSTAUX2 | 27351 | #2真空泵启顺控第2步完成条件 |  | digital
N1DCS.VACMPMPB_SEQSTAUX3 | 27352 | #2真空泵启顺控第3步完成条件 |  | digital
N1DCS.VACMPMPB_SEQSTLP | 27353 | #2真空泵启顺控状态 |  | digital
N1DCS.VACMPMPB_TRIP | 27354 | #2真空泵跳闸条件 |  | digital
N1DCS.VACMPMPB_TRIPTAG | 27355 | #2真空泵跳闸条件解除信号 |  | digital
N1DCS.10HAD74AA401_LP | 27356 | #1炉低压蒸发器排污至定排电动门 |  | digital
N1DCS.10HAD75AA001_LP | 27357 | #1炉低压汽包连排电动门 |  | digital
N1DCS.10HAD75AA101_MODE | 27358 | #1炉低压汽包连排电动调节门 |  | digital
N1DCS.10HAD76AA001_LP | 27359 | #1炉低压汽包启动放水电动门 |  | digital
N1DCS.10HAD76AA002_LP | 27360 | #2炉低压汽包启动放水电动调节门 |  | digital
N1DCS.10HAH70AA502_LP | 27361 | #1炉低压饱和蒸汽放空电动门 |  | digital
N1DCS.10HAJ80AA502_LP | 27362 | 一级再热器进口集箱放空门 |  | digital
N1DCS.10HAJ80AA504_LP | 27363 | 一级再热器出口集箱放空电动门 |  | digital
N1DCS.10HAJ81AA402_LP | 27364 | #1炉一级再热器连接管疏水电动门 |  | digital
N1DCS.10HAJ81AA404_LP | 27365 | #1炉二级再热器进口管疏水电动门 |  | digital
N1DCS.10LAA70AA501_LP | 27366 | #1炉除氧头放空电动门 |  | digital
N1DCS.10LAB70AA101_MODE | 27367 | #1炉低压给水调节阀 |  | digital
N1DCS.10LAF80AA002_LP | 27368 | #1炉一级再热器减温水电动门 |  | digital
N1DCS.10LAF80AA004_LP | 27369 | #1炉二级再热器减温水电动门 |  | digital
N1DCS.10LAF80AA101_MODE | 27370 | #1炉一级再热器减温水气动调节阀 |  | digital
N1DCS.10LAF80AA102_MODE | 27371 | #1炉二级再热器减温水气动调节阀 |  | digital
N1DCS.10LBA70AA402_LP | 27372 | #1炉低压过热器出口疏水电动门 |  | digital
N1DCS.10LBA70AA502_LP | 27373 | #1炉低压过热器启动排汽电动门 |  | digital
N1DCS.10LBB80AA502_LP | 27374 | #1炉热再主蒸汽启动排气电动门 |  | digital
N1DCS.10LBC80AA402_LP | 27375 | #1炉冷再进口疏水罐疏水电动门 |  | digital
N1DCS.10LBG70AA002_LP | 27376 | 辅汽至#1炉除氧头电动门 |  | digital
N1DCS.10LBG70AA101_MODE | 27377 | 辅汽至#1炉除氧头气动调节阀 |  | digital
N1DCS.10LCC70AA502_LP | 27378 | #1炉低压省煤器放空电动门 |  | digital
N1DCS.10LCC71AA101_MODE | 27379 | 低压省煤器再循环泵出口气动调阀 |  | digital
N1DCS.10LCC72AA003_LP | 27380 | 低压省煤器#1再循环泵出口电动门 |  | digital
N1DCS.10LCC72AP001_LP | 27381 | #1炉低压省煤器#1再循环泵 |  | digital
N1DCS.10LCC72AP001DY_LP | 27382 | 低压省煤器#1再循环泵电机电加热 |  | digital
N1DCS.10LCC73AA003_LP | 27383 | 低压省煤器#2再循环泵出口电动门 |  | digital
N1DCS.10LCC73AP001_LP | 27384 | #1炉低压省煤器#2再循环泵 |  | digital
N1DCS.10LCC73AP001DY_LP | 27385 | 低压省煤器#1再循环泵电机电加热 |  | digital
N1DCS.10LCQ74AA101_MODE | 27386 | #1炉连排至定排气动调节阀 |  | digital
N1DCS.LPDRUMCP_LP | 27387 | #1炉低压汽包压力 |  | digital
N1DCS.LPDRUMCTD_LP | 27388 | #1炉低压汽包下壁温 |  | digital
N1DCS.LPDRUMCTU_LP | 27389 | #1炉低压汽包上壁温 |  | digital
N1DCS.LPDRUMLVL_DIFLP | 27390 | Ovation Control Builder |  | int32
N1DCS.LPDRUMLVL_LP | 27391 | #1炉低压汽包液位 |  | digital
N1DCS.LPDSTCF_LP | 27392 | #1炉低压主蒸汽流量 |  | digital
N1DCS.LPDSTCP_LP | 27393 | #1炉低压主蒸汽压力 |  | digital
N1DCS.LPDSTCT_LP | 27394 | #1炉低压主蒸汽温度 |  | digital
N1DCS.LPDWTCF_LP | 27395 | #1炉低压汽包给水流量 |  | digital
N1DCS.LPDWTCT_LP | 27396 | #1炉低压汽包给水温度 |  | digital
N1DCS.LPECON_SEQST | 27397 | 低压省煤器再循环系统启顺控 |  | digital
N1DCS.LPECON_SEQSTAUX | 27398 | 低省再循环系统启顺控辅助点 |  | digital
N1DCS.LPECON_SEQSTLP | 27399 | 低压省煤器再循环系统启顺控状态 |  | digital
N1DCS.LPECONP_BYLP | 27400 | 低压省煤器再循环泵 |  | digital
N1DCS.LPECONPA_SEQSP | 27401 | #1低省再循环泵停顺控 |  | digital
N1DCS.LPECONPA_SEQSPAUX | 27402 | #1低省再循环泵停顺控辅助点 |  | digital
N1DCS.LPECONPA_SEQSPLP | 27403 | #1低省再循环泵停顺控状态 |  | digital
N1DCS.LPECONPA_SEQST | 27404 | #1低省再循环泵启顺控 |  | digital
N1DCS.LPECONPA_SEQSTAUX | 27405 | #1低省再循环泵启顺控辅助点 |  | digital
N1DCS.LPECONPA_SEQSTLP | 27406 | #1低省再循环泵启顺控状态 |  | digital
N1DCS.LPECONPA_STRPEM_LP | 27407 | #1低省再循环泵启允许条件 |  | digital
N1DCS.LPECONPA_TRIP | 27408 | #1低省再循环泵跳闸条件 |  | digital
N1DCS.LPECONPA_TRIPTAG | 27409 | #1低省再循环泵跳闸条件解除 |  | digital
N1DCS.LPECONPB_SEQSP | 27410 | #2低省再循环泵停顺控 |  | digital
N1DCS.LPECONPB_SEQSPAUX | 27411 | #2低省再循环泵停顺控辅助点 |  | digital
N1DCS.LPECONPB_SEQSPLP | 27412 | #2低省再循环泵停顺控状态 |  | digital
N1DCS.LPECONPB_SEQST | 27413 | #2低省再循环泵启顺控 |  | digital
N1DCS.LPECONPB_SEQSTAUX | 27414 | #2低省再循环泵启顺控辅助点 |  | digital
N1DCS.LPECONPB_SEQSTLP | 27415 | #2低省再循环泵启顺控状态 |  | digital
N1DCS.LPECONPB_STRPEM_LP | 27416 | #2低省再循环泵启允许条件 |  | digital
N1DCS.LPECONPB_TRIP | 27417 | #2低省再循环泵跳闸条件 |  | digital
N1DCS.LPECONPB_TRIPTAG | 27418 | #2低省再循环泵跳闸条件解除 |  | digital
N1DCS.LPFW_SEQST | 27419 | 低压汽包上水顺控 |  | digital
N1DCS.LPFW_SEQSTAUX | 27420 | 低压汽包上水顺控辅助点 |  | digital
N1DCS.LPFW_SEQSTAUX0 | 27421 | 低压汽包上水顺控启允许条件 |  | digital
N1DCS.LPFW_SEQSTAUX1 | 27422 | 低压汽包上水顺控第1步完成条件 |  | digital
N1DCS.LPFW_SEQSTAUX2 | 27423 | 低压汽包上水顺控第2步完成条件 |  | digital
N1DCS.LPFW_SEQSTAUX3 | 27424 | 低压汽包上水顺控第3步完成条件 |  | digital
N1DCS.LPFW_SEQSTAUX5 | 27425 | 低压汽包上水顺控第5步完成条件 |  | digital
N1DCS.LPFW_SEQSTLP | 27426 | 低压汽包上水顺控状态 |  | digital
N1DCS.LPMS_SEQST | 27427 | 低压主蒸汽升温升压顺控 |  | digital
N1DCS.LPMS_SEQSTAUX | 27428 | 低压主蒸汽升温升压顺控辅助点 |  | digital
N1DCS.LPMS_SEQSTAUX4 | 27429 | 低压主汽升温升压顺控第4步完成 |  | digital
N1DCS.LPMS_SEQSTLP | 27430 | 低压主蒸汽升温升压顺控状态 |  | digital
N1DCS.RH2INSTCT_LP | 27431 | #1炉一级再热器减温器后温度 |  | digital
N1DCS.RH2OUTSTCP_LP | 27432 | #1炉一级再热器减温器后压力 |  | digital
N1DCS.RH2OUTSTCT_LP | 27433 | #1炉热再主蒸汽温度 |  | digital
N1DCS.LPFW_SEQSTAUX4 | 27434 | 低压汽包上水顺控第4步完成条件 |  | digital
N1DCS.10HAD84AA401_LP | 27435 | #1炉中压蒸发器排污至定排电动门 |  | digital
N1DCS.10HAD85AA001_LP | 27436 | #1炉中压汽包连排电动门 |  | digital
N1DCS.10HAD85AA101_MODE | 27437 | #1炉中压汽包连排气动调节阀 |  | digital
N1DCS.10HAD86AA001_LP | 27438 | #1炉中压汽包启动放水电动门 |  | digital
N1DCS.10HAD86AA002_LP | 27439 | #1炉中压汽包启动放水电动调节门 |  | digital
N1DCS.10HAH80AA502_LP | 27440 | #1炉中压饱和蒸汽放空电动门 |  | digital
N1DCS.10HNE70AA001_LP | 27441 | #1炉烟囱出口挡板 |  | digital
N1DCS.10LAB81AA001_LP | 27442 | #1炉#1中压给水泵出口电动门 |  | digital
N1DCS.10LAB81AP001_LP | 27443 | #1炉#1中压给水泵 |  | digital
N1DCS.10LAB83AA101_MODE | 27444 | #1炉中压给水气动调节阀 |  | digital
N1DCS.10LAB91AA001_LP | 27445 | #1炉#1高压给水泵出口电动门 |  | digital
N1DCS.10LAB91AP001_LP | 27446 | #1炉#1高压给水泵 |  | digital
N1DCS.10LBA80AA001_LP | 27447 | #1炉中压主蒸汽电动门 |  | digital
N1DCS.10LBA80AA402_LP | 27448 | #1炉中压主蒸汽疏水至定排电动门 |  | digital
N1DCS.10LBA80AA502_LP | 27449 | #1炉中压主蒸汽启动排汽电动门 |  | digital
N1DCS.HPFWPA_SEQSP | 27450 | #1高压给水泵停顺控 |  | digital
N1DCS.HPFWPA_SEQSPAUX | 27451 | #1高压给水泵停顺控辅助点 |  | digital
N1DCS.HPFWPA_SEQSPAUX0 | 27452 | #1高压给水泵停顺控启允许条件 |  | int32
N1DCS.HPFWPA_SEQSPLP | 27453 | #1高压给水泵停顺控状态 |  | digital
N1DCS.HPFWPA_SEQST | 27454 | #1高压给水泵启顺控 |  | digital
N1DCS.HPFWPA_SEQSTAUX | 27455 | #1高压给水泵启顺控辅助点 |  | digital
N1DCS.HPFWPA_SEQSTLP | 27456 | #1高压给水泵启顺控状态 |  | digital
N1DCS.HPFWPA_STRPEM_LP | 27457 | #1高压给水泵启允许条件 |  | digital
N1DCS.HPFWPA_TRIP | 27458 | #1高压给水泵跳闸条件 |  | digital
N1DCS.HPFWPA_TRIPTAG | 27459 | #1高压给水泵跳闸条件解除信号 |  | digital
N1DCS.HPFWPATCUT | 27460 | #1高给泵超温保护报警解除信号 |  | digital
N1DCS.IPDRUMCP_LP | 27461 | #1炉中压汽包压力 |  | digital
N1DCS.IPDRUMCTD_LP | 27462 | #1炉中压汽包下壁温 |  | digital
N1DCS.IPDRUMCTU_LP | 27463 | #1炉中压汽包上壁温 |  | digital
N1DCS.IPDRUMLVL_DIFLP | 27464 | #1炉中压汽包液位偏差 |  | digital
N1DCS.IPDRUMLVL_LP | 27465 | #1炉中压汽包液位（计算后） |  | digital
N1DCS.IPDSTCF_LP | 27466 | #1炉中压主蒸汽流量 |  | digital
N1DCS.IPDSTCP_LP | 27467 | #1炉中压主蒸汽压力 |  | digital
N1DCS.IPDSTCT_LP | 27468 | #1炉中压主蒸汽温度 |  | digital
N1DCS.IPDWTCF_LP | 27469 | #1炉中压给水流量（计算后） |  | digital
N1DCS.IPDWTCT_LP | 27470 | #1炉中压给水温度 |  | digital
N1DCS.IPFW_SEQST | 27471 | 中压汽包上水顺控 |  | digital
N1DCS.IPFW_SEQSTAUX | 27472 | 中压汽包上水顺控辅助点 |  | digital
N1DCS.IPFW_SEQSTAUX0 | 27473 | 中压汽包上水顺控启允许条件 |  | digital
N1DCS.IPFW_SEQSTAUX1 | 27474 | 中压汽包上水顺控第1步完成条件 |  | digital
N1DCS.IPFW_SEQSTAUX2 | 27475 | 中压汽包上水顺控第2步完成条件 |  | digital
N1DCS.IPFW_SEQSTAUX3 | 27476 | 中压汽包上水顺控第3步完成条件 |  | digital
N1DCS.IPFW_SEQSTLP | 27477 | 中压汽包上水顺控状态 |  | digital
N1DCS.IPFWP_BYLP | 27478 | #1炉中压给水泵备用 |  | digital
N1DCS.IPFWPA_SEQSP | 27479 | #1中压给水泵停顺控 |  | digital
N1DCS.IPFWPA_SEQSPAUX | 27480 | #1中压给水泵停顺控辅助点 |  | digital
N1DCS.IPFWPA_SEQSPAUX0 | 27481 | #1中压给水泵停顺控启允许条件 |  | digital
N1DCS.IPFWPA_SEQSPLP | 27482 | #1中压给水泵停顺控状态 |  | digital
N1DCS.IPFWPA_SEQST | 27483 | #1中压给水泵启顺控 |  | digital
N1DCS.IPFWPA_SEQSTAUX | 27484 | #1中压给水泵启顺控辅助点 |  | digital
N1DCS.IPFWPA_SEQSTLP | 27485 | #1中压给水泵启顺控状态 |  | digital
N1DCS.IPFWPA_STRPEM_LP | 27486 | #1中压给水泵启顺控启允许条件 |  | digital
N1DCS.IPFWPA_TRIP | 27487 | #1中压给水泵跳闸条件 |  | digital
N1DCS.IPFWPA_TRIPTAG | 27488 | #1中压给水泵跳闸条件解除信号 |  | digital
N1DCS.IPFWPATCUT | 27489 | #1中给泵超温保护报警解除信号 |  | digital
N1DCS.IPMS_SEQST | 27490 | 中压主蒸汽升温升压顺控 |  | digital
N1DCS.IPMS_SEQSTAUX | 27491 | 中压主蒸汽升温升压顺控辅助点 |  | digital
N1DCS.IPMS_SEQSTAUX2 | 27492 | 中压主汽升温升压顺控第2步完成 |  | digital
N1DCS.IPMS_SEQSTAUX6 | 27493 | 中压主汽升温升压顺控第6步完成 |  | digital
N1DCS.IPMS_SEQSTAUX7 | 27494 | 中压主汽升温升压顺控第7步完成 |  | digital
N1DCS.IPMS_SEQSTLP | 27495 | 中压主蒸汽升温升压顺控状态 |  | digital
N1DCS.10XAV91GH001AP_BYLP | 27496 | #1高压给水泵稀油站油泵 |  | digital
N1DCS.10XAV91GH001AP1_LP | 27497 | #1炉#1稀油站#1润滑油泵 |  | digital
N1DCS.10XAV91GH001AP2_LP | 27498 | #1炉#1稀油站#2润滑油泵 |  | digital
N1DCS.10XAV91GH001HT_LP | 27499 | #1炉#1稀油站电加热器 |  | digital
N1DCS.HPFWPA_SEQBPST | 27500 | #1高压给水泵变频启顺控 |  | digital
N1DCS.HPFWPA_SEQBPSTAUX | 27501 | #1高压给水泵变频启顺控辅助点 |  | digital
N1DCS.HPFWPA_SEQBPSTAUX0 | 27502 | #1高给泵变频启顺控启允许条件 |  | digital
N1DCS.HPFWPA_SEQBPSTAUX1 | 27503 | #1高给泵变频启顺控1步完成条件 |  | digital
N1DCS.HPFWPA_SEQBPSTAUX2 | 27504 | #1高给泵变频启顺控2步完成条件 |  | digital
N1DCS.HPFWPA_SEQBPSTAUX3 | 27505 | #1高给泵变频启顺控3步完成条件 |  | digital
N1DCS.HPFWPA_SEQBPSTAUX4 | 27506 | #1高给泵变频启顺控4步完成条件 |  | digital
N1DCS.HPFWPA_SEQBPSTLP | 27507 | #1高压给水泵变频启顺控系统 |  | digital
N1DCS.HPFWPA_SEQSPAUX1 | 27508 | #1高压给水泵停顺控1步完成条件 |  | digital
N1DCS.HPFWPA_SEQSPAUX2 | 27509 | #1高压给水泵停顺控2步完成条件 |  | digital
N1DCS.HPFWPA_SEQSTAUX0 | 27510 | #1高给泵工频启顺控启允许条件 |  | digital
N1DCS.HPFWPA_SEQSTAUX1 | 27511 | #1高给泵工频启顺控1步完成条件 |  | digital
N1DCS.HPFWPA_SEQSTAUX2 | 27512 | #1高给泵工频启顺控2步完成条件 |  | digital
N1DCS.HPFWPA_SEQSTAUX3 | 27513 | #1高给泵工频启顺控3步完成条件 |  | digital
N1DCS.HPFWPA_SEQSTAUX4 | 27514 | #1高给泵工频启顺控4步完成条件 |  | digital
N1DCS.HRSGTRIPP | 27515 | #1余热锅炉主保护条件 |  | int32
N1DCS.IPFW_SEQSTAUX4 | 27516 | 中压汽包上水顺控第4步完成条件 |  | digital
N1DCS.IPFW_SEQSTAUX5 | 27517 | 中压汽包上水顺控第5步完成条件 |  | digital
N1DCS.IPMS_SEQSTAUX4 | 27518 | 中压主汽升温升压顺控第4步完成 |  | digital
N1DCS.IPMS_SEQSTAUX8 | 27519 | 中压主汽升温升压顺控第8步完成 |  | digital
N1DCS.STTRIPLP1 | 27520 | #1机主保护条件 |  | int32
N1DCS.STTRIPTAGLP1 | 27521 | #1机主保护条件解除信号 |  | int32
N1DCS.10HAC90AA502_LP | 27522 | #1炉高压省煤器放空电动门 |  | digital
N1DCS.10HAD91AA405_LP | 27523 | #1炉高压蒸发器排污至定排电动门 |  | digital
N1DCS.10HAD95AA001_LP | 27524 | #1炉高压汽包连排电动门 |  | digital
N1DCS.10HAD95AA101_MODE | 27525 | #1炉高压汽包连排气动调节阀 |  | digital
N1DCS.10HAD96AA001_LP | 27526 | #1炉高压汽包启动放水电动门 |  | digital
N1DCS.10HAD96AA002_LP | 27527 | #1炉高压汽包启动放水电动调节门 |  | digital
N1DCS.10HAH90AA402_LP | 27528 | 高压一级过热器出口疏水电动门 |  | digital
N1DCS.10HAH90AA412_LP | 27529 | 高压二级过热器出口疏水电动门 |  | int32
N1DCS.10HAH90AA502_LP | 27530 | #1炉高压饱和蒸汽放空电动门 |  | digital
N1DCS.10HAH90AA504_LP | 27531 | 高压二级过热器出口放空电动门 |  | digital
N1DCS.10LAB82AA001_LP | 27532 | #1炉#2中压给水泵出口电动门 |  | digital
N1DCS.10LAB82AP001_LP | 27533 | #1炉#2中压给水泵 |  | digital
N1DCS.10LAB90AA101_MODE | 27534 | #1炉高压给水气动调节阀 |  | digital
N1DCS.10LAB92AA001_LP | 27535 | #1炉#2高压给水泵出口电动门 |  | digital
N1DCS.10LAB92AP001_LP | 27536 | #1炉#2高压给水泵 |  | digital
N1DCS.10LAC91GX0001_LP | 27537 | 高压给水泵变频器 |  | digital
N1DCS.10LAC91GX0001_MODE | 27538 | 高压给水泵变频器频率控制 |  | digital
N1DCS.10LAE90AA002_LP | 27539 | #1炉高压二级过热器减温水电动门 |  | digital
N1DCS.10LAE90AA004_LP | 27540 | #1炉高压主蒸汽减温水电动门 |  | digital
N1DCS.10LAE90AA101_MODE | 27541 | 高压二级过热器减温水气动调节阀 |  | digital
N1DCS.10LAE90AA102_MODE | 27542 | #1炉高压主蒸汽减温水气动调节阀 |  | digital
N1DCS.10LAE91AA101_MODE | 27543 | #1炉高压省煤器旁路气动调节阀 |  | digital
N1DCS.10LBA90AA502_LP | 27544 | #1炉高压主蒸汽启动排汽电动门 |  | digital
N1DCS.10LBG90AA001_LP | 27545 | 辅汽至#1炉高压蒸发器电动门 |  | digital
N1DCS.GYSJGRQJKWD_LP | 27546 | #1炉高压三级过热器进口温度 |  | digital
N1DCS.HPDRUMCP_LP | 27547 | #1炉高压汽包压力 |  | digital
N1DCS.HPDRUMCTD_LP | 27548 | #1炉高压汽包下外壁温 |  | digital
N1DCS.HPDRUMCTU_LP | 27549 | #1炉高压汽包上外壁温 |  | digital
N1DCS.HPDRUMCTU2_LP | 27550 | #1炉高压汽包上内壁温 |  | digital
N1DCS.HPDRUMLVL_DIFLP | 27551 | #1炉高压汽包液位偏差 |  | digital
N1DCS.HPDRUMLVL_LP | 27552 | #1炉高压汽包液位 |  | digital
N1DCS.HPDSTCF_LP | 27553 | #1炉高压主蒸汽流量（计算后） |  | digital
N1DCS.HPDSTCP_LP | 27554 | #1炉高压主蒸汽压力 |  | digital
N1DCS.HPDSTCT_LP | 27555 | #1炉高压主蒸汽温度 |  | digital
N1DCS.HPDWTCF_LP | 27556 | #1炉高压给水流量（计算后） |  | digital
N1DCS.HPDWTCT_LP | 27557 | #1炉高压给水温度（计算后） |  | digital
N1DCS.HPFW_SEQST | 27558 | 高压汽包上水顺控 |  | digital
N1DCS.HPFW_SEQSTAUX | 27559 | 高压汽包上水顺控辅助点 |  | digital
N1DCS.HPFW_SEQSTAUX0 | 27560 | 高压汽包上水顺控启允许条件 |  | digital
N1DCS.HPFW_SEQSTAUX1 | 27561 | 高压汽包上水顺控第1步完成条件 |  | digital
N1DCS.HPFW_SEQSTAUX2 | 27562 | 高压汽包上水顺控第2步完成条件 |  | digital
N1DCS.HPFW_SEQSTAUX3 | 27563 | 高压汽包上水顺控第3步完成条件 |  | digital
N1DCS.HPFW_SEQSTAUX6 | 27564 | 高压汽包上水顺控第6步完成条件 |  | digital
N1DCS.HPFW_SEQSTLP | 27565 | 高压汽包上水顺控状态 |  | digital
N1DCS.HPFWP_BYLP | 27566 | #1炉高压给水泵 |  | digital
N1DCS.HPFWPB_SEQSP | 27567 | #2高压给水泵停顺控 |  | digital
N1DCS.HPFWPB_SEQSPAUX | 27568 | #2高压给水泵停顺控辅助点 |  | digital
N1DCS.HPFWPB_SEQSPAUX0 | 27569 | #2高压给水泵停顺控启允许条件 |  | digital
N1DCS.HPFWPB_SEQSPLP | 27570 | #2高压给水泵停顺控状态 |  | digital
N1DCS.HPFWPB_SEQST | 27571 | #2高压给水泵启顺控 |  | digital
N1DCS.HPFWPB_SEQSTAUX | 27572 | #2高压给水泵启顺控辅助点 |  | digital
N1DCS.HPFWPB_SEQSTLP | 27573 | #2高压给水泵启顺控状态 |  | digital
N1DCS.HPFWPB_STRPEM_LP | 27574 | #2高压给水泵启允许条件 |  | digital
N1DCS.HPFWPB_TRIP | 27575 | #2高压给水泵跳闸条件 |  | digital
N1DCS.HPFWPB_TRIPTAG | 27576 | #2高压给水泵跳闸条件解除信号 |  | digital
N1DCS.HPFWPBTCUT | 27577 | #2高给泵超温保护报警解除信号 |  | digital
N1DCS.HPMS_SEQST | 27578 | 高压主蒸汽升温升压顺控 |  | digital
N1DCS.HPMS_SEQSTAUX | 27579 | 高压主蒸汽升温升压顺控辅助点 |  | digital
N1DCS.HPMS_SEQSTAUX1 | 27580 | 高压主蒸汽升温升压顺控1步完成 |  | digital
N1DCS.HPMS_SEQSTAUX2 | 27581 | 高压主蒸汽升温升压顺控2步完成 |  | digital
N1DCS.HPMS_SEQSTAUX3 | 27582 | 高压主蒸汽升温升压顺控3步完成 |  | digital
N1DCS.HPMS_SEQSTAUX4 | 27583 | 高压主蒸汽升温升压顺控4步完成 |  | digital
N1DCS.HPMS_SEQSTLP | 27584 | 高压主蒸汽升温升压顺控状态 |  | digital
N1DCS.IPFWPB_SEQSP | 27585 | #2中压给水泵停顺控 |  | digital
N1DCS.IPFWPB_SEQSPAUX | 27586 | #2中压给水泵停顺控辅助点 |  | digital
N1DCS.IPFWPB_SEQSPAUX0 | 27587 | #2中压给水泵停顺控启允许条件 |  | digital
N1DCS.IPFWPB_SEQSPLP | 27588 | #2中压给水泵停顺控状态 |  | digital
N1DCS.IPFWPB_SEQST | 27589 | #2中压给水泵启顺控 |  | digital
N1DCS.IPFWPB_SEQSTAUX | 27590 | #2中压给水泵启顺控辅助点 |  | digital
N1DCS.IPFWPB_SEQSTLP | 27591 | #2中压给水泵启顺控状态 |  | digital
N1DCS.IPFWPB_STRPEM_LP | 27592 | #2中压给水泵启顺控启允许条件 |  | digital
N1DCS.IPFWPB_TRIP | 27593 | #2中压给水泵跳闸条件 |  | digital
N1DCS.IPFWPB_TRIPTAG | 27594 | #2中压给水泵跳闸条件解除信号 |  | digital
N1DCS.IPFWPBTCUT | 27595 | #2中给泵超温保护报警解除信号 |  | digital
N1DCS.10LBA90AA192_LP | 27596 | #1炉高压主蒸汽出口PCV阀 |  | digital
N1DCS.10XAV92GH001AP_BYLP | 27597 | #2高压给水泵稀油站油泵 |  | digital
N1DCS.10XAV92GH001AP1_LP | 27598 | #1炉#2稀油站#1润滑油泵 |  | digital
N1DCS.10XAV92GH001AP2_LP | 27599 | #1炉#2稀油站#2润滑油泵 |  | digital
N1DCS.10XAV92GH001HT_LP | 27600 | #1炉#2稀油站电加热器 |  | digital
N1DCS.HPDRUMCT_LP | 27601 | #1炉高压汽包下壁温 |  | digital
N1DCS.HPFW_SEQSTAUX4 | 27602 | 高压汽包上水顺控第4步完成条件 |  | digital
N1DCS.HPFW_SEQSTAUX5 | 27603 | 高压汽包上水顺控第5步完成条件 |  | digital
N1DCS.HPFWPB_SEQBPST | 27604 | #2高压给水泵变频启顺控 |  | digital
N1DCS.HPFWPB_SEQBPSTAUX | 27605 | #2高压给水泵变频启顺控辅助点 |  | digital
N1DCS.HPFWPB_SEQBPSTAUX0 | 27606 | #2高给泵变频启顺控启允许条件 |  | digital
N1DCS.HPFWPB_SEQBPSTAUX1 | 27607 | #2高给泵变频启顺控1步完成条件 |  | digital
N1DCS.HPFWPB_SEQBPSTAUX2 | 27608 | #2高给泵变频启顺控2步完成条件 |  | digital
N1DCS.HPFWPB_SEQBPSTAUX3 | 27609 | #2高给泵变频启顺控3步完成条件 |  | digital
N1DCS.HPFWPB_SEQBPSTAUX4 | 27610 | #2高给泵变频启顺控4步完成条件 |  | digital
N1DCS.HPFWPB_SEQBPSTLP | 27611 | #2高压给水泵变频启顺控系统 |  | digital
N1DCS.HPFWPB_SEQSPAUX1 | 27612 | #2高压给水泵停顺控1步完成条件 |  | digital
N1DCS.HPFWPB_SEQSPAUX2 | 27613 | #2高压给水泵停顺控2步完成条件 |  | digital
N1DCS.HPFWPB_SEQSTAUX0 | 27614 | #2高给泵工频启顺控启允许条件 |  | digital
N1DCS.HPFWPB_SEQSTAUX1 | 27615 | #2高给泵工频启顺控1步完成条件 |  | digital
N1DCS.HPFWPB_SEQSTAUX2 | 27616 | #2高给泵工频启顺控2步完成条件 |  | digital
N1DCS.HPFWPB_SEQSTAUX3 | 27617 | #2高给泵工频启顺控3步完成条件 |  | digital
N1DCS.HPFWPB_SEQSTAUX4 | 27618 | #2高给泵工频启顺控4步完成条件 |  | digital
N1DCS.HPMS_SEQSTAUX5 | 27619 | 高压主蒸汽升温升压顺控5步完成 |  | digital
N1DCS.HRSGTP | 27620 | 余热锅炉保护跳闸条件 |  | int32
N1DCS.10BBA00GS001_LP | 27621 | 6KV IA段工作电源开关61A01 |  | int32
N1DCS.10BBB00GS002_LP | 27622 | 6KV IB段备用电源开关61B02 |  | int32
N1DCS.10BFA00GS201_LP | 27623 | 工作PC IA段至保安段开关41A104 |  | int32
N1DCS.10BFB00GS001_LP | 27624 | 380V工作PC段分段开关41B021 |  | digital
N1DCS.10BFT10GS101_LP | 27625 | 工作1A变6kV侧开关61A10 |  | int32
N1DCS.10BFT10GS102_LP | 27626 | 工作1A变380V侧开关41A011 |  | int32
N1DCS.10BJD00GS201_LP | 27627 | 工作PC IA至#2机MCC A开关41A032 |  | digital
N1DCS.10BJE00GS201_LP | 27628 | 工作PC IA至#2机MCC B开关41A042 |  | digital
N1DCS.10BNA00GS201_LP | 27629 | 保安段至#2机EMCC段开关41E015 |  | digital
N1DCS.QJBW_SEQST | 27630 | #1机并网顺控 |  | digital
N1DCS.QJBW_SEQSTAUX | 27631 | #1机并网顺控辅助点 |  | digital
N1DCS.QJBW_SEQSTAUX0 | 27632 | #1机并网顺控启允许条件 |  | digital
N1DCS.QJBW_SEQSTAUX1 | 27633 | #1机并网顺控第1步完成条件 |  | digital
N1DCS.QJBW_SEQSTAUX2 | 27634 | #1机并网顺控第2步完成条件 |  | digital
N1DCS.QJBW_SEQSTAUX3 | 27635 | #1机并网顺控第3步完成条件 |  | digital
N1DCS.QJBW_SEQSTAUX4 | 27636 | #1机并网顺控第4步完成条件 |  | digital
N1DCS.QJBW_SEQSTAUX5 | 27637 | #1机并网顺控第5步完成条件 |  | digital
N1DCS.QJBW_SEQSTAUX6 | 27638 | #1机并网顺控第6步完成条件 |  | digital
N1DCS.QJBW_SEQSTLP | 27639 | #1机并网顺控状态 |  | digital
N1DCS.QJTQYX | 27640 | #1机同期允许条件 |  | digital
N1DCS.10BBA00GS002_LP | 27641 | 6kV IA段备用电源进线开关61A02 |  | int32
N1DCS.10BBB00GS001_LP | 27642 | 6kV IB段工作电源进线开关61B01 |  | int32
N1DCS.10BFB00GS201_LP | 27643 | 工作PC IB段至保安段开关41B103 |  | int32
N1DCS.10BFT20GS101_LP | 27644 | 工作IB变6kV侧开关61B10 |  | int32
N1DCS.10BFT20GS102_LP | 27645 | 工作IB变380V侧开关41B011 |  | int32
N1DCS.10BJD00GS202_LP | 27646 | 工作PC IB至#2机MCC A开关41B032 |  | digital
N1DCS.10BJE00GS202_LP | 27647 | 工作PC IB至#2机MCC B开关41B042 |  | digital
N1DCS.10BMA00GS001_LP | 27648 | 柴油发电机至保安段开关41E092 |  | digital
N1DCS.10BMA00GS002_LP | 27649 | 保安段工作电源K12开关41E101 |  | digital
N1DCS.10BMA00GS003_LP | 27650 | 保安段工作电源K13开关41E111 |  | digital
N1DCS.10BNA00GS202_LP | 27651 | 工作IB段至#2机EMCC段开关41B051 |  | digital
N1DCS.APSSPBP1_SEQ | 27652 | 降负荷断点1命令 |  | digital
N1DCS.APSSPBP1_SEQAUX | 27653 | 降负荷断点1辅助点 |  | digital
N1DCS.APSSPBP2_SEQ | 27654 | #2机打闸断点命令 |  | digital
N1DCS.APSSPBP2_SEQAUX | 27655 | #2机打闸断点辅助点 |  | digital
N1DCS.APSSPBP3_SEQ | 27656 | 余热锅炉停止断点命令 |  | int32
N1DCS.APSSPBP3_SEQAUX | 27657 | 余热锅炉停止断点辅助点 |  | int32
N1DCS.APSSPBP4_SEQ | 27658 | 机组停运断点命令 |  | int32
N1DCS.APSSPBP4_SEQAUX | 27659 | 机组停运断点辅助点 |  | int32
N1DCS.APSSTBP1_SEQ | 27660 | 系统准备断点命令 |  | int32
N1DCS.APSSTBP1_SEQAUX | 27661 | 系统准备断点辅助点 |  | int32
N1DCS.APSSTBP2_SEQ | 27662 | 机组上水断点命令 |  | int32
N1DCS.APSSTBP2_SEQAUX | 27663 | 机组上水断点辅助点 |  | int32
N1DCS.APSSTBP3_SEQ | 27664 | #2机点火断点指令 |  | digital
N1DCS.APSSTBP3_SEQAUX | 27665 | #2机点火断点辅助点 |  | digital
N1DCS.APSSTBP4_SEQ | 27666 | #1机并网断点指令 |  | digital
N1DCS.APSSTBP4_SEQAUX | 27667 | #1机并网断点辅助点 |  | digital
N1DCS.APSSTBP5_SEQ | 27668 | 升负荷断点指令 |  | int32
N1DCS.APSSTBP5_SEQAUX | 27669 | 升负荷断点辅助点 |  | int32
N1DCS.10MYB10EE102XB02DO | 27670 | Ovation Control Builder |  | int32
N1DCS.APSSPBP1_SEQ2 | 27671 | Ovation Control Builder |  | int32
N1DCS.APSSPBP1_SEQDV06 | 27672 | Ovation Control Builder |  | int32
N1DCS.APSSPBP1_SEQDV07 | 27673 | Ovation Control Builder |  | int32
N1DCS.APSSPBP1_SEQDV08 | 27674 | Ovation Control Builder |  | int32
N1DCS.APSSPBP1_SEQDV09 | 27675 | Ovation Control Builder |  | int32
N1DCS.APSSPBP1_SEQDV10 | 27676 | Ovation Control Builder |  | int32
N1DCS.APSSPBP2_SEQ2 | 27677 | Ovation Control Builder |  | int32
N1DCS.APSSPBP2_SEQDV06 | 27678 | Ovation Control Builder |  | int32
N1DCS.APSSPBP2_SEQDV07 | 27679 | Ovation Control Builder |  | int32
N1DCS.APSSPBP2_SEQDV08 | 27680 | Ovation Control Builder |  | int32
N1DCS.APSSPBP2_SEQDV09 | 27681 | Ovation Control Builder |  | int32
N1DCS.APSSPBP2_SEQDV10 | 27682 | Ovation Control Builder |  | int32
N1DCS.APSSPBP3_SEQ2 | 27683 | Ovation Control Builder |  | int32
N1DCS.APSSPBP3_SEQDV06 | 27684 | Ovation Control Builder |  | int32
N1DCS.APSSPBP3_SEQDV07 | 27685 | Ovation Control Builder |  | int32
N1DCS.APSSPBP3_SEQDV08 | 27686 | Ovation Control Builder |  | int32
N1DCS.APSSPBP3_SEQDV09 | 27687 | Ovation Control Builder |  | int32
N1DCS.APSSPBP3_SEQDV10 | 27688 | Ovation Control Builder |  | int32
N1DCS.APSSPBP4_SEQ2 | 27689 | Ovation Control Builder |  | int32
N1DCS.APSSPBP4_SEQDV06 | 27690 | Ovation Control Builder |  | int32
N1DCS.APSSPBP4_SEQDV07 | 27691 | Ovation Control Builder |  | int32
N1DCS.APSSPBP4_SEQDV08 | 27692 | Ovation Control Builder |  | int32
N1DCS.APSSPBP4_SEQDV09 | 27693 | Ovation Control Builder |  | int32
N1DCS.APSSPBP4_SEQDV10 | 27694 | Ovation Control Builder |  | int32
N1DCS.APSSTBP1_SEQ2 | 27695 | Ovation Control Builder |  | int32
N1DCS.APSSTBP1_SEQDV06 | 27696 | Ovation Control Builder |  | int32
N1DCS.APSSTBP2_SEQ2 | 27697 | Ovation Control Builder |  | int32
N1DCS.APSSTBP2_SEQDV06 | 27698 | Ovation Control Builder |  | int32
N1DCS.APSSTBP2_SEQDV07 | 27699 | Ovation Control Builder |  | int32
N1DCS.APSSTBP2_SEQDV08 | 27700 | Ovation Control Builder |  | int32
N1DCS.APSSTBP2_SEQDV09 | 27701 | Ovation Control Builder |  | int32
N1DCS.APSSTBP2_SEQDV10 | 27702 | Ovation Control Builder |  | int32
N1DCS.APSSTBP3_SEQ2 | 27703 | Ovation Control Builder |  | int32
N1DCS.APSSTBP3_SEQDV06 | 27704 | Ovation Control Builder |  | int32
N1DCS.APSSTBP3_SEQDV07 | 27705 | Ovation Control Builder |  | int32
N1DCS.APSSTBP3_SEQDV08 | 27706 | Ovation Control Builder |  | int32
N1DCS.APSSTBP3_SEQDV09 | 27707 | Ovation Control Builder |  | int32
N1DCS.APSSTBP3_SEQDV10 | 27708 | Ovation Control Builder |  | int32
N1DCS.APSSTBP4_SEQ2 | 27709 | Ovation Control Builder |  | int32
N1DCS.APSSTBP4_SEQDV06 | 27710 | Ovation Control Builder |  | int32
N1DCS.APSSTBP4_SEQDV07 | 27711 | Ovation Control Builder |  | int32
N1DCS.APSSTBP4_SEQDV08 | 27712 | Ovation Control Builder |  | int32
N1DCS.APSSTBP4_SEQDV09 | 27713 | Ovation Control Builder |  | int32
N1DCS.APSSTBP4_SEQDV10 | 27714 | Ovation Control Builder |  | int32
N1DCS.APSSTBP5_SEQ2 | 27715 | Ovation Control Builder |  | int32
N1DCS.APSSTBP5_SEQDV06 | 27716 | Ovation Control Builder |  | int32
N1DCS.APSSTBP5_SEQDV07 | 27717 | Ovation Control Builder |  | int32
N1DCS.APSSTBP5_SEQDV08 | 27718 | Ovation Control Builder |  | int32
N1DCS.APSSTBP5_SEQDV09 | 27719 | Ovation Control Builder |  | int32
N1DCS.APSSTBP5_SEQDV10 | 27720 | Ovation Control Builder |  | int32
N1DCS.TCSECSBW_SEQST | 27721 | Ovation Control Builder |  | int32
N1DCS.J0LBD20AA001_LP | 27722 | 供热计量站母管流量计前电动门 |  | digital
N1DCS.J0LBD20AA002_LP | 27723 | 供热计量站母管流量计后电动门 |  | digital
N1DCS.J0LBD20AA003_LP | 27724 | 供热计量站旁路流量计前电动门 |  | int32
N1DCS.J0LBD20AA004_LP | 27725 | 供热计量站旁路流量计后电动门 |  | int32
N1DCS.J0LBG10AA003_LP | 27726 | 辅汽母管#1机侧电动门 |  | digital
N1DCS.J0LBG10AA004_LP | 27727 | 辅汽母管#3机侧电动门 |  | digital
N1DCS.J0LBG10AA005_LP | 27728 | 一、二期辅汽母管联络电动门 |  | int32
N1DCS.J0LBG22AA001_LP | 27729 | 启动锅炉供辅汽母管电动门 |  | digital
N1DCS.J0PGA41AA011_LP | 27730 | #1机闭式水至空压机房供水电动门 |  | digital
N1DCS.J0PGA41AA012_LP | 27731 | #3机闭式水至空压机房供水电动门 |  | digital
N1DCS.J0PGA41AA021_LP | 27732 | 空压机房至#1机闭式水回水电动门 |  | digital
N1DCS.J0PGA41AA022_LP | 27733 | 空压机房至#3机闭式水回水电动门 |  | digital
N1DCS.J0QCA22AA001_LP | 27734 | #2氨溶液箱进氨电动门 |  | int32
N1DCS.J0QCA38AP001_LP | 27735 | #2凝结水加氨计量泵 |  | int32
N1DCS.J0QCA39AP001_LP | 27736 | #3凝结水加氨计量泵 |  | int32
N1DCS.J0QCA40AA001_LP | 27737 | #1、2中压给水加氨泵出口联络门 |  | digital
N1DCS.J0QCA40AA006_LP | 27738 | #2、3凝结水加氨泵出口联络门 |  | digital
N1DCS.J0QCB34AP001_LP | 27739 | #4联胺加药泵 |  | digital
N1DCS.J0QCB36AP001_LP | 27740 | #6联氨加药泵 |  | int32
N1DCS.J0QCB40AA002_LP | 27741 | #2、3联胺加药泵出口联络电动门 |  | digital
N1DCS.J0QCB40AA003_LP | 27742 | #4、5联胺加药泵出口联络电动门 |  | digital
N1DCS.J0QCB40AA004_LP | 27743 | #5、6联胺加药泵出口联络电动门 |  | digital
N1DCS.J0QCC22AM001_LP | 27744 | #2磷酸盐溶液箱电动搅拌器 |  | int32
N1DCS.J0QCC32AP001_LP | 27745 | #2磷酸盐加药泵 |  | digital
N1DCS.J0QCC33AP001_LP | 27746 | #3磷酸盐加药泵 |  | digital
N1DCS.J0QCC34AP001_LP | 27747 | #4磷酸盐加药泵 |  | digital
N1DCS.J0QCC35AP001_LP | 27748 | #5磷酸盐加药泵 |  | digital
N1DCS.J0QCC36AP001_LP | 27749 | #6磷酸盐加药泵 |  | digital
N1DCS.J0QCA21AA001_LP | 27750 | #1氨溶液箱进氨电动门 |  | digital
N1DCS.J0QCA21AA002_LP | 27751 | #1氨溶液箱进水电动门 |  | digital
N1DCS.J0QCA21AA003_LP | 27752 | #1氨溶液箱出口电动门 |  | digital
N1DCS.J0QCA21AM001_LP | 27753 | #1氨溶液箱电动搅拌器 |  | digital
N1DCS.J0QCA22AA002_LP | 27754 | #2氨溶液箱进水电动门 |  | digital
N1DCS.J0QCA22AA003_LP | 27755 | #2氨溶液箱出口电动门 |  | digital
N1DCS.J0QCA22AM001_LP | 27756 | #2氨溶液箱电动搅拌器 |  | digital
N1DCS.J0QCA31AP001_LP | 27757 | #1中压给水加氨计量泵 |  | digital
N1DCS.J0QCA31AP001MODE | 27758 | #1中压给水加氨计量泵变频器 |  | digital
N1DCS.J0QCA32AP001_LP | 27759 | #2中压给水加氨计量泵 |  | digital
N1DCS.J0QCA32AP001MODE | 27760 | #2中压给水加氨计量泵变频器 |  | digital
N1DCS.J0QCA33AP001_LP | 27761 | #3中压给水加氨计量泵 |  | digital
N1DCS.J0QCA33AP001MODE | 27762 | #3中压给水加氨计量泵变频器 |  | digital
N1DCS.J0QCA34AP001_LP | 27763 | #1高压给水加氨计量泵 |  | digital
N1DCS.J0QCA34AP001MODE | 27764 | #1高压给水加氨计量泵变频器 |  | digital
N1DCS.J0QCA35AP001_LP | 27765 | #2高压给水加氨计量泵 |  | digital
N1DCS.J0QCA35AP001MODE | 27766 | #2高压给水加氨计量泵变频器 |  | digital
N1DCS.J0QCA36AP001_LP | 27767 | #3高压给水加氨计量泵 |  | digital
N1DCS.J0QCA36AP001MODE | 27768 | #3高压给水加氨计量泵变频器 |  | digital
N1DCS.J0QCA37AP001_LP | 27769 | #1凝结水加氨计量泵 |  | digital
N1DCS.J0QCA37AP001MODE | 27770 | #1凝结水加氨计量泵变频器 |  | digital
N1DCS.J0QCA38AP001MODE | 27771 | #2凝结水加氨计量泵变频器 |  | digital
N1DCS.J0QCA39AP001MODE | 27772 | #3凝结水加氨计量泵变频器 |  | digital
N1DCS.J0QCA40AA002_LP | 27773 | #2、3中压给水加氨泵出口联络门 |  | digital
N1DCS.J0QCA40AA003_LP | 27774 | #1、2高压给水加氨泵出口联络门 |  | digital
N1DCS.J0QCA40AA004_LP | 27775 | #2、3高压给水加氨泵出口联络门 |  | digital
N1DCS.J0QCA40AA005_LP | 27776 | #1、2凝结水加氨泵出口联络门 |  | digital
N1DCS.J0QCB21AA004_LP | 27777 | #1联氨溶液箱出口电动门 |  | digital
N1DCS.J0QCB21AM001_LP | 27778 | #1联氨溶液箱电动搅拌器 |  | digital
N1DCS.J0QCB22AA004_LP | 27779 | #2联氨溶液箱出口电动门 |  | digital
N1DCS.J0QCB22AM001_LP | 27780 | #2联氨溶液箱出口电动搅拌器 |  | digital
N1DCS.J0QCB31AP001_LP | 27781 | #1联氨加药泵 |  | int32
N1DCS.J0QCB31AP001MODE | 27782 | #1联氨加药泵变频器 |  | digital
N1DCS.J0QCB32AP001_LP | 27783 | #2联氨加药泵 |  | int32
N1DCS.J0QCB32AP001MODE | 27784 | #2联氨加药泵变频器 |  | digital
N1DCS.J0QCB33AP001_LP | 27785 | #3联氨加药泵 |  | int32
N1DCS.J0QCB33AP001MODE | 27786 | #3联氨加药泵变频器 |  | digital
N1DCS.J0QCB34AP001MODE | 27787 | #4联氨加药泵变频器 |  | digital
N1DCS.J0QCB35AP001_LP | 27788 | #5联氨加药泵 |  | int32
N1DCS.J0QCB35AP001MODE | 27789 | #5联氨加药泵变频器 |  | digital
N1DCS.J0QCB36AP001MODE | 27790 | #6联氨加药泵变频器 |  | digital
N1DCS.J0QCB40AA001_LP | 27791 | #1、2联胺加药泵出口联络电动门 |  | digital
N1DCS.J0QCC21AM001_LP | 27792 | #1磷酸盐溶液箱搅拌器 |  | digital
N1DCS.J0QCC31AP001_LP | 27793 | #1磷酸盐加药泵 |  | digital
N1DCS.J0QCC31AP001MODE | 27794 | #1磷酸盐加药泵变频器 |  | digital
N1DCS.J0QCC32AP001MODE | 27795 | #2磷酸盐加药泵变频器 |  | digital
N1DCS.J0QCC33AP001MODE | 27796 | #3磷酸盐加药泵变频器 |  | digital
N1DCS.J0QCC34AP001MODE | 27797 | #4磷酸盐加药泵变频器 |  | digital
N1DCS.J0QCC35AP001MODE | 27798 | #5磷酸盐加药泵变频器 |  | digital
N1DCS.J0QCC36AP001MODE | 27799 | #6磷酸盐加药泵变频器 |  | digital
N1DCS.QDGLBMPWM_LP | 27800 | 启动锅炉锅炉本体表面排污电动门 |  | digital
N1DCS.QDGLDBPWM1_LP | 27801 | 启动锅炉锅炉本体#1排污电动门 |  | digital
N1DCS.QDGLDBPWM2_LP | 27802 | 启动锅炉锅炉本体#2排污电动门 |  | digital
N1DCS.QDGLGFJ_LP | 27803 | 启动锅炉鼓风机 |  | digital
N1DCS.QDGLGSB_LP | 27804 | 启动锅炉#1给水泵 |  | digital
N1DCS.QDGLGSB2_LP | 27805 | 启动锅炉#2给水泵 |  | digital
N1DCS.QDGLGSBCKM_LP | 27806 | 启动锅炉给水电动门 |  | digital
N1DCS.QDGLGSBZXHM_LP | 27807 | 启动锅炉给水再循环电动门 |  | digital
N1DCS.QDGLJWSJZF_LP | 27808 | 启动锅炉减温水调节阀前电动门 |  | digital
N1DCS.QDGLPQM_LP | 27809 | 启动锅炉过热蒸汽点火排汽电动门 |  | digital
N1DCS.QDGLPWKRQJSF_LP | 27810 | 启动锅炉排污扩容器冷却水电动门 |  | digital
N1DCS.QDGLZQM_LP | 27811 | 启动锅炉过热蒸汽出口电动门 |  | digital
N1DCS.CPRESSAIR_BYLP | 27812 | 空压机预选信号 |  | digital
N1DCS.CPRESSAIR_SEQSP | 27813 | 空压机系统停顺控 |  | digital
N1DCS.CPRESSAIR_SEQSPAUX | 27814 | 空压机系统停顺控辅助点 |  | digital
N1DCS.CPRESSAIR_SEQSPAUX0 | 27815 | 空压机系统停顺控启允许条件 |  | digital
N1DCS.CPRESSAIR_SEQSPAUX1 | 27816 | 空压机系统停顺控第1步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSPAUX2 | 27817 | 空压机系统停顺控第2步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSPAUX3 | 27818 | 空压机系统停顺控第3步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSPAUX4 | 27819 | 空压机系统停顺控第4步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSPAUX5 | 27820 | 空压机系统停顺控第5步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSPLP | 27821 | 空压机系统停顺控状态 |  | digital
N1DCS.CPRESSAIR_SEQSPOKLP | 27822 | 空压机系统停顺控已完成条件 |  | digital
N1DCS.CPRESSAIR_SEQST | 27823 | 空压机系统启顺控 |  | digital
N1DCS.CPRESSAIR_SEQSTAUX | 27824 | 空压机系统启顺控辅助点 |  | digital
N1DCS.CPRESSAIR_SEQSTAUX0 | 27825 | 空压机系统启顺控启允许条件 |  | digital
N1DCS.CPRESSAIR_SEQSTAUX1 | 27826 | 空压机系统启顺控第1步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSTAUX2 | 27827 | 空压机系统启顺控第2步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSTAUX3 | 27828 | 空压机系统启顺控第3步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSTAUX4 | 27829 | 空压机系统启顺控第4步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSTAUX5 | 27830 | 空压机系统启顺控第5步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSTAUX6 | 27831 | 空压机系统启顺控第6步完成条件 |  | digital
N1DCS.CPRESSAIR_SEQSTLP | 27832 | 空压机系统启顺控状态 |  | digital
N1DCS.CPRESSAIR_SEQSTOKLP | 27833 | 空压机系统启顺控已完成条件 |  | digital
N1DCS.J0PAA11AA003_LP | 27834 | #1旋转滤网冲洗水泵出口电动门 |  | digital
N1DCS.J0PAA11AP001_LP | 27835 | #1旋转滤网冲洗水泵 |  | int32
N1DCS.J0PAA11GH501_LP | 27836 | #1全自动滤水器 |  | int32
N1DCS.J0PAA12AA003_LP | 27837 | #2旋转滤网冲洗水泵出口电动门 |  | digital
N1DCS.J0PAA12AP001_LP | 27838 | #2旋转滤网冲洗水泵 |  | int32
N1DCS.J0PAA12GH501_LP | 27839 | #2全自动滤水器 |  | int32
N1DCS.J0PAB60AA004_LP | 27840 | 生活水至循环水泵冷却水电动门 |  | int32
N1DCS.J0QEB50AA002+_LP | 27841 | 杂用储气罐出口母管电动门 |  | digital
N1DCS.J0QEB50AA002_LP | 27842 | 杂用储气罐出口母管电动门 |  | digital
N1DCS.J0QFA11AA002_LP | 27843 | #1空压机出口电动门 |  | int32
N1DCS.J0QFA11AN001_LP | 27844 | #1空压机 |  | int32
N1DCS.J0QFA12AA002_LP | 27845 | #2空压机出口电动门 |  | int32
N1DCS.J0QFA12AN001_LP | 27846 | #2空压机 |  | int32
N1DCS.J0QFA21AA001_LP | 27847 | #1组合式压缩空气干燥机进口门 |  | digital
N1DCS.J0QFA21AT001_LP | 27848 | #1组合式压缩空气干燥机 |  | digital
N1DCS.J0QFA22AA001_LP | 27849 | #2组合式压缩空气干燥机进口门 |  | digital
N1DCS.J0QFA22AT001_LP | 27850 | #2组合式压缩空气干燥机 |  | digital
N1DCS.ROTFLTRWASHPMP_BYLP | 27851 | 旋转滤网冲洗水泵 |  | int32
N1DCS.DRYER_BYLP | 27852 | 组合式压缩空气干燥机 |  | digital
N1DCS.J0QFA13AA002_LP | 27853 | #3空压机出口电动门 |  | int32
N1DCS.J0QFA13AN001_LP | 27854 | #3空压机 |  | int32
N1DCS.J0QFA14AA002_LP | 27855 | #4空压机出口电动门 |  | int32
N1DCS.J0QFA14AN001_LP | 27856 | #4空压机 |  | int32
N1DCS.J0QFA23AA001_LP | 27857 | #3组合式压缩空气干燥机进口门 |  | digital
N1DCS.J0QFA23AT001_LP | 27858 | #3组合式压缩空气干燥机 |  | digital
N1DCS.1GLQ1PWF_LP | 27859 | #1精过滤器底部排污气动门 |  | digital
N1DCS.1GLQ2PWF_LP | 27860 | #1精过滤器低位排污气动门 |  | digital
N1DCS.1GTGASFSF_LP | 27861 | 调压站出口至#4机放散气动门 |  | digital
N1DCS.1HWBOILER_LP | 27862 | 调压站#1热水锅炉 |  | digital
N1DCS.2GLQ1PWF_LP | 27863 | #2精过滤器底部排污气动门 |  | digital
N1DCS.2GLQ2PWF_LP | 27864 | #2精过滤器低位排污气动门 |  | digital
N1DCS.2GTGASFSF_LP | 27865 | 调压站出口至#2机放散气动门 |  | digital
N1DCS.2HWBOILER_LP | 27866 | 调压站#2热水锅炉 |  | digital
N1DCS.3HWBOILER_LP | 27867 | 调压站#3热水锅炉 |  | digital
N1DCS.BOILEREH_LP | 27868 | 调压站电加热器 |  | digital
N1DCS.HJF_LP | 27869 | 调压站火警阀 |  | digital
N1DCS.JLMKPLF_LP | 27870 | 调压站计量模块联络手动门 |  | digital
N1DCS.PWB_LP | 27871 | 调压站排污罐排污泵 |  | digital
N1DCS.J0BFA00GS001_LP | 27872 | 380V机组公用段分段开关45A021 |  | int32
N1DCS.J0BFT10GS001_LP | 27873 | 机组公用A变6kV侧开关61A12 |  | int32
N1DCS.J0BFT10GS002_LP | 27874 | 机组公用A变380V侧开关45A011 |  | int32
N1DCS.J0BHT30GS001_LP | 27875 | 厂区公用A变6kV侧开关61B12 |  | int32
N1DCS.J0BHT50GS001_LP | 27876 | 补给水A变6kV侧开关61B11 |  | int32
N1DCS.J0BHT70GS001_LP | 27877 | 进气冷却A变6kV侧开关61B07 |  | int32
N1DCS.J0BLA00GS201_LP | 27878 | 机组公用A至#1照明MCC开关45A031 |  | int32
N1DCS.J0BLA00GS202_LP | 27879 | 机组公用B至#1照明MCC开关45B031 |  | int32
N1DCS.J0BLC00GS201_LP | 27880 | 机组公用A至#1检修MCC开关45A041 |  | int32
N1DCS.J0BLC00GS202_LP | 27881 | 机组公用B至#1检修MCC开关45B041 |  | int32
N1DCS.J0BLE00GS201_LP | 27882 | 机组公用A至集控楼MCC开关45A051 |  | int32
N1DCS.J0BLF00GS201_LP | 27883 | 机组公用A至联合间MCC开关45A084 |  | int32
N1DCS.J0BLG00GS201_LP | 27884 | 机组公用A至GIS楼MCC开关45A052 |  | int32
N1DCS.Y0AEA12GS101_LP | 27885 | #1主变至220KV母线开关2201 |  | int32
N1DCS.Y0BHT10GS001_LP | 27886 | 生产办公楼A变6kV侧开关61A07 |  | int32
N1DCS.J0BFA08EGS101_LP | 27887 | #1检修和材料库电源一45A085 |  | int32
N1DCS.J0BFB08EGS101_LP | 27888 | #1检修和材料库电源二45B085 |  | int32
N1DCS.J0BFT20GS001_LP | 27889 | 机组公用B变6kV侧开关62A12 |  | int32
N1DCS.J0BFT20GS002_LP | 27890 | 机组公用B变380V侧开关45B011 |  | int32
N1DCS.J0BHT40GS001_LP | 27891 | 厂区公用B变6kV侧开关62B12 |  | int32
N1DCS.J0BHT60GS001_LP | 27892 | 补给水B变6kV侧开关62B11 |  | int32
N1DCS.J0BHT80GS001_LP | 27893 | 进气冷却B变6kV侧开关62B07 |  | int32
N1DCS.J0BLB00GS201_LP | 27894 | 机组公用A至#2照明MCC开关45A032 |  | int32
N1DCS.J0BLB00GS202_LP | 27895 | 机组公用B至#2照明MCC开关45B032 |  | int32
N1DCS.J0BLD00GS201_LP | 27896 | 机组公用A至#2检修MCC开关45A042 |  | int32
N1DCS.J0BLD00GS202_LP | 27897 | 机组公用B至#2检修MCC开关45B042 |  | int32
N1DCS.J0BLE00GS202_LP | 27898 | 机组公用B至集控楼MCC开关45B051 |  | int32
N1DCS.J0BLF00GS202_LP | 27899 | 机组公用B至联合间MCC开关45B084 |  | int32
N1DCS.J0BLG00GS202_LP | 27900 | 机组公用B至GIS楼MCC开关45B052 |  | int32
N1DCS.Y0AEA14GS101_LP | 27901 | #3主变至220KV母线开关2203 |  | int32
N1DCS.Y0BHT20GS001_LP | 27902 | 生产办公楼B变6kV侧开关62A07 |  | digital
N1DCS.J0BFA09EGS101_LP | 27903 | #2检修和材料库电源一45A095 |  | int32
N1DCS.J0BFB09EGS101_LP | 27904 | #2检修和材料库电源二45B095 |  | int32
N1DCS.10LBS45AA001_LP | 27905 | Ovation Control Builder |  | int32
N1DCS.10LBS46AA001_LP | 27906 | Ovation Control Builder |  | int32
N1DCS.10MAA11AA011_LP | 27907 | Ovation Control Builder |  | int32
N1DCS.10MAA11AA013_LP | 27908 | Ovation Control Builder |  | int32
N1DCS.10MAA11AA014_LP | 27909 | Ovation Control Builder |  | int32
N1DCS.10MAA12AA013_LP | 27910 | Ovation Control Builder |  | int32
N1DCS.10MAA12AA014_LP | 27911 | Ovation Control Builder |  | int32
N1DCS.10MAB11AA011_LP | 27912 | Ovation Control Builder |  | int32
N1DCS.10MAB11AA013_LP | 27913 | Ovation Control Builder |  | int32
N1DCS.10MAB11AA014_LP | 27914 | Ovation Control Builder |  | int32
N1DCS.10MAB12AA013_LP | 27915 | Ovation Control Builder |  | int32
N1DCS.10MAB12AA014_LP | 27916 | Ovation Control Builder |  | int32
N1DCS.10MAC45AA001_LP | 27917 | Ovation Control Builder |  | int32
N1DCS.10MAC46AA001_LP | 27918 | Ovation Control Builder |  | int32
N1DCS.10MAC45AA011_LP | 27919 | Ovation Control Builder |  | int32
N1DCS.10MAL23AA051A_LP | 27920 | Ovation Control Builder |  | int32
N1DCS.10MAL26AA051A_LP | 27921 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV51 | 27922 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV52 | 27923 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV53 | 27924 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV54 | 27925 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV55 | 27926 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV56 | 27927 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV57 | 27928 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV58 | 27929 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV59 | 27930 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV60 | 27931 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_DDV61 | 27932 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV01 | 27933 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV02 | 27934 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV03 | 27935 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV04 | 27936 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV05 | 27937 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV06 | 27938 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV07 | 27939 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV08 | 27940 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV09 | 27941 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV10 | 27942 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV11 | 27943 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV12 | 27944 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV13 | 27945 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV14 | 27946 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV15 | 27947 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV16 | 27948 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV17 | 27949 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV18 | 27950 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV19 | 27951 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV20 | 27952 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV21 | 27953 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV22 | 27954 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV23 | 27955 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV24 | 27956 | Ovation Control Builder |  | int32
N1DCS.10MAY10EC001_UDV25 | 27957 | Ovation Control Builder |  | int32
N1DCS.GV_CMD | 27958 | Ovation Control Builder |  | int32
N1DCS.GV_COIL_FAILUE | 27959 | Ovation Control Builder |  | int32
N1DCS.GV_MODE | 27960 | Ovation Control Builder |  | int32
N1DCS.GV_STAT | 27961 | Ovation Control Builder |  | int32
N1DCS.IV_CMD | 27962 | Ovation Control Builder |  | int32
N1DCS.IV_COIL_FAILUE | 27963 | Ovation Control Builder |  | int32
N1DCS.IV_MODE | 27964 | Ovation Control Builder |  | int32
N1DCS.IV_STAT | 27965 | Ovation Control Builder |  | int32
N1DCS.SHUTDOWN_MODE | 27966 | Ovation Control Builder |  | int32
N1DCS.STARTUP_MODE | 27967 | Ovation Control Builder |  | int32
N1DCS.TEST_LP | 27968 | test |  | int32
N1DCS.10LBC41AA051A_LP | 27969 | Ovation Control Builder |  | int32
N1DCS.10LBC41AA051B_LP | 27970 | Ovation Control Builder |  | int32
N1DCS.10MAC01AA001A_LP | 27971 | Ovation Control Builder |  | int32
N1DCS.10MAC01AA002A_LP | 27972 | Ovation Control Builder |  | int32
N1DCS.10MAV51AA012_LP_DEH | 27973 | Ovation Control Builder |  | int32
N1DCS.10MAV51AA012_LP | 27974 | Ovation Control Builder |  | int32
FW.20PAB10CP10102 | 27975 |  |  | float32
FW.J0GNL31CF101ACC | 27976 | PH值调整池进口母管累积流量 | t | float32
FW.J0GNL40CF101ACC | 27977 | 厂区回用水管进口母管累积流量 | t | float32
FW.Y0GRK11CF101ACC | 27978 | 生活污水提升泵出口母管累积流量 | t | float32
FW.Y0GRK11CF101TON | 27979 | 生活污水提升泵出口母管流量 | t/h | float32
FW.Y0GRK51CF101ACC | 27980 | 厂区绿化用水累积流量 | t | float32
FW.Y0GRK51CF101TON | 27981 | 厂区绿化用水流量 | t/h | float32
FW.J0BHD01BUAL | 27982 | 厂区公用B段电压(计算后 |  | float32
FW.J0GCK60CQ102L | 27983 | 除盐水供水母管硅酸根浓度 |  | float32
FW.SHEBEITYTZ1 | 27984 | #1空擦重力滤池步序设备停止指令 |  | digital
FW.SHEBEITYTZ2 | 27985 | #2空擦重力滤池步序设备停止指令 |  | digital
FW.SHEBEITYTZ3 | 27986 | #3空擦重力滤池步序设备停止指令 |  | digital
N2DCS.ZPKD | 27987 | 中旁开度 |  | float32
N2DCS.JQSQAT | 27988 | #1胶球系统收球时间 |  | float32
N2DCS.JQSQAT1 | 27989 | #1胶球系统投球时间 |  | float32
N2DCS.JQSQBT | 27990 | #2胶球系统收球时间 |  | float32
N2DCS.JQSQBT1 | 27991 | #2胶球系统投球时间 |  | float32
N2DCS.LPLVLPVADD_OUT | 27992 | 低压给水调门副调测量值 |  | float32
N2DCS.20TCSAI04 | 27993 | Ovation Control Builder |  | float32
N2DCS.OPH2BYPS | 27994 | 停#3机时开高中压旁路 |  | digital
N2DCS.CIRPMPA_ALM | 27995 | #3循环水泵启允许 |  | digital
N2DCS.CIRPMPB_ALM | 27996 | #4循环水泵启允许 |  | digital
N2DCS.BALM028 | 27997 | #3余热锅炉污染物排放超标 |  | digital
N2DCS.LPECON_SEQNFINSH | 27998 | Ovation Control Builder |  | digital
N2DCS.20MYY01EZ011_XK465 | 27999 | #3机遮断系统已遮断5 |  | digital
N2DCS.BALMALL1 | 28000 | 发电机漏水 |  | digital
N2DCS.BALMUNACK1 | 28001 | 发电机漏水确认 |  | digital
N2DCS.ON10 | 28002 | 开关量1 |  | digital
N2DCS.21AGCFVFRP | 28003 | AGC在投入状态 |  | digital
N2DCS.AGCPMT | 28004 | AGC投入允许 |  | digital
N2DCS.CIRWTR_SEQSTFINISH | 28005 | 开式水系统启顺控已完成 |  | digital
N2DCS.DEH_DCS_DI1 | 28006 | #3机低压调阀已关 |  | digital
N2DCS.EXHOT | 28007 | #3炉极热态模式启动 |  | digital
N2DCS.GLDSYS_SEQSPFINISH | 28008 | 轴封系统停顺控已完成 |  | digital
N2DCS.GTCBOFF | 28009 | #4机已解列 |  | digital
N2DCS.GTSTOP | 28010 | #4机已停止 |  | digital
N2DCS.HPFWPASTOP | 28011 | #1高压给水泵已停止 |  | digital
N2DCS.HPFWPBSTOP | 28012 | #2高压给水泵已停止 |  | digital
N2DCS.STCBOFF | 28013 | #3机已并网 |  | digital
N2DCS.TURBLATCHED | 28014 | #3机无跳闸信号 |  | digital
N2DCS.VACM_SEQSPFINISH | 28015 | 抽真空系统停顺控已完成 |  | digital
N2DCS.VACM_SEQSTFINISH | 28016 | 抽真空系统启顺控已完成 |  | digital
N2DCS.20DEHCLDSTUP | 28017 | #3机DEH为冷态启动 |  | digital
N2DCS.20DEHHOTSTUP | 28018 | #3机DEH为热态启动 |  | digital
N2DCS.20DEHWAMSTUP | 28019 | #3机DEH为温态启动 |  | digital
N2DCS.22AVCAUTORG | 28020 | AVC在投入状态 |  | digital
N2DCS.2XHSPUMPRUN | 28021 | Ovation Control Builder |  | digital
N2DCS.Y0AEA12GS101OK | 28022 | Ovation Control Builder |  | digital
N2DCS.DCSETSTP | 28023 | ETS跳闸条件画面显示 |  | digital
N2DCS.ZQPSSYS_SEQSP | 28024 | 蒸汽喷射装置停顺控 |  | digital
N2DCS.ZQPSSYS_SEQSPAUX | 28025 | 蒸汽喷射装置停顺控辅助点 |  | digital
N2DCS.ZQPSSYS_SEQSPAUX0 | 28026 | 蒸汽喷射装置停顺控启允许条件 |  | digital
N2DCS.ZQPSSYS_SEQSPAUX1 | 28027 | 蒸汽喷射装置停顺控1步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSPAUX2 | 28028 | 蒸汽喷射装置停顺控2步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSPAUX3 | 28029 | 蒸汽喷射装置停顺控3步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSPAUX4 | 28030 | 蒸汽喷射装置停顺控4步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSPAUX5 | 28031 | 蒸汽喷射装置停顺控5步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSPLP | 28032 | 蒸汽喷射装置停顺控状态 |  | digital
N2DCS.ZQPSSYS_SEQST | 28033 | 蒸汽喷射装置启顺控 |  | digital
N2DCS.ZQPSSYS_SEQSTAUX | 28034 | 蒸汽喷射装置启顺控辅助点 |  | digital
N2DCS.ZQPSSYS_SEQSTAUX0 | 28035 | 蒸汽喷射装置启顺控启允许条件 |  | digital
N2DCS.ZQPSSYS_SEQSTAUX1 | 28036 | 蒸汽喷射装置启顺控1步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSTAUX2 | 28037 | 蒸汽喷射装置启顺控2步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSTAUX3 | 28038 | 蒸汽喷射装置启顺控3步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSTAUX4 | 28039 | 蒸汽喷射装置启顺控4步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSTAUX5 | 28040 | 蒸汽喷射装置启顺控5步完成条件 |  | digital
N2DCS.ZQPSSYS_SEQSTLP | 28041 | 蒸汽喷射装置启顺控状态 |  | digital
N2DCS.QJBW_SEQSTAUX6 | 28042 | #3机并网顺控第6步完成条件 |  | digital
N2DCS.QJTQYX | 28043 | #3机同期允许条件 |  | digital
N2DCS.TCSECSBW_SEQST | 28044 | Ovation Control Builder |  | digital
N1DCS.TEMSUM | 28045 | 主蒸汽温度与高压缸温度差值 | ℃ | float32
CALC.N1ES_WKWH_U1_TODAY | 28046 | 1号机组今日发电量 | 万kWh | float32
CALC.N1ES_WKWH_U2_TODAY | 28047 | 2号机组今日发电量 | 万kWh | float32
CALC.N2ES_WKWH_U3_TODAY | 28048 | 3号机组今日发电量 | 万kWh | float32
CALC.N2ES_WKWH_U4_TODAY | 28049 | 4号机组今日发电量 | 万kWh | float32
CALC.N1ES_WKWH_U1_YESTERDAY | 28050 | 1号机组昨日发电量 | 万kWh | float32
CALC.N1ES_WKWH_U2_YESTERDAY | 28051 | 2号机组昨日发电量 | 万kWh | float32
CALC.N2ES_WKWH_U3_YESTERDAY | 28052 | 3号机组昨日发电量 | 万kWh | float32
CALC.N2ES_WKWH_U4_YESTERDAY | 28053 | 4号机组昨日发电量 | 万kWh | float32
CALC.N1ES_WKWH_U1_THISMONTH | 28054 | 1号机组本月发电量 | 万kWh | float32
CALC.N1ES_WKWH_U2_THISMONTH | 28055 | 2号机组本月发电量 | 万kWh | float32
CALC.N2ES_WKWH_U3_THISMONTH | 28056 | 3号机组本月发电量 | 万kWh | float32
CALC.N2ES_WKWH_U4_THISMONTH | 28057 | 4号机组本月发电量 | 万kWh | float32
CALC.N1ES_WKWH_U1_LASTMONTH | 28058 | 1号机组上月发电量 | 万kWh | float32
CALC.N1ES_WKWH_U2_LASTMONTH | 28059 | 2号机组上月发电量 | 万kWh | float32
CALC.N2ES_WKWH_U3_LASTMONTH | 28060 | 3号机组上月发电量 | 万kWh | float32
CALC.N2ES_WKWH_U4_LASTMONTH | 28061 | 4号机组上月发电量 | 万kWh | float32
CALC.N1ES_WKWH_U1_THISYEAR | 28062 | 1号机组本年发电量 | 万kWh | float32
CALC.N1ES_WKWH_U2_THISYEAR | 28063 | 2号机组本年发电量 | 万kWh | float32
CALC.N2ES_WKWH_U3_THISYEAR | 28064 | 3号机组本年发电量 | 万kWh | float32
CALC.N2ES_WKWH_U4_THISYEAR | 28065 | 4号机组本年发电量 | 万kWh | float32
CALC.N1ES_WKWH_UNIT_TODAY | 28066 | 1套机组今日发电量 | 万kWh | float32
CALC.N2ES_WKWH_UNIT_TODAY | 28067 | 1套机组今日发电量 | 万kWh | float32
CALC.N1ES_WKWH_UNIT_YESTERDAY | 28068 | 1套机组昨日发电量 | 万kWh | float32
CALC.N2ES_WKWH_UNIT_YESTERDAY | 28069 | 1套机组昨日发电量 | 万kWh | float32
CALC.N1ES_WKWH_UNIT_THISMONTH | 28070 | 1套机组本月发电量 | 万kWh | float32
CALC.N2ES_WKWH_UNIT_THISMONTH | 28071 | 1套机组本月发电量 | 万kWh | float32
CALC.N1ES_WKWH_UNIT_LASTMONTH | 28072 | 1套机组上月发电量 | 万kWh | float32
CALC.N2ES_WKWH_UNIT_LASTMONTH | 28073 | 1套机组上月发电量 | 万kWh | float32
CALC.N1ES_WKWH_UNIT_THISYEAR | 28074 | 1套机组今年发电量 | 万kWh | float32
CALC.N2ES_WKWH_UNIT_THISYEAR | 28075 | 1套机组今年发电量 | 万kWh | float32
CALC.N1EC_WKWH_AVG_CHANGE | 28076 | 1套机AGC指令偏差量 | MW | float32
CALC.N2EC_WKWH_AVG_CHANGE | 28077 | 2套机AGC指令偏差量 | MW | float32
FW.SZSL_ANDAN | 28078 | 工业废水氨氮含量 | mg/L | float32
FW.SZSL_TSS | 28079 | 工业废水TSS含量 | mg/L | float32
FW.SZSL_LL | 28080 | 工业废水流量计 | t/h | float32
N1DCS.HEATINGSUPPLYFLOW1 | 28081 | 供热计量站母管流量 | t/h | float32
N1DCS.HEATINGSUPPLYFLOW2 | 28082 | 供热计量站旁路流量 | t/h | float32
N1DCS.VGLBS461 | 28083 | Ovation Control Builder |  | float32
N1DCS.VGLBS451 | 28084 | Ovation Control Builder |  | float32
N2DCS.VGLBS461 | 28085 | Ovation Control Builder |  | float32
N2DCS.VGLBS451 | 28086 | Ovation Control Builder |  | float32
FW.SZSL_PH | 28087 | 工业废水PH含量 |  | float32
FW.SZSL_COD | 28088 | 工业废水COD含量 | mg/L | float32
N2DCS.20LBS45AA001_IPEIN2 | 28089 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_HPEIN2 | 28090 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_IPEIN2 | 28091 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_HPEIN2 | 28092 | Ovation Control Builder |  | digital
N1DCS.OUT11 | 28093 | Ovation Control Builder |  | float32
N1DCS.10MAA50CT121A | 28094 | 高压排汽蒸汽温度 1# | ℃ | float32
N1DCS.10MAA50CT122A | 28095 | 高压排汽蒸汽温度 2# | ℃ | float32
N1DCS.10MAA50CT123A | 28096 | 高压排汽蒸汽温度 3# | ℃ | float32
N1DCS.10MAB50CT121A | 28097 | 中压排汽蒸汽温度 1# | ℃ | float32
N1DCS.10MAB50CT122A | 28098 | 中压排汽蒸汽温度 2# | ℃ | float32
N1DCS.10MAD11CT114A | 28099 | #1支持轴承前右下温度A | ℃ | float32
N1DCS.10MAD11CT114B | 28100 | #1支持轴承前右下温度B | ℃ | float32
N1DCS.10MAD11CT114C | 28101 | #1支持轴承前右下温度C | ℃ | float32
N1DCS.10MAD11CT118A | 28102 | #1支持轴承后右下温度A | ℃ | float32
N1DCS.10MAD11CT118B | 28103 | #1支持轴承后右下温度B | ℃ | float32
N1DCS.10MAD11CT118C | 28104 | #1支持轴承后右下温度C | ℃ | float32
N1DCS.10MAD12CT111A | 28105 | #2支持轴承前左上温度A | ℃ | float32
N1DCS.10MAD12CT111B | 28106 | #2支持轴承前左上温度B | ℃ | float32
N1DCS.10MAD12CT111C | 28107 | #2支持轴承前左上温度C | ℃ | float32
N1DCS.10MAD12CT112A | 28108 | #2支持轴承前右上温度A | ℃ | float32
N1DCS.10MAD12CT112B | 28109 | #2支持轴承前右上温度B | ℃ | float32
N1DCS.10MAD12CT112C | 28110 | #2支持轴承前右上温度C | ℃ | float32
N1DCS.10MAD12CT113A | 28111 | #2支持轴承前左下温度A | ℃ | float32
N1DCS.10MAD12CT113B | 28112 | #2支持轴承前左下温度B | ℃ | float32
N1DCS.10MAD12CT113C | 28113 | #2支持轴承前左下温度C | ℃ | float32
N1DCS.10MAD12CT114A | 28114 | #2支持轴承前右下温度A | ℃ | float32
N1DCS.10MAD12CT114B | 28115 | #2支持轴承前右下温度B | ℃ | float32
N1DCS.10MAD12CT114C | 28116 | #2支持轴承前右下温度C | ℃ | float32
N1DCS.10MAD12CT131A | 28117 | 推力轴承前左上温度A | ℃ | float32
N1DCS.10MAD12CT131B | 28118 | 推力轴承前左上温度B | ℃ | float32
N1DCS.10MAD12CT131C | 28119 | 推力轴承前左上温度C | ℃ | float32
N1DCS.10MAD12CT132A | 28120 | 推力轴承前右上温度A | ℃ | float32
N1DCS.10MAD12CT132B | 28121 | 推力轴承前右上温度B | ℃ | float32
N1DCS.10MAD12CT132C | 28122 | 推力轴承前右上温度C | ℃ | float32
N1DCS.10MAD12CT133A | 28123 | 推力轴承前左下温度A | ℃ | float32
N1DCS.10MAD12CT133B | 28124 | 推力轴承前左下温度B | ℃ | float32
N1DCS.10MAD12CT133C | 28125 | 推力轴承前左下温度C | ℃ | float32
N1DCS.10MAD12CT134A | 28126 | 推力轴承前右下温度A | ℃ | float32
N1DCS.10MAD12CT134B | 28127 | 推力轴承前右下温度B | ℃ | float32
N1DCS.10MAD12CT134C | 28128 | 推力轴承前右下温度C | ℃ | float32
N1DCS.10MAD13CT111A | 28129 | #3支持轴承汽轮机侧前左上温度A | ℃ | float32
N1DCS.10MAD13CT111B | 28130 | #3支持轴承汽轮机侧前左上温度B | ℃ | float32
N1DCS.10MAD13CT111C | 28131 | #3支持轴承汽轮机侧前左上温度C | ℃ | float32
N1DCS.10MAD13CT112A | 28132 | #3支持轴承汽轮机侧前右上温度A | ℃ | float32
N1DCS.10MAD13CT112B | 28133 | #3支持轴承汽轮机侧前右上温度B | ℃ | float32
N1DCS.10MAD13CT112C | 28134 | #3支持轴承汽轮机侧前右上温度C | ℃ | float32
N1DCS.10MAD13CT113A | 28135 | #3支持轴承汽轮机侧前左下温度A | ℃ | float32
N1DCS.10MAD13CT113B | 28136 | #3支持轴承汽轮机侧前左下温度B | ℃ | float32
N1DCS.10MAD13CT113C | 28137 | #3支持轴承汽轮机侧前左下温度C | ℃ | float32
N1DCS.10MAD13CT114A | 28138 | #3支持轴承汽轮机侧前右下温度A | ℃ | float32
N1DCS.10MAD13CT114B | 28139 | #3支持轴承汽轮机侧前右下温度B | ℃ | float32
N1DCS.10MAD13CT114C | 28140 | #3支持轴承汽轮机侧前右下温度C | ℃ | float32
N1DCS.10MAD13CT115A | 28141 | #3支持轴承汽轮机侧后右下温度A | ℃ | float32
N1DCS.10MAD13CT115B | 28142 | #3支持轴承汽轮机侧后右下温度B | ℃ | float32
N1DCS.10MAD13CT115C | 28143 | #3支持轴承汽轮机侧后右下温度C | ℃ | float32
N1DCS.10MKD11CT113A | 28144 | #1汽轮发电机轴承左下温度A | ℃ | float32
N1DCS.10MKD11CT113B | 28145 | #1汽轮发电机轴承左下温度B | ℃ | float32
N1DCS.10MKD11CT114A | 28146 | #1汽轮发电机轴承右下温度A | ℃ | float32
N1DCS.10MKD11CT114B | 28147 | #1汽轮发电机轴承右下温度B | ℃ | float32
N1DCS.10MKD12CT113A | 28148 | #2汽轮发电机轴承左下温度A | ℃ | float32
N1DCS.10MKD12CT113B | 28149 | #2汽轮发电机轴承左下温度B | ℃ | float32
N1DCS.10MKD12CT114A | 28150 | #2汽轮发电机轴承右下温度A | ℃ | float32
N1DCS.10MKD12CT114B | 28151 | #2汽轮发电机轴承右下温度B | ℃ | float32
N1DCS.10MYA01CS111 | 28152 | 高中压汽轮机转速 1 |  | float32
N1DCS.10MYA01CS112 | 28153 | 高中压汽轮机转速 2 |  | float32
N1DCS.10MYA01CS113 | 28154 | 高中压汽轮机转速 3 |  | float32
N1DCS.10MYA01CS114 | 28155 | 高中压汽轮机转速 4 |  | float32
N1DCS.10MYA01CS115 | 28156 | 高中压汽轮机转速 5 |  | float32
N1DCS.10MYA01CS116 | 28157 | 高中压汽轮机转速 6 |  | float32
N1DCS.10LBS45AA112A | 28158 | 中压抽汽快关调节阀控制设定 |  | float32
N1DCS.10LBS45CG151 | 28159 | 中压抽汽快关调节阀阀位反馈 | % | float32
N1DCS.10LBS46AA112A | 28160 | 高压抽汽快关调节阀控制设定 |  | float32
N1DCS.10MAA11CG151 | 28161 | 高压主汽门阀位 | % | float32
N1DCS.10MAA12AA112A | 28162 | 高压调门指令1 |  | float32
N1DCS.10MAA12AA112B | 28163 | 高压调门指令2 |  | float32
N1DCS.10MAA12CG151 | 28164 | 高压调门阀位 |  | float32
N1DCS.10MAB11CG151 | 28165 | 中压主汽门阀位 | % | float32
N1DCS.10MAB12AA112A | 28166 | 中压调门指令1 |  | float32
N1DCS.10MAB12AA112B | 28167 | 中压调门指令2 |  | float32
N1DCS.10MAB12CG151 | 28168 | 中压调门阀位 |  | float32
N1DCS.10MAB50CP121 | 28169 | 中压缸排汽压力 #1 | MPa | float32
N1DCS.10MAB50CP122 | 28170 | 中压缸排汽压力 #2 | MPa | float32
N1DCS.10MAB50CP123 | 28171 | 中压缸排汽压力 #3 | MPa | float32
N1DCS.10MAC46AA112A | 28172 | 低压补汽调阀控制设定 | % | float32
N1DCS.10MYA01CS111C | 28173 | 汽轮机转速 1 | RPM | float32
N1DCS.10MYA01CS112C | 28174 | 汽轮机转速 2 | RPM | float32
N1DCS.10MYA01CS113C | 28175 | 汽轮机转速 3 | RPM | float32
N1DCS.10MYA01CS121C | 28176 | 汽轮机转速 4 | RPM | float32
N1DCS.10MYA01CS122C | 28177 | 汽轮机转速 5 | RPM | float32
N1DCS.10MYA01CS123C | 28178 | 汽轮机转速 6 | RPM | float32
N1DCS.10NAA02CP101 | 28179 | 中压抽汽蒸汽压力(调阀后)#1 | MPa | float32
N1DCS.DCS_HPFLOW | 28180 | Ovation Control Builder |  | float32
N1DCS.DCS_IPFLOW | 28181 | Ovation Control Builder |  | float32
N1DCS.DCS_IP_BP_D_PRESS | 28182 | Ovation Control Builder |  | float32
N1DCS.DCS_IP_BP_POS | 28183 | Ovation Control Builder |  | float32
N1DCS.DCS_IP_BP_U_PRESS | 28184 | Ovation Control Builder |  | float32
N1DCS.10LBA20CT107A | 28185 | 主汽门前蒸汽温度1# | ℃ | float32
N1DCS.10LBA20CT108A | 28186 | 主汽门前蒸汽温度2# | ℃ | float32
N1DCS.10LBA20CT109A | 28187 | 主汽门前蒸汽温度3# | ℃ | float32
N1DCS.10LBA90CT101A | 28188 | 低压主汽门前蒸汽温度 | ℃ | float32
N1DCS.10LBB50CT107A | 28189 | 中压主汽门前蒸汽温度1# | ℃ | float32
N1DCS.10LBB50CT108A | 28190 | 中压主汽门前蒸汽温度2# | ℃ | float32
N1DCS.10LBB50CT109A | 28191 | 再热门阀前蒸汽温度3# | ℃ | float32
N1DCS.10LBC40CT101 | 28192 | 高排逆止门前蒸汽温度 | ℃ | float32
N1DCS.10MAA11CT121A | 28193 | 高压主汽门内壁温度A（100%） | ℃ | float32
N1DCS.10MAA11CT122A | 28194 | 高压主汽门中壁温度A（50%） | ℃ | float32
N1DCS.10MAA12CT121A | 28195 | 高压调节汽门内壁温度A（100%） | ℃ | float32
N1DCS.10MAA12CT122A | 28196 | 高压调节汽门中壁温度A（50%） | ℃ | float32
N1DCS.10MAA50CT104A | 28197 | 高压调节门后蒸汽温度1 | ℃ | float32
N1DCS.10MAA50CT105A | 28198 | 高压调节门后蒸汽温度2 | ℃ | float32
N1DCS.10MAA50CT106A | 28199 | 高压调节门后蒸汽温度3 | ℃ | float32
N1DCS.10MAA50CT131A | 28200 | 高压缸内壁温度A（100%） | ℃ | float32
N1DCS.10MAA50CT132A | 28201 | 高压缸中壁温度A（50%） | ℃ | float32
N1DCS.10MAA50CT141A | 28202 | 高压缸外壁温（50%） | ℃ | float32
N1DCS.10MAA50CT142A | 28203 | 高压缸中壁温（50%） | ℃ | float32
N1DCS.10MAA50CT143A | 28204 | 高压缸内壁温（50%） | ℃ | float32
N1DCS.10MAA50CT151A | 28205 | 高压缸上中壁温A | ℃ | float32
N1DCS.10MAA50CT152A | 28206 | 高压缸下中壁温A | ℃ | float32
N1DCS.10MAA50CT322A | 28207 | 高压主汽门中壁温度A（50%） |  | float32
N1DCS.10MAB50CT111A | 28208 | 中压缸排汽口壁温1 | ℃ | float32
N1DCS.10MAB50CT112A | 28209 | 中压缸排汽口壁温2 | ℃ | float32
N1DCS.10MAB50CT113A | 28210 | 中压缸排汽口壁温3 | ℃ | float32
N1DCS.10MAB50CT151A | 28211 | 中压缸上中壁温度A | ℃ | float32
N1DCS.10MAB50CT152A | 28212 | 中压缸中下壁温度A | ℃ | float32
N1DCS.10MAC10CT111A | 28213 | 末级蒸汽温度1#(静叶环温度) | ℃ | float32
N1DCS.10MAC10CT112A | 28214 | 末级蒸汽温度2#(静叶环温度) | ℃ | float32
N1DCS.10MAC10CT181A | 28215 | 低压后缸支柱壁温上 | ℃ | float32
N1DCS.10MAC10CT182A | 28216 | 低压后缸支柱壁温下 | ℃ | float32
N1DCS.10MAC10CT183A | 28217 | 低压排汽支架温度1#（排汽温度） | ℃ | float32
N1DCS.10MAC10CT184A | 28218 | 低压排汽支架温度2#（排汽温度） | ℃ | float32
N1DCS.10MAC10CT185A | 28219 | 低压排汽支架温度3#（排汽温度） | ℃ | float32
N1DCS.10LBS45AA001_XG04 | 28220 | 中压抽汽快关调节阀控制电源故障 |  | digital
N1DCS.10LBS45AA013_ZB21 | 28221 | 中压抽汽快关调节阀油动机关闭电 |  | digital
N1DCS.10LBS46AA001_XG04 | 28222 | 高压抽汽快关调节阀控制电源故障 |  | digital
N1DCS.10LBS46AA013_ZB21 | 28223 | 高压抽汽快关调节阀油动机关闭电 |  | digital
N1DCS.10MAA21AA013_ZB21 | 28224 | 主汽门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAA21AA014_ZB21 | 28225 | 主汽门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAA22AA013_ZB21 | 28226 | 高压调门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAA22AA014_ZB21 | 28227 | 高压调门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAB21AA013_ZB21 | 28228 | 再热主汽门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAB21AA014_ZB21 | 28229 | 再热主汽门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAB22AA013_ZB21 | 28230 | 中压调门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAB22AA014_ZB21 | 28231 | 中压调门油动机关闭电磁阀#2 |  | digital
N1DCS.10MAC45AA013_ZB21 | 28232 | 低压补汽主门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAC46AA013_ZB21 | 28233 | 低压补汽调门油动机关闭电磁阀#1 |  | digital
N1DCS.10MAY01GS001_A | 28234 | 汽轮机遮断按钮1#常开接点 |  | digital
N1DCS.10MAY01GS001_B | 28235 | 汽轮机遮断按钮1#常闭接点 |  | digital
N1DCS.10MAY01GS001_C | 28236 | 汽轮机遮断按钮1#常闭接点 |  | digital
N1DCS.10MAY01GS001_D | 28237 | 汽轮机遮断按钮1#常闭接点 |  | digital
N1DCS.10MAY01GS001_E | 28238 | 汽轮机遮断按钮1#常闭接点 |  | digital
N1DCS.10MAY01GS002_A | 28239 | 汽轮机遮断按钮2#常开接点 |  | digital
N1DCS.10MAY01GS002_B | 28240 | 汽轮机遮断按钮2#常闭接点 |  | digital
N1DCS.10MAY01GS002_C | 28241 | 汽轮机遮断按钮2#常闭接点 |  | digital
N1DCS.10MAY01GS002_D | 28242 | 汽轮机遮断按钮2#常闭接点 |  | digital
N1DCS.10MAY01GS002_E | 28243 | 汽轮机遮断按钮2#常闭接点 |  | digital
N1DCS.10MAY01GS003_A | 28244 | 汽轮机遮断按钮3#常开接点 |  | digital
N1DCS.10MAY01GS003_B | 28245 | 汽轮机遮断按钮3#常闭接点 |  | digital
N1DCS.10MAY01GS003_C | 28246 | 汽轮机遮断按钮3#常闭接点 |  | digital
N1DCS.10MAY01GS003_D | 28247 | 汽轮机遮断按钮3#常闭接点 |  | digital
N1DCS.10MYA01DG030_FD2TEST | 28248 | Ovation Control Builder |  | digital
N1DCS.DROP41GW001_XM09 | 28249 | 机柜空开正常 |  | digital
N1DCS.DROP41GW001_XM10 | 28250 | 机柜电源正常 |  | digital
N1DCS.10BFA01CE004 | 28251 | BFA01 VOLTAGE MEASURE |  | float32
N1DCS.10BFA02CE004 | 28252 | BFA02 VOLTAGE MEASURE |  | float32
N1DCS.10BNA01CE004 | 28253 | EMCC BUS BAR VOLATGE |  | float32
N1DCS.10BNA01GS001A_1 | 28254 | EMCC INC CB A VOLTAGE |  | float32
N1DCS.10BNA01GS001A_2 | 28255 | EMCC INC CB A CURRENT |  | float32
N1DCS.10BNA01GS001B_1 | 28256 | EMCC INC CB B VOLTAGE |  | float32
N1DCS.10BNA01GS001B_2 | 28257 | EMCC INC CB B CURRENT |  | float32
N1DCS.10BRA01EG001 | 28258 | 1XBRA 220VAC BUS BAR VOLTAGE |  | float32
N1DCS.10BUA01CE001 | 28259 | BUS BAR VOLTAGE |  | float32
N1DCS.10EKG60FF001 | 28260 | 天然气流量 |  | float32
N1DCS.10MBA10CG101 | 28261 | 燃机轴位移1 |  | float32
N1DCS.10MBA10CG102 | 28262 | 燃机轴位移2 |  | float32
N1DCS.10MBA11CP101 | 28263 | 压气机入口压力 |  | float32
N1DCS.10MBA12CP101 | 28264 | 压气机排气压力1 |  | float32
N1DCS.10MBA12CP102 | 28265 | 压气机排气压力2 |  | float32
N1DCS.10MBD11CY101 | 28266 | 燃机透平侧轴承振动1 |  | float32
N1DCS.10MBD11CY102 | 28267 | 燃机透平侧轴承振动2 |  | float32
N1DCS.10MBD11CY111 | 28268 | 燃机轴振动1 |  | float32
N1DCS.10MBD11CY112 | 28269 | 燃机轴振动2 |  | float32
N1DCS.10MBD12CT101A | 28270 | 燃机推力轴承温度A |  | float32
N1DCS.10MBD12CT101B | 28271 | 燃机推力轴承温度B |  | float32
N1DCS.10MBD12CT101C | 28272 | 燃机推力轴承温度C |  | float32
N1DCS.10MBD12CY101 | 28273 | 燃机压气机侧轴承振动1 |  | float32
N1DCS.10MBD12CY102 | 28274 | 燃机压气机侧轴承振动2 |  | float32
N1DCS.10MBD12CY111 | 28275 | 压气机轴振动1 |  | float32
N1DCS.10MBD12CY112 | 28276 | 压气机轴振动2 |  | float32
N1DCS.10MBH22AA101 | 28277 | 第2级冷却空气阀1阀位反馈 |  | float32
N1DCS.10MBH22AA102 | 28278 | 第2级冷却空气阀2阀位反馈 |  | float32
N1DCS.10MBH22CP101 | 28279 | 燃机二级冷却空气压力3 |  | float32
N1DCS.10MBH22CP102 | 28280 | 燃机二级冷却空气压力1 |  | float32
N1DCS.10MBH22CP103 | 28281 | 燃机二级冷却空气压力2 |  | float32
N1DCS.10MBH23AA101 | 28282 | 第3级冷却空气阀1阀位反馈 |  | float32
N1DCS.10MBH23AA102 | 28283 | 第3级冷却空气阀2阀位反馈 |  | float32
N1DCS.10MBH23CP101 | 28284 | 燃机三级冷却空气压力3 |  | float32
N1DCS.10MBH23CP102 | 28285 | 燃机三级冷却空气压力1 |  | float32
N1DCS.10MBH23CP103 | 28286 | 燃机三级冷却空气压力2 |  | float32
N1DCS.10MBL14CP101 | 28287 | 两级总差压 |  | float32
N1DCS.10MBL14CP102 | 28288 | 粗过滤系统差压 |  | float32
N1DCS.10MBM10CP101 | 28289 | 燃机燃烧室进出口差压 |  | float32
N1DCS.10MBM10CY101 | 28290 | 燃烧室振动1 |  | float32
N1DCS.10MBM10CY102 | 28291 | 燃烧室振动2 |  | float32
N1DCS.10MBM10CY103 | 28292 | 燃烧室振动3 |  | float32
N1DCS.10MBM11CP101 | 28293 | 燃烧室嗡鸣1 |  | float32
N1DCS.10MBM11CP102 | 28294 | 燃烧室嗡鸣2 |  | float32
N1DCS.10MBM12CP107 | 28295 | 燃烧器嗡鸣1 |  | float32
N1DCS.10MBM12CP110 | 28296 | 燃烧器嗡鸣2 |  | float32
N1DCS.10MBM12CP115 | 28297 | 燃烧器嗡鸣3 |  | float32
N1DCS.10MBP32CP101 | 28298 | 预混燃气控制阀后压力 |  | float32
N1DCS.10MBP34CF101 | 28299 | 天然气流量 |  | float32
N1DCS.10MBP34CP101 | 28300 | 值班燃气控制阀后压力 |  | float32
N1DCS.10MBV10CL101 | 28301 | 润滑油油箱液位 |  | float32
N1DCS.10MBV26CP101 | 28302 | 润滑油供油压力 |  | float32
N1DCS.10MBV26CT101 | 28303 | 润滑油供油温度 |  | float32
N1DCS.10MBV31CP101 | 28304 | 顶轴油压力1 |  | float32
N1DCS.10MBV31CP102 | 28305 | 顶轴油压力2 |  | float32
N1DCS.10MBX01CL101 | 28306 | 控制油油箱液位 |  | float32
N1DCS.10MBX01CT101A | 28307 | 燃机控制油油箱油温1 |  | float32
N1DCS.10MBX01CT101B | 28308 | 燃机控制油油箱油温2 |  | float32
N1DCS.10MBX03CP101 | 28309 | 燃机控制油母管压力 |  | float32
N1DCS.10MKA25CT301 | 28310 | 发电机钉子线圈出水温度1 |  | float32
N1DCS.10MKA25CT302 | 28311 | 发电机钉子线圈出水温度2 |  | float32
N1DCS.10MKA25CT303 | 28312 | 发电机钉子线圈出水温度3 |  | float32
N1DCS.10MKA25CT304 | 28313 | 发电机钉子线圈出水温度4 |  | float32
N1DCS.10MKA26CT301 | 28314 | 发电机出线盒热氢温度1 |  | float32
N1DCS.10MKA26CT302 | 28315 | 发电机出线盒热氢温度2 |  | float32
N1DCS.10MKA30CT301_TCS | 28316 | 发电机励端冷氢温度1 |  | float32
N1DCS.10MKA30CT302_TCS | 28317 | 发电机励端冷氢温度2 |  | float32
N1DCS.10MKA30CT303_TCS | 28318 | 发电机励端冷氢温度3 |  | float32
N1DCS.10MKA30CT304_TCS | 28319 | 发电机励端冷氢温度4 |  | float32
N1DCS.10MKA30CT311_TCS | 28320 | 发电机汽端冷氢温度1 |  | float32
N1DCS.10MKA30CT312_TCS | 28321 | 发电机汽端冷氢温度2 |  | float32
N1DCS.10MKA30CT313_TCS | 28322 | 发电机汽端冷氢温度3 |  | float32
N1DCS.10MKA30CT314_TCS | 28323 | 发电机汽端冷氢温度4 |  | float32
N1DCS.10MKA31CT301 | 28324 | 发电机励端热氢温度1 |  | float32
N1DCS.10MKA31CT311 | 28325 | 发电机汽端热氢温度1 |  | float32
N1DCS.10MKD11CY021 | 28326 | 发电机汽端轴承振动 |  | float32
N1DCS.10MKD11CY022 | 28327 | 发电机汽端轴承振动 |  | float32
N1DCS.10MKD11CY041 | 28328 | 发电机汽端轴承X向振动 |  | float32
N1DCS.10MKD11CY042 | 28329 | 发电机汽端轴承Y向振动 |  | float32
N1DCS.10MKD12CY021 | 28330 | 发电机励端轴承振动 |  | float32
N1DCS.10MKD12CY022 | 28331 | 发电机励端轴承振动 |  | float32
N1DCS.10MKD12CY041 | 28332 | 发电机励端轴承X向振动 |  | float32
N1DCS.10MKD12CY042 | 28333 | 发电机励端轴承Y向振动 |  | float32
N1DCS.10MKD13CY021 | 28334 | 发电机集电环轴承振动1 |  | float32
N1DCS.10MKD13CY022 | 28335 | 发电机集电环轴承振动2 |  | float32
N1DCS.10MKD13CY041 | 28336 | 发电机集电环轴承X向振动 |  | float32
N1DCS.10MKD13CY042 | 28337 | 发电机集电环轴承Y向振动 |  | float32
N1DCS.10MKF05CL101 | 28338 | 发电机定子冷却水箱液位 |  | float32
N1DCS.10MKF18CQ101 | 28339 | 发电机定子线圈进水电导率 |  | float32
N1DCS.10MKF19CF101 | 28340 | 发电机定子冷却水流量 |  | float32
N1DCS.10MKW06CL101 | 28341 | 氢侧油箱液位 |  | float32
N1DCS.10SAM30CT102 | 28342 | 燃机罩壳温度1 |  | float32
N1DCS.10SAM30CT102A | 28343 | 燃机罩壳温度2 |  | float32
N1DCS.DAY | 28344 | 日 |  | float32
N1DCS.DAY_CHANGE | 28345 | 天数改变 |  | float32
N1DCS.HOUR | 28346 | 时 |  | float32
N1DCS.MIN | 28347 | 分 |  | float32
N1DCS.MONTH | 28348 | 月 |  | float32
N1DCS.SEC | 28349 | 秒 |  | float32
N1DCS.YEAR | 28350 | 年 |  | float32
N1DCS.ZPKD | 28351 | 中旁阀最小阀位开度 |  | float32
N1DCS.DYTJZFH | 28352 | #2机负荷 |  | float32
N1DCS.10CFE40CQ104I | 28353 | 烟囱出口CO折算含量 | mg/m3 | float32
N1DCS.10LBD60CF101ACC | 28354 | 第1套机组供热母管蒸汽流量累计 | t | float32
N1DCS.10LBD60CF101FLOW | 28355 | 第1套机组抽汽供热母管蒸汽流量 | t/h | float32
N1DCS.J0LBD20CF101ACC | 28356 | 供热计量站母管流量累计值 | t | float32
N1DCS.J0LBD20CF102ACC | 28357 | 供热计量站旁路流量累计值 | t | float32
N1DCS.QDGL30029ACC | 28358 | 启动锅炉天然气供气流量累计值 |  | float32
N1DCS.10LBS45AA012B | 28359 | Ovation Control Builder |  | float32
N1DCS.10LBS46AA012B | 28360 | Ovation Control Builder |  | float32
N1DCS.10MAA50FP121_XQ01 | 28361 | 高压缸前后压差（计算值） |  | float32
N1DCS.10BAC01GS002 | 28362 | EARTH DISC SW TRANSF SIDE CLOS |  | digital
N1DCS.10BAC01GS002A | 28363 | EARTH DISC SW TRANSF SIDE OPEN |  | digital
N1DCS.10BAC01GS003 | 28364 | EARTH DISC SW GEN SIDE CLOSED |  | digital
N1DCS.10BAC01GS003A | 28365 | EARTH DISC SW GEN SIDE OPEN |  | digital
N1DCS.10BFA01EA001 | 28366 | ATS DEVICE FAULT |  | digital
N1DCS.10BFA01EA001A | 28367 | AUTO TRANSFER SWITCH POSITION |  | digital
N1DCS.10BFA01EA001B | 28368 | AUTO TRANSFER SWITCH POSITION |  | digital
N1DCS.10BFA02EA001 | 28369 | ATS DEVICE FAULT |  | digital
N1DCS.10BFA02EA001A | 28370 | AUTO TRANSFER SWITCH POSITION |  | digital
N1DCS.10BFA02EA001B | 28371 | AUTO TRANSFER SWITCH POSITION |  | digital
N1DCS.10BNA01GS001A_3 | 28372 | EMCC INC CB A CB CLOSED |  | digital
N1DCS.10BNA01GS001A_4 | 28373 | EMCC INC CB A CB OPENED |  | digital
N1DCS.10BNA01GS001A_5 | 28374 | EMCC INC CB A REMOTE POSITION |  | digital
N1DCS.10BNA01GS001B_3 | 28375 | EMCC INC CB B CB CLOSED |  | digital
N1DCS.10BNA01GS001B_4 | 28376 | EMCC INC CB B CB OPENED |  | digital
N1DCS.10BNA01GS001B_5 | 28377 | EMCC INC CB B REMOTE POSITION |  | digital
N1DCS.10BRA01EG003 | 28378 | 220Vac 11BRA FEEDER CB TRIP |  | digital
N1DCS.10BRA01EG003A | 28379 | 220VAC 11BRA FEEDER CB TRIP |  | digital
N1DCS.10BUA01GS001 | 28380 | 110Vdc BUA INC LINE BKR CLOSED |  | digital
N1DCS.10BUA01GS002 | 28381 | 110Vdc BUA INC LINE BKR CLOSED |  | digital
N1DCS.10MBX30AA051XB03 | 28382 | FAIL SAFE SOV1 IGV ACTOR AVAIL |  | digital
N1DCS.10MBX30AA051YB01 | 28383 | FAIL SAFE SOV1 IGV ACTR ERG CM |  | digital
N1DCS.10MBX30AA052YB01 | 28384 | FAIL SAFE SOV2 IGV ACTR ERG CM |  | digital
N1DCS.10MBX40AA051XB03 | 28385 | FAIL SAFE SOV1 CV1 ACTOR AVAIL |  | digital
N1DCS.10MBX40AA051YB01 | 28386 | FAIL SAFE SOV1 CV1 ACTR ERG CM |  | digital
N1DCS.10MBX40AA051YB11 | 28387 | FAIL SAFE SOV1 CV1 ACTR ERG CM |  | digital
N1DCS.10MBX40AA052XB03 | 28388 | FAIL SAFE SOV2 CV1 ACTOR AVAIL |  | digital
N1DCS.10MBX40AA052XB03A | 28389 | FAIL SAFE SOV2 CV1 ACTOR AVAIL |  | digital
N1DCS.10MBX40AA052YB01 | 28390 | FAIL SAFE SOV2 CV1 ACTR ERG CM |  | digital
N1DCS.10MBX40AA052YB11 | 28391 | FAIL SAFE SOV2 CV1 ACTR ERG CM |  | digital
N1DCS.BALM033 | 28392 | #1余热锅炉污染物排放超标 |  | digital
N1DCS.CHROINSTFAULT | 28393 | 调压站色谱仪故障 |  | digital
N1DCS.10LBS45AA001_ALARM | 28394 | Ovation Control Builder |  | digital
N1DCS.10LBS45AA001_IPEOUT2 | 28395 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_ALARM | 28396 | Ovation Control Builder |  | digital
N1DCS.10LBS46AA001_HPEOUT2 | 28397 | Ovation Control Builder |  | digital
N1DCS.10MAA50FP011_XH53 | 28398 | 高调门阀后蒸汽压力<6.5MPa |  | digital
N1DCS.10NAA01FP101_MRE | 28399 | 热网抽汽调阀后压力（高排）坏点 |  | digital
N1DCS.10NAA01FP101_LP | 28400 | 热网抽汽调阀后压力（高排） |  | digital
N2DCS.20BFA01CE004 | 28401 | BFA01 VOLTAGE MEASURE |  | float32
N2DCS.20BFA02CE004 | 28402 | BFA02 VOLTAGE MEASURE |  | float32
N2DCS.20BNA01CE004 | 28403 | EMCC BUS BAR VOLATGE |  | float32
N2DCS.20BNA01GS001A_1 | 28404 | EMCC INC CB A VOLTAGE |  | float32
N2DCS.20BNA01GS001A_2 | 28405 | EMCC INC CB A CURRENT |  | float32
N2DCS.20BNA01GS001B_1 | 28406 | EMCC INC CB B VOLTAGE |  | float32
N2DCS.20BNA01GS001B_2 | 28407 | EMCC INC CB B CURRENT |  | float32
N2DCS.20BRA01EG001 | 28408 | 1XBRA 220VAC BUS BAR VOLTAGE |  | float32
N2DCS.20BUA01CE001 | 28409 | BUS BAR VOLTAGE |  | float32
N2DCS.20EKG60FF001 | 28410 | 天然气流量 |  | float32
N2DCS.20MBA10CG101 | 28411 | 燃机轴位移1 |  | float32
N2DCS.20MBA10CG102 | 28412 | 燃机轴位移2 |  | float32
N2DCS.20MBA11CP101 | 28413 | 压气机入口压力 |  | float32
N2DCS.20MBA12CP101 | 28414 | 压气机排气压力1 |  | float32
N2DCS.20MBA12CP102 | 28415 | 压气机排气压力2 |  | float32
N2DCS.20MBD11CY101 | 28416 | 燃机透平侧轴承振动1 |  | float32
N2DCS.20MBD11CY102 | 28417 | 燃机透平侧轴承振动2 |  | float32
N2DCS.20MBD11CY111 | 28418 | 燃机轴振动1 |  | float32
N2DCS.20MBD11CY112 | 28419 | 燃机轴振动2 |  | float32
N2DCS.20MBD12CT101A | 28420 | 燃机推力轴承温度A |  | float32
N2DCS.20MBD12CT101B | 28421 | 燃机推力轴承温度B |  | float32
N2DCS.20MBD12CT101C | 28422 | 燃机推力轴承温度C |  | float32
N2DCS.20MBD12CY101 | 28423 | 燃机压气机侧轴承振动1 |  | float32
N2DCS.20MBD12CY102 | 28424 | 燃机压气机侧轴承振动2 |  | float32
N2DCS.20MBD12CY111 | 28425 | 压气机轴振动1 |  | float32
N2DCS.20MBD12CY112 | 28426 | 压气机轴振动2 |  | float32
N2DCS.20MBH22AA101 | 28427 | 第2级冷却空气阀1阀位反馈 |  | float32
N2DCS.20MBH22AA102 | 28428 | 第2级冷却空气阀2阀位反馈 |  | float32
N2DCS.20MBH22CP101 | 28429 | 燃机二级冷却空气压力3 |  | float32
N2DCS.20MBH22CP102 | 28430 | 燃机二级冷却空气压力1 |  | float32
N2DCS.20MBH22CP103 | 28431 | 燃机二级冷却空气压力2 |  | float32
N2DCS.20MBH23AA101 | 28432 | 第3级冷却空气阀1阀位反馈 |  | float32
N2DCS.20MBH23AA102 | 28433 | 第3级冷却空气阀2阀位反馈 |  | float32
N2DCS.20MBH23CP101 | 28434 | 燃机三级冷却空气压力3 |  | float32
N2DCS.20MBH23CP102 | 28435 | 燃机三级冷却空气压力1 |  | float32
N2DCS.20MBH23CP103 | 28436 | 燃机三级冷却空气压力2 |  | float32
N2DCS.20MBL14CP101 | 28437 | 两级总差压 |  | float32
N2DCS.20MBL14CP102 | 28438 | 粗过滤系统差压 |  | float32
N2DCS.20MBM10CP101 | 28439 | 燃机燃烧室进出口差压 |  | float32
N2DCS.20MBM10CY101 | 28440 | 燃烧室振动1 |  | float32
N2DCS.20MBM10CY102 | 28441 | 燃烧室振动2 |  | float32
N2DCS.20MBM10CY103 | 28442 | 燃烧室振动3 |  | float32
N2DCS.20MBM11CP101 | 28443 | 燃烧室嗡鸣1 |  | float32
N2DCS.20MBM11CP102 | 28444 | 燃烧室嗡鸣2 |  | float32
N2DCS.20MBM12CP107 | 28445 | 燃烧器嗡鸣1 |  | float32
N2DCS.20MBM12CP110 | 28446 | 燃烧器嗡鸣2 |  | float32
N2DCS.20MBM12CP115 | 28447 | 燃烧器嗡鸣3 |  | float32
N2DCS.20MBP32CP101 | 28448 | 预混燃气控制阀后压力 |  | float32
N2DCS.20MBP34CF101 | 28449 | 天然气流量 |  | float32
N2DCS.20MBP34CP101 | 28450 | 值班燃气控制阀后压力 |  | float32
N2DCS.20MBV10CL101 | 28451 | 润滑油油箱液位 |  | float32
N2DCS.20MBV26CP101 | 28452 | 润滑油供油压力 |  | float32
N2DCS.20MBV26CT101 | 28453 | 润滑油供油温度 |  | float32
N2DCS.20MBV31CP101 | 28454 | 顶轴油压力1 |  | float32
N2DCS.20MBV31CP102 | 28455 | 顶轴油压力2 |  | float32
N2DCS.20MBX01CL101 | 28456 | 控制油油箱液位 |  | float32
N2DCS.20MBX01CT101A | 28457 | 燃机控制油油箱油温1 |  | float32
N2DCS.20MBX01CT101B | 28458 | 燃机控制油油箱油温2 |  | float32
N2DCS.20MBX03CP101 | 28459 | 燃机控制油母管压力 |  | float32
N2DCS.20MKA25CT301 | 28460 | 发电机钉子线圈出水温度1 |  | float32
N2DCS.20MKA25CT302 | 28461 | 发电机钉子线圈出水温度2 |  | float32
N2DCS.20MKA25CT303 | 28462 | 发电机钉子线圈出水温度3 |  | float32
N2DCS.20MKA25CT304 | 28463 | 发电机钉子线圈出水温度4 |  | float32
N2DCS.20MKA26CT301 | 28464 | 发电机出线盒热氢温度1 |  | float32
N2DCS.20MKA26CT302 | 28465 | 发电机出线盒热氢温度2 |  | float32
N2DCS.20MKA30CT301_TCS | 28466 | 发电机励端冷氢温度1 |  | float32
N2DCS.20MKA30CT302_TCS | 28467 | 发电机励端冷氢温度2 |  | float32
N2DCS.20MKA30CT303_TCS | 28468 | 发电机励端冷氢温度3 |  | float32
N2DCS.20MKA30CT304_TCS | 28469 | 发电机励端冷氢温度4 |  | float32
N2DCS.20MKA30CT311_TCS | 28470 | 发电机汽端冷氢温度1 |  | float32
N2DCS.20MKA30CT312_TCS | 28471 | 发电机汽端冷氢温度2 |  | float32
N2DCS.20MKA30CT313_TCS | 28472 | 发电机汽端冷氢温度3 |  | float32
N2DCS.20MKA30CT314_TCS | 28473 | 发电机汽端冷氢温度4 |  | float32
N2DCS.20MKA31CT301 | 28474 | 发电机励端热氢温度1 |  | float32
N2DCS.20MKA31CT311 | 28475 | 发电机汽端热氢温度1 |  | float32
N2DCS.20MKD11CY021 | 28476 | 发电机汽端轴承振动 |  | float32
N2DCS.20MKD11CY022 | 28477 | 发电机汽端轴承振动 |  | float32
N2DCS.20MKD11CY041 | 28478 | 发电机汽端轴承X向振动 |  | float32
N2DCS.20MKD11CY042 | 28479 | 发电机汽端轴承Y向振动 |  | float32
N2DCS.20MKD12CY021 | 28480 | 发电机励端轴承振动 |  | float32
N2DCS.20MKD12CY022 | 28481 | 发电机励端轴承振动 |  | float32
N2DCS.20MKD12CY041 | 28482 | 发电机励端轴承X向振动 |  | float32
N2DCS.20MKD12CY042 | 28483 | 发电机励端轴承Y向振动 |  | float32
N2DCS.20MKD13CY021 | 28484 | 发电机集电环轴承振动1 |  | float32
N2DCS.20MKD13CY022 | 28485 | 发电机集电环轴承振动2 |  | float32
N2DCS.20MKD13CY041 | 28486 | 发电机集电环轴承X向振动 |  | float32
N2DCS.20MKD13CY042 | 28487 | 发电机集电环轴承Y向振动 |  | float32
N2DCS.20MKF05CL101 | 28488 | 发电机定子冷却水箱液位 |  | float32
N2DCS.20MKF18CQ101 | 28489 | 发电机定子线圈进水电导率 |  | float32
N2DCS.20MKF19CF101 | 28490 | 发电机定子冷却水流量 |  | float32
N2DCS.20MKW06CL101 | 28491 | 氢侧油箱液位 |  | float32
N2DCS.20SAM30CT102 | 28492 | 燃机罩壳温度1 |  | float32
N2DCS.20SAM30CT102A | 28493 | 燃机罩壳温度2 |  | float32
N2DCS.DAY | 28494 | 日 |  | float32
N2DCS.HOUR | 28495 | 时 |  | float32
N2DCS.MIN | 28496 | 分 |  | float32
N2DCS.MONTH | 28497 | 月 |  | float32
N2DCS.SEC | 28498 | 秒 |  | float32
N2DCS.YEAR | 28499 | 年 |  | float32
N2DCS.20LBD60CF101ACC | 28500 | 第2套机组供热母管蒸汽流量累计 | t | float32
N2DCS.20LBD60CF101FLOW | 28501 | 第2套机组抽汽供热母管蒸汽流量 | t/h | float32
N2DCS.#4GTLOADAO | 28502 | #4机负荷 | MW | float32
N2DCS.20CFE40CQ104I | 28503 | 烟囱出口CO折算值 | mg/m3 | float32
N2DCS.20LBS45AA012B | 28504 | Ovation Control Builder |  | float32
N2DCS.20LBS46AA012B | 28505 | Ovation Control Builder |  | float32
N2DCS.20MAA50FP121_XQ01 | 28506 | 高压缸前后压差(计算值) |  | float32
N2DCS.TEMSUM | 28507 | 主蒸汽温度与高压缸温度差值 |  | float32
N2DCS.20BAC01GS002 | 28508 | EARTH DISC SW TRANSF SIDE CLOS |  | digital
N2DCS.20BAC01GS002A | 28509 | EARTH DISC SW TRANSF SIDE OPEN |  | digital
N2DCS.20BAC01GS003 | 28510 | EARTH DISC SW GEN SIDE CLOSED |  | digital
N2DCS.20BAC01GS003A | 28511 | EARTH DISC SW GEN SIDE OPEN |  | digital
N2DCS.20BFA01EA001 | 28512 | ATS DEVICE FAULT |  | digital
N2DCS.20BFA01EA001A | 28513 | AUTO TRANSFER SWITCH POSITION |  | digital
N2DCS.20BFA01EA001B | 28514 | AUTO TRANSFER SWITCH POSITION |  | digital
N2DCS.20BFA02EA001 | 28515 | ATS DEVICE FAULT |  | digital
N2DCS.20BFA02EA001A | 28516 | AUTO TRANSFER SWITCH POSITION |  | digital
N2DCS.20BFA02EA001B | 28517 | AUTO TRANSFER SWITCH POSITION |  | digital
N2DCS.20BNA01GS001A_3 | 28518 | EMCC INC CB A CB CLOSED |  | digital
N2DCS.20BNA01GS001A_4 | 28519 | EMCC INC CB A CB OPENED |  | digital
N2DCS.20BNA01GS001A_5 | 28520 | EMCC INC CB A REMOTE POSITION |  | digital
N2DCS.20BNA01GS001B_3 | 28521 | EMCC INC CB B CB CLOSED |  | digital
N2DCS.20BNA01GS001B_4 | 28522 | EMCC INC CB B CB OPENED |  | digital
N2DCS.20BNA01GS001B_5 | 28523 | EMCC INC CB B REMOTE POSITION |  | digital
N2DCS.20BRA01EG003 | 28524 | 220Vac 11BRA FEEDER CB TRIP |  | digital
N2DCS.20BRA01EG003A | 28525 | 220VAC 11BRA FEEDER CB TRIP |  | digital
N2DCS.20BUA01GS001 | 28526 | 110Vdc BUA INC LINE BKR CLOSED |  | digital
N2DCS.20BUA01GS002 | 28527 | 110Vdc BUA INC LINE BKR CLOSED |  | digital
N2DCS.20MBX30AA051XB03 | 28528 | FAIL SAFE SOV1 IGV ACTOR AVAIL |  | digital
N2DCS.20MBX30AA051YB01 | 28529 | FAIL SAFE SOV1 IGV ACTR ERG CM |  | digital
N2DCS.20MBX30AA052YB01 | 28530 | FAIL SAFE SOV2 IGV ACTR ERG CM |  | digital
N2DCS.20MBX40AA051XB03 | 28531 | FAIL SAFE SOV1 CV1 ACTOR AVAIL |  | digital
N2DCS.20MBX40AA051YB01 | 28532 | FAIL SAFE SOV1 CV1 ACTR ERG CM |  | digital
N2DCS.20MBX40AA051YB11 | 28533 | FAIL SAFE SOV1 CV1 ACTR ERG CM |  | digital
N2DCS.20MBX40AA052XB03 | 28534 | FAIL SAFE SOV2 CV1 ACTOR AVAIL |  | digital
N2DCS.20MBX40AA052XB03A | 28535 | FAIL SAFE SOV2 CV1 ACTOR AVAIL |  | digital
N2DCS.20MBX40AA052YB01 | 28536 | FAIL SAFE SOV2 CV1 ACTR ERG CM |  | digital
N2DCS.20MBX40AA052YB11 | 28537 | FAIL SAFE SOV2 CV1 ACTR ERG CM |  | digital
N2DCS.20LBS45AA001_ALARM | 28538 | Ovation Control Builder |  | digital
N2DCS.20LBS45AA001_IPEOUT2 | 28539 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_ALARM | 28540 | Ovation Control Builder |  | digital
N2DCS.20LBS46AA001_HPEOUT2 | 28541 | Ovation Control Builder |  | digital
N2DCS.20MAA50FP011_XH53 | 28542 | Ovation Control Builder |  | digital
N2DCS.20NAA01FP101_MRE | 28543 | 冷再抽汽减压阀前压力（3选中） |  | digital
N2DCS.20NAA01FP101_LP | 28544 | 冷再抽汽减压阀前压力（3选中） |  | digital
N1DCS.10LBD60CF101THMACC | 28545 | 第一套机组供热母管蒸汽热量累计 | GJ | float32
N2DCS.20LBD60CF101THMACC | 28546 | 第二套机组供热母管蒸汽热量累计 | GJ | float32
CALC.N1TC_RW_CoaguPump | 28547 | 凝结水泵耗电率 | A | float32
CALC.N2TC_RW_CoaguPump | 28548 | 凝结水泵耗电率 | A | float32
CALC.N1TC_RW_CirPump | 28549 | 循环水泵耗电率 | % | float32
CALC.N2TC_RW_CirPump | 28550 | 循环水泵耗电率 | % | float32
CALC.N1TC_RATEW_COAGUPUMP | 28551 | 凝结水泵单耗 | t/kWh | float32
CALC.N2TC_RATEW_COAGUPUMP | 28552 | 凝结水泵单耗 | t/kWh | float32
CALC.N1TC_RATEW_CIRPUMP | 28553 | 循环水泵单耗 | t/kWh | float32
CALC.N2TC_RATEW_CIRPUMP | 28554 | 循环水泵单耗 | t/kWh | float32
CALC.N1TS_W_CirPumpA | 28555 | 循环水泵A功率 | kW | float32
CALC.N1TS_W_CirPumpB | 28556 | 循环水泵B功率 | kW | float32
CALC.N1TS_W_CoaguPumpA | 28557 | 凝结水泵A功率 | kW | float32
CALC.N1TS_W_CoaguPumpB | 28558 | 凝结水泵B功率 | kW | float32
CALC.N2TS_W_CirPumpA | 28559 | 循环水泵A功率 | kW | float32
CALC.N2TS_W_CirPumpB | 28560 | 循环水泵B功率 | kW | float32
CALC.N2TS_W_CoaguPumpA | 28561 | 凝结水泵A功率 | kW | float32
CALC.N2TS_W_CoaguPumpB | 28562 | 凝结水泵B功率 | kW | float32
N1DCS.10LBD60CF101FLOW1 | 28563 | 第1套机组抽汽供热母管蒸汽流量 | t/h | float32
N2DCS.20LBD60CF101FLOW1 | 28564 | 第2套机组抽汽供热母管蒸汽流量 | m/s | float32
N1DCS.GASAVECAL1 | 28565 | #1流量计算机当日平均高位热值 | KJ/m3 | float32
N1DCS.GASAVECAL2 | 28566 | #2流量计算机当日平均高位热值 | KJ/m3 | float32
RTU.RTU_YC_0001 | 28567 | #1汽机有功1 |  | float32
RTU.RTU_YC_0002 | 28568 | #1汽机有功2 |  | float32
RTU.RTU_YC_0003 | 28569 | #1汽机无功1 |  | float32
RTU.RTU_YC_0004 | 28570 | #1汽机端线电压Uab |  | float32
RTU.RTU_YC_0005 | 28571 | #1汽#2燃机总有功 |  | float32
RTU.RTU_YC_0006 | 28572 | 1G（汽机）无功第二量测 |  | float32
RTU.RTU_YC_0007 | 28573 | 1G（汽机）无功设定值返回 |  | float32
RTU.RTU_YC_0008 | 28574 | 1G（汽机）子站无功设定值 |  | float32
RTU.RTU_YC_0009 | 28575 | #2燃机有功1 |  | float32
RTU.RTU_YC_0010 | 28576 | #2燃机有功2 |  | float32
RTU.RTU_YC_0011 | 28577 | #2燃机无功1 |  | float32
RTU.RTU_YC_0012 | 28578 | #2燃机端线电压Uab |  | float32
RTU.RTU_YC_0013 | 28579 | 2G（燃机）无功第二量测 |  | float32
RTU.RTU_YC_0014 | 28580 | 2G（燃机）无功设定值返回 |  | float32
RTU.RTU_YC_0015 | 28581 | 2G（燃机）子站无功设定值 |  | float32
RTU.RTU_YC_0016 | 28582 | #3汽机有功1 |  | float32
RTU.RTU_YC_0017 | 28583 | #3汽机有功2 |  | float32
RTU.RTU_YC_0018 | 28584 | #3汽机无功1 |  | float32
RTU.RTU_YC_0019 | 28585 | #3汽机端线电压Uab |  | float32
RTU.RTU_YC_0020 | 28586 | #3汽#4燃机总有功 |  | float32
RTU.RTU_YC_0021 | 28587 | 3G（汽机）无功第二量测 |  | float32
RTU.RTU_YC_0022 | 28588 | 3G（汽机）无功设定值返回 |  | float32
RTU.RTU_YC_0023 | 28589 | 3G（汽机）子站无功设定值 |  | float32
RTU.RTU_YC_0024 | 28590 | #4燃机有功1 |  | float32
RTU.RTU_YC_0025 | 28591 | #4燃机有功2 |  | float32
RTU.RTU_YC_0026 | 28592 | #4燃机无功 |  | float32
RTU.RTU_YC_0027 | 28593 | #4燃机端线电压Uab |  | float32
RTU.RTU_YC_0028 | 28594 | 4G（燃机）无功第二量测 |  | float32
RTU.RTU_YC_0029 | 28595 | 4G（燃机）无功设定值返回 |  | float32
RTU.RTU_YC_0030 | 28596 | 4G（燃机）子站无功设定值 |  | float32
RTU.RTU_YC_0031 | 28597 | #1、#2机总有功P2 |  | float32
RTU.RTU_YC_0032 | 28598 | #1、#2机组出力上限 |  | float32
RTU.RTU_YC_0033 | 28599 | #1、#2机组出力下限 |  | float32
RTU.RTU_YC_0034 | 28600 | #1、#2机组响应速率 |  | float32
RTU.RTU_YC_0035 | 28601 | #1、#2机组目标定值返回值 |  | float32
RTU.RTU_YC_0036 | 28602 | #3、#4机总有功P2 |  | float32
RTU.RTU_YC_0037 | 28603 | #3、#4机组出力上限 |  | float32
RTU.RTU_YC_0038 | 28604 | #3、#4机组出力下限 |  | float32
RTU.RTU_YC_0039 | 28605 | #3、#4机组响应速率 |  | float32
RTU.RTU_YC_0040 | 28606 | #3、#4机组目标定值返回值 |  | float32
RTU.RTU_YC_0041 | 28607 | 空点 |  | float32
RTU.RTU_YC_0042 | 28608 | 空点 |  | float32
RTU.RTU_YC_0043 | 28609 | 空点 |  | float32
RTU.RTU_YC_0044 | 28610 | 空点 |  | float32
RTU.RTU_YC_0045 | 28611 | 空点 |  | float32
RTU.RTU_YC_0046 | 28612 | 空点 |  | float32
RTU.RTU_YC_0047 | 28613 | #1汽变有功 |  | float32
RTU.RTU_YC_0048 | 28614 | #1汽变无功 |  | float32
RTU.RTU_YC_0049 | 28615 | #1汽变电流Ib |  | float32
RTU.RTU_YC_0050 | 28616 | #2燃变有功 |  | float32
RTU.RTU_YC_0051 | 28617 | #2燃变无功 |  | float32
RTU.RTU_YC_0052 | 28618 | #2燃变电流Ib |  | float32
RTU.RTU_YC_0053 | 28619 | #3汽变有功 |  | float32
RTU.RTU_YC_0054 | 28620 | #3汽变无功 |  | float32
RTU.RTU_YC_0055 | 28621 | #3汽变电流Ib |  | float32
RTU.RTU_YC_0056 | 28622 | #4燃变有功 |  | float32
RTU.RTU_YC_0057 | 28623 | #4燃变无功 |  | float32
RTU.RTU_YC_0058 | 28624 | #4燃变电流Ib |  | float32
RTU.RTU_YC_0059 | 28625 | 空点 |  | float32
RTU.RTU_YC_0060 | 28626 | 空点 |  | float32
RTU.RTU_YC_0061 | 28627 | 空点 |  | float32
RTU.RTU_YC_0062 | 28628 | #1汽机Ⅰ级供热抽汽流量 |  | float32
RTU.RTU_YC_0063 | 28629 | #1汽机Ⅰ级供热抽汽压力 |  | float32
RTU.RTU_YC_0064 | 28630 | #1汽机Ⅰ级供热抽汽温度 |  | float32
RTU.RTU_YC_0065 | 28631 | 高备变有功 |  | float32
RTU.RTU_YC_0066 | 28632 | 高备变无功 |  | float32
RTU.RTU_YC_0067 | 28633 | 高备变电流Ib |  | float32
RTU.RTU_YC_0068 | 28634 | 桔布甲线有功 |  | float32
RTU.RTU_YC_0069 | 28635 | 桔布甲线无功 |  | float32
RTU.RTU_YC_0070 | 28636 | 桔布甲线电流Ib |  | float32
RTU.RTU_YC_0071 | 28637 | 桔布乙线有功 |  | float32
RTU.RTU_YC_0072 | 28638 | 桔布乙无功 |  | float32
RTU.RTU_YC_0073 | 28639 | 桔布乙电流Ib |  | float32
RTU.RTU_YC_0074 | 28640 | 2012母联有功 |  | float32
RTU.RTU_YC_0075 | 28641 | 2012母联无功 |  | float32
RTU.RTU_YC_0076 | 28642 | 2012母联电流Ib |  | float32
RTU.RTU_YC_0077 | 28643 | 220KV 1母线电压Uab |  | float32
RTU.RTU_YC_0078 | 28644 | 220kV 1母频率 |  | float32
RTU.RTU_YC_0079 | 28645 | 1M电压第二量测 |  | float32
RTU.RTU_YC_0080 | 28646 | 1M电压设定值返回 |  | float32
RTU.RTU_YC_0081 | 28647 | 1M子站电压设定值 |  | float32
RTU.RTU_YC_0082 | 28648 | 220KV 2母线电压Uab |  | float32
RTU.RTU_YC_0083 | 28649 | 220kV 2母频率 |  | float32
RTU.RTU_YC_0084 | 28650 | 2M电压第二量测 |  | float32
RTU.RTU_YC_0085 | 28651 | 2M电压设定值返回 |  | float32
RTU.RTU_YC_0086 | 28652 | 2M子站电压设定值 |  | float32
RTU.RTU_YC_0087 | 28653 | #3汽机Ⅰ级供热抽汽流量 |  | float32
RTU.RTU_YC_0088 | 28654 | #3汽机Ⅰ级供热抽汽压力 |  | float32
RTU.RTU_YC_0089 | 28655 | #3汽机Ⅰ级供热抽汽温度 |  | float32
RTU.RTU_YC_0090 | 28656 | #1变压器档位 |  | float32
RTU.RTU_YC_0091 | 28657 | #2变压器档位 |  | float32
RTU.RTU_YC_0092 | 28658 | #2变压器档位 |  | float32
RTU.RTU_YC_0093 | 28659 | #4变压器档位 |  | float32
RTU.RTU_YC_0094 | 28660 | #9变压器档位 |  | float32
RTU.RTU_YC_0095 | 28661 | (______) Undefined |  | float32
RTU.RTU_YC_0096 | 28662 | (______) Undefined |  | float32
RTU.RTU_YC_0097 | 28663 | (______) Undefined |  | float32
RTU.RTU_YC_0098 | 28664 | (______) Undefined |  | float32
RTU.RTU_YC_0099 | 28665 | (______) Undefined |  | float32
RTU.RTU_YC_0100 | 28666 | (______) Undefined |  | float32
RTU.RTU_YC_0101 | 28667 | 220kV1M线电压Uab |  | float32
RTU.RTU_YC_0102 | 28668 | 220kV1M线电压Ubc |  | float32
RTU.RTU_YC_0103 | 28669 | 220kV1M线电压Uca |  | float32
RTU.RTU_YC_0104 | 28670 | 220kV1M相电压Ua |  | float32
RTU.RTU_YC_0105 | 28671 | 220kV1M相电压Ub |  | float32
RTU.RTU_YC_0106 | 28672 | 220kV1M相电压Uc |  | float32
RTU.RTU_YC_0107 | 28673 | 220kV1M频率F |  | float32
RTU.RTU_YC_0108 | 28674 | 220kV2M线电压Uab |  | float32
RTU.RTU_YC_0109 | 28675 | 220kV2M线电压Ubc |  | float32
RTU.RTU_YC_0110 | 28676 | 220kV2M线电压Uca |  | float32
RTU.RTU_YC_0111 | 28677 | 220kV2M相电压Ua |  | float32
RTU.RTU_YC_0112 | 28678 | 220kV2M相电压Ub |  | float32
RTU.RTU_YC_0113 | 28679 | 220kV2M相电压Uc |  | float32
RTU.RTU_YC_0114 | 28680 | 220kV2M频率F |  | float32
RTU.RTU_YC_0115 | 28681 | #1主变变高2201开关P |  | float32
RTU.RTU_YC_0116 | 28682 | #1主变变高2201开关Q |  | float32
RTU.RTU_YC_0117 | 28683 | #1主变变高2201开关Ia |  | float32
RTU.RTU_YC_0118 | 28684 | #1主变变高2201开关Ib |  | float32
RTU.RTU_YC_0119 | 28685 | #1主变变高2201开关Ic |  | float32
RTU.RTU_YC_0120 | 28686 | #1主变变高2201开关cos |  | float32
RTU.RTU_YC_0121 | 28687 | #2主变变高2202开关P |  | float32
RTU.RTU_YC_0122 | 28688 | #2主变变高2202开关Q |  | float32
RTU.RTU_YC_0123 | 28689 | #2主变变高2202开关Ia |  | float32
RTU.RTU_YC_0124 | 28690 | #2主变变高2202开关Ib |  | float32
RTU.RTU_YC_0125 | 28691 | #2主变变高2202开关Ic |  | float32
RTU.RTU_YC_0126 | 28692 | #2主变变高2202开关cos |  | float32
RTU.RTU_YC_0127 | 28693 | #3主变变高2203开关P |  | float32
RTU.RTU_YC_0128 | 28694 | #3主变变高2203开关Q |  | float32
RTU.RTU_YC_0129 | 28695 | #3主变变高2203开关Ia |  | float32
RTU.RTU_YC_0130 | 28696 | #3主变变高2203开关Ib |  | float32
RTU.RTU_YC_0131 | 28697 | #3主变变高2203开关Ic |  | float32
RTU.RTU_YC_0132 | 28698 | #3主变变高2203开关cos |  | float32
RTU.RTU_YC_0133 | 28699 | #4主变变高2204开关P |  | float32
RTU.RTU_YC_0134 | 28700 | #4主变变高2204开关Q |  | float32
RTU.RTU_YC_0135 | 28701 | #4主变变高2204开关Ia |  | float32
RTU.RTU_YC_0136 | 28702 | #4主变变高2204开关Ib |  | float32
RTU.RTU_YC_0137 | 28703 | #4主变变高2204开关Ic |  | float32
RTU.RTU_YC_0138 | 28704 | #4主变变高2204开关cos |  | float32
RTU.RTU_YC_0139 | 28705 | #9主变变高2209开关P |  | float32
RTU.RTU_YC_0140 | 28706 | #9主变变高2209开关Q |  | float32
RTU.RTU_YC_0141 | 28707 | #9主变变高2209开关Ia |  | float32
RTU.RTU_YC_0142 | 28708 | #9主变变高2209开关Ib |  | float32
RTU.RTU_YC_0143 | 28709 | #9主变变高2209开关Ic |  | float32
RTU.RTU_YC_0144 | 28710 | #9主变变高2209开关cos |  | float32
RTU.RTU_YC_0145 | 28711 | 220kV母联2012开关P |  | float32
RTU.RTU_YC_0146 | 28712 | 220kV母联2012开关Q |  | float32
RTU.RTU_YC_0147 | 28713 | 220kV母联2012开关Ia |  | float32
RTU.RTU_YC_0148 | 28714 | 220kV母联2012开关Ib |  | float32
RTU.RTU_YC_0149 | 28715 | 220kV母联2012开关Ic |  | float32
RTU.RTU_YC_0150 | 28716 | 220kV母联2012开关cos |  | float32
RTU.RTU_YC_0151 | 28717 | 220kV桔布甲线4527开关P |  | float32
RTU.RTU_YC_0152 | 28718 | 220kV桔布甲线4527开关Q |  | float32
RTU.RTU_YC_0153 | 28719 | 220kV桔布甲线4527开关Ia |  | float32
RTU.RTU_YC_0154 | 28720 | 220kV桔布甲线4527开关Ib |  | float32
RTU.RTU_YC_0155 | 28721 | 220kV桔布甲线4527开关Ic |  | float32
RTU.RTU_YC_0156 | 28722 | 220kV桔布甲线4527开关cos |  | float32
RTU.RTU_YC_0157 | 28723 | 220kV桔布乙线4528开关P |  | float32
RTU.RTU_YC_0158 | 28724 | 220kV桔布乙线4528开关Q |  | float32
RTU.RTU_YC_0159 | 28725 | 220kV桔布乙线4528开关Ia |  | float32
RTU.RTU_YC_0160 | 28726 | 220kV桔布乙线4528开关Ib |  | float32
RTU.RTU_YC_0161 | 28727 | 220kV桔布乙线4528开关Ic |  | float32
RTU.RTU_YC_0162 | 28728 | 220kV桔布乙线4528开关cos |  | float32
RTU.RTU_YC_0163 | 28729 | #1发电机P |  | float32
RTU.RTU_YC_0164 | 28730 | #1发电机Q |  | float32
RTU.RTU_YC_0165 | 28731 | #1发电机Uab |  | float32
RTU.RTU_YC_0166 | 28732 | #1发电机Ia |  | float32
RTU.RTU_YC_0167 | 28733 | #1发电机cos |  | float32
RTU.RTU_YC_0168 | 28734 | #2发电机P |  | float32
RTU.RTU_YC_0169 | 28735 | #2发电机Q |  | float32
RTU.RTU_YC_0170 | 28736 | #2发电机Uab |  | float32
RTU.RTU_YC_0171 | 28737 | #2发电机Ia |  | float32
RTU.RTU_YC_0172 | 28738 | #2发电机cos |  | float32
RTU.RTU_YC_0173 | 28739 | #3发电机P |  | float32
RTU.RTU_YC_0174 | 28740 | #3发电机Q |  | float32
RTU.RTU_YC_0175 | 28741 | #3发电机Uab |  | float32
RTU.RTU_YC_0176 | 28742 | #3发电机Ia |  | float32
RTU.RTU_YC_0177 | 28743 | #3发电机cos |  | float32
RTU.RTU_YC_0178 | 28744 | #4发电机P |  | float32
RTU.RTU_YC_0179 | 28745 | #4发电机Q |  | float32
RTU.RTU_YC_0180 | 28746 | #4发电机Uab |  | float32
RTU.RTU_YC_0181 | 28747 | #4发电机Ia |  | float32
RTU.RTU_YC_0182 | 28748 | #4发电机cos |  | float32
RTU.RTU_YC_0183 | 28749 | (______) Undefined |  | float32
RTU.RTU_YC_0184 | 28750 | (______) Undefined |  | float32
RTU.RTU_YC_0185 | 28751 | (______) Undefined |  | float32
RTU.RTU_YC_0186 | 28752 | (______) Undefined |  | float32
RTU.RTU_YC_0187 | 28753 | (______) Undefined |  | float32
RTU.RTU_YC_0188 | 28754 | (______) Undefined |  | float32
RTU.RTU_YC_0189 | 28755 | (______) Undefined |  | float32
RTU.RTU_YC_0190 | 28756 | (______) Undefined |  | float32
RTU.RTU_YC_0191 | 28757 | (______) Undefined |  | float32
RTU.RTU_YC_0192 | 28758 | (______) Undefined |  | float32
RTU.RTU_YC_0193 | 28759 | (______) Undefined |  | float32
RTU.RTU_YC_0194 | 28760 | (______) Undefined |  | float32
RTU.RTU_YC_0195 | 28761 | (______) Undefined |  | float32
RTU.RTU_YC_0196 | 28762 | (______) Undefined |  | float32
RTU.RTU_YC_0197 | 28763 | (______) Undefined |  | float32
RTU.RTU_YC_0198 | 28764 | (______) Undefined |  | float32
RTU.RTU_YC_0199 | 28765 | (______) Undefined |  | float32
RTU.RTU_YC_0200 | 28766 | (______) Undefined |  | float32
RTU.RTU_YX_0001 | 28767 | 事故总信号 |  | digital
RTU.RTU_YX_0002 | 28768 | #1#2机AGC投入/退出信号 |  | digital
RTU.RTU_YX_0003 | 28769 | #1#2机组DCS系统是否允许AGC投入信号 |  | digital
RTU.RTU_YX_0004 | 28770 | #1#2机组负荷增闭锁信号 |  | digital
RTU.RTU_YX_0005 | 28771 | #1#2机组负荷减闭锁信号 |  | digital
RTU.RTU_YX_0006 | 28772 | #1#2机组一次调频投退信号 |  | digital
RTU.RTU_YX_0007 | 28773 | #1G 低频振荡稳定控制PSS投退信号 |  | digital
RTU.RTU_YX_0008 | 28774 | #1G AVC投入/退出信号 |  | digital
RTU.RTU_YX_0009 | 28775 | #1G AVC下位G异常信号 |  | digital
RTU.RTU_YX_0010 | 28776 | #1G 上调节闭锁 |  | digital
RTU.RTU_YX_0011 | 28777 | #1G 下调节闭锁 |  | digital
RTU.RTU_YX_0012 | 28778 | #2G 一次调频投退信号 |  | digital
RTU.RTU_YX_0013 | 28779 | #2G 低频振荡稳定控制PSS投退信号 |  | digital
RTU.RTU_YX_0014 | 28780 | #2G AVC投入/退出信号 |  | digital
RTU.RTU_YX_0015 | 28781 | #2G AVC下位G异常信号 |  | digital
RTU.RTU_YX_0016 | 28782 | #2G 上调节闭锁 |  | digital
RTU.RTU_YX_0017 | 28783 | #2G 下调节闭锁 |  | digital
RTU.RTU_YX_0018 | 28784 | #3#4机AGC投入/退出信号 |  | digital
RTU.RTU_YX_0019 | 28785 | #3#4机组DCS系统是否允许AGC投入信号 |  | digital
RTU.RTU_YX_0020 | 28786 | #3#4机组负荷增闭锁信号 |  | digital
RTU.RTU_YX_0021 | 28787 | #3#4机组负荷减闭锁信号 |  | digital
RTU.RTU_YX_0022 | 28788 | #3#4机组一次调频投退信号 |  | digital
RTU.RTU_YX_0023 | 28789 | #3G 低频振荡稳定控制PSS投退信号 |  | digital
RTU.RTU_YX_0024 | 28790 | #3G AVC投入/退出信号 |  | digital
RTU.RTU_YX_0025 | 28791 | #3G AVC下位机异常信号 |  | digital
RTU.RTU_YX_0026 | 28792 | #3G 上调节闭锁 |  | digital
RTU.RTU_YX_0027 | 28793 | #3G 下调节闭锁 |  | digital
RTU.RTU_YX_0028 | 28794 | #4G 一次调频投退信号 |  | digital
RTU.RTU_YX_0029 | 28795 | #4G 低频振荡稳定控制PSS投退信号 |  | digital
RTU.RTU_YX_0030 | 28796 | #4G AVC投入/退出信号 |  | digital
RTU.RTU_YX_0031 | 28797 | #4G AVC下位G异常信号 |  | digital
RTU.RTU_YX_0032 | 28798 | #4G 上调节闭锁 |  | digital
RTU.RTU_YX_0033 | 28799 | #4G 下调节闭锁 |  | digital
RTU.RTU_YX_0034 | 28800 | #2G 802断路器 |  | digital
RTU.RTU_YX_0035 | 28801 | #2G 8020出线刀闸 |  | digital
RTU.RTU_YX_0036 | 28802 | #4G 804断路器 |  | digital
RTU.RTU_YX_0037 | 28803 | #4G 8040出线刀闸 |  | digital
RTU.RTU_YX_0038 | 28804 | #1主变断路器开关 |  | digital
RTU.RTU_YX_0039 | 28805 | #1主变 1母刀闸 |  | digital
RTU.RTU_YX_0040 | 28806 | #1主变 2母刀闸 |  | digital
RTU.RTU_YX_0041 | 28807 | #1主变 出线刀闸 |  | digital
RTU.RTU_YX_0042 | 28808 | #1主变出线接地刀闸 |  | digital
RTU.RTU_YX_0043 | 28809 | #1主变中性点接地刀闸 |  | digital
RTU.RTU_YX_0044 | 28810 | 空点 |  | digital
RTU.RTU_YX_0045 | 28811 | 空点 |  | digital
RTU.RTU_YX_0046 | 28812 | #2主变断路器开关 |  | digital
RTU.RTU_YX_0047 | 28813 | #2主变 1母刀闸 |  | digital
RTU.RTU_YX_0048 | 28814 | #2主变 2母刀闸 |  | digital
RTU.RTU_YX_0049 | 28815 | #2主变 出线刀闸 |  | digital
RTU.RTU_YX_0050 | 28816 | #2主变出线接地刀闸 |  | digital
RTU.RTU_YX_0051 | 28817 | #2主变中性点接地刀闸 |  | digital
RTU.RTU_YX_0052 | 28818 | 空点 |  | digital
RTU.RTU_YX_0053 | 28819 | 空点 |  | digital
RTU.RTU_YX_0054 | 28820 | #3主变断路器开关 |  | digital
RTU.RTU_YX_0055 | 28821 | #3主变 1母刀闸 |  | digital
RTU.RTU_YX_0056 | 28822 | #3主变 2母刀闸 |  | digital
RTU.RTU_YX_0057 | 28823 | #3主变 出线刀闸 |  | digital
RTU.RTU_YX_0058 | 28824 | #3主变出线接地刀闸 |  | digital
RTU.RTU_YX_0059 | 28825 | #3主变中性点接地刀闸 |  | digital
RTU.RTU_YX_0060 | 28826 | 空点 |  | digital
RTU.RTU_YX_0061 | 28827 | 空点 |  | digital
RTU.RTU_YX_0062 | 28828 | #4主变断路器开关 |  | digital
RTU.RTU_YX_0063 | 28829 | #4主变 1母刀闸 |  | digital
RTU.RTU_YX_0064 | 28830 | #4主变 2母刀闸 |  | digital
RTU.RTU_YX_0065 | 28831 | #4主变 出线刀闸 |  | digital
RTU.RTU_YX_0066 | 28832 | #4主变出线接地刀闸 |  | digital
RTU.RTU_YX_0067 | 28833 | #4主变中性点接地刀闸 |  | digital
RTU.RTU_YX_0068 | 28834 | 空点 |  | digital
RTU.RTU_YX_0069 | 28835 | 空点 |  | digital
RTU.RTU_YX_0070 | 28836 | #高备变断路器开关 |  | digital
RTU.RTU_YX_0071 | 28837 | #高备变 1母刀闸 |  | digital
RTU.RTU_YX_0072 | 28838 | #高备变 2母刀闸 |  | digital
RTU.RTU_YX_0073 | 28839 | #高备变 出线刀闸 |  | digital
RTU.RTU_YX_0074 | 28840 | #高备变 出线接地刀闸 |  | digital
RTU.RTU_YX_0075 | 28841 | 空点 |  | digital
RTU.RTU_YX_0076 | 28842 | 空点 |  | digital
RTU.RTU_YX_0077 | 28843 | 桔布甲线 断路器 |  | digital
RTU.RTU_YX_0078 | 28844 | 桔布甲线 1母刀闸 |  | digital
RTU.RTU_YX_0079 | 28845 | 桔布甲线 2母刀闸 |  | digital
RTU.RTU_YX_0080 | 28846 | 桔布甲线 出线刀闸 |  | digital
RTU.RTU_YX_0081 | 28847 | 桔布甲线 出线接地刀闸 |  | digital
RTU.RTU_YX_0082 | 28848 | 空点 |  | digital
RTU.RTU_YX_0083 | 28849 | 空点 |  | digital
RTU.RTU_YX_0084 | 28850 | 桔布乙线 断路器 |  | digital
RTU.RTU_YX_0085 | 28851 | 桔布乙线 1母刀闸 |  | digital
RTU.RTU_YX_0086 | 28852 | 桔布乙线 2母刀闸 |  | digital
RTU.RTU_YX_0087 | 28853 | 桔布乙线 出线刀闸 |  | digital
RTU.RTU_YX_0088 | 28854 | 桔布乙线 出线接地刀闸 |  | digital
RTU.RTU_YX_0089 | 28855 | 空点 |  | digital
RTU.RTU_YX_0090 | 28856 | 空点 |  | digital
RTU.RTU_YX_0091 | 28857 | 2012母联断路器开关 |  | digital
RTU.RTU_YX_0092 | 28858 | 2012母联 1母刀闸 |  | digital
RTU.RTU_YX_0093 | 28859 | 空点 |  | digital
RTU.RTU_YX_0094 | 28860 | 2012母联 2母刀闸 |  | digital
RTU.RTU_YX_0095 | 28861 | 空点 |  | digital
RTU.RTU_YX_0096 | 28862 | 220KV 1母PT刀闸 |  | digital
RTU.RTU_YX_0097 | 28863 | 220KV 1母PT接地刀闸 |  | digital
RTU.RTU_YX_0098 | 28864 | 220KV 2母PT刀闸 |  | digital
RTU.RTU_YX_0099 | 28865 | 220KV 2母PT接地刀闸 |  | digital
RTU.RTU_YX_0100 | 28866 | AVC系统当地/远方切换信号 |  | digital
RTU.RTU_YX_0101 | 28867 | 是否单G无功模式 |  | digital
RTU.RTU_YX_0102 | 28868 | AVC子站投入/退出信号 |  | digital
RTU.RTU_YX_0103 | 28869 | AVC通信异常 |  | digital
RTU.RTU_YX_0104 | 28870 | #高备变 中性点地刀 |  | digital
RTU.RTU_YX_0105 | 28871 | (______) Undefined |  | digital
RTU.RTU_YX_0106 | 28872 | (______) Undefined |  | digital
RTU.RTU_YX_0107 | 28873 | (______) Undefined |  | digital
RTU.RTU_YX_0108 | 28874 | (______) Undefined |  | digital
RTU.RTU_YX_0109 | 28875 | (______) Undefined |  | digital
RTU.RTU_YX_0110 | 28876 | (______) Undefined |  | digital
RTU.RTU_YX_0111 | 28877 | (______) Undefined |  | digital
RTU.RTU_YX_0112 | 28878 | (______) Undefined |  | digital
RTU.RTU_YX_0113 | 28879 | (______) Undefined |  | digital
RTU.RTU_YX_0114 | 28880 | (______) Undefined |  | digital
RTU.RTU_YX_0115 | 28881 | (______) Undefined |  | digital
RTU.RTU_YX_0116 | 28882 | (______) Undefined |  | digital
RTU.RTU_YX_0117 | 28883 | (______) Undefined |  | digital
RTU.RTU_YX_0118 | 28884 | (______) Undefined |  | digital
RTU.RTU_YX_0119 | 28885 | (______) Undefined |  | digital
RTU.RTU_YX_0120 | 28886 | (______) Undefined |  | digital
RTU.RTU_YX_0121 | 28887 | (______) Undefined |  | digital
RTU.RTU_YX_0122 | 28888 | (______) Undefined |  | digital
RTU.RTU_YX_0123 | 28889 | (______) Undefined |  | digital
RTU.RTU_YX_0124 | 28890 | (______) Undefined |  | digital
RTU.RTU_YX_0125 | 28891 | (______) Undefined |  | digital
RTU.RTU_YX_0126 | 28892 | (______) Undefined |  | digital
RTU.RTU_YX_0127 | 28893 | (______) Undefined |  | digital
RTU.RTU_YX_0128 | 28894 | (______) Undefined |  | digital
RTU.RTU_YX_0129 | 28895 | (______) Undefined |  | digital
RTU.RTU_YX_0130 | 28896 | (______) Undefined |  | digital
RTU.RTU_YX_0131 | 28897 | (______) Undefined |  | digital
RTU.RTU_YX_0132 | 28898 | (______) Undefined |  | digital
RTU.RTU_YX_0133 | 28899 | (______) Undefined |  | digital
RTU.RTU_YX_0134 | 28900 | (______) Undefined |  | digital
RTU.RTU_YX_0135 | 28901 | (______) Undefined |  | digital
RTU.RTU_YX_0136 | 28902 | (______) Undefined |  | digital
RTU.RTU_YX_0137 | 28903 | (______) Undefined |  | digital
RTU.RTU_YX_0138 | 28904 | (______) Undefined |  | digital
RTU.RTU_YX_0139 | 28905 | (______) Undefined |  | digital
RTU.RTU_YX_0140 | 28906 | (______) Undefined |  | digital
RTU.RTU_YX_0141 | 28907 | (______) Undefined |  | digital
RTU.RTU_YX_0142 | 28908 | (______) Undefined |  | digital
RTU.RTU_YX_0143 | 28909 | (______) Undefined |  | digital
RTU.RTU_YX_0144 | 28910 | (______) Undefined |  | digital
RTU.RTU_YX_0145 | 28911 | (______) Undefined |  | digital
RTU.RTU_YX_0146 | 28912 | (______) Undefined |  | digital
RTU.RTU_YX_0147 | 28913 | (______) Undefined |  | digital
RTU.RTU_YX_0148 | 28914 | (______) Undefined |  | digital
RTU.RTU_YX_0149 | 28915 | (______) Undefined |  | digital
RTU.RTU_YX_0150 | 28916 | (______) Undefined |  | digital
RTU.RTU_YX_0151 | 28917 | 全站事故总信号 |  | digital
RTU.RTU_YX_0152 | 28918 | #1主变变高2201开关 |  | digital
RTU.RTU_YX_0153 | 28919 | #1主变变高22011刀闸 |  | digital
RTU.RTU_YX_0154 | 28920 | #1主变变高22012刀闸 |  | digital
RTU.RTU_YX_0155 | 28921 | #1主变变高22014刀闸 |  | digital
RTU.RTU_YX_0156 | 28922 | #1主变变高2201B0接地刀闸 |  | digital
RTU.RTU_YX_0157 | 28923 | #1主变变高2201C0接地刀闸 |  | digital
RTU.RTU_YX_0158 | 28924 | #1主变变高220140接地刀闸 |  | digital
RTU.RTU_YX_0159 | 28925 | #1主变中性点221000接地刀闸 |  | digital
RTU.RTU_YX_0160 | 28926 | #2主变变高2202开关 |  | digital
RTU.RTU_YX_0161 | 28927 | #2主变变高22021刀闸 |  | digital
RTU.RTU_YX_0162 | 28928 | #2主变变高22022刀闸 |  | digital
RTU.RTU_YX_0163 | 28929 | #2主变变高22024刀闸 |  | digital
RTU.RTU_YX_0164 | 28930 | #2主变变高2202B0接地刀闸 |  | digital
RTU.RTU_YX_0165 | 28931 | #2主变变高2202C0接地刀闸 |  | digital
RTU.RTU_YX_0166 | 28932 | #2主变变高220240接地刀闸 |  | digital
RTU.RTU_YX_0167 | 28933 | #2主变中性点222000接地刀闸 |  | digital
RTU.RTU_YX_0168 | 28934 | #3主变变高2203开关 |  | digital
RTU.RTU_YX_0169 | 28935 | #3主变变高22031刀闸 |  | digital
RTU.RTU_YX_0170 | 28936 | #3主变变高22032刀闸 |  | digital
RTU.RTU_YX_0171 | 28937 | #3主变变高22034刀闸 |  | digital
RTU.RTU_YX_0172 | 28938 | #3主变变高2203B0接地刀闸 |  | digital
RTU.RTU_YX_0173 | 28939 | #3主变变高2203C0接地刀闸 |  | digital
RTU.RTU_YX_0174 | 28940 | #3主变变高220340接地刀闸 |  | digital
RTU.RTU_YX_0175 | 28941 | #3主变中性点223000接地刀闸 |  | digital
RTU.RTU_YX_0176 | 28942 | #4主变变高2204开关 |  | digital
RTU.RTU_YX_0177 | 28943 | #4主变变高22041刀闸 |  | digital
RTU.RTU_YX_0178 | 28944 | #4主变变高22042刀闸 |  | digital
RTU.RTU_YX_0179 | 28945 | #4主变变高22044刀闸 |  | digital
RTU.RTU_YX_0180 | 28946 | #4主变变高2204B0接地刀闸 |  | digital
RTU.RTU_YX_0181 | 28947 | #4主变变高2204C0接地刀闸 |  | digital
RTU.RTU_YX_0182 | 28948 | #4主变变高220440接地刀闸 |  | digital
RTU.RTU_YX_0183 | 28949 | #4主变中性点224000接地刀闸 |  | digital
RTU.RTU_YX_0184 | 28950 | #9主变（#1高备变）变高2209开关 |  | digital
RTU.RTU_YX_0185 | 28951 | #9主变（#1高备变）变高22091刀闸 |  | digital
RTU.RTU_YX_0186 | 28952 | #9主变（#1高备变）变高22092刀闸 |  | digital
RTU.RTU_YX_0187 | 28953 | #9主变（#1高备变）变高22094刀闸 |  | digital
RTU.RTU_YX_0188 | 28954 | #9主变（#1高备变）变高2209B0接地刀闸 |  | digital
RTU.RTU_YX_0189 | 28955 | #9主变（#1高备变）变高2209C0接地刀闸 |  | digital
RTU.RTU_YX_0190 | 28956 | #9主变（#1高备变）变高220940接地刀闸 |  | digital
RTU.RTU_YX_0191 | 28957 | #9主变（#1高备变）中性点229000接地刀闸 |  | digital
RTU.RTU_YX_0192 | 28958 | 220kV母联2012开关 |  | digital
RTU.RTU_YX_0193 | 28959 | 220kV母联20121刀闸 |  | digital
RTU.RTU_YX_0194 | 28960 | 220kV母联20122刀闸 |  | digital
RTU.RTU_YX_0195 | 28961 | 220kV母联201210接地刀闸 |  | digital
RTU.RTU_YX_0196 | 28962 | 220kV母联201220接地刀闸 |  | digital
RTU.RTU_YX_0197 | 28963 | 220kV1M221甲00接地刀闸 |  | digital
RTU.RTU_YX_0198 | 28964 | 220kV2M222甲00接地刀闸 |  | digital
RTU.RTU_YX_0199 | 28965 | 220kV#1PT221PT刀闸 |  | digital
RTU.RTU_YX_0200 | 28966 | 220kV#1PT221PT0接地刀闸 |  | digital
RTU.RTU_YX_0201 | 28967 | 220kV#2PT222PT刀闸 |  | digital
RTU.RTU_YX_0202 | 28968 | 220kV#2PT222PT0接地刀闸 |  | digital
RTU.RTU_YX_0203 | 28969 | 220kV桔布甲线4527开关 |  | digital
RTU.RTU_YX_0204 | 28970 | 220kV桔布甲线45271刀闸 |  | digital
RTU.RTU_YX_0205 | 28971 | 220kV桔布甲线45272刀闸 |  | digital
RTU.RTU_YX_0206 | 28972 | 220kV桔布甲线45274刀闸 |  | digital
RTU.RTU_YX_0207 | 28973 | 220kV桔布甲线4527B0接地刀闸 |  | digital
RTU.RTU_YX_0208 | 28974 | 220kV桔布甲线4527C0接地刀闸 |  | digital
RTU.RTU_YX_0209 | 28975 | 220kV桔布甲线452740接地刀闸 |  | digital
RTU.RTU_YX_0210 | 28976 | 220kV桔布乙线4528开关 |  | digital
RTU.RTU_YX_0211 | 28977 | 220kV桔布乙线45281刀闸 |  | digital
RTU.RTU_YX_0212 | 28978 | 220kV桔布乙线45282刀闸 |  | digital
RTU.RTU_YX_0213 | 28979 | 220kV桔布乙线45284刀闸 |  | digital
RTU.RTU_YX_0214 | 28980 | 220kV桔布乙线4528B0接地刀闸 |  | digital
RTU.RTU_YX_0215 | 28981 | 220kV桔布乙线4528C0接地刀闸 |  | digital
RTU.RTU_YX_0216 | 28982 | 220kV桔布乙线452840接地刀闸 |  | digital
RTU.RTU_YX_0217 | 28983 | (______) Undefined |  | digital
RTU.RTU_YX_0218 | 28984 | (______) Undefined |  | digital
RTU.RTU_YX_0219 | 28985 | (______) Undefined |  | digital
RTU.RTU_YX_0220 | 28986 | (______) Undefined |  | digital
RTU.RTU_YX_0221 | 28987 | (______) Undefined |  | digital
RTU.RTU_YX_0222 | 28988 | (______) Undefined |  | digital
RTU.RTU_YX_0223 | 28989 | (______) Undefined |  | digital
RTU.RTU_YX_0224 | 28990 | (______) Undefined |  | digital
RTU.RTU_YX_0225 | 28991 | (______) Undefined |  | digital
RTU.RTU_YX_0226 | 28992 | (______) Undefined |  | digital
RTU.RTU_YX_0227 | 28993 | (______) Undefined |  | digital
RTU.RTU_YX_0228 | 28994 | (______) Undefined |  | digital
RTU.RTU_YX_0229 | 28995 | (______) Undefined |  | digital
RTU.RTU_YX_0230 | 28996 | (______) Undefined |  | digital
RTU.RTU_YX_0231 | 28997 | (______) Undefined |  | digital
RTU.RTU_YX_0232 | 28998 | (______) Undefined |  | digital
RTU.RTU_YX_0233 | 28999 | (______) Undefined |  | digital
RTU.RTU_YX_0234 | 29000 | (______) Undefined |  | digital
RTU.RTU_YX_0235 | 29001 | (______) Undefined |  | digital
RTU.RTU_YX_0236 | 29002 | (______) Undefined |  | digital
RTU.RTU_YX_0237 | 29003 | (______) Undefined |  | digital
RTU.RTU_YX_0238 | 29004 | (______) Undefined |  | digital
RTU.RTU_YX_0239 | 29005 | (______) Undefined |  | digital
RTU.RTU_YX_0240 | 29006 | (______) Undefined |  | digital
RTU.RTU_YX_0241 | 29007 | (______) Undefined |  | digital
RTU.RTU_YX_0242 | 29008 | (______) Undefined |  | digital
RTU.RTU_YX_0243 | 29009 | (______) Undefined |  | digital
RTU.RTU_YX_0244 | 29010 | (______) Undefined |  | digital
RTU.RTU_YX_0245 | 29011 | (______) Undefined |  | digital
RTU.RTU_YX_0246 | 29012 | (______) Undefined |  | digital
RTU.RTU_YX_0247 | 29013 | (______) Undefined |  | digital
RTU.RTU_YX_0248 | 29014 | (______) Undefined |  | digital
RW.MBX.F001 | 29015 | 瞬时流量 | t/h | float32
RW.MBX.F002 | 29016 | 瞬时流量 | t/h | float32
RW.MBX.F003 | 29017 | 瞬时流量 | t/h | float32
RW.MBX.F004 | 29018 | 瞬时流量 | t/h | float32
RW.MBX.F005 | 29019 | 瞬时流量 | t/h | float32
RW.MBX.F006 | 29020 | 瞬时流量 | t/h | float32
RW.MBX.F007 | 29021 | 瞬时流量 | t/h | float32
RW.MBX.F009 | 29022 | 瞬时流量 | t/h | float32
RW.MBX.F010 | 29023 | 瞬时流量 | t/h | float32
RW.MBX.F011 | 29024 | 瞬时流量 | t/h | float32
RW.MBX.F012 | 29025 | 瞬时流量 | t/h | float32
RW.MBX.F013 | 29026 | 瞬时流量 | t/h | float32
RW.MBX.P001 | 29027 | 压力 | mPa | float32
RW.MBX.P002 | 29028 | 压力 | mPa | float32
RW.MBX.P003 | 29029 | 压力 | mPa | float32
RW.MBX.P004 | 29030 | 压力 | mPa | float32
RW.MBX.P005 | 29031 | 压力 | mPa | float32
RW.MBX.P006 | 29032 | 压力 | mPa | float32
RW.MBX.P007 | 29033 | 压力 | mPa | float32
RW.MBX.P009 | 29034 | 压力 | mPa | float32
RW.MBX.P010 | 29035 | 压力 | mPa | float32
RW.MBX.P011 | 29036 | 压力 | mPa | float32
RW.MBX.P012 | 29037 | 压力 | mPa | float32
RW.MBX.P013 | 29038 | 压力 | mPa | float32
RW.MBX.P014 | 29039 | 压力 | mPa | float32
RW.MBX.SUM001 | 29040 | 累计流量 | t | float32
RW.MBX.SUM002 | 29041 | 累计流量 | t | float32
RW.MBX.SUM003 | 29042 | 累计流量 | t | float32
RW.MBX.SUM004 | 29043 | 累计流量 | t | float32
RW.MBX.SUM005 | 29044 | 累计流量 | t | float32
RW.MBX.SUM006 | 29045 | 累计流量 | t | float32
RW.MBX.SUM007 | 29046 | 累计流量 | t | float32
RW.MBX.SUM009 | 29047 | 累计流量 | t | float32
RW.MBX.SUM010 | 29048 | 累计流量 | t | float32
RW.MBX.SUM011 | 29049 | 累计流量 | t | float32
RW.MBX.SUM012 | 29050 | 累计流量 | t | float32
RW.MBX.SUM013 | 29051 | 累计流量 | t | float32
RW.MBX.T001 | 29052 | 温度 | ℃ | float32
RW.MBX.T002 | 29053 | 温度 | ℃ | float32
RW.MBX.T003 | 29054 | 温度 | ℃ | float32
RW.MBX.T004 | 29055 | 温度 | ℃ | float32
RW.MBX.T005 | 29056 | 温度 | ℃ | float32
RW.MBX.T006 | 29057 | 温度 | ℃ | float32
RW.MBX.T007 | 29058 | 温度 | ℃ | float32
RW.MBX.T009 | 29059 | 温度 | ℃ | float32
RW.MBX.T010 | 29060 | 温度 | ℃ | float32
RW.MBX.T011 | 29061 | 温度 | ℃ | float32
RW.MBX.T012 | 29062 | 温度 | ℃ | float32
RW.MBX.T013 | 29063 | 温度 | ℃ | float32
RW.MBX.T014 | 29064 | 温度 | ℃ | float32
CALC.NPPC_Han_GRZ | 29065 | 供热计量站蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_JYIn | 29066 | 金叶进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_JDSIn | 29067 | 金大少印染进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_JTFZIn | 29068 | 晋泰纺织进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_DYFZIn | 29069 | 东岳纺织进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_JSFZIn | 29070 | 嘉顺纺织进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_HSYZIn | 29071 | 和生染整进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_HTFZIn | 29072 | 华泰纺织进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_DHYZIn | 29073 | 敦煌染整进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_Han_JLSNIn | 29074 | 加力水泥进厂蒸汽焓值 | kJ/kg | float32
CALC.NPPC_QLoss_JY | 29075 | 金叶管线损失热量 | GJ/h | float32
CALC.NPPC_QLoss_JDS | 29076 | 金大少印染管线损失热量 | GJ/h | float32
CALC.NPPC_QLoss_JTFZ | 29077 | 晋泰纺织管线损失热量 | GJ/h | float32
CALC.NPPC_QLoss_DYFZ | 29078 | 东岳纺织管线损失热量 | GJ/h | float32
CALC.NPPC_QLoss_JSFZ | 29079 | 嘉顺纺织管线损失热量 | GJ/h | float32
CALC.NPPC_QLoss_HSYZ | 29080 | 和生染整管线损失热量 | GJ/h | float32
CALC.NPPC_QLoss_HTFZ | 29081 | 华泰纺织管线损失热量 | GJ/h | float32
CALC.NPPC_QLoss_DHYZ | 29082 | 敦煌染整管线损失热量 | GJ/h | float32
CALC.NPPC_QLoss_JLSN | 29083 | 加力水泥管线损失热量 | GJ/h | float32
RW.MBX.F_HJ1 | 29084 | 用户瞬时合计流量 | t/h | float32
RW.MBX.SUM_HJ1 | 29085 | 用户瞬时累计流量 | t | float32
CALC.NPPC_QLoss_HeatSupply | 29086 | 总管线损失热量累加 | GJ/h | float32
CALC.NPPC_F_HeatSupplySum | 29087 | 各管线实时流量累加 | t/h | float32
CALC.NPPC_Q_JYIn | 29088 | 金叶进厂热量 | GJ/h | float32
CALC.NPPC_Q_JDSIn | 29089 | 金大少印染进厂热量 | GJ/h | float32
CALC.NPPC_Q_JTFZIn | 29090 | 晋泰纺织进厂热量 | GJ/h | float32
CALC.NPPC_Q_DYFZIn | 29091 | 东岳纺织进厂热量 | GJ/h | float32
CALC.NPPC_Q_JSFZIn | 29092 | 嘉顺纺织进厂热量 | GJ/h | float32
CALC.NPPC_Q_HSYZIn | 29093 | 和生染整进厂热量 | GJ/h | float32
CALC.NPPC_Q_HTFZIn | 29094 | 华泰纺织进厂热量 | GJ/h | float32
CALC.NPPC_Q_DHYZIn | 29095 | 敦煌染整进厂热量 | GJ/h | float32
CALC.NPPC_Q_JLSNIn | 29096 | 加力水泥进厂热量 | GJ/h | float32
CALC.NPPC_Q_HeatSupplySum | 29097 | 各管线实时热量累加 | GJ/h | float32
CALC.N1TS_Q_SupplyHeatLoad | 29098 | 供热量 | GJ/h | float32
CALC.N2TS_Q_SupplyHeatLoad | 29099 | 供热量 | GJ/h | float32
CALC.NPPC_Q_SupplyHeatLoad | 29100 | 供热量 | GJ/h | float32
CALC.NPPC_RQLoss_JY | 29101 | 金叶管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_JDS | 29102 | 金大少印染管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_JTFZ | 29103 | 晋泰纺织管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_DYFZ | 29104 | 东岳纺织管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_JSFZ | 29105 | 嘉顺纺织管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_HSYZ | 29106 | 和生染整管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_HTFZ | 29107 | 华泰纺织管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_DHYZ | 29108 | 敦煌染整管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_JLSN | 29109 | 加力水泥管线损失热量占比 | % | float32
CALC.NPPC_RQLoss_HeatSupply | 29110 | 总管线损失热量占比累加 | % | float32
CALC.NPPC_Q_GRZ | 29111 | 供热计量站供热量 | GJ/h | float32
CALC.N2YJ_JKD_GYBB | 29112 | 模型健康度_#2高压泵 |  | float32
CALC.N2YJ_JZZ_GYBB | 29113 | 基准值_#2高压泵 |  | float32
CALC.N2YJ_YCZ_20LAB92AP001I | 29114 | 预测值_#2高压给水泵电流 |  | float32
CALC.N2YJ_XSD_20LAB92AP001I | 29115 | 相似度值_#2高压给水泵电流 |  | float32
SLIDER.MIN_I | 29116 | #N/A |  | digital
SLIDER.MAX_I | 29117 | #N/A |  | digital
FW.XHPS_PH | 29118 | 冷却塔排水PH含量 |  | float32
FW.XHPS_COD | 29119 | 冷却塔排水COD含量 | mg/L | float32
FW.XHPS_ANDAN | 29120 | 冷却塔排水氨氮含量 | mg/L | float32
FW.XHPS_TSS | 29121 | 冷却塔排水TSS含量 | mg/L | float32
FW.XHPSLL | 29122 | 冷却塔排水流量计 | t/h | float32
FW.YJFSTNSPS_PH | 29123 | 一级反渗透浓水PH含量 |  | float32
FW.YJFSTNSPS_COD | 29124 | 一级反渗透浓水COD含量 | mg/L | float32
FW.YJFSTNSPS_ANDAN | 29125 | 一级反渗透浓水氨氮含量 | mg/L | float32
FW.YJFSTNSPS_TSS | 29126 | 一级反渗透浓水TSS含量 | mg/L | float32
FW.YJFSTNSPS_LL | 29127 | 一级反渗透浓水流量计 | t/h | float32
CALC.N2YJ_CCZ_20LAB92AP001I | 29128 | 残差值_#2高压给水泵电流 |  | float32
CALC.N2YJ_CCB_20LAB92AP001I | 29129 | 残差百分比_#2高压给水泵电流 |  | float32
CALC.N2YJ_JKD_GYBA | 29130 | 模型健康度_#1高压泵 |  | float32
CALC.N2YJ_JZZ_GYBA | 29131 | 基准值_#1高压泵 |  | float32
CALC.N2YJ_JKD_ZYBA | 29132 | 模型健康度_#1中压泵 |  | float32
CALC.N2YJ_JZZ_ZYBA | 29133 | 基准值_#1中压泵 |  | float32
CALC.N2YJ_JKD_ZYBB | 29134 | 模型健康度_#2中压泵 |  | float32
CALC.N2YJ_JZZ_ZYBB | 29135 | 基准值_#2中压泵 |  | float32
CALC.N2YJ_JKD_ZXHBA | 29136 | 模型健康度_#1再循环泵 |  | float32
CALC.N2YJ_JZZ_ZXHBA | 29137 | 基准值_#1再循环泵 |  | float32
CALC.N2YJ_JKD_ZXHBB | 29138 | 模型健康度_#2再循环泵 |  | float32
CALC.N2YJ_JZZ_ZXHBB | 29139 | 基准值_#2再循环泵 |  | float32
CALC.N2YJ_JKD_ZKBA | 29140 | 模型健康度_#1真空泵 |  | float32
CALC.N2YJ_JZZ_ZKBA | 29141 | 基准值_#1真空泵 |  | float32
CALC.N2YJ_JKD_ZKBB | 29142 | 模型健康度_#2真空泵 |  | float32
CALC.N2YJ_JZZ_ZKBB | 29143 | 基准值_#2真空泵 |  | float32
CALC.N2YJ_JKD_BSSBA | 29144 | 模型健康度_#1闭式水泵 |  | float32
CALC.N2YJ_JZZ_BSSBA | 29145 | 基准值_#1闭式水泵 |  | float32
CALC.N2YJ_JKD_BSSBB | 29146 | 模型健康度_#2闭式水泵 |  | float32
CALC.N2YJ_JZZ_BSSBB | 29147 | 基准值_#2闭式水泵 |  | float32
CALC.N2YJ_JKD_KSSBA | 29148 | 模型健康度_#1开式水泵 |  | float32
CALC.N2YJ_JZZ_KSSBA | 29149 | 基准值_#1开式水泵 |  | float32
CALC.N2YJ_JKD_KSSBB | 29150 | 模型健康度_#2开式水泵 |  | float32
CALC.N2YJ_JZZ_KSSBB | 29151 | 基准值_#2开式水泵 |  | float32
CALC.N2YJ_JKD_NJSBA | 29152 | 模型健康度_#1凝结水泵 |  | float32
CALC.N2YJ_JZZ_NJSBA | 29153 | 基准值_#1凝结水泵 |  | float32
CALC.N2YJ_JKD_NJSBB | 29154 | 模型健康度_#2凝结水泵 |  | float32
CALC.N2YJ_JZZ_NJSBB | 29155 | 基准值_#2凝结水泵 |  | float32
CALC.N2YJ_JKD_XHSBA | 29156 | 模型健康度_#1循环水泵 |  | float32
CALC.N2YJ_JZZ_XHSBA | 29157 | 基准值_#1循环水泵 |  | float32
CALC.N2YJ_JKD_XHSBB | 29158 | 模型健康度_#2循环水泵 |  | float32
CALC.N2YJ_JZZ_XHSBB | 29159 | 基准值_#2循环水泵 |  | float32
CALC.N2YJ_JKD_QJRHY | 29160 | 模型健康度_汽机润滑油 |  | float32
CALC.N2YJ_JZZ_QJRHY | 29161 | 基准值_汽机润滑油 |  | float32
CALC.N2YJ_JKD_QJFDJ | 29162 | 模型健康度_汽机发电机 |  | float32
CALC.N2YJ_JZZ_QJFDJ | 29163 | 基准值_汽机发电机 |  | float32
CALC.N2YJ_JKD_QJZX | 29164 | 模型健康度_汽机轴系 |  | float32
CALC.N2YJ_JZZ_QJZX | 29165 | 基准值_汽机轴系 |  | float32
CALC.N1YJ_JKD_GYBA | 29166 | 模型健康度_#1高压泵 |  | float32
CALC.N1YJ_JZZ_GYBA | 29167 | 基准值_#1高压泵 |  | float32
CALC.N1YJ_JKD_GYBB | 29168 | 模型健康度_#2高压泵 |  | float32
CALC.N1YJ_JZZ_GYBB | 29169 | 基准值_#2高压泵 |  | float32
CALC.N1YJ_JKD_ZYBA | 29170 | 模型健康度_#1中压泵 |  | float32
CALC.N1YJ_JZZ_ZYBA | 29171 | 基准值_#1中压泵 |  | float32
CALC.N1YJ_JKD_ZYBB | 29172 | 模型健康度_#2中压泵 |  | float32
CALC.N1YJ_JZZ_ZYBB | 29173 | 基准值_#2中压泵 |  | float32
CALC.N1YJ_JKD_ZXHBA | 29174 | 模型健康度_#1再循环泵 |  | float32
CALC.N1YJ_JZZ_ZXHBA | 29175 | 基准值_#1再循环泵 |  | float32
CALC.N1YJ_JKD_ZXHBB | 29176 | 模型健康度_#2再循环泵 |  | float32
CALC.N1YJ_JZZ_ZXHBB | 29177 | 基准值_#2再循环泵 |  | float32
CALC.N1YJ_JKD_ZKBA | 29178 | 模型健康度_#1真空泵 |  | float32
CALC.N1YJ_JZZ_ZKBA | 29179 | 基准值_#1真空泵 |  | float32
CALC.N1YJ_JKD_ZKBB | 29180 | 模型健康度_#2真空泵 |  | float32
CALC.N1YJ_JZZ_ZKBB | 29181 | 基准值_#2真空泵 |  | float32
CALC.N1YJ_JKD_BSSBA | 29182 | 模型健康度_#1闭式水泵 |  | float32
CALC.N1YJ_JZZ_BSSBA | 29183 | 基准值_#1闭式水泵 |  | float32
CALC.N1YJ_JKD_BSSBB | 29184 | 模型健康度_#2闭式水泵 |  | float32
CALC.N1YJ_JZZ_BSSBB | 29185 | 基准值_#2闭式水泵 |  | float32
CALC.N1YJ_JKD_KSSBA | 29186 | 模型健康度_#1开式水泵 |  | float32
CALC.N1YJ_JZZ_KSSBA | 29187 | 基准值_#1开式水泵 |  | float32
CALC.N1YJ_JKD_KSSBB | 29188 | 模型健康度_#2开式水泵 |  | float32
CALC.N1YJ_JZZ_KSSBB | 29189 | 基准值_#2开式水泵 |  | float32
CALC.N1YJ_JKD_NJSBA | 29190 | 模型健康度_#1凝结水泵 |  | float32
CALC.N1YJ_JZZ_NJSBA | 29191 | 基准值_#1凝结水泵 |  | float32
CALC.N1YJ_JKD_NJSBB | 29192 | 模型健康度_#2凝结水泵 |  | float32
CALC.N1YJ_JZZ_NJSBB | 29193 | 基准值_#2凝结水泵 |  | float32
CALC.N1YJ_JKD_XHSBA | 29194 | 模型健康度_#1循环水泵 |  | float32
CALC.N1YJ_JZZ_XHSBA | 29195 | 基准值_#1循环水泵 |  | float32
CALC.N1YJ_JKD_XHSBB | 29196 | 模型健康度_#2循环水泵 |  | float32
CALC.N1YJ_JZZ_XHSBB | 29197 | 基准值_#2循环水泵 |  | float32
CALC.N1YJ_JKD_QJRHY | 29198 | 模型健康度_汽机润滑油 |  | float32
CALC.N1YJ_JZZ_QJRHY | 29199 | 基准值_汽机润滑油 |  | float32
CALC.N1YJ_JKD_QJZX | 29200 | 模型健康度_汽机轴系 |  | float32
CALC.N1YJ_JZZ_QJZX | 29201 | 基准值_汽机轴系 |  | float32
CALC.N1YJ_JKD_QJFDJ | 29202 | 模型健康度_汽机发电机 |  | float32
CALC.N1YJ_JZZ_QJFDJ | 29203 | 基准值_汽机发电机 |  | float32
CALC.N1PC_CHR_P_GASTIn | 29204 | 燃机进口压力损失对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_P_GASTIn | 29205 | 燃机进口压力损失对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CPR_P_GASTIn | 29206 | 燃机进口压力损失对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_P_GASTIn | 29207 | 燃机进口压力损失对联合循环功率的影响 | kJ/kWh | float32
CALC.N1PC_CPH_P_GASTIn | 29208 | 燃机进口压力损失对热负荷修正系数 |  | float32
CALC.N1PC_PH_P_GASTIn | 29209 | 燃机进口压力损失对热负荷的影响 | MW | float32
CALC.N1PC_CHR_T_FuelIn | 29210 | 燃气温度对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_T_FuelIn | 29211 | 燃气温度对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CPR_T_FuelIn | 29212 | 燃气温度对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_T_FuelIn | 29213 | 燃气温度对联合循环功率的影响 | MW | float32
CALC.N1PC_CPH_T_FuelIn | 29214 | 燃气温度对热负荷修正系数 |  | float32
CALC.N1PC_PH_T_FuelIn | 29215 | 燃气温度对热负荷的影响 | MW | float32
CALC.N1PC_CHR_F_WaterRep | 29216 | 补给水流量对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_F_WaterRep | 29217 | 补给水流量对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CPR_F_WaterRep | 29218 | 补给水流量对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_F_WaterRep | 29219 | 补给水流量对联合循环功率的影响 | MW | float32
CALC.N1PC_CPH_F_WaterRep | 29220 | 补给水流量对热负荷修正系数 |  | float32
CALC.N1PC_PH_F_WaterRep | 29221 | 补给水流量对热负荷的影响 | MW | float32
CALC.N1PC_CHR_T_CicWi | 29222 | 循环水温度对联合循环热耗修正系数 |  | float32
CALC.N1PC_HR_T_CicWi | 29223 | 循环水温度对联合循环热耗的影响 | kJ/kWh | float32
CALC.N1PC_CPR_T_CicWi | 29224 | 循环水温度对联合循环功率修正系数 |  | float32
CALC.N1PC_PR_T_CicWi | 29225 | 循环水温度对联合循环功率的影响 | MW | float32
CALC.N1PC_CPH_T_CicWi | 29226 | 循环水温度对热负荷修正系数 |  | float32
CALC.N1PC_PH_T_CicWi | 29227 | 循环水温度对热负荷的影响 | MW | float32
CALC.N2PC_CHR_P_GASTIn | 29228 | 燃机进口压力损失对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_P_GASTIn | 29229 | 燃机进口压力损失对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CPR_P_GASTIn | 29230 | 燃机进口压力损失对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_P_GASTIn | 29231 | 燃机进口压力损失对联合循环功率的影响 | MW | float32
CALC.N2PC_CPH_P_GASTIn | 29232 | 燃机进口压力损失对热负荷修正系数 |  | float32
CALC.N2PC_PH_P_GASTIn | 29233 | 燃机进口压力损失对热负荷的影响 | MW | float32
CALC.N2PC_CHR_T_FuelIn | 29234 | 燃气温度对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_T_FuelIn | 29235 | 燃气温度对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CPR_T_FuelIn | 29236 | 燃气温度对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_T_FuelIn | 29237 | 燃气温度对联合循环功率的影响 | MW | float32
CALC.N2PC_CPH_T_FuelIn | 29238 | 燃气温度对热负荷修正系数 |  | float32
CALC.N2PC_PH_T_FuelIn | 29239 | 燃气温度对热负荷的影响 | MW | float32
CALC.N2PC_CHR_F_WaterRep | 29240 | 补给水流量对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_F_WaterRep | 29241 | 补给水流量对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CPR_F_WaterRep | 29242 | 补给水流量对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_F_WaterRep | 29243 | 补给水流量对联合循环功率的影响 | MW | float32
CALC.N2PC_CPH_F_WaterRep | 29244 | 补给水流量对热负荷修正系数 |  | float32
CALC.N2PC_PH_F_WaterRep | 29245 | 补给水流量对热负荷的影响 | MW | float32
CALC.N2PC_CHR_T_CicWi | 29246 | 循环水温度对联合循环热耗修正系数 |  | float32
CALC.N2PC_HR_T_CicWi | 29247 | 循环水温度对联合循环热耗的影响 | kJ/kWh | float32
CALC.N2PC_CPR_T_CicWi | 29248 | 循环水温度对联合循环功率修正系数 |  | float32
CALC.N2PC_PR_T_CicWi | 29249 | 循环水温度对联合循环功率的影响 | MW | float32
CALC.N2PC_CPH_T_CicWi | 29250 | 循环水温度对热负荷修正系数 |  | float32
CALC.N2PC_PH_T_CicWi | 29251 | 循环水温度对热负荷的影响 | MW | float32
CALC.N1BC_CEFB_HPSHOutP | 29252 | 余热锅炉效率随高压主汽压力修正系数 |  | float32
CALC.N1BC_CEFB_IPSHOutP | 29253 | 余热锅炉效率随热再热汽压力修正系数 |  | float32
CALC.N1BC_CEFB_Runtime | 29254 | 余热锅炉效率随老化修正系数 |  | float32
CALC.N1BC_CEFB_T_atm | 29255 | 余热锅炉效率随大气温度修正系数 |  | float32
CALC.N2BC_CEFB_HPSHOutP | 29256 | 余热锅炉效率随高压主汽压力修正系数 |  | float32
CALC.N2BC_CEFB_IPSHOutP | 29257 | 余热锅炉效率随热再热汽压力修正系数 |  | float32
CALC.N2BC_CEFB_Runtime | 29258 | 余热锅炉效率随老化修正系数 |  | float32
CALC.N2BC_CEFB_T_atm | 29259 | 余热锅炉效率随大气温度修正系数 |  | float32
CALC.N1BC_P_HPSHOut_T | 29260 | 余热锅炉高压过热蒸汽压力(目标) | Mpa | float32
CALC.N1BC_P_IPSHOut_T | 29261 | 余热锅炉中压再热蒸汽压力(目标) | Mpa | float32
CALC.N2BC_P_HPSHOut_T | 29262 | 余热锅炉高压过热蒸汽压力(目标) | Mpa | float32
CALC.N2BC_P_IPSHOut_T | 29263 | 余热锅炉中压再热蒸汽压力(目标) | Mpa | float32
CALC.N1BC_COGasDiffP_StkH2O | 29264 | 排气压降随含水率修正系数 |  | float32
CALC.N2BC_COGasDiffP_StkH2O | 29265 | 排气压降随含水率修正系数 |  | float32
CALC.N1TC_Q_STM | 29266 | 汽机蒸汽侧吸热量 | MJ/h | float32
CALC.N2TC_Q_STM | 29267 | 汽机蒸汽侧吸热量 | MJ/h | float32
CALC.N1PS_W_G_D | 29268 | 联合循环发电机功率优化值 | MW | float32
CALC.N2PS_W_G_D | 29269 | 联合循环发电机功率优化值 | MW | float32
CALC.N1TS_F_SupplyHeat_D | 29270 | 蒸汽轮机供热抽汽流量优化值 | t/h | float32
CALC.N2TS_F_SupplyHeat_D | 29271 | 蒸汽轮机供热抽汽流量优化值 | t/h | float32
CALC.NPPC_F_FuelIn_D | 29272 | 燃料流量优化值 | t/h | float32
CALC.NPPC_F_FuelIn_ADD | 29273 | 燃料流量节约值 | t/h | float32
RW.MBX.F008 | 29274 | 瞬时流量 | t/h | float32
RW.MBX.P008 | 29275 | 压力 | mPa | float32
RW.MBX.T008 | 29276 | 温度 | ℃ | float32
RW.MBX.SUM008 | 29277 | 累计流量 | t | float32
CALC.NPPC_F_FuelIn_ADD_New | 29278 | 燃料流量节约值 | t/h | float32
CALC.NPPC_F_LS | 29279 | 优化分配状态 |  | float32
TCS1.10CJA01DE002_XQ01 | 29280 | EXTERNAL LOAD REFERENCE CH1 | MW | float32
TCS1.10CJA01DE003_XQ01 | 29281 | EXTERNAL LOAD REFERENCE CH2 | MW | float32
TCS1.10EKG01C2H6_XQ01 | 29282 | ETHANE (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01C3H8_XQ01 | 29283 | PROPANE (GAS CROM. MODBUS) | mol% | float32
TCS1.10EKG01C6H14_XQ01 | 29284 | SUM OF C6+ (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01CF_XQ01 | 29285 | DATA FROM GAS CROMATOGRAPH | % | float32
TCS1.10EKG01CH4_XQ01 | 29286 | METHANE (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01CO2_XQ01 | 29287 | CARBON DIOXIDE (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01CP_XQ01 | 29288 | DATA FROM GAS CROMATOGRAPH | kPa | float32
TCS1.10EKG01GD1_XQ01 | 29289 | GAS DENSITY (GAS CHROM. MODBUS) | kg/m? | float32
TCS1.10EKG01HV1_XQ01 | 29290 | HEAT VALUE (GAS CHROM. MODBUS) | Kg/m? | float32
TCS1.10EKG01IC4H10_XQ01 | 29291 | i-BUTANE (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01IC5H12_XQ01 | 29292 | i-PENTANE (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01ICV_XQ01 | 29293 | ICV (GAS CHROM. MODBUS) | MJ/m? | float32
TCS1.10EKG01N2_XQ01 | 29294 | NITROGEN (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01NC4H10_XQ01 | 29295 | n-BUTANE (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01NC5H12_XQ01 | 29296 | n-PENTANE (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01NEC5H12_XQ01 | 29297 | neo-PENTANE (GAS CHROM. MODBUS) | mol% | float32
TCS1.10EKG01OT_XQ01 | 29298 | DATA FROM GAS CROMATOGRAPH | °C | float32
TCS1.10EKG01RDHE1_XQ01 | 29299 | DATA FROM GAS CROMATOGRAPH | p.u. | float32
TCS1.10EKG01TR_XQ01 | 29300 | DATA FROM GAS CROMATOGRAPH | mol% | float32
TCS1.10EKG01WI1_XQ01 | 29301 | WOBBE INDEX (GAS CROM. MODBUS) | MJ/m? | float32
TCS1.10EKG10CQ902_PCIRED | 29302 | GAS COMPOSITION | Kg/s | float32
TCS1.10EKG10CQ902_WOBBERED | 29303 | GAS COMPOSITION | Kg/s | float32
TCS1.10EKG10CQ902_XQ01 | 29304 | GAS COMPOSITION | °C | float32
TCS1.10EKG10CQ902_XQ02 | 29305 | GAS DENSITY | Kg/m? | float32
TCS1.10EKG10CQ902_XQ10 | 29306 | CALC. WOBBE INDEX |  | float32
TCS1.10EKG12CQ102_XQ01 | 29307 | SUM OF C6+ (PV1 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ02 | 29308 | PROPANE (PV2 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ03 | 29309 | i-BUTANE (PV3 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ04 | 29310 | n-BUTANE (PV4 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ05 | 29311 | neo-PENTANE (PV5 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ06 | 29312 | i-PENTANE (PV6 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ07 | 29313 | n-PENTANE (PV7 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ08 | 29314 | NITROGEN (PV8 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ09 | 29315 | METHANE (PV9 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ10 | 29316 | CARBON DIOXIDE (PV10 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ11 | 29317 | ETHANE (PV11 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ12 | 29318 | HEAT VALUE (PV12 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ13 | 29319 | GAS DENSITY (PV13 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ14 | 29320 | WOBBE INDEX (PV14 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ15 | 29321 | COMPRESSIBILITY FACTOR (PV15 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ16 | 29322 | TOTAL OF RAW CONCENTRATIONS (PV16 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ17 | 29323 | OVEN TEMP (PV17 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ18 | 29324 | CARRIER GAS PRESS (PV18 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ19 | 29325 | ICV (PV19 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG12CQ102_XQ20 | 29326 | RELATIVE DENSITY (PV20 - GAS CHROMATOGRAPH) |  | float32
TCS1.10EKG60FF001_XQ01 | 29327 |  |  | float32
TCS1.10EKG70CP101_XQ01 | 29328 | PRESSURE SIGNAL FLOW METER | bar | float32
TCS1.10EKG70CT101_XQ01 | 29329 | TEMP. GAS BEFORE ESV | °C | float32
TCS1.10MBA10CG101_XQ01 | 29330 | ROTOR AXIAL DISPLACEMENT CH A | mm | float32
TCS1.10MBA10CG102_XQ01 | 29331 | ROTOR AXIAL DISPLACEMENT CH B | mm | float32
TCS1.10MBA10CS101_XQ01 | 29332 | TURBINE SPEED 1 | s-1 | float32
TCS1.10MBA10CS102_XQ01 | 29333 | TURBINE SPEED 2 | s-1 | float32
TCS1.10MBA10CS103_XQ01 | 29334 | TURBINE SPEED 3 | s-1 | float32
TCS1.10MBA10FG100_ZQ01 | 29335 | ROTOR AXIAL DISPLACEMENT | mm | float32
TCS1.10MBA11CP101_XQ01 | 29336 | ABS COMPRESSOR AIR INLET PRESS 1 | mbar | float32
TCS1.10MBA11CT101A_XQ01 | 29337 | COMPRESSOR AIR INLET TEMP A 1 | °C | float32
TCS1.10MBA11CT101B_XQ11 | 29338 | COMPRESSOR AIR INLET TEMP B 1 | °C | float32
TCS1.10MBA11CT102A_XQ01 | 29339 | COMPRESSOR AIR INLET TEMP A 2 | °C | float32
TCS1.10MBA11CT102B_XQ11 | 29340 | COMPRESSOR AIR INLET TEMP B 2 | °C | float32
TCS1.10MBA11CT103A_XQ01 | 29341 | COMPRESSOR AIR INLET TEMP A 3 | °C | float32
TCS1.10MBA11CT103B_XQ11 | 29342 | COMPRESSOR AIR INLET TEMP B 3 | °C | float32
TCS1.10MBA11CT104A_XQ01 | 29343 | COMPRESSOR AIR INLET TEMP A 4 | °C | float32
TCS1.10MBA11CT104B_XQ11 | 29344 | COMPRESSOR AIR INLET TEMP B 4 | °C | float32
TCS1.10MBA11CT901_ZQ01 | 29345 | COMPRESSOR AIR INLET TEMP |  | float32
TCS1.10MBA11CT901_ZQ11 | 29346 | COMPRESSOR AIR INLET TEMP |  | float32
TCS1.10MBA12CP101_XQ01 | 29347 | COMPRESSOR AIR DISCHARGE PRESS 1 | bar | float32
TCS1.10MBA12CP102_XQ01 | 29348 | COMPRESSOR AIR DISCHARGE PRESS 2 | bar | float32
TCS1.10MBA12CT101A_XQ01 | 29349 | COMPRESSOR AIR DISCHARGE TEMP A 1 | °C | float32
TCS1.10MBA12CT101B_XQ11 | 29350 | COMPRESSOR AIR DISCHARGE TEMP B 1 | °C | float32
TCS1.10MBA12CT102A_XQ01 | 29351 | COMPRESSOR AIR DISCHARGE TEMP A 2 | °C | float32
TCS1.10MBA12CT102B_XQ11 | 29352 | COMPRESSOR AIR DISCHARGE TEMP B 2 | °C | float32
TCS1.10MBA12CT103A_XQ01 | 29353 | COMPRESSOR AIR DISCHARGE TEMP A 3 | °C | float32
TCS1.10MBA12CT103B_XQ11 | 29354 | COMPRESSOR AIR DISCHARGE TEMP B 3 | °C | float32
TCS1.10MBA12CT901_ZQ01 | 29355 | COMPRESSOR AIR DISCHARGE TEMP | °C | float32
TCS1.10MBA12FP100_ZQ03 | 29356 | COMPRESSOR AIR DISCHARGE PRESS | bar | float32
TCS1.10MBA25CT101_XQ01 | 29357 | DRAIN LINES HEADER TEMP | C | float32
TCS1.10MBA26CT101A_XQ01 | 29358 | TURBINE EXHAUST GAS TEMP A 1 | °C | float32
TCS1.10MBA26CT101B_XQ11 | 29359 | TURBINE EXHAUST GAS TEMP B 1 | °C | float32
TCS1.10MBA26CT102A_XQ01 | 29360 | TURBINE EXHAUST GAS TEMP A 2 | °C | float32
TCS1.10MBA26CT102B_XQ11 | 29361 | TURBINE EXHAUST GAS TEMP B 2 | °C | float32
TCS1.10MBA26CT103A_XQ01 | 29362 | TURBINE EXHAUST GAS TEMP A 3 | °C | float32
TCS1.10MBA26CT103B_XQ11 | 29363 | TURBINE EXHAUST GAS TEMP B 3 | °C | float32
TCS1.10MBA26CT104A_XQ01 | 29364 | TURBINE EXHAUST GAS TEMP A 4 | °C | float32
TCS1.10MBA26CT104B_XQ11 | 29365 | TURBINE EXHAUST GAS TEMP B 4 | °C | float32
TCS1.10MBA26CT105A_XQ01 | 29366 | TURBINE EXHAUST GAS TEMP A 5 | °C | float32
TCS1.10MBA26CT105B_XQ11 | 29367 | TURBINE EXHAUST GAS TEMP B 5 | °C | float32
TCS1.10MBA26CT106A_XQ01 | 29368 | TURBINE EXHAUST GAS TEMP A 6 | °C | float32
TCS1.10MBA26CT106B_XQ11 | 29369 | TURBINE EXHAUST GAS TEMP B 6 | °C | float32
TCS1.10MBA26CT107A_XQ01 | 29370 | TURBINE EXHAUST GAS TEMP A 7 | °C | float32
TCS1.10MBA26CT107B_XQ11 | 29371 | TURBINE EXHAUST GAS TEMP B 7 | °C | float32
TCS1.10MBA26CT108A_XQ01 | 29372 | TURBINE EXHAUST GAS TEMP A 8 | °C | float32
TCS1.10MBA26CT108B_XQ11 | 29373 | TURBINE EXHAUST GAS TEMP B 8 | °C | float32
TCS1.10MBA26CT109A_XQ01 | 29374 | TURBINE EXHAUST GAS TEMP A 9 | °C | float32
TCS1.10MBA26CT109B_XQ11 | 29375 | TURBINE EXHAUST GAS TEMP B 9 | °C | float32
TCS1.10MBA26CT110A_XQ01 | 29376 | TURBINE EXHAUST GAS TEMP A 10 | °C | float32
TCS1.10MBA26CT110B_XQ11 | 29377 | TURBINE EXHAUST GAS TEMP B 10 | °C | float32
TCS1.10MBA26CT111A_XQ01 | 29378 | TURBINE EXHAUST GAS TEMP A 11 | °C | float32
TCS1.10MBA26CT111B_XQ11 | 29379 | TURBINE EXHAUST GAS TEMP B 11 | °C | float32
TCS1.10MBA26CT112A_XQ01 | 29380 | TURBINE EXHAUST GAS TEMP A 12 | °C | float32
TCS1.10MBA26CT112B_XQ11 | 29381 | TURBINE EXHAUST GAS TEMP B 12 | °C | float32
TCS1.10MBA26CT113A_XQ01 | 29382 | TURBINE EXHAUST GAS TEMP A 13 | °C | float32
TCS1.10MBA26CT113B_XQ11 | 29383 | TURBINE EXHAUST GAS TEMP B 13 | °C | float32
TCS1.10MBA26CT114A_XQ01 | 29384 | TURBINE EXHAUST GAS TEMP A 14 | °C | float32
TCS1.10MBA26CT114B_XQ11 | 29385 | TURBINE EXHAUST GAS TEMP B 14 | °C | float32
TCS1.10MBA26CT115A_XQ01 | 29386 | TURBINE EXHAUST GAS TEMP A 15 | °C | float32
TCS1.10MBA26CT115B_XQ11 | 29387 | TURBINE EXHAUST GAS TEMP B 15 | °C | float32
TCS1.10MBA26CT116A_XQ01 | 29388 | TURBINE EXHAUST GAS TEMP A 16 | °C | float32
TCS1.10MBA26CT116B_XQ11 | 29389 | TURBINE EXHAUST GAS TEMP B 16 | °C | float32
TCS1.10MBA26CT117A_XQ01 | 29390 | TURBINE EXHAUST GAS TEMP A 17 | °C | float32
TCS1.10MBA26CT117B_XQ11 | 29391 | TURBINE EXHAUST GAS TEMP B 17 | °C | float32
TCS1.10MBA26CT118A_XQ01 | 29392 | TURBINE EXHAUST GAS TEMP A 18 | °C | float32
TCS1.10MBA26CT118B_XQ11 | 29393 | TURBINE EXHAUST GAS TEMP B 18 | °C | float32
TCS1.10MBA26CT119A_XQ01 | 29394 | TURBINE EXHAUST GAS TEMP A 19 | °C | float32
TCS1.10MBA26CT119B_XQ11 | 29395 | TURBINE EXHAUST GAS TEMP B 19 | °C | float32
TCS1.10MBA26CT120A_XQ01 | 29396 | TURBINE EXHAUST GAS TEMP A 20 | °C | float32
TCS1.10MBA26CT120B_XQ11 | 29397 | TURBINE EXHAUST GAS TEMP B 20 | °C | float32
TCS1.10MBA26CT121A_XQ01 | 29398 | TURBINE EXHAUST GAS TEMP A 21 | °C | float32
TCS1.10MBA26CT121B_XQ11 | 29399 | TURBINE EXHAUST GAS TEMP B 21 | °C | float32
TCS1.10MBA26CT122A_XQ01 | 29400 | TURBINE EXHAUST GAS TEMP A 22 | °C | float32
TCS1.10MBA26CT122B_XQ11 | 29401 | TURBINE EXHAUST GAS TEMP B 22 | °C | float32
TCS1.10MBA26CT123A_XQ01 | 29402 | TURBINE EXHAUST GAS TEMP A 23 | °C | float32
TCS1.10MBA26CT123B_XQ11 | 29403 | TURBINE EXHAUST GAS TEMP B 23 | °C | float32
TCS1.10MBA26CT124A_XQ01 | 29404 | TURBINE EXHAUST GAS TEMP A 24 | °C | float32
TCS1.10MBA26CT124B_XQ11 | 29405 | TURBINE EXHAUST GAS TEMP B 24 | °C | float32
TCS1.10MBA26CT900_ZQ01 | 29406 | TURBINE EXHAUST GAS TEMP | ?C | float32
TCS1.10MBA26CT901_OUT | 29407 | MAX TURBINE EXHAUST GAS TEMP | °C | float32
TCS1.10MBA26CT901_XQ04 | 29408 | MAX TURBINE EXHAUST GAS TEMP | °C | float32
TCS1.10MBA26CT901_ZQ01 | 29409 | MAX TURBINE EXHAUST GAS TEMP | °C | float32
TCS1.10MBA26CT902_OUT | 29410 | SPREAD AVG MIN | °C | float32
TCS1.10MBA26CT902_XQ04 | 29411 | MIN TURBINE EXHAUST GAS TEMP | °C | float32
TCS1.10MBA26CT902_ZQ01 | 29412 | MIN TURBINE EXHAUST GAS TEMP | °C | float32
TCS1.10MBA26FT901_TRIP VAL_ZQ03 | 29413 | CALC TURB OT | °C | float32
TCS1.10MBA26FT901_WARN VAL_ZQ02 | 29414 | CALC TURB OT | °C | float32
TCS1.10MBA26FT901_ATK | 29415 | CALC TURB OT |  | float32
TCS1.10MBA50EU001_ZQ01 | 29416 | MAIN FLUSH CTRL | min | float32
TCS1.10MBA51AP001_DCO | 29417 | RDS PUMP 1 |  | float32
TCS1.10MBA51AP002_DCO | 29418 | RDS PUMP 2 |  | float32
TCS1.10MBA51CP101_XQ01 | 29419 | RDS FEED LINE PRESSURE | bar | float32
TCS1.10MBA51CP102_XQ01 | 29420 | RDS FEED LINE PRESSURE | bar | float32
TCS1.10MBA51CP103_XQ01 | 29421 | RDS FEED LINE PRESSURE | bar | float32
TCS1.10MBA51FP100_ZQ01 | 29422 | RDS SYSTEM PRES | Bar | float32
TCS1.10MBA53CP101_XQ01 | 29423 | RDS MAIN CH RETURN PRESSURE | bar | float32
TCS1.10MBA53CP102_XQ01 | 29424 | RDS MAIN CH RETURN PRESSURE | bar | float32
TCS1.10MBA53CP103_XQ01 | 29425 | RDS SECOND CH RETURN PRESSURE | bar | float32
TCS1.10MBA53CP104_XQ01 | 29426 | RDS SECOND CH RETURN PRESSURE | bar | float32
TCS1.10MBA53CP105_XQ01 | 29427 | RDS MAIN CH RETURN PRESSURE | bar | float32
TCS1.10MBA53CP106_XQ01 | 29428 | RDS SECOND CH RETURN PRESSURE | bar | float32
TCS1.10MBA53FP101_ZQ01 | 29429 | MAIN RETURN LINE PRESS | Bar | float32
TCS1.10MBA53FP102_ZQ01 | 29430 | SEC RETURN LINE PRESS | Bar | float32
TCS1.10MBD11CT101A_XQ01 | 29431 | TURBINE BEARING TEMP | °C | float32
TCS1.10MBD11CT101B_XQ11 | 29432 | TURBINE BEARING TEMP | °C | float32
TCS1.10MBD11CT101C_XQ21 | 29433 | TURBINE BEARING TEMP | °C | float32
TCS1.10MBD11CT102A_XQ01 | 29434 | TURBINE BEARING TEMP | °C | float32
TCS1.10MBD11CT102B_XQ11 | 29435 | TURBINE BEARING TEMP | °C | float32
TCS1.10MBD11CT102C_XQ21 | 29436 | TURBINE BEARING TEMP | °C | float32
TCS1.10MBD11CY101_XQ01 | 29437 | TURBINE SIDE BEARING ABS VIBR CH. A | mm/s | float32
TCS1.10MBD11CY102_XQ01 | 29438 | TURBINE SIDE BEARING ABS VIBR CH. B | mm/s | float32
TCS1.10MBD11CY940_XQ01 | 29439 | TURBINE SIDE BEARING REL VIBR Smax CH. | ?m res | float32
TCS1.10MBD12CT101A_XQ01 | 29440 | COMPRESSOR BEARING TEMP | °C | float32
TCS1.10MBD12CT101B_XQ11 | 29441 | COMPRESSOR BEARING TEMP | °C | float32
TCS1.10MBD12CT101C_XQ21 | 29442 | COMPRESSOR BEARING TEMP | °C | float32
TCS1.10MBD12CT102A_XQ01 | 29443 | COMP. THRUST BEARING TEMP GEN UPPER PART | °C | float32
TCS1.10MBD12CT102B_XQ11 | 29444 | COMP. THRUST BEARING TEMP GEN UPPER PART | °C | float32
TCS1.10MBD12CT103A_XQ01 | 29445 | COMP. THRUST BEARING TEMP GEN LOWER PART | °C | float32
TCS1.10MBD12CT103B_XQ11 | 29446 | COMP. THRUST BEARING TEMP GEN LOWER PART | °C | float32
TCS1.10MBD12CT104A_XQ01 | 29447 | COMP. THRUST BEARING TEMP COMP UPPER PART | °C | float32
TCS1.10MBD12CT104B_XQ11 | 29448 | COMP. THRUST BEARING TEMP COMP UPPER PART | °C | float32
TCS1.10MBD12CT105A_XQ01 | 29449 | COMP. THRUST BEARING TEMP COMP LOWER PART | °C | float32
TCS1.10MBD12CT105B_XQ11 | 29450 | COMP. THRUST BEARING TEMP COMP LOWER PART | °C | float32
TCS1.10MBD12CT112A_XQ01 | 29451 | COMP. THRUST BEARING TEMP GEN UPPER PART | °C | float32
TCS1.10MBD12CT112B_XQ11 | 29452 | COMP. THRUST BEARING TEMP GEN UPPER PART | °C | float32
TCS1.10MBD12CT113A_XQ01 | 29453 | COMP. THRUST BEARING TEMP GEN LOWER PART | °C | float32
TCS1.10MBD12CT113B_XQ11 | 29454 | COMP. THRUST BEARING TEMP GEN LOWER PART | °C | float32
TCS1.10MBD12CT114A_XQ01 | 29455 | COMP. THRUST BEARING TEMP COMP UPPER PART | °C | float32
TCS1.10MBD12CT114B_XQ11 | 29456 | COMP. THRUST BEARING TEMP COMP UPPER PART | °C | float32
TCS1.10MBD12CT115A_XQ01 | 29457 | COMP. THRUST BEARING TEMP COMP LOWER PART | °C | float32
TCS1.10MBD12CT115B_XQ11 | 29458 | COMP. THRUST BEARING TEMP COMP LOWER PART | °C | float32
TCS1.10MBD12CY101_XQ01 | 29459 | COMP SIDE BEARING ABS VIBR CH. A | mm/s | float32
TCS1.10MBD12CY102_XQ01 | 29460 | COMP SIDE BEARING ABS VIBR CH. B | mm/s | float32
TCS1.10MBD12CY115_XQ01 | 29461 | Compressor Secondary Thrust Bearing Load Cell Upper Part | kN | float32
TCS1.10MBD12CY116_XQ01 | 29462 | Compressor Secondary Thrust Bearing Load Cell Upper Part | kN | float32
TCS1.10MBD12CY117_XQ01 | 29463 | Compressor Secondary Thrust Bearing Load Cell Upper Part | kN | float32
TCS1.10MBD12CY118_XQ01 | 29464 | Compressor Secondary Thrust Bearing Load Cell Upper Part | kN | float32
TCS1.10MBD12CY125_XQ01 | 29465 | Compressor Main Thrust Bearing Load Cell Upper Part | kN | float32
TCS1.10MBD12CY126_XQ01 | 29466 | Compressor Main Thrust Bearing Load Cell Upper Part | kN | float32
TCS1.10MBD12CY127_XQ01 | 29467 | Compressor Main Thrust Bearing Load Cell Upper Part | kN | float32
TCS1.10MBD12CY128_XQ01 | 29468 | Compressor Main Thrust Bearing Load Cell Upper Part | kN | float32
TCS1.10MBD12CY940_XQ01 | 29469 | COMP SIDE BEARING REL VIBR Smax CH. OK | ?m res | float32
TCS1.10MBH22AA101_XQ01 | 29470 | COOL AIR DAMPER 1 STAGE 2 | % | float32
TCS1.10MBH22AA101_YQ01 | 29471 | COOL AIR DAMPER 1 STAGE 2 | % | float32
TCS1.10MBH22AA102_PID | 29472 | COOL AIR DAMPER 2 STAGE 2 | % | float32
TCS1.10MBH22AA102_XQ01 | 29473 | COOL AIR DAMPER 2 STAGE 2 | % | float32
TCS1.10MBH22AA102_YQ01 | 29474 | COOL AIR DAMPER 2 STAGE 2 | % | float32
TCS1.10MBH22CP102_XQ01 | 29475 | COOL AIR DAMPER STAGE 2 PRESSURE | bar | float32
TCS1.10MBH22CP103_XQ01 | 29476 | COOL AIR DAMPER STAGE 2 PRESSURE | bar | float32
TCS1.10MBH22CP104_XQ01 | 29477 | COOL AIR DAMPER STAGE 2 PRESSURE | bar | float32
TCS1.10MBH22DP100_912339_OUT | 29478 | COOLING AIR PRESS GV2 PV |  | float32
TCS1.10MBH22DP100_XD | 29479 | COOLING AIR PRESS GV2 | % | float32
TCS1.10MBH22DP100_ZQ01 | 29480 | COOLING AIR PRESS GV2 |  | float32
TCS1.10MBH22DP100_ZQ02 | 29481 | COOLING AIR PRESS GV2 | % | float32
TCS1.10MBH23AA101_PID | 29482 | COOL AIR DAMPER 1 STAGE 3 | % | float32
TCS1.10MBH23AA101_XQ01 | 29483 | COOL AIR DAMPER 1 STAGE 3 | % | float32
TCS1.10MBH23AA101_YQ01 | 29484 | COOL AIR DAMPER 1 STAGE 3 | % | float32
TCS1.10MBH23AA102_PID | 29485 | COOL AIR DAMPER 2 STAGE 3 | % | float32
TCS1.10MBH23AA102_XQ01 | 29486 | COOL AIR DAMPER 2 STAGE 3 | % | float32
TCS1.10MBH23AA102_YQ01 | 29487 | COOL AIR DAMPER 2 STAGE 3 | % | float32
TCS1.10MBH23CP102_XQ01 | 29488 | COOL AIR DAMPER STAGE 3 PRESSURE | bar | float32
TCS1.10MBH23CP103_XQ01 | 29489 | COOL AIR DAMPER STAGE 3 PRESSURE | bar | float32
TCS1.10MBH23CP104_XQ01 | 29490 | COOL AIR DAMPER STAGE 3 PRESSURE | bar | float32
TCS1.10MBH23DP100_PVGV3 | 29491 | COOLING AIR PRESSURE GV3 |  | float32
TCS1.10MBH23DP100_XD | 29492 | COOLING AIR PRESSURE GV3 | % | float32
TCS1.10MBH23DP100_ZQ02 | 29493 | COOLING AIR PRESSURE GV3 | % | float32
TCS1.10MBH23DP100_ZQ04 | 29494 | COOLING AIR PRESSURE GV3 | % | float32
TCS1.10MBH23DP100_ZQ05 | 29495 | ~COOLING AIR PRESS GV2 |  | float32
TCS1.10MBK22CS101_XQ01 | 29496 | TURNING GEAR SPEED 1 | Hz | float32
TCS1.10MBK22CS102_XQ01 | 29497 | TURNING GEAR SPEED 2 | Hz | float32
TCS1.10MBL10CM101_XQ01 | 29498 | INTAKE AIR FILTRATION ENVIRONMENT RH % (HUMIDITY) | % | float32
TCS1.10MBL10CM102_XQ01 | 29499 | INTAKE AIR FILTRATION ENVIRONMENT RH % (HUMIDITY) | % | float32
TCS1.10MBL10CM901_XQ01 | 29500 | ~INTAKE AIR FILTRATION ENVIRONMENT RH % (HUMIDITY) | % | float32
TCS1.10MBL10CP101_XQ01 | 29501 | ENVIRONMENT PRESSURE | mbar | float32
TCS1.10MBL10CT101_XQ01 | 29502 | INTAKE AIR FILTRATION ENVIRONMENT TEMP 1 | C | float32
TCS1.10MBL10CT102_XQ01 | 29503 | INTAKE AIR FILTRATION ENVIRONMENT TEMP 2 | °C | float32
TCS1.10MBL10CT901_XQ01 | 29504 | ~INTAKE AIR FILTRATION ENVIRONMENT TEMP |  | float32
TCS1.10MBL13CP101_XQ01 | 29505 | DP PRE FILTER | kPa | float32
TCS1.10MBL14CP101_XQ01 | 29506 | INTAKE TOTAL FILTER DP | kPa | float32
TCS1.10MBL14CP102_XQ01 | 29507 | DP PULSE FILTER | kPa | float32
TCS1.10MBL21CQ101_XQ01 | 29508 | ICE DETECTOR | % | float32
TCS1.10MBM00EU006_XQ01 | 29509 | ~HUM/ACC MON T REC 1 | s | float32
TCS1.10MBM00EU006_XQ02 | 29510 | ~HUM/ACC MON T REC 2 | s | float32
TCS1.10MBM00EU006_XQ03 | 29511 | ~ACCUM OPERATING HRS | h | float32
TCS1.10MBM10CP101_XQ01 | 29512 | DIFF PRESS COMB CHAMBER | mbar | float32
TCS1.10MBM10CY101_XQ01 | 29513 | COMB CHAMBER ACCELERATION CH. A | g | float32
TCS1.10MBM10CY102_XQ01 | 29514 | COMB CHAMBER ACCELERATION CH. B | g | float32
TCS1.10MBM10CY103_XQ01 | 29515 | COMB CHAMBER ACCELERATION CH. C | g | float32
TCS1.10MBM11CP101_XQ01 | 29516 | COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS1.10MBM11CP102_XQ01 | 29517 | COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS1.10MBM12CP107_XQ01 | 29518 | ~COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS1.10MBM12CP110_XQ01 | 29519 | ~COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS1.10MBM12CP115_XQ01 | 29520 | ~COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS1.10MBM13CR101_XQ01 | 29521 | FG/FO FLAME INTENSITY FLAME 1 | nm | float32
TCS1.10MBM13CR102_XQ01 | 29522 | FG/FO FLAME INTENSITY FLAME 2 | nm | float32
TCS1.10MBP03DU003_1FEGVB_GV | 29523 | ~PREMIX FUEL MASS FLOW GAS REQ | Kg/s | float32
TCS1.10MBP03DU003_COMB_LOAD_VAR_NG_JVAREGG | 29524 | ~COMB_LOAD_VAR_NG | % | float32
TCS1.10MBP03DU003_FEGDB | 29525 | ~DIFF FUEL GAS REQ | Kg/sec | float32
TCS1.10MBP03DU003_FMIGD | 29526 | ~DIFF MIN FLOW GAS REQ | Kg/sec | float32
TCS1.10MBP03DU003_FMIGV | 29527 | ~PREMIX MIN FLOW GAS REQ | Kg/s | float32
TCS1.10MBP03DU003_FP | 29528 | ~COMB_LOAD_VAR_NG | Kg/s | float32
TCS1.10MBP03DU003_GD | 29529 | ~DIFF MASS FLOW FUEL GAS REQ | Kg/sec | float32
TCS1.10MBP03DU003_GV | 29530 | ~PREMIX FUEL MASS FLOW GAS REQ | Kg/s | float32
TCS1.10MBP03DU003_OUT | 29531 | ~FUEL CONTROLLER NG STEP |  | float32
TCS1.10MBP03DU003_UAGV | 29532 | ~FG PREMIX PROPORTION | % | float32
TCS1.10MBP13CP101_XQ01 | 29533 | FG PRESS UPST STOP VLV - PREMIX LINE 1 | bar | float32
TCS1.10MBP13CP102_XQ01 | 29534 | FG PRESS UPST STOP VLV - PREMIX LINE 2 | bar | float32
TCS1.10MBP13CT101A_XQ01 | 29535 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS1.10MBP13CT101B_XQ01 | 29536 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS1.10MBP13CT102A_XQ01 | 29537 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS1.10MBP13CT102B_XQ01 | 29538 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS1.10MBP13CT103A_XQ01 | 29539 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS1.10MBP13CT103B_XQ01 | 29540 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS1.10MBP13EU010_193350_OUT | 29541 | \ |  | float32
TCS1.10MBP13FQ101_XQ01 | 29542 | DENSITY/HUMIDITY GAS | kg/m? | float32
TCS1.10MBP13FQ101_XQ02 | 29543 | DENSITY/HUMIDITY GAS | MJ/m? | float32
TCS1.10MBP13FT901_ZQ01 | 29544 | \ |  | float32
TCS1.10MBP14CP101_XQ01 | 29545 | FG PRESS DOWNST STOP VLV - PREMIX LINE | bar | float32
TCS1.10MBP22DG151_XQ01 | 29546 | NG PREMIX CTRL POSN |  | float32
TCS1.10MBP23DG151_XQ01 | 29547 | PILOT 1 CTRL POSN |  | float32
TCS1.10MBP23DU071_PGSTRT_PGSTRT | 29548 | MASS-F SETP CV PILOT GAS | Kg/s | float32
TCS1.10MBP23DU071_XQ01 | 29549 | MASS-F SETP CV PILOT GAS | Kg/s | float32
TCS1.10MBP24DG151_XQ01HW | 29550 | NG PILOT 2 CTRL POSN |  | float32
TCS1.10MBP24DU070_FP | 29551 | ~COMB_LOAD_VAR_NG | Kg/s | float32
TCS1.10MBP24DU070_PGSTRT | 29552 | ~LIFTING CALC CV PILOT 2 GAS | Kg/s | float32
TCS1.10MBP24DU070_XQ01 | 29553 | ~LIFTING CALC CV PILOT 2 GAS | Kg/s | float32
TCS1.10MBP32CP101_XQ01 | 29554 | FUEL GAS PRESSURE PREMIX HEADER | bar | float32
TCS1.10MBP32CT101_XQ01 | 29555 | TEMP GAS PREMIX LINE | °C | float32
TCS1.10MBP32CT102_XQ01 | 29556 | TEMP GAS PREMIX LINE | ?C | float32
TCS1.10MBP32CT901_XQ01 | 29557 | \ |  | float32
TCS1.10MBP34CF101_XQ01 | 29558 | PILOT 2 FLOW GAS | kg/s | float32
TCS1.10MBP34CF101_ZQ01 | 29559 | PILOT 2 FLOW GAS | kg/s | float32
TCS1.10MBP34CP101_XQ01 | 29560 | FUEL GAS PRESSURE PILOT 2 HEADER | bar | float32
TCS1.10MBP34CT101_XQ01 | 29561 | TEMP GAS PILOT 2 LINE | % | float32
TCS1.10MBP34CT102_XQ01 | 29562 | TEMP GAS PILOT 2 LINE | C | float32
TCS1.10MBP34CT901_XQ01 | 29563 | \ |  | float32
TCS1.10MBR20CP101_XQ01 | 29564 | DP EXHAUST GAS 1 | mbar | float32
TCS1.10MBR20CP102_XQ01 | 29565 | DP EXHAUST GAS 2 | mbar | float32
TCS1.10MBR20CP103_XQ01 | 29566 | DP EXHAUST GAS 3 | mbar | float32
TCS1.10MBR20CT101_XQ01 | 29567 | EXHAUST DIFFUSOR TEMP 1 | °C | float32
TCS1.10MBR20CT102_XQ01 | 29568 | EXHAUST DIFFUSOR TEMP 2 | °C | float32
TCS1.10MBR20CT103_XQ01 | 29569 | EXHAUST DIFFUSOR TEMP 3 | °C | float32
TCS1.10MBR20CT104_XQ01 | 29570 | EXHAUST DIFFUSOR TEMP 4 | °C | float32
TCS1.10MBR20CT105_XQ01 | 29571 | EXHAUST DIFFUSOR TEMP 5 | °C | float32
TCS1.10MBR20CT106_XQ01 | 29572 | EXHAUST DIFFUSOR TEMP 6 | °C | float32
TCS1.10MBR20CT901_OUT | 29573 | EXHAUST DIFFUSOR TEMP | °C | float32
TCS1.10MBR20CT901_XQ01 | 29574 | EXHAUST DIFFUSOR TEMP |  | float32
TCS1.10MBV10CL101_XQ01 | 29575 | LUBE OIL TANK LVL | mm | float32
TCS1.10MBV10CP101_XQ01 | 29576 | PRESSURE LUBE OIL TANK | kPa | float32
TCS1.10MBV10CT101_XQ01 | 29577 | LUBE OIL TANK TEMP | °C | float32
TCS1.10MBV21AP001_XQ01 | 29578 | MAIN LUBE OIL PUMP CURRENT | A | float32
TCS1.10MBV21AP002_DCO | 29579 | AUX LUBE OIL PUMP |  | float32
TCS1.10MBV21AP002_XQ01 | 29580 | AUX LUBE OIL PUMP CURRENT | A | float32
TCS1.10MBV21AP003_XQ05 | 29581 | EMERG LUBE OIL PUMP |  | float32
TCS1.10MBV26CP101_XQ01 | 29582 | LUBE OIL PRESS DWNSTR. FILTERS | bar | float32
TCS1.10MBV26CT101_XQ01 | 29583 | LUBE OIL TEMP DWNSTR. FILTERS | °C | float32
TCS1.10MBV30AP001_XQ01 | 29584 | LIFT OIL PUMP 1 CURRENT | A | float32
TCS1.10MBV30AP002_XQ01 | 29585 | AUX LIFT OIL PUMP 2 CURRENT | A | float32
TCS1.10MBV31CP101_XQ01 | 29586 | LIFT OIL PRESSURE DWNSTR LIFTING OIL FILTER | bar | float32
TCS1.10MBV31CP102_XQ01 | 29587 | LIFT OIL PRESSURE DWNSTR LIFTING OIL FILTER | bar | float32
TCS1.10MBV50AN001_DCO | 29588 | LUBE OIL TANK VENT FAN 1 |  | float32
TCS1.10MBV50AN002_DCO | 29589 | LUBE OIL TANK VENT FAN 2 |  | float32
TCS1.10MBV90CT071_XQ01 | 29590 | GEN LUBE OIL TEMP OCE BEARING | C | float32
TCS1.10MBV90CT081_XQ01 | 29591 | GEN LUBE OIL TEMP CE BEARING | °C | float32
TCS1.10MBX01CL101_XQ01 | 29592 | HYD OIL TANK LEVEL 1 | mm | float32
TCS1.10MBX01CT101A_XQ01 | 29593 | HYD OIL TANK TEMP 1 | °C | float32
TCS1.10MBX01CT101B_XQ02 | 29594 | HYD OIL TANK TEMP 2 | °C | float32
TCS1.10MBX01EZ001_912688_OUT | 29595 |  |  | float32
TCS1.10MBX02AP001_DCO | 29596 | HYD OIL PUMP 1 |  | float32
TCS1.10MBX02AP002_DCO | 29597 | HYD OIL PUMP 2 |  | float32
TCS1.10MBX03CP101_XQ01 | 29598 | HYD OIL DELIVERY LINE PRESSURE | bar | float32
TCS1.10MBY01DU001_BAGVAR | 29599 | ~PROPN FUEL OIL | % | float32
TCS1.10MBY01DU001_BAOVAR | 29600 | ~PROPN FUEL OIL | % | float32
TCS1.10MBY10CE901_XQ01 | 29601 | ACTIVE POWER |  | float32
TCS1.10MBY10CE901_XQ03 | 29602 | ACTIVE POWER | MW | float32
TCS1.10MBY10CE901_XQ91 | 29603 | ACTIVE POWER | MW | float32
TCS1.10MBY10CS901_XQ01 | 29604 | TURBINE SPEED | Hz | float32
TCS1.10MBY10CS901_ZQ01 | 29605 | TURBINE SPEED | s-1 | float32
TCS1.10MBY10CS901_ZQ11 | 29606 | TURBINE SPEED | Hz | float32
TCS1.10MBY10CS901_ZQ12 | 29607 | TURBINE SPEED | rpm | float32
TCS1.10MBY10DE010_134646_OUT | 29608 | \ |  | float32
TCS1.10MBY10DE010_134681_OUT | 29609 | \ |  | float32
TCS1.10MBY10DE010_134682_OUT | 29610 | \ |  | float32
TCS1.10MBY10DE010_94330_OUT | 29611 | \ |  | float32
TCS1.10MBY10DE010_94339_OUT | 29612 | \ |  | float32
TCS1.10MBY10DE010_MARGIN_XQ01 | 29613 | LOAD SETPOINT | MW | float32
TCS1.10MBY10DE010_PSV | 29614 | ~LOAD SETP DELAYED | MW | float32
TCS1.10MBY10DE010_XQ01 | 29615 | LOAD SETPOINT | MW | float32
TCS1.10MBY10DE010_XQ03 | 29616 | LOAD SETPOINT | MW/min | float32
TCS1.10MBY10DE010_XQ04 | 29617 | LOAD SETPOINT | MW/min | float32
TCS1.10MBY10DE010_XQ05 | 29618 | LOAD SETPOINT | MW/min | float32
TCS1.10MBY10DE010_XQ51 | 29619 | ~INPUT LOAD SETPOINT | MW | float32
TCS1.10MBY10DE010_YN | 29620 | LOAD SETPOINT | MW | float32
TCS1.10MBY10DE010_ZQ02 | 29621 | LOAD SETPOINT | MW | float32
TCS1.10MBY10DE020_XQ01 | 29622 | ~LOAD SET POINT REF FROM AGC | MW | float32
TCS1.10MBY10DE051_XQ01 | 29623 | CALC GT LOAD | MW | float32
TCS1.10MBY10DP080_XQ01 | 29624 | ~COMPRESSOR MASS FLOW | % | float32
TCS1.10MBY10DS010_OM_XQ52 | 29625 | ~EXT TARG FREQ SETP | s-1 | float32
TCS1.10MBY10DS010_XQ51 | 29626 | \ |  | float32
TCS1.10MBY10DS010_ZQ01 | 29627 | SPEED SETPOINT | s-1 | float32
TCS1.10MBY10DS010_ZQ02 | 29628 | ~SPEED SETP DELAYED | s-1 | float32
TCS1.10MBY10DT010_XQ01 | 29629 | ~EFFECTIVE TEMPERATURE SETPOINT FOR IGV | °C | float32
TCS1.10MBY10DT010_XQ02 | 29630 | ~TEMPERATURE SETPOINT AT BASE LOAD | °C | float32
TCS1.10MBY10DT010_XQ03 | 29631 | ~SETPOINT DELAYED OTC-CONTROL | °C | float32
TCS1.10MBY10DT010_XQ04 | 29632 | ~DELTA ON SETPOINT OTC-CONTROLLER | °C | float32
TCS1.10MBY10DT010_XQ05 | 29633 | ~SETPOINT OTC-CONTROLLER | °C | float32
TCS1.10MBY10DT040_1_XQ51 | 29634 | ~IGV TEMP CONTROLLER | % | float32
TCS1.10MBY10DT040_1YLTR | 29635 | ~IGV TEMP CONTROLLER | % | float32
TCS1.10MBY10DT040_XQ01 | 29636 | ~IGV POS SETPOINT | % | float32
TCS1.10MBY10DT040_XQ02 | 29637 | ~ACTUAL POSN IGV |  | float32
TCS1.10MBY10DT040_XQ03 | 29638 | ACTUAL POSN CV | % | float32
TCS1.10MBY10DT040_XQ51 | 29639 | ~INPUT IGV POSN SETP | % | float32
TCS1.10MBY10DU050_DF_XQ53 | 29640 | ~DELTA F PER TEST | Hz | float32
TCS1.10MBY10DU050_PSF_XQ01 | 29641 | ~KDELTAF FROM FUEL CONTROLLER |  | float32
TCS1.10MBY10DU050_XQ07_OUT | 29642 | \ |  | float32
TCS1.10MBY10DU050_XQ08_OUT | 29643 | \ |  | float32
TCS1.10MBY10DU050_XQ02 | 29644 | ~DELTA FREQ | Hz | float32
TCS1.10MBY10DU050_XQ03 | 29645 | ~FREQUENCY DEVIATION | Hz | float32
TCS1.10MBY10DU060_1PIVMAX_OUT | 29646 |  |  | float32
TCS1.10MBY10DU060_1PIVMXL_OUT | 29647 |  |  | float32
TCS1.10MBY10DU060_1PIV_YKLGR | 29648 | ~COOLING AIR LIMIT CTRL (KLGR) | % | float32
TCS1.10MBY10DU060_1WPGR_OUT | 29649 |  |  | float32
TCS1.10MBY10DU060_1YNPR_OUT | 29650 | \ |  | float32
TCS1.10MBY10DU060_IGV FF | 29651 | ~TEMP CONTROLLER FEED FORWARD | % | float32
TCS1.10MBY10DU060_LTRY | 29652 | ~OUTPUT OID TEMP CONTROLLER | % | float32
TCS1.10MBY10DU060_WLTR | 29653 | ~SETPOINT IGV POSITION CONTROLLER | °C | float32
TCS1.10MBY10DU060_YATK | 29654 | ~OTC CONTROLLER (ATKR) | % | float32
TCS1.10MBY10DU060_YHLG | 29655 | ~RUN UP FUNCTION (HLG) | % | float32
TCS1.10MBY10DU060_YKLGR | 29656 | ~COOLING AIR LIMIT CTRL (KLGR) | % | float32
TCS1.10MBY10DU060_YMIN | 29657 | ~THERMANL LOAD REQUEST |  | float32
TCS1.10MBY10DU060_YPG | 29658 | ~LIMIT LOAD CONTROLLER (PGR) | % | float32
TCS1.10MBY10DU060_YVPVR | 29659 | ~COMPR PRES RATIO LMT CTRL (VPVR) | % | float32
TCS1.10MBY10EP801_1XQ15 | 29660 | EQUIV OP HOURS | h | float32
TCS1.10MBY10EP801_XQ04 | 29661 | ~COMPTEUR DEMARRAGE NORMAL TG |  | float32
TCS1.10MBY10EP801_XQ10 | 29662 | ~TOTALE HEURES FONCTIONNEMENT TG |  | float32
TCS1.10MBY10EP801_XQ11 | 29663 | EQUIV OP HOURS |  | float32
TCS1.10MBY10EP801_XQ12 | 29664 | EQUIV OP HOURS |  | float32
TCS1.10MBY10EP801_XQ13 | 29665 | ~OP HOURS <= BASE LOAD | h | float32
TCS1.10MBY10EP801_XQ14 | 29666 | ~OP HOURS > BASE LOAD | h | float32
TCS1.10MBY10EP801_XQ15 | 29667 | ~DYN OP HOURS | h | float32
TCS1.10MBY10EP801_XQ21 | 29668 | EQUIV OP HOURS | h | float32
TCS1.10MBY10EP802_XQ01 | 29669 | OVER-/UNDERFREQUENCY | s | float32
TCS1.10MBY10EP803_XQ01 | 29670 | ~FO PREM CHANGEOVER |  | float32
TCS1.10MBY10EP804_XQ01 | 29671 |  |  | float32
TCS1.10MBY10EP804_XQ03 | 29672 | GT START UP MONITORING |  | float32
TCS1.10MBY10EP811_XQ01 | 29673 | ~EQUIV OP HOURS | h | float32
TCS1.10MBY10EP811_XQ02 | 29674 | ~EQUIV OP HOURS | h | float32
TCS1.10MBY10EP811_XQ03 | 29675 | ~EQUIV OP HOURS | h | float32
TCS1.10MBY10EP811_XQ04 | 29676 | ~EQUIV OP HOURS | h | float32
TCS1.10MBY10EP811_XQ10 | 29677 | ~EQUIV OP HOURS | h | float32
TCS1.10MBY10EP811_XQ20 | 29678 | ~EQUIV OP HOURS | h | float32
TCS1.10MBY10EP813_XQ01 | 29679 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ02 | 29680 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ03 | 29681 | ~TOTAL TRIP NG |  | float32
TCS1.10MBY10EP813_XQ04 | 29682 | ~COMPTEUR DECL A GASOIL TG |  | float32
TCS1.10MBY10EP813_XQ05 | 29683 | ~COMPTEUR SYNCHRONISATION TG AVEC RESEAU |  | float32
TCS1.10MBY10EP813_XQ11 | 29684 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ12 | 29685 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ13 | 29686 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ14 | 29687 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ15 | 29688 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ16 | 29689 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ17 | 29690 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ18 | 29691 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ19 | 29692 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ20 | 29693 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ21 | 29694 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ22 | 29695 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ23 | 29696 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ24 | 29697 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ25 | 29698 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ26 | 29699 | EQUIV STARTS |  | float32
TCS1.10MBY10EP813_XQ27 | 29700 | ~NG LOAD REJ |  | float32
TCS1.10MBY10EP813_XQ28 | 29701 | ~FO LOAD REJ |  | float32
TCS1.10MBY10FE901_XQ05 | 29702 | ~NORMALIZED LOAD | % | float32
TCS1.10PGT_CO_XQ01 | 29703 | MISURE TEMPORANEA CO | ppm | float32
TCS1.10PGT_NOX_XQ01 | 29704 | MISURE TEMPORANEA NOX | ppm | float32
TCS1.10PGT_O2_XQ01 | 29705 | MISURE TEMPORANEA O2 | vol% | float32
TCS1.10SAM10AN001_XQ01 | 29706 | GT ENC VENT FAN 1 | A | float32
TCS1.10SAM10AN002_XQ01 | 29707 | GT ENC VENT FAN 2 | A | float32
TCS1.10SAM10AN003_XQ01 | 29708 | GT ENC VENT FAN 3 | A | float32
TCS1.10SAM10CT101_XQ01 | 29709 | TEMP GT ENCLOSURE 1 | C | float32
TCS1.10SAM10CT102_XQ01 | 29710 | TEMP GT ENCLOSURE 2 | C | float32
TCS1.11BFA01CE004_XQ02 | 29711 | BFA01 VOLTAGE MEASURE | V | float32
TCS1.11BFA02CE004_XQ02 | 29712 | BFA02 VOLTAGE MEASURE | V | float32
TCS1.11BNA01CE004_XQ02 | 29713 | EMCC BUS BAR VOLATGE | V | float32
TCS1.11BNA01GS001A_XQ01 | 29714 | EMCC INC CB A CURRENT | A | float32
TCS1.11BNA01GS001A_XQ02 | 29715 | EMCC INC CB A VOLTAGE | V | float32
TCS1.11BNA01GS001B_XQ01 | 29716 | EMCC INC CB B CURRENT | V | float32
TCS1.11BNA01GS001B_XQ02 | 29717 | EMCC INC CB B VOLTAGE | A | float32
TCS1.11BRA01EG001_XQ01 | 29718 | 1XBRA 220Vac BUS BAR VOLTAGE | V | float32
TCS1.11BUA01CE001_XQ01 | 29719 | 110 VDC BUA BUS BAR VOLTAGE | V | float32
TCS1.11MBR20CP101_XQ01B | 29720 | AI FROM SIL3 SYSTEM | mbar | float32
TCS1.11MBR20CP102_XQ01B | 29721 | AI FROM SIL3 SYSTEM | mbar | float32
TCS1.11MBR20CP103_XQ01B | 29722 | AI FROM SIL3 SYSTEM | mbar | float32
TCS1.11MBY10EP801A_XQ01 | 29723 | ~DYN OP HOURS | h | float32
TCS1.11MKA01CE001_XQ01 | 29724 | GEN VOLTAGE | KV | float32
TCS1.11MKA01CE001_XQ02 | 29725 | GEN VOLTAGE | KV | float32
TCS1.11MKA01CE001_XQ03 | 29726 | GEN VOLTAGE | KV | float32
TCS1.11MKA01CE002_XQ01 | 29727 | GEN CURRENT | A | float32
TCS1.11MKA01CE002_XQ02 | 29728 | GEN CURRENT | A | float32
TCS1.11MKA01CE002_XQ03 | 29729 | GEN CURRENT | A | float32
TCS1.11MKA01CE003_XQ02 | 29730 | GENERATOR ACTIVE POWER | MW | float32
TCS1.11MKA01CE004_XQ01 | 29731 | GEN REACTIVE POWER | MVAR | float32
TCS1.11MKA01CE006_XQ01 | 29732 | GENERATOR FREQUENCY | Hz | float32
TCS1.11MKA01CE011_XQ01 | 29733 | GENERATOR STATOR NEC CURRENT | kV | float32
TCS1.11MKA01CE013_XQ01 | 29734 | GENERATOR STATOR ZERO VOLTAGE | A | float32
TCS1.11MKA01GH001_XQ01 | 29735 | GEN SHAFT VOLTAGE MONITORING | V | float32
TCS1.11MKA01GH001_XQ02 | 29736 | GEN SHAFT CURRENT MONITORING | A | float32
TCS1.11MKA20CT301_XQ01 | 29737 | STR CO END SHID TEMP EE 01 | C | float32
TCS1.11MKA20CT302_XQ01 | 29738 | STR CO END SHID TEMP EE 02 | C | float32
TCS1.11MKA20CT303_XQ01 | 29739 | STR CO END SHID TEMP EE 03 | C | float32
TCS1.11MKA20CT304_XQ01 | 29740 | STR CO END SHID TEMP EE 04 | C | float32
TCS1.11MKA20CT311_XQ01 | 29741 | STR CO END SHID TEMP GTE 01 | C | float32
TCS1.11MKA20CT312_XQ01 | 29742 | STR CO END SHID TEMP GTE 02 | C | float32
TCS1.11MKA20CT313_XQ01 | 29743 | STR CO END SHID TEMP GTE 03 | C | float32
TCS1.11MKA20CT314_XQ01 | 29744 | STR CO END SHID TEMP GTE 04 | C | float32
TCS1.11MKA21CT301_XQ01 | 29745 | STR END SHID TEMP EE 01 | C | float32
TCS1.11MKA21CT302_XQ01 | 29746 | STR END SHID TEMP EE 02 | C | float32
TCS1.11MKA21CT303_XQ01 | 29747 | STR END SHID TEMP EE 03 | C | float32
TCS1.11MKA21CT304_XQ01 | 29748 | STR END SHID TEMP EE 04 | C | float32
TCS1.11MKA21CT311_XQ01 | 29749 | STR END SHID TEMP GTE 01 | C | float32
TCS1.11MKA21CT312_XQ01 | 29750 | STR END SHID TEMP GTE 02 | C | float32
TCS1.11MKA21CT313_XQ01 | 29751 | STR END SHID TEMP GTE 03 | C | float32
TCS1.11MKA21CT314_XQ01 | 29752 | STR END SHID TEMP GTE 04 | C | float32
TCS1.11MKA22CT301_XQ01 | 29753 | STR FINGER PL EE 01 | C | float32
TCS1.11MKA22CT302_XQ01 | 29754 | STR FINGER PL EE 02 | C | float32
TCS1.11MKA22CT303_XQ01 | 29755 | STR FINGER PL EE 03 | C | float32
TCS1.11MKA22CT304_XQ01 | 29756 | STR FINGER PL EE 04 | C | float32
TCS1.11MKA22CT311_XQ01 | 29757 | STR FINGER PL TE 01 | C | float32
TCS1.11MKA22CT312_XQ01 | 29758 | STR FINGER PL TE 02 | C | float32
TCS1.11MKA22CT313_XQ01 | 29759 | STR FINGER PL TE 03 | C | float32
TCS1.11MKA22CT314_XQ01 | 29760 | STR FINGER PL TE 04 | C | float32
TCS1.11MKA23CT301_XQ01 | 29761 | STR CORE TEMP EE 01 | C | float32
TCS1.11MKA23CT302_XQ01 | 29762 | STR CORE TEMP EE 02 | C | float32
TCS1.11MKA23CT303_XQ01 | 29763 | STR CORE TEMP EE 03 | C | float32
TCS1.11MKA23CT304_XQ01 | 29764 | STR CORE TEMP EE 04 | C | float32
TCS1.11MKA23CT305_XQ01 | 29765 | STR CORE TEMP EE 05 | C | float32
TCS1.11MKA23CT306_XQ01 | 29766 | STR CORE TEMP EE 06 | C | float32
TCS1.11MKA23CT307_XQ01 | 29767 | STR CORE TEMP EE 07 | C | float32
TCS1.11MKA23CT308_XQ01 | 29768 | STR CORE TEMP EE 08 | C | float32
TCS1.11MKA23CT309_XQ01 | 29769 | STR CORE TEMP MID 01 | C | float32
TCS1.11MKA23CT310_XQ01 | 29770 | STR CORE TEMP MID 02 | C | float32
TCS1.11MKA23CT311_XQ01 | 29771 | STR CORE TEMP MID 03 | C | float32
TCS1.11MKA23CT312_XQ01 | 29772 | STR CORE TEMP MID 04 | C | float32
TCS1.11MKA23CT313_XQ01 | 29773 | STR CORE TEMP MID 05 | C | float32
TCS1.11MKA23CT314_XQ01 | 29774 | STR CORE TEMP MID 06 | C | float32
TCS1.11MKA23CT315_XQ01 | 29775 | STR CORE TEMP MID 07 | C | float32
TCS1.11MKA23CT316_XQ01 | 29776 | STR CORE TEMP MID 08 | C | float32
TCS1.11MKA23CT317_XQ01 | 29777 | STR CORE TEMP MID 09 | C | float32
TCS1.11MKA23CT318_XQ01 | 29778 | STR CORE TEMP MID 10 | C | float32
TCS1.11MKA23CT319_XQ01 | 29779 | STR CORE TEMP MID 11 | C | float32
TCS1.11MKA23CT320_XQ01 | 29780 | STR CORE TEMP MID 12 | C | float32
TCS1.11MKA24CT301_XQ01 | 29781 | STR WINDG SLOT TEMP 01 | C | float32
TCS1.11MKA24CT302_XQ01 | 29782 | STR WINDG SLOT TEMP 02 | C | float32
TCS1.11MKA24CT303_XQ01 | 29783 | STR WINDG SLOT TEMP 03 | C | float32
TCS1.11MKA24CT304_XQ01 | 29784 | STR WINDG SLOT TEMP 04 | C | float32
TCS1.11MKA24CT305_XQ01 | 29785 | STR WINDG SLOT TEMP 05 | C | float32
TCS1.11MKA24CT306_XQ01 | 29786 | STR WINDG SLOT TEMP 06 | C | float32
TCS1.11MKA24CT307_XQ01 | 29787 | STR WINDG SLOT TEMP 07 | C | float32
TCS1.11MKA24CT308_XQ01 | 29788 | STR WINDG SLOT TEMP 08 | C | float32
TCS1.11MKA24CT309_XQ01 | 29789 | STR WINDG SLOT TEMP 09 | C | float32
TCS1.11MKA24CT310_XQ01 | 29790 | STR WINDG SLOT TEMP 10 | C | float32
TCS1.11MKA24CT311_XQ01 | 29791 | STR WINDG SLOT TEMP 11 | C | float32
TCS1.11MKA24CT312_XQ01 | 29792 | STR WINDG SLOT TEMP 12 | C | float32
TCS1.11MKA24CT313_XQ01 | 29793 | STR WINDG SLOT TEMP 13 | C | float32
TCS1.11MKA24CT314_XQ01 | 29794 | STR WINDG SLOT TEMP 14 | C | float32
TCS1.11MKA24CT315_XQ01 | 29795 | STR WINDG SLOT TEMP 15 | C | float32
TCS1.11MKA24CT316_XQ01 | 29796 | STR WINDG SLOT TEMP 16 | C | float32
TCS1.11MKA24CT317_XQ01 | 29797 | STR WINDG SLOT TEMP 17 | C | float32
TCS1.11MKA24CT318_XQ01 | 29798 | STR WINDG SLOT TEMP 18 | C | float32
TCS1.11MKA24CT319_XQ01 | 29799 | STR WINDG SLOT TEMP 19 | C | float32
TCS1.11MKA24CT320_XQ01 | 29800 | STR WINDG SLOT TEMP 20 | C | float32
TCS1.11MKA24CT321_XQ01 | 29801 | STR WINDG SLOT TEMP 21 | C | float32
TCS1.11MKA24CT322_XQ01 | 29802 | STR WINDG SLOT TEMP 22 | C | float32
TCS1.11MKA24CT323_XQ01 | 29803 | STR WINDG SLOT TEMP 23 | C | float32
TCS1.11MKA24CT324_XQ01 | 29804 | STR WINDG SLOT TEMP 24 | C | float32
TCS1.11MKA24CT325_XQ01 | 29805 | STR WINDG SLOT TEMP 25 | C | float32
TCS1.11MKA24CT326_XQ01 | 29806 | STR WINDG SLOT TEMP 26 | C | float32
TCS1.11MKA24CT327_XQ01 | 29807 | STR WINDG SLOT TEMP 27 | C | float32
TCS1.11MKA24CT328_XQ01 | 29808 | STR WINDG SLOT TEMP 28 | C | float32
TCS1.11MKA24CT329_XQ01 | 29809 | STR WINDG SLOT TEMP 29 | C | float32
TCS1.11MKA24CT330_XQ01 | 29810 | STR WINDG SLOT TEMP 30 | C | float32
TCS1.11MKA24CT331_XQ01 | 29811 | STR WINDG SLOT TEMP 31 | C | float32
TCS1.11MKA24CT332_XQ01 | 29812 | STR WINDG SLOT TEMP 32 | C | float32
TCS1.11MKA24CT333_XQ01 | 29813 | STR WINDG SLOT TEMP 33 | C | float32
TCS1.11MKA24CT334_XQ01 | 29814 | STR WINDG SLOT TEMP 34 | C | float32
TCS1.11MKA24CT335_XQ01 | 29815 | STR WINDG SLOT TEMP 35 | C | float32
TCS1.11MKA24CT336_XQ01 | 29816 | STR WINDG SLOT TEMP 36 | C | float32
TCS1.11MKA24CT337_XQ01 | 29817 | STR WINDG SLOT TEMP 37 | C | float32
TCS1.11MKA24CT338_XQ01 | 29818 | STR WINDG SLOT TEMP 38 | C | float32
TCS1.11MKA24CT339_XQ01 | 29819 | STR WINDG SLOT TEMP 39 | C | float32
TCS1.11MKA24CT340_XQ01 | 29820 | STR WINDG SLOT TEMP 40 | C | float32
TCS1.11MKA24CT341_XQ01 | 29821 | STR WINDG SLOT TEMP 41 | C | float32
TCS1.11MKA24CT342_XQ01 | 29822 | STR WINDG SLOT TEMP 42 | C | float32
TCS1.11MKA24CT343_XQ01 | 29823 | STR WINDG SLOT TEMP 43 | C | float32
TCS1.11MKA24CT344_XQ01 | 29824 | STR WINDG SLOT TEMP 44 | C | float32
TCS1.11MKA24CT345_XQ01 | 29825 | STR WINDG SLOT TEMP 45 | C | float32
TCS1.11MKA24CT346_XQ01 | 29826 | STR WINDG SLOT TEMP 46 | C | float32
TCS1.11MKA24CT347_XQ01 | 29827 | STR WINDG SLOT TEMP 47 | C | float32
TCS1.11MKA24CT348_XQ01 | 29828 | STR WINDG SLOT TEMP 48 | C | float32
TCS1.11MKA24CT349_XQ01 | 29829 | STR WINDG SLOT TEMP 49 | C | float32
TCS1.11MKA24CT350_XQ01 | 29830 | STR WINDG SLOT TEMP 50 | C | float32
TCS1.11MKA24CT351_XQ01 | 29831 | STR WINDG SLOT TEMP 51 | C | float32
TCS1.11MKA24CT352_XQ01 | 29832 | STR WINDG SLOT TEMP 52 | C | float32
TCS1.11MKA24CT353_XQ01 | 29833 | STR WINDG SLOT TEMP 53 | C | float32
TCS1.11MKA24CT354_XQ01 | 29834 | STR WINDG SLOT TEMP 54 | C | float32
TCS1.11MKA25CT301_XQ01 | 29835 | STR COIL WTR OUT TEMP 01 | C | float32
TCS1.11MKA25CT302_XQ01 | 29836 | STR COIL WTR OUT TEMP 02 | C | float32
TCS1.11MKA25CT303_XQ01 | 29837 | STR COIL WTR OUT TEMP 03 | C | float32
TCS1.11MKA25CT304_XQ01 | 29838 | STR COIL WTR OUT TEMP 04 | C | float32
TCS1.11MKA25CT305_XQ01 | 29839 | STR COIL WTR OUT TEMP 05 | C | float32
TCS1.11MKA25CT306_XQ01 | 29840 | STR COIL WTR OUT TEMP 06 | C | float32
TCS1.11MKA25CT307_XQ01 | 29841 | STR COIL WTR OUT TEMP 07 | C | float32
TCS1.11MKA25CT308_XQ01 | 29842 | STR COIL WTR OUT TEMP 08 | C | float32
TCS1.11MKA25CT309_XQ01 | 29843 | STR COIL WTR OUT TEMP 09 | C | float32
TCS1.11MKA25CT310_XQ01 | 29844 | STR COIL WTR OUT TEMP 10 | C | float32
TCS1.11MKA25CT311_XQ01 | 29845 | STR COIL WTR OUT TEMP 11 | C | float32
TCS1.11MKA25CT312_XQ01 | 29846 | STR COIL WTR OUT TEMP 12 | C | float32
TCS1.11MKA25CT313_XQ01 | 29847 | STR COIL WTR OUT TEMP 13 | C | float32
TCS1.11MKA25CT314_XQ01 | 29848 | STR COIL WTR OUT TEMP 14 | C | float32
TCS1.11MKA25CT315_XQ01 | 29849 | STR COIL WTR OUT TEMP 15 | C | float32
TCS1.11MKA25CT316_XQ01 | 29850 | STR COIL WTR OUT TEMP 16 | C | float32
TCS1.11MKA25CT317_XQ01 | 29851 | STR COIL WTR OUT TEMP 17 | C | float32
TCS1.11MKA25CT318_XQ01 | 29852 | STR COIL WTR OUT TEMP18 | C | float32
TCS1.11MKA25CT319_XQ01 | 29853 | STR COIL WTR OUT TEMP 19 | C | float32
TCS1.11MKA25CT320_XQ01 | 29854 | STR COIL WTR OUT TEMP 20 | C | float32
TCS1.11MKA25CT321_XQ01 | 29855 | STR COIL WTR OUT TEMP 21 | C | float32
TCS1.11MKA25CT322_XQ01 | 29856 | STR COIL WTR OUT TEMP 22 | C | float32
TCS1.11MKA25CT323_XQ01 | 29857 | STR COIL WTR OUT TEMP 23 | C | float32
TCS1.11MKA25CT324_XQ01 | 29858 | STR COIL WTR OUT TEMP 24 | C | float32
TCS1.11MKA25CT325_XQ01 | 29859 | STR COIL WTR OUT TEMP 25 | C | float32
TCS1.11MKA25CT326_XQ01 | 29860 | STR COIL WTR OUT TEMP 26 | C | float32
TCS1.11MKA25CT327_XQ01 | 29861 | STR COIL WTR OUT TEMP 27 | C | float32
TCS1.11MKA25CT328_XQ01 | 29862 | STR COIL WTR OUT TEMP 28 | C | float32
TCS1.11MKA25CT329_XQ01 | 29863 | STR COIL WTR OUT TEMP 29 | C | float32
TCS1.11MKA25CT330_XQ01 | 29864 | STR COIL WTR OUT TEMP 30 | C | float32
TCS1.11MKA25CT331_XQ01 | 29865 | STR COIL WTR OUT TEMP 31 | C | float32
TCS1.11MKA25CT332_XQ01 | 29866 | STR COIL WTR OUT TEMP 32 | C | float32
TCS1.11MKA25CT333_XQ01 | 29867 | STR COIL WTR OUT TEMP 33 | C | float32
TCS1.11MKA25CT334_XQ01 | 29868 | STR COIL WTR OUT TEMP 34 | C | float32
TCS1.11MKA25CT335_XQ01 | 29869 | STR COIL WTR OUT TEMP 35 | C | float32
TCS1.11MKA25CT336_XQ01 | 29870 | STR COIL WTR OUT TEMP 36 | C | float32
TCS1.11MKA25CT337_XQ01 | 29871 | STR COIL WTR OUT TEMP 37 | C | float32
TCS1.11MKA25CT338_XQ01 | 29872 | STR COIL WTR OUT TEMP 38 | C | float32
TCS1.11MKA25CT339_XQ01 | 29873 | STR COIL WTR OUT TEMP 39 | C | float32
TCS1.11MKA25CT340_XQ01 | 29874 | STR COIL WTR OUT TEMP 40 | C | float32
TCS1.11MKA25CT341_XQ01 | 29875 | STR COIL WTR OUT TEMP 41 | C | float32
TCS1.11MKA25CT342_XQ01 | 29876 | STR COIL WTR OUT TEMP 42 | C | float32
TCS1.11MKA25CT343_XQ01 | 29877 | STR COIL WTR OUT TEMP 43 | C | float32
TCS1.11MKA25CT344_XQ01 | 29878 | STR COIL WTR OUT TEMP 44 | C | float32
TCS1.11MKA25CT345_XQ01 | 29879 | STR COIL WTR OUT TEMP 45 | C | float32
TCS1.11MKA25CT346_XQ01 | 29880 | STR COIL WTR OUT TEMP 46 | C | float32
TCS1.11MKA25CT347_XQ01 | 29881 | STR COIL WTR OUT TEMP 47 | C | float32
TCS1.11MKA25CT348_XQ01 | 29882 | STR COIL WTR OUT TEMP 48 | C | float32
TCS1.11MKA25CT349_XQ01 | 29883 | STR COIL WTR OUT TEMP 49 | C | float32
TCS1.11MKA25CT350_XQ01 | 29884 | STR COIL WTR OUT TEMP 50 | C | float32
TCS1.11MKA25CT351_XQ01 | 29885 | STR COIL WTR OUT TEMP 51 | C | float32
TCS1.11MKA25CT352_XQ01 | 29886 | STR COIL WTR OUT TEMP 52 | C | float32
TCS1.11MKA25CT353_XQ01 | 29887 | STR COIL WTR OUT TEMP 53 | C | float32
TCS1.11MKA25CT354_XQ01 | 29888 | STR COIL WTR OUT TEMP 54 | C | float32
TCS1.11MKA26CT301_XQ01 | 29889 | MAIN BSHG AIR TEMP 1 | C | float32
TCS1.11MKA26CT302_XQ01 | 29890 | MAIN BSHG AIR TEMP 2 | C | float32
TCS1.11MKA30CT301A_XQ01 | 29891 | GEN COLD GAS TEMP EE | C | float32
TCS1.11MKA30CT302A_XQ01 | 29892 | GEN COLD GAS TEMP EE | C | float32
TCS1.11MKA30CT303A_XQ01 | 29893 | GEN COLD GAS TEMP EE | C | float32
TCS1.11MKA30CT304A_XQ01 | 29894 | GEN COLD GAS TEMP EE | C | float32
TCS1.11MKA30CT311A_XQ01 | 29895 | GEN COLD GAS TEMP GTE | C | float32
TCS1.11MKA30CT312A_XQ01 | 29896 | GEN COLD GAS TEMP GTE | C | float32
TCS1.11MKA30CT313A_XQ01 | 29897 | GEN COLD GAS TEMP GTE | C | float32
TCS1.11MKA30CT314A_XQ01 | 29898 | GEN COLD GAS TEMP GTE | C | float32
TCS1.11MKA31CT301_XQ01 | 29899 | GEN WARM GAS TEMP EE | C | float32
TCS1.11MKA31CT311_XQ01 | 29900 | GEN WARM GAS TEMP TE | C | float32
TCS1.11MKA31CT901_ZQ01 | 29901 | \ |  | float32
TCS1.11MKC10CE002_XQ01 | 29902 | EXC TRASNF CURRENT | A | float32
TCS1.11MKC10CE003_XQ01 | 29903 | EXC TRASNF ACTIVE POWER | MW | float32
TCS1.11MKC10CE004_XQ01 | 29904 | EXC TRASNF REACTIVE POWER | KVAR | float32
TCS1.11MKC10CT001_XQ01 | 29905 | LV WINDINGS TEMP PH R | °C | float32
TCS1.11MKC10CT002_XQ01 | 29906 | LV WINDINGS TEMP PH S | °C | float32
TCS1.11MKC10CT003_XQ01 | 29907 | LV WINDINGS TEMP PH T | °C | float32
TCS1.11MKC10FT002_XQ01 | 29908 | ROTOR EARTH RESISTANCE | M? | float32
TCS1.11MKC20CE001_XQ01 | 29909 | EXCITATION CURRENT | A | float32
TCS1.11MKC20CE002_XQ01 | 29910 | EXCITATION VOLTAGE | V | float32
TCS1.11MKD11CT601_XQ01 | 29911 | BRG OIL OUTLET TEMP GTE | C | float32
TCS1.11MKD11CT602_XQ01 | 29912 | GEN GTE SIDE BEARING TEMP | °C | float32
TCS1.11MKD11CT602_XQ11 | 29913 | GEN GTE SIDE BEARING TEMP | °C | float32
TCS1.11MKD11CY021_XQ01 | 29914 | GEN GTE SIDE BEARING ABS VIBR CH. A | mm/s | float32
TCS1.11MKD11CY022_XQ01 | 29915 | GEN GTE SIDE BEARING ABS VIBR CH. B | mm/s | float32
TCS1.11MKD11CY940_XQ01 | 29916 | GEN GTE SIDE BEARING REL VIBR Smax VALUE | um | float32
TCS1.11MKD12CT601_XQ01 | 29917 | BRG OIL OUTLET TEMP EE | C | float32
TCS1.11MKD12CT602_XQ01 | 29918 | GEN EE SIDE BEARING TEMP | °C | float32
TCS1.11MKD12CT602_XQ11 | 29919 | GEN EE SIDE BEARING TEMP | °C | float32
TCS1.11MKD12CY021_XQ01 | 29920 | GEN ABS VIBR CE BEARING CH. A | mm/s | float32
TCS1.11MKD12CY022_XQ01 | 29921 | GEN ABS VIBR CE BEARING CH. B | mm/s | float32
TCS1.11MKD12CY940_XQ01 | 29922 | GEN CE SIDE BEARING REL VIBR Smax VALUE | um | float32
TCS1.11MKD13CT601_XQ01 | 29923 | BRG OIL OUTLET TEMP COLLECTOR | C | float32
TCS1.11MKD13CT602_XQ01 | 29924 | BRG TEMP COLLECTOR | °C | float32
TCS1.11MKD13CT602_XQ11 | 29925 | BRG TEMP COLLECTOR | °C | float32
TCS1.11MKD13CY021_XQ01 | 29926 | GEN COLLECTOR SIDE BEARING ABS VIBR CH. A | mm/s | float32
TCS1.11MKD13CY022_XQ01 | 29927 | GEN COLLECTOR SIDE BEARING ABS VIBR CH. B | mm/s | float32
TCS1.11MKD13CY940_XQ01 | 29928 | GEN COLLECTOR SIDE BEARING REL VIBR Smax | um | float32
TCS1.11MKF05CL101_XQ01 | 29929 | STATOR WTR PRIMARY TANK | mm | float32
TCS1.11MKF11AP001_DCO | 29930 | PRIMARY WTR PUMP 1 |  | float32
TCS1.11MKF11AP001_XQ01 | 29931 | PRIMARY WTR PUMP 1 CURRENT | A | float32
TCS1.11MKF12AP001_DCO | 29932 | PRIMARY WTR PUMP 2 |  | float32
TCS1.11MKF12AP001_XQ01 | 29933 | PRIMARY WTR PUMP 2 CURRENT | A | float32
TCS1.11MKF18CQ101_XQ01 | 29934 | CONDUCT MAIL LOOP | ?S/cm | float32
TCS1.11MKF19CF101_XQ01 | 29935 | F STATOR WATER | m?/h | float32
TCS1.11MKF20CT301_XQ01 | 29936 | T U/S STATOR WATER | C | float32
TCS1.11MKF20CT302_XQ01 | 29937 | T D/S STATOR WATER | C | float32
TCS1.11MKF23CQ101_XQ01 | 29938 | CONDUCT TREATMENT LOOP | ?S/cm | float32
TCS1.11MKF30CP101_XQ01 | 29939 | DP STATOR WINDING | kPa | float32
TCS1.11MKG21CP101_XQ01 | 29940 | PRES HYDROGEN SUPPLY | MPa | float32
TCS1.11MKG24CF101_XQ01 | 29941 | M/U H2 FLOW | m?/h | float32
TCS1.11MKG26CP101_XQ01 | 29942 | PRES H2 GEN CASING | kPa | float32
TCS1.11MKG30CQ901_XQ01 | 29943 | H2 GAS ANALYZER 1 | % H2 | float32
TCS1.11MKG30CQ901_XQ01_MULTIPLY | 29944 | H2 GAS ANALYZER 1 | %H2 | float32
TCS1.11MKG35CQ401_XQ01 | 29945 | H2 LEAKAGE DETECTOR 1 | % | float32
TCS1.11MKG35CQ401_XQ02 | 29946 | H2 LEAKAGE DETECTOR 2 | % | float32
TCS1.11MKG35CQ401_XQ03 | 29947 | LEAKAGE DETECTOR 3 | % | float32
TCS1.11MKG35CQ401_XQ04 | 29948 | LEAKAGE DETECTOR 4 | % | float32
TCS1.11MKG35CQ401_XQ05 | 29949 | LEAKAGE DETECTOR 5 | % | float32
TCS1.11MKG35CQ401_XQ06 | 29950 | LEAKAGE DETECTOR 6 | % | float32
TCS1.11MKG35CQ401_XQ07 | 29951 | LEAKAGE DETECTOR 7 | % | float32
TCS1.11MKG51CM101_XQ01 | 29952 | DEW POINT D/STR DRY | Td | float32
TCS1.11MKG52CM102_XQ01 | 29953 | DEW POINT D/STR DRY | Td | float32
TCS1.11MKW06CL101_XQ01 | 29954 | LEVEL TANK HYDROGEN | mm | float32
TCS1.11MKW11AP001_DCO | 29955 | ~AIR SEAL OIL PUMP 1 |  | float32
TCS1.11MKW11AP001_XQ01 | 29956 | SEAL OIL PUMP 1 CURRENT | A | float32
TCS1.11MKW12AP001_DCO | 29957 | ~AIR SEAL OIL PUMP 2 |  | float32
TCS1.11MKW12AP001_XQ01 | 29958 | SEAL OIL PUMP 2 CURRENT | A | float32
TCS1.11MKW13AP001_XQ01 | 29959 | DC SEAL OIL PUMP CURRENT | A | float32
TCS1.11MKW14CT301_XQ01 | 29960 | TEMP D/S COOLER AIR SIDE | C | float32
TCS1.11MKW19CP101_XQ01 | 29961 | PRES SEAL OIL TE REG A/S | kPa | float32
TCS1.11MKW25AP001_DCO | 29962 | ~H2 GAS SEAL OIL PUMP 1 |  | float32
TCS1.11MKW25AP001_XQ01 | 29963 | ~SEAL OIL PUMP 1#(H2) | A | float32
TCS1.11MKW26AP001_DCO | 29964 | ~H2 GAS SEAL OIL PUMP 2 |  | float32
TCS1.11MKW26AP001_XQ01 | 29965 | H2 GAS SEAL OIL PUMP 5 | A | float32
TCS1.11MKW27CT301_XQ01 | 29966 | TEMP D/S COOLER GAS SIDE | C | float32
TCS1.11MKW51AN001_DCO | 29967 | GEN EXH BLWR 1 |  | float32
TCS1.11MKW51CP101_XQ01 | 29968 | PRES U/S EXH BLWR 1 | kPa | float32
TCS1.11MKW52AN001_DCO | 29969 | GEN EXH BLWR 2 |  | float32
TCS1.11MKW52CP101_XQ01 | 29970 | PRES U/S EXH BLWR 2 | kPa | float32
TCS1.EKG60FF_COUNT_49184_OUT | 29971 |  |  | float32
TCS1.10CJQ02GS001_XM11 | 29972 | \ |  | digital
TCS1.10CJQ02GW001_XM31 | 29973 | \ |  | digital
TCS1.10CYE01EG001_XB01 | 29974 | ENCLOSURE TG/GAS | \ | digital
TCS1.10CYE01EG001_XB02 | 29975 | ENCLOSURE TG/GAS | \ | digital
TCS1.10CYE01EG001_XB11 | 29976 | ENCLOSURE TG/GAS | \ | digital
TCS1.10EKE31CL081_XB01 | 29977 | FILTER 1 STAGE 2 | \ | digital
TCS1.10EKE31CL083_XB01 | 29978 | FILTER 1 STAGE 1 | \ | digital
TCS1.10EKE31CP081_XB01 | 29979 | DIFF PRESSURE GAS FINAL FILTER 1 | \ | digital
TCS1.10EKE31CQ501_XB03HW | 29980 | \ |  | digital
TCS1.10EKE32CL081_XB01 | 29981 | FILTER 2 STAGE 2 | \ | digital
TCS1.10EKE32CL083_XB01 | 29982 | FILTER 2 STAGE 1 | \ | digital
TCS1.10EKE32CP081_XB01 | 29983 | DIFF PRESSURE GAS FINAL FILTER 2 | \ | digital
TCS1.10EKE32CQ501_XH01 | 29984 | \ |  | digital
TCS1.10EKG60CQ501_XH01 | 29985 | LEAKAGE ALARM 1 HIGH & HIGH | \ | digital
TCS1.10EKG60FF001_XB03 | 29986 | \ |  | digital
TCS1.10EKG60FF101_COUNT_ZV10 | 29987 | \ |  | digital
TCS1.10EKG60FF101_XQ01 | 29988 | \ |  | digital
TCS1.10EKG70AA001_XG01 | 29989 | BLOCK VLV AA001 | \ | digital
TCS1.10EKG70CQ501_XH01 | 29990 | LEAK ALARM H | \ | digital
TCS1.10MBA10AT001_XB01 | 29991 | AIR DRYER | \ | digital
TCS1.10MBA10CG001_XG02 | 29992 | SAFETY SWITCH FOR INTERM. SHAFT | \ | digital
TCS1.10MBA10CG002_XG02 | 29993 | SAFETY SWITCH FOR INTERM. SHAFT | \ | digital
TCS1.10MBA10CG003_XG02 | 29994 | SAFETY SWITCH FOR INTERM. SHAFT | \ | digital
TCS1.10MBA10EU010_ZV51 | 29995 | SAFETY SWITCH FOR INTERM. SHAFT | \ | digital
TCS1.10MBA10EZ001_ZV01 | 29996 | OVER-/UNDERFREQUENCY | \ | digital
TCS1.10MBA10EZ001_ZV13 | 29997 | OVER-/UNDERFREQUENCY | \ | digital
TCS1.10MBA10FG100_ZV01 | 29998 | ROTOR AXIAL DISPLACEMENT | \ | digital
TCS1.10MBA10FG100_ZV02 | 29999 | ROTOR AXIAL DISPLACEMENT | \ | digital
TCS1.10MBA10FS010_XK01 | 30000 | HW TRIP (BRAUN) | \ | digital
TCS1.10MBA11AS001_XG01 | 30001 | IGV MAX LIMIT POSITION ON ACTUATOR | \ | digital
TCS1.10MBA11AS002_XG01 | 30002 | CV MAX LIMIT POSITION ON ACTUATOR | \ | digital
TCS1.10MBA11CG001_XG01 | 30003 | IGV MAX LIMIT POSITION ON RING | \ | digital
TCS1.10MBA11CG002_XG01 | 30004 | IGV MIN LIMIT POSITION ON RING | \ | digital
TCS1.10MBA11CG011_XG01 | 30005 | CV MAX LIMIT POSITION ON RING | \ | digital
TCS1.10MBA11CG012_XG01 | 30006 | CV MIN LIMIT POSITION ON RING | \ | digital
TCS1.10MBA11CT901_ZV02 | 30007 | COMPRESSOR AIR INLET TEMP | \ | digital
TCS1.10MBA11DG012_804189_OUT | 30008 | \ |  | digital
TCS1.10MBA26EZ001_B1 | 30009 | \ |  | digital
TCS1.10MBA26EZ001_B24 | 30010 | \ |  | digital
TCS1.10MBA26EZ001_B24_1 | 30011 | \ |  | digital
TCS1.10MBA26EZ001_ZV01 | 30012 | TURBINE EXHAUST GAS TEMP ANALYSIS | \ | digital
TCS1.10MBA26EZ001_ZV02 | 30013 | TURBINE EXHAUST GAS TEMP ANALYSIS | \ | digital
TCS1.10MBA26EZ001_ZV91 | 30014 | TURBINE EXHAUST GAS TEMP ANALYSIS | \ | digital
TCS1.10MBA40EZ001_ZV01 | 30015 | COMPR BLOWOFF PROT | \ | digital
TCS1.10MBA41AA051_XB02 | 30016 | COMP BLOWOFF VLV 1.1 | \ | digital
TCS1.10MBA42AA051_XB02 | 30017 | COMP BLOWOFF VLV 1.2 | \ | digital
TCS1.10MBA43AA051_XB02 | 30018 | COMP BLOWOFF VLV 2 | \ | digital
TCS1.10MBA44AA051_XB02 | 30019 | COMP BLOWOFF VLV 3 | \ | digital
TCS1.10MBA50EC001_REG_TIME_OUT | 30020 | \ |  | digital
TCS1.10MBA50EC001_ON | 30021 | SGC RDS | \ | digital
TCS1.10MBA50EC001_XA01 | 30022 | SGC RDS | \ | digital
TCS1.10MBA50EC001_ZV03 | 30023 | SGC RDS | \ | digital
TCS1.10MBA50EC001_ZV04 | 30024 | SGC RDS | \ | digital
TCS1.10MBA50EC001_ZV12 | 30025 | \ |  | digital
TCS1.10MBA50EC001_ZV21 | 30026 | \ |  | digital
TCS1.10MBA50EU003_ZV20 | 30027 | \ |  | digital
TCS1.10MBA50EU005_ON | 30028 | \ |  | digital
TCS1.10MBA50EU005_RUN2 | 30029 | \ |  | digital
TCS1.10MBA51AA251_XG02 | 30030 | RDS PUMP 1 FEED VLV | \ | digital
TCS1.10MBA51AA252_XG02 | 30031 | RDS PUMP 2 FEED VLV | \ | digital
TCS1.10MBA51AP001_XB01 | 30032 | RDS PUMP 1 | \ | digital
TCS1.10MBA51AP002_XB01 | 30033 | RDS PUMP 2 | \ | digital
TCS1.10MBA51CP001_XB01 | 30034 | RDS DOWSTR PUMP 1 PRESSURE | \ | digital
TCS1.10MBA51CP002_XB01 | 30035 | RDS DOWSTR PUMP 2 PRESSURE | \ | digital
TCS1.10MBA51CP003_XB01 | 30036 | RDS FEED LINE 1 DP FILTER | \ | digital
TCS1.10MBA51CP004_XB01 | 30037 | RDS FEED LINE 2 DP FILTER | \ | digital
TCS1.10MBA52CP001_XB01 | 30038 | RDS LUBE OIL DP FILTER | \ | digital
TCS1.10MBA53AA001_XG52 | 30039 | RDS MAIN CH RETURN VLV | \ | digital
TCS1.10MBA53AA002_XG01 | 30040 | RDS MAIN CH SUPPLY VLV | \ | digital
TCS1.10MBA53AA003_XG01 | 30041 | RDS MAIN CH SUPPLY VLV | \ | digital
TCS1.10MBA53AA004_XG52 | 30042 | RDS SECOND CH FEED VLV | \ | digital
TCS1.10MBA53AA005_XG01 | 30043 | RDS SECOND CH RETURN VLV | \ | digital
TCS1.10MBA53AA006_XG01 | 30044 | RDS MAIN CH SUPPLY VLV | \ | digital
TCS1.10MBA53FP101_ZV11 | 30045 | MAIN RETURN LINE PRESS | \ | digital
TCS1.10MBA53FP102_ZV11 | 30046 | SEC RETURN LINE PRESS | \ | digital
TCS1.10MBD11EZ110_XK01 | 30047 | TURBINE BEARING TEMP CH.1 | \ | digital
TCS1.10MBD11EZ120_XK01 | 30048 | TURBINE BEARING TEMP CH.2 | \ | digital
TCS1.10MBD11EZ210_XK01 | 30049 | TURBINE BEARING VIBR | \ | digital
TCS1.10MBD12EZ110_XK01 | 30050 | COMP. BEARINGS TEMP | \ | digital
TCS1.10MBD12EZ120_XK01 | 30051 | THRUST BEARINGS TEMP GEN PART | \ | digital
TCS1.10MBD12EZ130_XK01 | 30052 | COMP. THRUST BEARING UPPER PART | \ | digital
TCS1.10MBD12EZ210_XK01 | 30053 | ~COMP. BEARINGS VIBR. | \ | digital
TCS1.10MBH22AA101_XG01 | 30054 | COOL AIR DAMPER 1 STAGE 2 | \ | digital
TCS1.10MBH22AA102_XG01 | 30055 | COOL AIR DAMPER 2 STAGE 2 | \ | digital
TCS1.10MBH22FP100_ZQ01 | 30056 | \ |  | digital
TCS1.10MBH23AA101_XG01 | 30057 | COOL AIR DAMPER 1 STAGE 3 | \ | digital
TCS1.10MBH23AA102_XG01 | 30058 | COOL AIR DAMPER 2 STAGE 3 | \ | digital
TCS1.10MBH23FP100_ZQ01 | 30059 | \ |  | digital
TCS1.10MBJ01EC001_XA03 | 30060 |  |  | digital
TCS1.10MBJ01EU003_89901_OUT | 30061 | \ |  | digital
TCS1.10MBJ01EU003_963297_OUT | 30062 | \ |  | digital
TCS1.10MBJ01EZ001_SLC_ON | 30063 |  |  | digital
TCS1.10MBJ20EA008_RESET_ON | 30064 |  |  | digital
TCS1.10MBJ20EU001_PRESEL_SEL2 | 30065 |  |  | digital
TCS1.10MBJ20EU001_XT42 | 30066 | SFC MODE | \ | digital
TCS1.10MBJ20EU005_EN_ON | 30067 | SFC START/STOP | \ | digital
TCS1.10MBJ20EU006_239237_SEL3 | 30068 |  |  | digital
TCS1.10MBK21EU001_ZV55 | 30069 | TURNING GEAR LIMIT SWITCH | \ | digital
TCS1.10MBK21EU001_ZV56 | 30070 | TURNING GEAR LIMIT SWITCH | \ | digital
TCS1.10MBK21EU001_ZV62 | 30071 | TURNING GEAR LIMIT SWITCH | \ | digital
TCS1.10MBL10CG101_XG01 | 30072 | INSPECTION DOOR 1 | \ | digital
TCS1.10MBL10CG102_XG01 | 30073 | INSPECTION DOOR 2 | \ | digital
TCS1.10MBL10CG103_XG01 | 30074 | INSPECTION DOOR 3 | \ | digital
TCS1.10MBL10CG104_XG01 | 30075 | INSPECTION DOOR 4 | \ | digital
TCS1.10MBL10CU00X_XB01 | 30076 | GT INLET AIR FILTRATION SYSTEM | \ | digital
TCS1.10MBL14CP001_XG01 | 30077 | INTAKE TOTAL FILTER DP 1 | \ | digital
TCS1.10MBL14CP002_XG01 | 30078 | INTAKE TOTAL FILTER DP 2 | \ | digital
TCS1.10MBL17EU001_ZV52 | 30079 | ANTI IMPLOSION DOOR 1 | \ | digital
TCS1.10MBL17EU002_ZV52 | 30080 | ANTI IMPLOSION DOOR 2 | \ | digital
TCS1.10MBL17EU003_ZV52 | 30081 | ANTI IMPLOSION DOOR 3 | \ | digital
TCS1.10MBL17EU004_ZV52 | 30082 | ANTI IMPLOSION DOOR 4 | \ | digital
TCS1.10MBL20AA001_XB01 | 30083 | AIR DAMPER | \ | digital
TCS1.10MBL20CG011_XG01 | 30084 | INSPECTION DOOR 1 | \ | digital
TCS1.10MBL20CG012_XG01 | 30085 | INSPECTION DOOR 2 | \ | digital
TCS1.10MBL20CG013_XG01 | 30086 | INSPECTION DOOR 3 | \ | digital
TCS1.10MBL20CG014_XG01 | 30087 | INSPECTION DOOR 4 | \ | digital
TCS1.10MBL20EU001_ZV01 | 30088 | ~INSPECTION DOORS PERM. | \ | digital
TCS1.10MBL21CQ101_XB01 | 30089 | ICE DETECTOR | \ | digital
TCS1.10MBL30CP001_XG01 | 30090 | ~INLET AIR FILTR PRESS FROM AUX COMPR | \ | digital
TCS1.10MBM00EU006_XT51 | 30091 | \ |  | digital
TCS1.10MBM00EU007_ZV01 | 30092 | \ |  | digital
TCS1.10MBM12GT001_XB01 | 30093 | IGN TRF | \ | digital
TCS1.10MBM13CR101_XB12 | 30094 | FLAME 1 | \ | digital
TCS1.10MBM13CR102_XB12 | 30095 | FLAME 2 | \ | digital
TCS1.10MBM13EU010_ZV01 | 30096 | FLAME | \ | digital
TCS1.10MBM13EU010_ZV01HW | 30097 | FLAME |  | digital
TCS1.10MBM13EU011_ZV09 | 30098 | FLAME MONITORING | \ | digital
TCS1.10MBP00EU001_XV01 | 30099 | \ |  | digital
TCS1.10MBP01EC001_ON | 30100 |  |  | digital
TCS1.10MBP01EC001_ZA01 | 30101 | \ |  | digital
TCS1.10MBP03DU001_ZV01 | 30102 | NG CONTROLLER TRIP | \ | digital
TCS1.10MBP03DU003_1FEGVB_OUT | 30103 | \ |  | digital
TCS1.10MBP03DU003_COMB_LOAD_VAR_NG_OUT | 30104 |  |  | digital
TCS1.10MBP03DU003_STEP_OUT | 30105 |  |  | digital
TCS1.10MBP13AA051_ZG01 | 30106 | FG STOP VALVE | \ | digital
TCS1.10MBP13AA051_ZV01 | 30107 | \ |  | digital
TCS1.10MBP13AA501_ZG01 | 30108 | \ |  | digital
TCS1.10MBP22AA151_ZV01HW | 30109 | \ |  | digital
TCS1.10MBP22DG151_XG01 | 30110 | ~PILOT 1 CTRL POSN | \ | digital
TCS1.10MBP24AA151_ZV01HW | 30111 | \ |  | digital
TCS1.10MBP24DG151_XG01 | 30112 | NG PILOT 2 CTRL POSN | \ | digital
TCS1.10MBP32AH001_XT01 | 30113 | FG PREMIX HEAT. | \ | digital
TCS1.10MBP34AH001_XT01 | 30114 | FG PILOT 2 HEAT. | \ | digital
TCS1.10MBV00EE010_XA01 | 30115 | LUBE OIL HEATING | \ | digital
TCS1.10MBV01EC001_XA41 | 30116 | \ |  | digital
TCS1.10MBV02EC001_XA03 | 30117 | \ |  | digital
TCS1.10MBV10CL001_XG01 | 30118 | LUBE OIL TANK LEVEL | \ | digital
TCS1.10MBV10CL001_XG02 | 30119 | LUBE OIL TANK LEVEL | \ | digital
TCS1.10MBV10CL001_XG03 | 30120 | LUBE OIL TANK LEVEL | \ | digital
TCS1.10MBV10CL001_XG04 | 30121 | LUBE OIL TANK LEVEL | \ | digital
TCS1.10MBV10CL002_XG01 | 30122 | LUBE OIL TANK LEVEL | \ | digital
TCS1.10MBV10CL002_XG02 | 30123 | LUBE OIL TANK LEVEL | \ | digital
TCS1.10MBV10CL002_XG03 | 30124 | LUBE OIL TANK LEVEL | \ | digital
TCS1.10MBV10CL002_XG04 | 30125 | LUBE OIL TANK LEVEL | \ | digital
TCS1.10MBV10EZ001_ZK51 | 30126 | LUBE OIL TANK LVL | \ | digital
TCS1.10MBV21AP001_EN_START | 30127 | MAIN LUBE OIL PUMP | \ | digital
TCS1.10MBV21AP001_XB01 | 30128 | MAIN LUBE OIL PUMP | \ | digital
TCS1.10MBV21AP002_EN_START | 30129 | AUX LUBE OIL PUMP | \ | digital
TCS1.10MBV21AP002_XB01 | 30130 | AUX LUBE OIL PUMP | \ | digital
TCS1.10MBV21AP003_696654_ON | 30131 | \ |  | digital
TCS1.10MBV21AP003_EN_START | 30132 | EMERG LUBE OIL PUMP | \ | digital
TCS1.10MBV21AP003_XB01 | 30133 | EMERG LUBE OIL PUMP | \ | digital
TCS1.10MBV21AP003_XB04 | 30134 | EMERG LUBE OIL PUMP | \ | digital
TCS1.10MBV21CP001_XG51 | 30135 | LUBE OIL PUMP PRESS | \ | digital
TCS1.10MBV21EU007_ZV01 | 30136 | ~STARTUP FROM SPEED ZERO | \ | digital
TCS1.10MBV21EU008_291005_OUT | 30137 | \ |  | digital
TCS1.10MBV21EU009_240332_ON | 30138 | \ |  | digital
TCS1.10MBV21EZ001_ZV01 | 30139 | LUBE OIL PUMP OFF | \ | digital
TCS1.10MBV25CP001_XG51 | 30140 | OIL FILTER DIFF PRESS | \ | digital
TCS1.10MBV26AA510_YB11HW | 30141 | EMERG LUBE OIL PUMP VLV |  | digital
TCS1.10MBV26CP002_XG11 | 30142 | LUBE OIL PRESS DOWNSTR. FILTERS | \ | digital
TCS1.10MBV26CP003_XG02 | 30143 | LUBE OIL PRESS DOWNSTR. FILTERS | \ | digital
TCS1.10MBV26EZ001_XK52 | 30144 | LUBE OIL SYSTEM PRESS. | \ | digital
TCS1.10MBV30AP001_XB01 | 30145 | LIFT OIL PUMP | \ | digital
TCS1.10MBV30AP002_XB01 | 30146 | AUX LIFT OIL PUMP | \ | digital
TCS1.10MBV30CP001_XG01 | 30147 | LIFT OIL FILTER | \ | digital
TCS1.10MBV35AA001_XB01 | 30148 | TURNING GEAR CLUTCH A001 VLV | \ | digital
TCS1.10MBV35AA002_XB01 | 30149 | TURNING GEAR CLUTCH A002 VLV | \ | digital
TCS1.10MBV35AA003_XB01 | 30150 | TURNING GEAR A003 VLV | \ | digital
TCS1.10MBV35AA101_YB01HW | 30151 | \ |  | digital
TCS1.10MBV35AA101_YB21HW | 30152 | \ |  | digital
TCS1.10MBV50AN001_XB01 | 30153 | LUBE OIL TANK VENT FAN 1 | \ | digital
TCS1.10MBV50AN002_XB01 | 30154 | LUBE OIL TANK VENT FAN 2 | \ | digital
TCS1.10MBV50EE010_309391_ON | 30155 | \ |  | digital
TCS1.10MBX01CL001_XG02 | 30156 | HYD OIL TANK LEVEL | \ | digital
TCS1.10MBX01CL002_XG02 | 30157 | HYD OIL TANK LEVEL | \ | digital
TCS1.10MBX01CL002_XG12 | 30158 | HYD OIL TANK LEVEL | \ | digital
TCS1.10MBX01EE001_309616_RUN2 | 30159 |  |  | digital
TCS1.10MBX01EE001_309844_RUN2 | 30160 |  |  | digital
TCS1.10MBX01EZ001_XQ01 | 30161 | \ |  | digital
TCS1.10MBX02AP001_XB01 | 30162 | HYD OIL PUMP 1 | \ | digital
TCS1.10MBX02AP002_XB01 | 30163 | HYD OIL PUMP 2 | \ | digital
TCS1.10MBX03CP002_XG52 | 30164 | HYD OIL FILTER 2 | \ | digital
TCS1.10MBX03CP005_XG11 | 30165 | HYD OIL DELIVERY LINE PRESSURE | \ | digital
TCS1.10MBX03CP006_XG02 | 30166 | HYD OIL DELIVERY LINE PRESSURE | \ | digital
TCS1.10MBX03CP101_XH54 | 30167 | HYD OIL DELIVERY LINE PRESSURE | \ | digital
TCS1.10MBX03CQ001_XG01 | 30168 | HYD OIL CONTAMINATION DEGREE (OIL PURITY) | \ | digital
TCS1.10MBX03CQ001_XG11 | 30169 | HYD OIL CONTAMINATION DEGREE (OIL PURITY) | \ | digital
TCS1.10MBX03EZ001_ZV02 | 30170 | HYD OIL LINE STATUS | \ | digital
TCS1.10MBX06AH001_YB01HW | 30171 | HYD OIL COOLER FAN |  | digital
TCS1.10MBX06CP001_XG51 | 30172 | HYD OIL FILTRATION LINE PRESSURE | \ | digital
TCS1.10MBX08CP001_XG52 | 30173 | HYD OIL COOLING LINE FILTER | \ | digital
TCS1.10MBX70CP001_XG01 | 30174 | HYD OIL FILTER STOP VLV ACTUATOR (PREMIX LINE) | \ | digital
TCS1.10MBX81CP001_XG01 | 30175 | HYD OIL FILTER PREMIX CV ACTUATOR | \ | digital
TCS1.10MBX90AA002A_YB11HW | 30176 | SOV A MBA41AA051 |  | digital
TCS1.10MBX90AA002A_ZV03 | 30177 | SOV A MBA41AA051 | \ | digital
TCS1.10MBX90AA002B_YB11HW | 30178 | SOV B MBA41AA051 |  | digital
TCS1.10MBX90AA002B_ZV03 | 30179 | SOV B MBA41AA051 | \ | digital
TCS1.10MBX91AA002A_YB11HW | 30180 | SOV A MBA42AA051 |  | digital
TCS1.10MBX91AA002A_ZV03 | 30181 | SOV A MBA42AA051 | \ | digital
TCS1.10MBX91AA002B_YB11HW | 30182 | SOV B MBA42AA051 |  | digital
TCS1.10MBX91AA002B_ZV03 | 30183 | SOV B MBA42AA051 | \ | digital
TCS1.10MBX92AA002A_YB11HW | 30184 | SOV A MBA43AA051 |  | digital
TCS1.10MBX92AA002A_ZV03 | 30185 | SOV A MBA43AA051 | \ | digital
TCS1.10MBX92AA002B_ZV03 | 30186 | SOV B MBA43AA051 | \ | digital
TCS1.10MBX93AA002A_YB11HW | 30187 | SOV A MBA44AA051 |  | digital
TCS1.10MBX93AA002A_ZV03 | 30188 | SOV A MBA44AA051 | \ | digital
TCS1.10MBX93AA002B_YB11HW | 30189 | SOV B MBA44AA051 |  | digital
TCS1.10MBX93AA002B_ZV03 | 30190 | SOV B MBA44AA051 | \ | digital
TCS1.10MBY00DU100_XK01 | 30191 | ~GT CONTROLLER | \ | digital
TCS1.10MBY00EY010_ZV01 | 30192 | FIRE PROTECTION GT | \ | digital
TCS1.10MBY10DE010_134664_OUT | 30193 | \ |  | digital
TCS1.10MBY10DE010_134666_ON | 30194 | \ |  | digital
TCS1.10MBY10DE010_711763_ON | 30195 | \ |  | digital
TCS1.10MBY10DE010_XA01 | 30196 | LOAD SETPOINT | \ | digital
TCS1.10MBY10DE010_XT61 | 30197 | \ |  | digital
TCS1.10MBY10DE050_PSFE_XT03 | 30198 | \ |  | digital
TCS1.10MBY10DT040_XT04 | 30199 | ~COMPR RA-C ON IGV | \ | digital
TCS1.10MBY10DT040_XT05 | 30200 | ~COOL AIR LMT CTRL ON IGV | \ | digital
TCS1.10MBY10DT040_ZV01 | 30201 | \ |  | digital
TCS1.10MBY10DT060_1PIV_OUT | 30202 | \ |  | digital
TCS1.10MBY10DU010_ZV01 | 30203 | \ |  | digital
TCS1.10MBY10DU050_128725_ON | 30204 | \ |  | digital
TCS1.10MBY10DU050_PSFE_XT03 | 30205 | ~PRIM FREQ INFL | \ | digital
TCS1.10MBY10DU050_XA01 | 30206 | SPEED/LOAD CTRL | \ | digital
TCS1.10MBY10DU050_XQ04 | 30207 | \ |  | digital
TCS1.10MBY10DU050_XQ05 | 30208 | \ |  | digital
TCS1.10MBY10DU050_XQ06 | 30209 | \ |  | digital
TCS1.10MBY10DU050_XT01 | 30210 | ~LOAD OP SPEED CTRL | \ | digital
TCS1.10MBY10DU050_XT02 | 30211 | ~LOAD OP LOAD CTRL | \ | digital
TCS1.10MBY10DU050_XT03 | 30212 | \ |  | digital
TCS1.10MBY10DU050_XT04 | 30213 | \ |  | digital
TCS1.10MBY10DU050_XT05 | 30214 | \ |  | digital
TCS1.10MBY10DU050_XT06 | 30215 | \ |  | digital
TCS1.10MBY10DU050_XT07 | 30216 | \ |  | digital
TCS1.10MBY10DU050_XT13 | 30217 | \ |  | digital
TCS1.10MBY10DU050_XT14 | 30218 | \ |  | digital
TCS1.10MBY10DU050_XT52 | 30219 | \ |  | digital
TCS1.10MBY10DU050_XT53 | 30220 | \ |  | digital
TCS1.10MBY10DU050_XT54 | 30221 | \ |  | digital
TCS1.10MBY10DU050_ZV02 | 30222 | SPEED/LOAD CTRL | \ | digital
TCS1.10MBY10DU060_XA03 | 30223 | \ |  | digital
TCS1.10MBY10DU060_XT03 | 30224 | COMBUSTION LOAD SETPOINT | \ | digital
TCS1.10MBY10DU060_XT04 | 30225 | COMBUSTION LOAD SETPOINT | \ | digital
TCS1.10MBY10DU060_XT05 | 30226 | ~RUN UP FUNCTION | \ | digital
TCS1.10MBY10DU060_XT06 | 30227 | COMBUSTION LOAD SETPOINT | \ | digital
TCS1.10MBY10DU060_XT07 | 30228 | ~OTC CONTROLLER | \ | digital
TCS1.10MBY10DU060_XT13 | 30229 | ~COMPR PRES RATIO LMT CTRL | \ | digital
TCS1.10MBY10DU060_XT14 | 30230 | ~COOLING AIR LMT CTRL | \ | digital
TCS1.10MBY10DU060_ZV03 | 30231 | COMBUSTION LOAD SETPOINT | \ | digital
TCS1.10MBY10DU090_XM63 | 30232 | \ |  | digital
TCS1.10MBY10EP801_ZV01 | 30233 | EQUIV OP HOURS | \ | digital
TCS1.10MBY10EU001_ZV99 | 30234 | GT UNLOAD | \ | digital
TCS1.10MYB00EU103_ZV13 | 30235 | MONIT COMM. AP2-AP1 | \ | digital
TCS1.10MYB00EU120_XA41 | 30236 | GT FAIL SAFE FUNCTIONS | \ | digital
TCS1.10MYB00EU120_ZV01 | 30237 | \ |  | digital
TCS1.10MYB01EC001_XA01 | 30238 | \ |  | digital
TCS1.10MYB01EC001_XA03 | 30239 | SGC GAS TURBINE | \ | digital
TCS1.10MYB01EC001_ZV01 | 30240 | SGC GAS TURBINE | \ | digital
TCS1.10MYB01EC001_ZV02 | 30241 | \ |  | digital
TCS1.10MYB01EC001_ZV20 | 30242 | \ |  | digital
TCS1.10MYB01EZ002_ZV01 | 30243 | GT TRIP CIRCUIT | \ | digital
TCS1.10MYB01EZ002_ZV10 | 30244 |  |  | digital
TCS1.10MYB01EZ141_XK01 | 30245 | TURB EXHAUST GAS TEMP HH | \ | digital
TCS1.10MYB01EZ201_COM | 30246 | HMI TRIP | \ | digital
TCS1.10MYB01EZ201_XA41 | 30247 | HMI TRIP | \ | digital
TCS1.10MYB01EZ201_ZV04A | 30248 | \ |  | digital
TCS1.10MYB01EZ201_ZV05A | 30249 | \ |  | digital
TCS1.10MYB01EZ201_ZV08A | 30250 | \ |  | digital
TCS1.10MYB01EZ201_ZV11A | 30251 | \ |  | digital
TCS1.10MYB01EZ201_ZV13A | 30252 | \ |  | digital
TCS1.10MYB01EZ201_ZV15A | 30253 | \ |  | digital
TCS1.10MYB01EZ201_ZV16A | 30254 | \ |  | digital
TCS1.10MYB01EZ201_ZV18A | 30255 | \ |  | digital
TCS1.10MYB01EZ201_ZV22A | 30256 | \ |  | digital
TCS1.10MYB01EZ902_ZV02 | 30257 | \ |  | digital
TCS1.10MYB01EZ902_ZV03 | 30258 | \ |  | digital
TCS1.10MYB01EZ902_ZV05 | 30259 | \ |  | digital
TCS1.10MYB01EZ902_ZV06 | 30260 | \ |  | digital
TCS1.10MYB01EZ902_ZV09 | 30261 | \ |  | digital
TCS1.10MYB01EZ902_ZV10 | 30262 | \ |  | digital
TCS1.10MYB01EZ902_ZV100 | 30263 | \ |  | digital
TCS1.10MYB01EZ902_ZV11 | 30264 | \ |  | digital
TCS1.10MYB01EZ902_ZV12 | 30265 | \ |  | digital
TCS1.10MYB01EZ902_ZV14 | 30266 | \ |  | digital
TCS1.10MYB01EZ902_ZV15 | 30267 | \ |  | digital
TCS1.10MYB01EZ902_ZV17 | 30268 | \ |  | digital
TCS1.10MYB01EZ902_ZV19 | 30269 | \ |  | digital
TCS1.10MYB01EZ902_ZV21 | 30270 | \ |  | digital
TCS1.10MYB01EZ902_ZV22 | 30271 | \ |  | digital
TCS1.10MYB01EZ902_ZV24 | 30272 | \ |  | digital
TCS1.10MYB01EZ902_ZV26 | 30273 | \ |  | digital
TCS1.10MYB01EZ902_ZV27 | 30274 | \ |  | digital
TCS1.10MYB01EZ902_ZV28 | 30275 | \ |  | digital
TCS1.10MYB01EZ902_ZV29 | 30276 | \ |  | digital
TCS1.10MYB01EZ902_ZV30 | 30277 | \ |  | digital
TCS1.10MYB01EZ902_ZV32 | 30278 | \ |  | digital
TCS1.10MYB01EZ902_ZV33 | 30279 | \ |  | digital
TCS1.10MYB01EZ902_ZV36 | 30280 | \ |  | digital
TCS1.10MYB01EZ902_ZV37 | 30281 | \ |  | digital
TCS1.10MYB01EZ902_ZV39 | 30282 | \ |  | digital
TCS1.10MYB01EZ902_ZV40 | 30283 | \ |  | digital
TCS1.10MYB01EZ902_ZV41 | 30284 | \ |  | digital
TCS1.10MYB01EZ902_ZV44 | 30285 | \ |  | digital
TCS1.10MYB01EZ902_ZV45 | 30286 | \ |  | digital
TCS1.10MYB01EZ902_ZV46 | 30287 | \ |  | digital
TCS1.10MYB01EZ902_ZV47 | 30288 | \ |  | digital
TCS1.10MYB01EZ902_ZV48 | 30289 | \ |  | digital
TCS1.10MYB01EZ902_ZV53 | 30290 | \ |  | digital
TCS1.10MYB01EZ902_ZV54 | 30291 | \ |  | digital
TCS1.10MYB01EZ902_ZV55 | 30292 | \ |  | digital
TCS1.10MYB01EZ902_ZV58 | 30293 | \ |  | digital
TCS1.10MYB01EZ902_ZV59 | 30294 | \ |  | digital
TCS1.10MYB01EZ902_ZV66 | 30295 | \ |  | digital
TCS1.10MYB01EZ902_ZV68 | 30296 | \ |  | digital
TCS1.10MYB01EZ902_ZV69 | 30297 | \ |  | digital
TCS1.10MYB01EZ902_ZV71 | 30298 | \ |  | digital
TCS1.10MYB01EZ902_ZV72 | 30299 | \ |  | digital
TCS1.10MYB01EZ902_ZV77 | 30300 | \ |  | digital
TCS1.10MYB01EZ902_ZV90 | 30301 | \ |  | digital
TCS1.10MYB01EZ902_ZV95 | 30302 | \ |  | digital
TCS1.10MYB01EZ902_ZV98 | 30303 | \ |  | digital
TCS1.10MYB01EZ902_ZV99 | 30304 | \ |  | digital
TCS1.10MYB10EU006_XA02 | 30305 | \ |  | digital
TCS1.10MYB10EU006_XT02 | 30306 | ~EXT LOAD SETPOINT ENABLED | \ | digital
TCS1.10SAM10AA001_XG01 | 30307 | GT ENC INLET FLAP 1 | \ | digital
TCS1.10SAM10AA002_XG01 | 30308 | GT ENC INLET FLAP 2 | \ | digital
TCS1.10SAM10AA003_XG01 | 30309 | GT ENC INLET FLAP 3 | \ | digital
TCS1.10SAM10AA004_XG01 | 30310 | GT ENC INLET FLAP 4 | \ | digital
TCS1.10SAM10AA005_XG01 | 30311 | GT ENC OUTLET FLAP 1 | \ | digital
TCS1.10SAM10AA006_XG01 | 30312 | GT ENC OUTLET FLAP 2 | \ | digital
TCS1.10SAM10AN001_XB01 | 30313 | GT ENC VENT FAN 1 | \ | digital
TCS1.10SAM10AN002_XB01 | 30314 | GT ENC VENT FAN 2 | \ | digital
TCS1.10SAM10AN003_XB01 | 30315 | GT ENC VENT FAN 3 | \ | digital
TCS1.10SAM10CF001_XG02 | 30316 | AIR FLOW ENC VENT | \ | digital
TCS1.10SAM10CF002_XG02 | 30317 | AIR FLOW ENC VENT | \ | digital
TCS1.10SAM10CF003_XG02 | 30318 | AIR FLOW ENC VENT | \ | digital
TCS1.10SAM10CP001_XG02 | 30319 | DP GT ENC VENT FAN 1 | \ | digital
TCS1.10SAM10CP002_XG02 | 30320 | DP GT ENC VENT FAN 2 | \ | digital
TCS1.10SAM10CP003_XG02 | 30321 | DP GT ENC VENT FAN 3 | \ | digital
TCS1.10SAM10EE010_SLC_ON | 30322 | \ |  | digital
TCS1.10SAM10EE010_PRESEL | 30323 | \ |  | digital
TCS1.10SAM10EE010_XA01 | 30324 | SLC GT ENC VENT M/A FLAP | \ | digital
TCS1.110MBP13EU010_193350_OUT | 30325 | \ |  | digital
TCS1.11AEA01GS001_XB02 | 30326 | HVCB | \ | digital
TCS1.11AYG02GT001_728751_ON | 30327 |  |  | digital
TCS1.11BAC01GS001_XB02 | 30328 | G.C.B. | \ | digital
TCS1.11BAC01GS002_XB02 | 30329 | EARTH DISC. SW. TRANSF. SIDE | \ | digital
TCS1.11BAC01GS003_XB02 | 30330 | EARTH DISC. SW. GEN. SIDE | \ | digital
TCS1.11BAC01GS004_MOTOR_XB02 | 30331 | SFC DISC SW MBM | \ | digital
TCS1.11BAC01GS008_XB02 | 30332 | LINE DISC. | \ | digital
TCS1.11BAW20GS301_MOTOR_RUNNING | 30333 | \ |  | digital
TCS1.11BAW20GS301_XB02 | 30334 | G.T.G. DISCONNECTOR | \ | digital
TCS1.11BBA10GS001_MOTOR_RUNNING | 30335 | \ |  | digital
TCS1.11BFA01EA001_453390_XB02 | 30336 | AUTO TRANSFER SWITCH | \ | digital
TCS1.11BFA01EA001_XB01 | 30337 | AUTO TRANSFER SWITCH | \ | digital
TCS1.11BFA01EA001_XB02 | 30338 | AUTO TRANSFER SWITCH | \ | digital
TCS1.11BFA01EG001_XB27 | 30339 | 380 BUS BAR | \ | digital
TCS1.11BFA02EA001_453390_XB02 | 30340 | AUTO TRANSFER SWITCH | \ | digital
TCS1.11BFA02EA001_XB01 | 30341 | AUTO TRANSFER SWITCH | \ | digital
TCS1.11BFA02EA001_XB02 | 30342 | AUTO TRANSFER SWITCH | \ | digital
TCS1.11BFA02EG001_XB27 | 30343 | 380 BUS BAR | \ | digital
TCS1.11BNA01EA001_XB01 | 30344 | ATD ACTION | \ | digital
TCS1.11BNA01EG003_453470_XB01 | 30345 | VT DISCONNECTOR | \ | digital
TCS1.11BNA01EG003_453471_XB01 | 30346 | DEVICE BLOCK OR ALARM SIGNAL | \ | digital
TCS1.11BNA01EG003_453472_XB01 | 30347 | LOSS OF DEVICE SUPPLY DC POWER | \ | digital
TCS1.11BNA01GS001A_XB02 | 30348 | EMCC INC CB A | \ | digital
TCS1.11BNA01GS001A_XB07 | 30349 | EMCC INC CB A | \ | digital
TCS1.11BNA01GS001B_XB02 | 30350 | EMCC INC CB B | \ | digital
TCS1.11BNA01GS001B_XB07 | 30351 | EMCC INC CB B | \ | digital
TCS1.11BRA01EG003_XB01 | 30352 | 220VAC 11BRA FEEDER | \ | digital
TCS1.11BUA01EG002_XB02 | 30353 | 110Vdc BUA INC. LINE BKR | \ | digital
TCS1.11MBA10EU010_ZV51 | 30354 | \ |  | digital
TCS1.11MBA10FS010_XT23A | 30355 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBA11CP001_XG01A | 30356 | \ |  | digital
TCS1.11MBA11CP002_XG01A | 30357 | \ |  | digital
TCS1.11MBA11CP003_XG01A | 30358 | \ |  | digital
TCS1.11MBJ10GT001_XB02 | 30359 | SFC FEEDER BKR | \ | digital
TCS1.11MBJ20EA001_XB01 | 30360 | SFC 1 IS ON | \ | digital
TCS1.11MBJ20EA001_XB02 | 30361 | SFC 1 IS OFF | \ | digital
TCS1.11MBJ20EA004_XB01 | 30362 | SFC 1 | \ | digital
TCS1.11MBJ20EA006_XB01 | 30363 | SFC X IS SELECTED BY UNIT X | \ | digital
TCS1.11MBJ20EA006_XB02 | 30364 | SFC X IS SELECTED BY OTHER UNIT | \ | digital
TCS1.11MBJ20EA007_XB01 | 30365 | SFC 1 STATUS | \ | digital
TCS1.11MBJ20EA007_XB02 | 30366 | SFC 1 STATUS | \ | digital
TCS1.11MBJ20EA011_XB01 | 30367 | SFC SPEED 2100 RPM REACHED | \ | digital
TCS1.11MBJ20EA013_XB01 | 30368 | SFC IS READY FOR OPERATION | \ | digital
TCS1.11MBJ20EA020_XB01 | 30369 | SFC MODE DIRECT STARTUP SELECTED | \ | digital
TCS1.11MBJ20EA021_XB01 | 30370 | SFC MODE PURGING SELECTED | \ | digital
TCS1.11MBJ20EA022_XB01 | 30371 | SFC MODE WASHING SELECTED | \ | digital
TCS1.11MBJ20EG001_XB01 | 30372 | SFC CUMULATIVE ALARM | \ | digital
TCS1.11MBJ20EZ001_XB01 | 30373 | SFC X | \ | digital
TCS1.11MBJ20GS002_XB02 | 30374 | SFC SW CROSS MBM03 | \ | digital
TCS1.11MBJ20GS003_XB02 | 30375 | SFC SW DIRECT MBM01 | \ | digital
TCS1.11MBM13CR900_ZV01 | 30376 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBN04DU001_ZV51A | 30377 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBN04DU001_ZV52A | 30378 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBN04DU001_ZV53A | 30379 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBP03DU001_ZV01A | 30380 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBP03DU001_ZV02A | 30381 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBP03DU001_ZV03A | 30382 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBP03DU900_ZV01 | 30383 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBR20CP001_XH03 | 30384 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBR20CP002_XH03 | 30385 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBR20CP003_XH03 | 30386 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBR20CP900_ZV01 | 30387 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MBX70AA001_ZV32FS | 30388 | \ |  | digital
TCS1.11MBX70AA001_ZV33FS | 30389 | \ |  | digital
TCS1.11MBX70AA031_ZV32FS | 30390 | \ |  | digital
TCS1.11MBX70AA031_ZV33FS | 30391 | \ |  | digital
TCS1.11MBX81AA002_ZV32FS | 30392 | \ |  | digital
TCS1.11MBX81AA002_ZV33FS | 30393 | \ |  | digital
TCS1.11MBX84AA001_ZV32FS | 30394 | \ |  | digital
TCS1.11MBX84AA001_ZV33FS | 30395 | \ |  | digital
TCS1.11MKA01CE005_XQ01 | 30396 | \ |  | digital
TCS1.11MKA01DE020_187610_COM | 30397 | BAC SELECTION | \ | digital
TCS1.11MKA01DE020_EN_SEL2 | 30398 | SEL BAC / AEA | \ | digital
TCS1.11MKA01DE020_XT01 | 30399 | AEA SELECTION | \ | digital
TCS1.11MKC10EA032_XB02 | 30400 | DE-EXC SWITCH | \ | digital
TCS1.11MKC10GT001_XB02 | 30401 | EXC FEEDER S201 BKR | \ | digital
TCS1.11MKC20EA001_453931_XB01 | 30402 | EXCITATION STATUS | \ | digital
TCS1.11MKC20EA001_XB01 | 30403 | EXCITATION STATUS | \ | digital
TCS1.11MKC20EA001_XB02 | 30404 | EXCITATION STATUS | \ | digital
TCS1.11MKC20EA014_XB01 | 30405 | EXCITATION MODE REG | \ | digital
TCS1.11MKC20EA014_XB02 | 30406 | EXCITATION MODE REG | \ | digital
TCS1.11MKC20EA014_XB03 | 30407 | EXCITATION MODE REG | \ | digital
TCS1.11MKC20EA020_XB01 | 30408 | ROTOR CURRENT LIMIT OPERATING | \ | digital
TCS1.11MKC20EA021_XB01 | 30409 | UNDER EXCIT LIMIT | \ | digital
TCS1.11MKC20EA023_XB01 | 30410 | V/Hz LIMIT | \ | digital
TCS1.11MKC20EA026_XB01 | 30411 | EXC LOC/REM | \ | digital
TCS1.11MKC20EA029_452005_ON | 30412 |  |  | digital
TCS1.11MKC20EA029_XB01 | 30413 | POWER SYSTEM STABILIZER | \ | digital
TCS1.11MKC20EA029_XB02 | 30414 | POWER SYSTEM STABILIZER | \ | digital
TCS1.11MKC20EA033_XB01 | 30415 | EXCITATION SELECTED BY SFC | \ | digital
TCS1.11MKC20EU001_ZV01 | 30416 | EXCITATION ON/OFF CMD | \ | digital
TCS1.11MKC20EU002_PRESEL_SEL3 | 30417 |  |  | digital
TCS1.11MKC20EU002_XQ01 | 30418 | \ |  | digital
TCS1.11MKC20EU005_ZV01 | 30419 | AVR REF. UP-DOWN | \ | digital
TCS1.11MKC20EU005_ZV02 | 30420 | AVR REF. UP-DOWN | \ | digital
TCS1.11MKC20EU007_117650_ON | 30421 |  |  | digital
TCS1.11MKC20EU007_COM | 30422 | ZERO REACTIVE POWER REQUEST | \ | digital
TCS1.11MKC20EZ001_XB01 | 30423 | EXCITATION TRIP | \ | digital
TCS1.11MKC20GT001_XB01 | 30424 | EXC FEEDER S102 BKR (STARTUP EXC) | \ | digital
TCS1.11MKC20GT002_XB28 | 30425 | ESC FEEDER S103 CLOSED | \ | digital
TCS1.11MKC30GT001_XB01HW | 30426 | EXC FEEDER BRK CLOSED S104 (FILED FLUSHING EXC |  | digital
TCS1.11MKD12CY021A_XQ01 | 30427 | \ |  | digital
TCS1.11MKD13EZ002_XK01 | 30428 | GEN COLLECTOR SIDE BEARING TEMP | \ | digital
TCS1.11MKF00EU001_ZV01 | 30429 | \ |  | digital
TCS1.11MKF05CL101_XG52 | 30430 | \ |  | digital
TCS1.11MKF05CP001_XG02 | 30431 | P WATER TANK | \ | digital
TCS1.11MKF10EE001_XA01 | 30432 | \ |  | digital
TCS1.11MKF11AP001_XB01 | 30433 | PRIMARY WTR PUMP 1 | \ | digital
TCS1.11MKF11CP001_XG02 | 30434 | P D/STR PRIM WTR PUMP1 | \ | digital
TCS1.11MKF12AP001_XB01 | 30435 | PRIMARY WTR PUMP 2 | \ | digital
TCS1.11MKF12CP001_XG02 | 30436 | P D/STR PRIM WTR PUMP2 | \ | digital
TCS1.11MKF16CP001_XG02 | 30437 | DP U/S FILTER | \ | digital
TCS1.11MKF23CQ101_XH01 | 30438 | CONDUCT TREATMENT LOOP | \ | digital
TCS1.11MKF30CP101_XH01 | 30439 | DP STATOR WINDING | \ | digital
TCS1.11MKF30EU001_XA01 | 30440 | STATOR COIL DIFF PRESSURE | \ | digital
TCS1.11MKF30EU001_XA02 | 30441 | STATOR COIL DIFF PRESSURE | \ | digital
TCS1.11MKF30EU001_XA03 | 30442 | STATOR COIL DIFF PRESSURE | \ | digital
TCS1.11MKF30EU001_XK01 | 30443 | STATOR COIL DIFF PRESSURE | \ | digital
TCS1.11MKF31CP001_XG02_XG02 | 30444 | P H2 TO WATER | \ | digital
TCS1.11MKG24CF101_XH01 | 30445 | M/U H2 FLOW | \ | digital
TCS1.11MKG24CF101_XH02 | 30446 | \ |  | digital
TCS1.11MKG26CP101_ZV01 | 30447 | PRES H2 GEN CASING | \ | digital
TCS1.11MKG30CQ901_XH01 | 30448 | H2 GAS PURITY ANALYZER | \ | digital
TCS1.11MKG30CQ901_ZV01 | 30449 |  |  | digital
TCS1.11MKG32CQ401_XG51 | 30450 | OVERHEATING MONITOR | \ | digital
TCS1.11MKG41CL001_XG01 | 30451 | \ |  | digital
TCS1.11MKG42CL001_XG01 | 30452 | \ |  | digital
TCS1.11MKG43CL001_XG01 | 30453 | \ |  | digital
TCS1.11MKG44CL001_XG01 | 30454 | \ |  | digital
TCS1.11MKG51AN001_47935_OUT | 30455 |  |  | digital
TCS1.11MKG51AN001_MOTOR_RUNNING | 30456 |  |  | digital
TCS1.11MKG51AN001_47935 | 30457 | \ |  | digital
TCS1.11MKG52AT001_MOTOR_RUNNING | 30458 |  |  | digital
TCS1.11MKW01CL001_XG52 | 30459 | \ |  | digital
TCS1.11MKW06CL001_XG52 | 30460 | \ |  | digital
TCS1.11MKW07CL001_XG02 | 30461 | L DEFOAMING TANK EE | \ | digital
TCS1.11MKW08CL001_XG02 | 30462 | L DEFOAMING TANK TE | \ | digital
TCS1.11MKW11AP001_XB01 | 30463 | ~AIR SEAL OIL PUMP 1 | \ | digital
TCS1.11MKW11CP001_XG01 | 30464 | PRES D/STR SO PUMP 1 | \ | digital
TCS1.11MKW11EE001_XA01 | 30465 | \ |  | digital
TCS1.11MKW11EU001_ZV01 | 30466 | \ |  | digital
TCS1.11MKW12AP001_XB01 | 30467 | ~AIR SEAL OIL PUMP 2 | \ | digital
TCS1.11MKW12CP001_XG01 | 30468 | PRES D/STR SO PUMP 2 | \ | digital
TCS1.11MKW13AP001_XB01 | 30469 | SEAL OIL PUMP 3 | \ | digital
TCS1.11MKW13AP001_ZV02 | 30470 | \ |  | digital
TCS1.11MKW13CP001_XG01 | 30471 | PRES D/STR SEAL OIL PUMP 3 | \ | digital
TCS1.11MKW17CP001_XG01 | 30472 | DP SEAL OIL FILTER AIR SIDE | \ | digital
TCS1.11MKW19CP001_XG51 | 30473 | PRES SEAL OIL FOR DC PUMP | \ | digital
TCS1.11MKW21EE001_XA01 | 30474 | \ |  | digital
TCS1.11MKW25AP001_XB01 | 30475 | ~H2 GAS SEAL OIL PUMP 1 | \ | digital
TCS1.11MKW25CP001_XG01 | 30476 | PRES D/STR SO PUMP 4 | \ | digital
TCS1.11MKW26AP001_XB01 | 30477 | ~H2 GAS SEAL OIL PUMP 2 | \ | digital
TCS1.11MKW26CP001_XG01 | 30478 | PRES D/STR SO PUMP 5 | \ | digital
TCS1.11MKW30CP001_XG01 | 30479 | DP SEAL OIL FILTER GAS SIDE | \ | digital
TCS1.11MKW30CQ901_XM71 | 30480 | \ |  | digital
TCS1.11MKW50EE001_DCO_SEL1 | 30481 | \ |  | digital
TCS1.11MKW50EE001_XA01 | 30482 | SLC BRG CHMB EXH BLWR | \ | digital
TCS1.11MKW51AN001_MOTOR_RUNNING | 30483 | \ |  | digital
TCS1.11MKW51AN001_XB01 | 30484 | GEN EXH BLWR 1 | \ | digital
TCS1.11MKW52AN001_XB01 | 30485 | GEN EXH BLWR 2 | \ | digital
TCS1.11MKW52AT001_MOTOR_RUNNING | 30486 | \ |  | digital
TCS1.11MKY01EU003_ZV01 | 30487 | RESYNCH SELECT | \ | digital
TCS1.11MKY01EZ112_XB01A | 30488 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MKY01EZ212_XB01A | 30489 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MKY01EZ900_ZV01 | 30490 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYA01EA001_SEL2 | 30491 | SYNCH MODE SELECT | \ | digital
TCS1.11MYA01EA001_YB01 | 30492 | \ |  | digital
TCS1.11MYA01EA001_ZV01 | 30493 | SEMI-AUTO SYNCH | \ | digital
TCS1.11MYA01EA001_ZV03 | 30494 |  |  | digital
TCS1.11MYA01EA001_ZV04 | 30495 | \ |  | digital
TCS1.11MYA01EA001_ZV11 | 30496 | SYNCHRO AUTOSTOP P31CBP01 | \ | digital
TCS1.11MYA01EA002_XB01 | 30497 | INPUT FROM SYNCHRO. | \ | digital
TCS1.11MYA01EA020_XB02 | 30498 | INPUT FROM SYNCHRO. | \ | digital
TCS1.11MYA01EA099_XB01 | 30499 | INPUT FROM SYNCHRO. | \ | digital
TCS1.11MYA02EA001_COM | 30500 | SYNCHRO AUTOSTOP P31CBP01 | \ | digital
TCS1.11MYB00EU110_ZV90A | 30501 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB00EU110_ZV92A | 30502 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB00EU110_ZV99A | 30503 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB00EU902_ZV01 | 30504 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB00EY011_XG01A | 30505 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB00EY013_XG01A | 30506 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB00EY202_XG02A | 30507 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB00EY900_ZV01 | 30508 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB01EE200_ZV02 | 30509 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB01EU002_ZV10 | 30510 | OVERSPEED MANUAL TEST TO BRAUN | \ | digital
TCS1.11MYB01EU002_ZV90 | 30511 | RESET PASSIVATION TRIP DO | \ | digital
TCS1.11MYB01EU002_ZV91 | 30512 | RESET PASSIVATION | \ | digital
TCS1.11MYB01EU002_ZV99 | 30513 | RESET BRAUN | \ | digital
TCS1.11MYB10CS902_ZV01 | 30514 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11MYB10CS902_ZV02 | 30515 | DI FROM SIL3 SYSTEM | \ | digital
TCS1.11SAM10EE005_ZV51 | 30516 | ENCLOSURE VENT TRIP CIRCUIT | \ | digital
TCS2.20CJA01DE002_XQ01 | 30517 | EXTERNAL LOAD REFERENCE CH1 | MW | float32
TCS2.20CJA01DE003_XQ01 | 30518 | EXTERNAL LOAD REFERENCE CH2 | MW | float32
TCS2.20EKG01C2H6_XQ01 | 30519 | ETHANE (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01C3H8_XQ01 | 30520 | PROPANE (GAS CROM. MODBUS) | mol% | float32
TCS2.20EKG01C6H14_XQ01 | 30521 | SUM OF C6+ (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01CF_XQ01 | 30522 | DATA FROM GAS CROMATOGRAPH | % | float32
TCS2.20EKG01CH4_XQ01 | 30523 | METHANE (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01CO2_XQ01 | 30524 | CARBON DIOXIDE (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01CP_XQ01 | 30525 | DATA FROM GAS CROMATOGRAPH | kPa | float32
TCS2.20EKG01GD1_XQ01 | 30526 | GAS DENSITY (GAS CHROM. MODBUS) | kg/m? | float32
TCS2.20EKG01HV1_XQ01 | 30527 | HEAT VALUE (GAS CHROM. MODBUS) | Kg/m? | float32
TCS2.20EKG01IC4H10_XQ01 | 30528 | i-BUTANE (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01IC5H12_XQ01 | 30529 | i-PENTANE (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01ICV_XQ01 | 30530 | ICV (GAS CHROM. MODBUS) | MJ/m? | float32
TCS2.20EKG01N2_XQ01 | 30531 | NITROGEN (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01NC4H10_XQ01 | 30532 | n-BUTANE (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01NC5H12_XQ01 | 30533 | n-PENTANE (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01NEC5H12_XQ01 | 30534 | neo-PENTANE (GAS CHROM. MODBUS) | mol% | float32
TCS2.20EKG01OT_XQ01 | 30535 | DATA FROM GAS CROMATOGRAPH | °C | float32
TCS2.20EKG01RDHE1_XQ01 | 30536 | DATA FROM GAS CROMATOGRAPH | p.u. | float32
TCS2.20EKG01TR_XQ01 | 30537 | DATA FROM GAS CROMATOGRAPH | mol% | float32
TCS2.20EKG01WI1_XQ01 | 30538 | WOBBE INDEX (GAS CROM. MODBUS) | MJ/m? | float32
TCS2.20EKG10CQ902_PCIRED | 30539 | GAS COMPOSITION | Kg/s | float32
TCS2.20EKG10CQ902_WOBBERED | 30540 | GAS COMPOSITION | Kg/s | float32
TCS2.20EKG10CQ902_XQ01 | 30541 | GAS COMPOSITION | °C | float32
TCS2.20EKG10CQ902_XQ02 | 30542 | GAS DENSITY | Kg/m? | float32
TCS2.20EKG10CQ902_XQ10 | 30543 | CALC. WOBBE INDEX |  | float32
TCS2.20EKG12CQ102_XQ01 | 30544 | SUM OF C6+ (PV1 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ02 | 30545 | PROPANE (PV2 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ03 | 30546 | i-BUTANE (PV3 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ04 | 30547 | n-BUTANE (PV4 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ05 | 30548 | neo-PENTANE (PV5 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ06 | 30549 | i-PENTANE (PV6 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ07 | 30550 | n-PENTANE (PV7 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ08 | 30551 | NITROGEN (PV8 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ09 | 30552 | METHANE (PV9 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ10 | 30553 | CARBON DIOXIDE (PV10 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ11 | 30554 | ETHANE (PV11 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ12 | 30555 | HEAT VALUE (PV12 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ13 | 30556 | GAS DENSITY (PV13 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ14 | 30557 | WOBBE INDEX (PV14 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ15 | 30558 | COMPRESSIBILITY FACTOR (PV15 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ16 | 30559 | TOTAL OF RAW CONCENTRATIONS (PV16 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ17 | 30560 | OVEN TEMP (PV17 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ18 | 30561 | CARRIER GAS PRESS (PV18 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ19 | 30562 | ICV (PV19 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG12CQ102_XQ20 | 30563 | RELATIVE DENSITY (PV20 - GAS CHROMATOGRAPH) |  | float32
TCS2.20EKG60FF001_XQ01 | 30564 |  |  | float32
TCS2.20EKG70CP101_XQ01 | 30565 | PRESSURE SIGNAL FLOW METER | bar | float32
TCS2.20EKG70CT101_XQ01 | 30566 | TEMP. GAS BEFORE ESV | °C | float32
TCS2.20MBA10CG101_XQ01 | 30567 | ROTOR AXIAL DISPLACEMENT CH A | mm | float32
TCS2.20MBA10CG102_XQ01 | 30568 | ROTOR AXIAL DISPLACEMENT CH B | mm | float32
TCS2.20MBA10CS101_XQ01 | 30569 | TURBINE SPEED 1 | s-1 | float32
TCS2.20MBA10CS102_XQ01 | 30570 | TURBINE SPEED 2 | s-1 | float32
TCS2.20MBA10CS103_XQ01 | 30571 | TURBINE SPEED 3 | s-1 | float32
TCS2.20MBA10FG100_ZQ01 | 30572 | ROTOR AXIAL DISPLACEMENT | mm | float32
TCS2.20MBA11CP101_XQ01 | 30573 | ABS COMPRESSOR AIR INLET PRESS 1 | mbar | float32
TCS2.20MBA11CT101A_XQ01 | 30574 | COMPRESSOR AIR INLET TEMP A 1 | °C | float32
TCS2.20MBA11CT101B_XQ11 | 30575 | COMPRESSOR AIR INLET TEMP B 1 | °C | float32
TCS2.20MBA11CT102A_XQ01 | 30576 | COMPRESSOR AIR INLET TEMP A 2 | °C | float32
TCS2.20MBA11CT102B_XQ11 | 30577 | COMPRESSOR AIR INLET TEMP B 2 | °C | float32
TCS2.20MBA11CT103A_XQ01 | 30578 | COMPRESSOR AIR INLET TEMP A 3 | °C | float32
TCS2.20MBA11CT103B_XQ11 | 30579 | COMPRESSOR AIR INLET TEMP B 3 | °C | float32
TCS2.20MBA11CT104A_XQ01 | 30580 | COMPRESSOR AIR INLET TEMP A 4 | °C | float32
TCS2.20MBA11CT104B_XQ11 | 30581 | COMPRESSOR AIR INLET TEMP B 4 | °C | float32
TCS2.20MBA11CT901_ZQ01 | 30582 | COMPRESSOR AIR INLET TEMP |  | float32
TCS2.20MBA11CT901_ZQ11 | 30583 | COMPRESSOR AIR INLET TEMP |  | float32
TCS2.20MBA12CP101_XQ01 | 30584 | COMPRESSOR AIR DISCHARGE PRESS 1 | bar | float32
TCS2.20MBA12CP102_XQ01 | 30585 | COMPRESSOR AIR DISCHARGE PRESS 2 | bar | float32
TCS2.20MBA12CT101A_XQ01 | 30586 | COMPRESSOR AIR DISCHARGE TEMP A 1 | °C | float32
TCS2.20MBA12CT101B_XQ11 | 30587 | COMPRESSOR AIR DISCHARGE TEMP B 1 | °C | float32
TCS2.20MBA12CT102A_XQ01 | 30588 | COMPRESSOR AIR DISCHARGE TEMP A 2 | °C | float32
TCS2.20MBA12CT102B_XQ11 | 30589 | COMPRESSOR AIR DISCHARGE TEMP B 2 | °C | float32
TCS2.20MBA12CT103A_XQ01 | 30590 | COMPRESSOR AIR DISCHARGE TEMP A 3 | °C | float32
TCS2.20MBA12CT103B_XQ11 | 30591 | COMPRESSOR AIR DISCHARGE TEMP B 3 | °C | float32
TCS2.20MBA12CT901_ZQ01 | 30592 | COMPRESSOR AIR DISCHARGE TEMP | °C | float32
TCS2.20MBA12FP100_ZQ03 | 30593 | COMPRESSOR AIR DISCHARGE PRESS | bar | float32
TCS2.20MBA25CT101_XQ01 | 30594 | DRAIN LINES HEADER TEMP | C | float32
TCS2.20MBA26CT101A_XQ01 | 30595 | TURBINE EXHAUST GAS TEMP A 1 | °C | float32
TCS2.20MBA26CT101B_XQ11 | 30596 | TURBINE EXHAUST GAS TEMP B 1 | °C | float32
TCS2.20MBA26CT102A_XQ01 | 30597 | TURBINE EXHAUST GAS TEMP A 2 | °C | float32
TCS2.20MBA26CT102B_XQ11 | 30598 | TURBINE EXHAUST GAS TEMP B 2 | °C | float32
TCS2.20MBA26CT103A_XQ01 | 30599 | TURBINE EXHAUST GAS TEMP A 3 | °C | float32
TCS2.20MBA26CT103B_XQ11 | 30600 | TURBINE EXHAUST GAS TEMP B 3 | °C | float32
TCS2.20MBA26CT104A_XQ01 | 30601 | TURBINE EXHAUST GAS TEMP A 4 | °C | float32
TCS2.20MBA26CT104B_XQ11 | 30602 | TURBINE EXHAUST GAS TEMP B 4 | °C | float32
TCS2.20MBA26CT105A_XQ01 | 30603 | TURBINE EXHAUST GAS TEMP A 5 | °C | float32
TCS2.20MBA26CT105B_XQ11 | 30604 | TURBINE EXHAUST GAS TEMP B 5 | °C | float32
TCS2.20MBA26CT106A_XQ01 | 30605 | TURBINE EXHAUST GAS TEMP A 6 | °C | float32
TCS2.20MBA26CT106B_XQ11 | 30606 | TURBINE EXHAUST GAS TEMP B 6 | °C | float32
TCS2.20MBA26CT107A_XQ01 | 30607 | TURBINE EXHAUST GAS TEMP A 7 | °C | float32
TCS2.20MBA26CT107B_XQ11 | 30608 | TURBINE EXHAUST GAS TEMP B 7 | °C | float32
TCS2.20MBA26CT108A_XQ01 | 30609 | TURBINE EXHAUST GAS TEMP A 8 | °C | float32
TCS2.20MBA26CT108B_XQ11 | 30610 | TURBINE EXHAUST GAS TEMP B 8 | °C | float32
TCS2.20MBA26CT109A_XQ01 | 30611 | TURBINE EXHAUST GAS TEMP A 9 | °C | float32
TCS2.20MBA26CT109B_XQ11 | 30612 | TURBINE EXHAUST GAS TEMP B 9 | °C | float32
TCS2.20MBA26CT110A_XQ01 | 30613 | TURBINE EXHAUST GAS TEMP A 10 | °C | float32
TCS2.20MBA26CT110B_XQ11 | 30614 | TURBINE EXHAUST GAS TEMP B 10 | °C | float32
TCS2.20MBA26CT111A_XQ01 | 30615 | TURBINE EXHAUST GAS TEMP A 11 | °C | float32
TCS2.20MBA26CT111B_XQ11 | 30616 | TURBINE EXHAUST GAS TEMP B 11 | °C | float32
TCS2.20MBA26CT112A_XQ01 | 30617 | TURBINE EXHAUST GAS TEMP A 12 | °C | float32
TCS2.20MBA26CT112B_XQ11 | 30618 | TURBINE EXHAUST GAS TEMP B 12 | °C | float32
TCS2.20MBA26CT113A_XQ01 | 30619 | TURBINE EXHAUST GAS TEMP A 13 | °C | float32
TCS2.20MBA26CT113B_XQ11 | 30620 | TURBINE EXHAUST GAS TEMP B 13 | °C | float32
TCS2.20MBA26CT114A_XQ01 | 30621 | TURBINE EXHAUST GAS TEMP A 14 | °C | float32
TCS2.20MBA26CT114B_XQ11 | 30622 | TURBINE EXHAUST GAS TEMP B 14 | °C | float32
TCS2.20MBA26CT115A_XQ01 | 30623 | TURBINE EXHAUST GAS TEMP A 15 | °C | float32
TCS2.20MBA26CT115B_XQ11 | 30624 | TURBINE EXHAUST GAS TEMP B 15 | °C | float32
TCS2.20MBA26CT116A_XQ01 | 30625 | TURBINE EXHAUST GAS TEMP A 16 | °C | float32
TCS2.20MBA26CT116B_XQ11 | 30626 | TURBINE EXHAUST GAS TEMP B 16 | °C | float32
TCS2.20MBA26CT117A_XQ01 | 30627 | TURBINE EXHAUST GAS TEMP A 17 | °C | float32
TCS2.20MBA26CT117B_XQ11 | 30628 | TURBINE EXHAUST GAS TEMP B 17 | °C | float32
TCS2.20MBA26CT118A_XQ01 | 30629 | TURBINE EXHAUST GAS TEMP A 18 | °C | float32
TCS2.20MBA26CT118B_XQ11 | 30630 | TURBINE EXHAUST GAS TEMP B 18 | °C | float32
TCS2.20MBA26CT119A_XQ01 | 30631 | TURBINE EXHAUST GAS TEMP A 19 | °C | float32
TCS2.20MBA26CT119B_XQ11 | 30632 | TURBINE EXHAUST GAS TEMP B 19 | °C | float32
TCS2.20MBA26CT120A_XQ01 | 30633 | TURBINE EXHAUST GAS TEMP A 20 | °C | float32
TCS2.20MBA26CT120B_XQ11 | 30634 | TURBINE EXHAUST GAS TEMP B 20 | °C | float32
TCS2.20MBA26CT121A_XQ01 | 30635 | TURBINE EXHAUST GAS TEMP A 21 | °C | float32
TCS2.20MBA26CT121B_XQ11 | 30636 | TURBINE EXHAUST GAS TEMP B 21 | °C | float32
TCS2.20MBA26CT122A_XQ01 | 30637 | TURBINE EXHAUST GAS TEMP A 22 | °C | float32
TCS2.20MBA26CT122B_XQ11 | 30638 | TURBINE EXHAUST GAS TEMP B 22 | °C | float32
TCS2.20MBA26CT123A_XQ01 | 30639 | TURBINE EXHAUST GAS TEMP A 23 | °C | float32
TCS2.20MBA26CT123B_XQ11 | 30640 | TURBINE EXHAUST GAS TEMP B 23 | °C | float32
TCS2.20MBA26CT124A_XQ01 | 30641 | TURBINE EXHAUST GAS TEMP A 24 | °C | float32
TCS2.20MBA26CT124B_XQ11 | 30642 | TURBINE EXHAUST GAS TEMP B 24 | °C | float32
TCS2.20MBA26CT900_ZQ01 | 30643 | TURBINE EXHAUST GAS TEMP | ?C | float32
TCS2.20MBA26CT901_OUT | 30644 | MAX TURBINE EXHAUST GAS TEMP | °C | float32
TCS2.20MBA26CT901_XQ04 | 30645 | MAX TURBINE EXHAUST GAS TEMP | °C | float32
TCS2.20MBA26CT901_ZQ01 | 30646 | MAX TURBINE EXHAUST GAS TEMP | °C | float32
TCS2.20MBA26CT902_OUT | 30647 | SPREAD AVG MIN | °C | float32
TCS2.20MBA26CT902_XQ04 | 30648 | MIN TURBINE EXHAUST GAS TEMP | °C | float32
TCS2.20MBA26CT902_ZQ01 | 30649 | MIN TURBINE EXHAUST GAS TEMP | °C | float32
TCS2.20MBA26FT901_TRIP VAL_ZQ03 | 30650 | CALC TURB OT | °C | float32
TCS2.20MBA26FT901_WARN VAL_ZQ02 | 30651 | CALC TURB OT | °C | float32
TCS2.20MBA26FT901_ATK | 30652 | CALC TURB OT |  | float32
TCS2.20MBA50EU001_ZQ01 | 30653 | MAIN FLUSH CTRL | min | float32
TCS2.20MBA51AP001_DCO | 30654 | RDS PUMP 1 |  | float32
TCS2.20MBA51AP002_DCO | 30655 | RDS PUMP 2 |  | float32
TCS2.20MBA51CP101_XQ01 | 30656 | RDS FEED LINE PRESSURE | bar | float32
TCS2.20MBA51CP102_XQ01 | 30657 | RDS FEED LINE PRESSURE | bar | float32
TCS2.20MBA51CP103_XQ01 | 30658 | RDS FEED LINE PRESSURE | bar | float32
TCS2.20MBA51FP100_ZQ01 | 30659 | RDS SYSTEM PRES | Bar | float32
TCS2.20MBA53CP101_XQ01 | 30660 | RDS MAIN CH RETURN PRESSURE | bar | float32
TCS2.20MBA53CP102_XQ01 | 30661 | RDS MAIN CH RETURN PRESSURE | bar | float32
TCS2.20MBA53CP103_XQ01 | 30662 | RDS SECOND CH RETURN PRESSURE | bar | float32
TCS2.20MBA53CP104_XQ01 | 30663 | RDS SECOND CH RETURN PRESSURE | bar | float32
TCS2.20MBA53CP105_XQ01 | 30664 | RDS MAIN CH RETURN PRESSURE | bar | float32
TCS2.20MBA53CP106_XQ01 | 30665 | RDS SECOND CH RETURN PRESSURE | bar | float32
TCS2.20MBA53FP101_ZQ01 | 30666 | MAIN RETURN LINE PRESS | Bar | float32
TCS2.20MBA53FP102_ZQ01 | 30667 | SEC RETURN LINE PRESS | Bar | float32
TCS2.20MBD11CT101A_XQ01 | 30668 | TURBINE BEARING TEMP | °C | float32
TCS2.20MBD11CT101B_XQ11 | 30669 | TURBINE BEARING TEMP | °C | float32
TCS2.20MBD11CT101C_XQ21 | 30670 | TURBINE BEARING TEMP | °C | float32
TCS2.20MBD11CT102A_XQ01 | 30671 | TURBINE BEARING TEMP | °C | float32
TCS2.20MBD11CT102B_XQ11 | 30672 | TURBINE BEARING TEMP | °C | float32
TCS2.20MBD11CT102C_XQ21 | 30673 | TURBINE BEARING TEMP | °C | float32
TCS2.20MBD11CY101_XQ01 | 30674 | TURBINE SIDE BEARING ABS VIBR CH. A | mm/s | float32
TCS2.20MBD11CY102_XQ01 | 30675 | TURBINE SIDE BEARING ABS VIBR CH. B | mm/s | float32
TCS2.20MBD11CY940_XQ01 | 30676 | TURBINE SIDE BEARING REL VIBR Smax CH. | ?m res | float32
TCS2.20MBD12CT101A_XQ01 | 30677 | COMPRESSOR BEARING TEMP | °C | float32
TCS2.20MBD12CT101B_XQ11 | 30678 | COMPRESSOR BEARING TEMP | °C | float32
TCS2.20MBD12CT101C_XQ21 | 30679 | COMPRESSOR BEARING TEMP | °C | float32
TCS2.20MBD12CT102A_XQ01 | 30680 | COMP. THRUST BEARING TEMP GEN UPPER PART | °C | float32
TCS2.20MBD12CT102B_XQ11 | 30681 | COMP. THRUST BEARING TEMP GEN UPPER PART | °C | float32
TCS2.20MBD12CT103A_XQ01 | 30682 | COMP. THRUST BEARING TEMP GEN LOWER PART | °C | float32
TCS2.20MBD12CT103B_XQ11 | 30683 | COMP. THRUST BEARING TEMP GEN LOWER PART | °C | float32
TCS2.20MBD12CT104A_XQ01 | 30684 | COMP. THRUST BEARING TEMP COMP UPPER PART | °C | float32
TCS2.20MBD12CT104B_XQ11 | 30685 | COMP. THRUST BEARING TEMP COMP UPPER PART | °C | float32
TCS2.20MBD12CT105A_XQ01 | 30686 | COMP. THRUST BEARING TEMP COMP LOWER PART | °C | float32
TCS2.20MBD12CT105B_XQ11 | 30687 | COMP. THRUST BEARING TEMP COMP LOWER PART | °C | float32
TCS2.20MBD12CT112A_XQ01 | 30688 | COMP. THRUST BEARING TEMP GEN UPPER PART | °C | float32
TCS2.20MBD12CT112B_XQ11 | 30689 | COMP. THRUST BEARING TEMP GEN UPPER PART | °C | float32
TCS2.20MBD12CT113A_XQ01 | 30690 | COMP. THRUST BEARING TEMP GEN LOWER PART | °C | float32
TCS2.20MBD12CT113B_XQ11 | 30691 | COMP. THRUST BEARING TEMP GEN LOWER PART | °C | float32
TCS2.20MBD12CT114A_XQ01 | 30692 | COMP. THRUST BEARING TEMP COMP UPPER PART | °C | float32
TCS2.20MBD12CT114B_XQ11 | 30693 | COMP. THRUST BEARING TEMP COMP UPPER PART | °C | float32
TCS2.20MBD12CT115A_XQ01 | 30694 | COMP. THRUST BEARING TEMP COMP LOWER PART | °C | float32
TCS2.20MBD12CT115B_XQ11 | 30695 | COMP. THRUST BEARING TEMP COMP LOWER PART | °C | float32
TCS2.20MBD12CY101_XQ01 | 30696 | COMP SIDE BEARING ABS VIBR CH. A | mm/s | float32
TCS2.20MBD12CY102_XQ01 | 30697 | COMP SIDE BEARING ABS VIBR CH. B | mm/s | float32
TCS2.20MBD12CY115_XQ01 | 30698 | Compressor Secondary Thrust Bearing Load Cell Upper Part | kN | float32
TCS2.20MBD12CY116_XQ01 | 30699 | Compressor Secondary Thrust Bearing Load Cell Upper Part | kN | float32
TCS2.20MBD12CY117_XQ01 | 30700 | Compressor Secondary Thrust Bearing Load Cell Upper Part | kN | float32
TCS2.20MBD12CY118_XQ01 | 30701 | Compressor Secondary Thrust Bearing Load Cell Upper Part | kN | float32
TCS2.20MBD12CY125_XQ01 | 30702 | Compressor Main Thrust Bearing Load Cell Upper Part | kN | float32
TCS2.20MBD12CY126_XQ01 | 30703 | Compressor Main Thrust Bearing Load Cell Upper Part | kN | float32
TCS2.20MBD12CY127_XQ01 | 30704 | Compressor Main Thrust Bearing Load Cell Upper Part | kN | float32
TCS2.20MBD12CY128_XQ01 | 30705 | Compressor Main Thrust Bearing Load Cell Upper Part | kN | float32
TCS2.20MBD12CY940_XQ01 | 30706 | COMP SIDE BEARING REL VIBR Smax CH. OK | ?m res | float32
TCS2.20MBH22AA101_XQ01 | 30707 | COOL AIR DAMPER 1 STAGE 2 | % | float32
TCS2.20MBH22AA101_YQ01 | 30708 | COOL AIR DAMPER 1 STAGE 2 | % | float32
TCS2.20MBH22AA102_PID | 30709 | COOL AIR DAMPER 2 STAGE 2 | % | float32
TCS2.20MBH22AA102_XQ01 | 30710 | COOL AIR DAMPER 2 STAGE 2 | % | float32
TCS2.20MBH22AA102_YQ01 | 30711 | COOL AIR DAMPER 2 STAGE 2 | % | float32
TCS2.20MBH22CP102_XQ01 | 30712 | COOL AIR DAMPER STAGE 2 PRESSURE | bar | float32
TCS2.20MBH22CP103_XQ01 | 30713 | COOL AIR DAMPER STAGE 2 PRESSURE | bar | float32
TCS2.20MBH22CP104_XQ01 | 30714 | COOL AIR DAMPER STAGE 2 PRESSURE | bar | float32
TCS2.20MBH22DP100_912339_OUT | 30715 | COOLING AIR PRESS GV2 PV |  | float32
TCS2.20MBH22DP100_XD | 30716 | COOLING AIR PRESS GV2 | % | float32
TCS2.20MBH22DP100_ZQ01 | 30717 | COOLING AIR PRESS GV2 |  | float32
TCS2.20MBH22DP100_ZQ02 | 30718 | COOLING AIR PRESS GV2 | % | float32
TCS2.20MBH23AA101_PID | 30719 | COOL AIR DAMPER 1 STAGE 3 | % | float32
TCS2.20MBH23AA101_XQ01 | 30720 | COOL AIR DAMPER 1 STAGE 3 | % | float32
TCS2.20MBH23AA101_YQ01 | 30721 | COOL AIR DAMPER 1 STAGE 3 | % | float32
TCS2.20MBH23AA102_PID | 30722 | COOL AIR DAMPER 2 STAGE 3 | % | float32
TCS2.20MBH23AA102_XQ01 | 30723 | COOL AIR DAMPER 2 STAGE 3 | % | float32
TCS2.20MBH23AA102_YQ01 | 30724 | COOL AIR DAMPER 2 STAGE 3 | % | float32
TCS2.20MBH23CP102_XQ01 | 30725 | COOL AIR DAMPER STAGE 3 PRESSURE | bar | float32
TCS2.20MBH23CP103_XQ01 | 30726 | COOL AIR DAMPER STAGE 3 PRESSURE | bar | float32
TCS2.20MBH23CP104_XQ01 | 30727 | COOL AIR DAMPER STAGE 3 PRESSURE | bar | float32
TCS2.20MBH23DP100_PVGV3 | 30728 | COOLING AIR PRESSURE GV3 |  | float32
TCS2.20MBH23DP100_XD | 30729 | COOLING AIR PRESSURE GV3 | % | float32
TCS2.20MBH23DP100_ZQ02 | 30730 | COOLING AIR PRESSURE GV3 | % | float32
TCS2.20MBH23DP100_ZQ04 | 30731 | COOLING AIR PRESSURE GV3 | % | float32
TCS2.20MBH23DP100_ZQ05 | 30732 | ~COOLING AIR PRESS GV2 |  | float32
TCS2.20MBK22CS101_XQ01 | 30733 | TURNING GEAR SPEED 1 | Hz | float32
TCS2.20MBK22CS102_XQ01 | 30734 | TURNING GEAR SPEED 2 | Hz | float32
TCS2.20MBL10CM101_XQ01 | 30735 | INTAKE AIR FILTRATION ENVIRONMENT RH % (HUMIDITY) | % | float32
TCS2.20MBL10CM102_XQ01 | 30736 | INTAKE AIR FILTRATION ENVIRONMENT RH % (HUMIDITY) | % | float32
TCS2.20MBL10CM901_XQ01 | 30737 | ~INTAKE AIR FILTRATION ENVIRONMENT RH % (HUMIDITY) | % | float32
TCS2.20MBL10CP101_XQ01 | 30738 | ENVIRONMENT PRESSURE | mbar | float32
TCS2.20MBL10CT101_XQ01 | 30739 | INTAKE AIR FILTRATION ENVIRONMENT TEMP 1 | C | float32
TCS2.20MBL10CT102_XQ01 | 30740 | INTAKE AIR FILTRATION ENVIRONMENT TEMP 2 | °C | float32
TCS2.20MBL10CT901_XQ01 | 30741 | ~INTAKE AIR FILTRATION ENVIRONMENT TEMP |  | float32
TCS2.20MBL13CP101_XQ01 | 30742 | DP PRE FILTER | kPa | float32
TCS2.20MBL14CP101_XQ01 | 30743 | INTAKE TOTAL FILTER DP | kPa | float32
TCS2.20MBL14CP102_XQ01 | 30744 | DP PULSE FILTER | kPa | float32
TCS2.20MBL21CQ101_XQ01 | 30745 | ICE DETECTOR | % | float32
TCS2.20MBM00EU006_XQ01 | 30746 | ~HUM/ACC MON T REC 1 | s | float32
TCS2.20MBM00EU006_XQ02 | 30747 | ~HUM/ACC MON T REC 2 | s | float32
TCS2.20MBM00EU006_XQ03 | 30748 | ~ACCUM OPERATING HRS | h | float32
TCS2.20MBM10CP101_XQ01 | 30749 | DIFF PRESS COMB CHAMBER | mbar | float32
TCS2.20MBM10CY101_XQ01 | 30750 | COMB CHAMBER ACCELERATION CH. A | g | float32
TCS2.20MBM10CY102_XQ01 | 30751 | COMB CHAMBER ACCELERATION CH. B | g | float32
TCS2.20MBM10CY103_XQ01 | 30752 | COMB CHAMBER ACCELERATION CH. C | g | float32
TCS2.20MBM11CP101_XQ01 | 30753 | COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS2.20MBM11CP102_XQ01 | 30754 | COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS2.20MBM12CP107_XQ01 | 30755 | ~COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS2.20MBM12CP110_XQ01 | 30756 | ~COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS2.20MBM12CP115_XQ01 | 30757 | ~COMB CHAMBER DYNAMIC PRESSURE | mbar | float32
TCS2.20MBM13CR101_XQ01 | 30758 | FG/FO FLAME INTENSITY FLAME 1 | nm | float32
TCS2.20MBM13CR102_XQ01 | 30759 | FG/FO FLAME INTENSITY FLAME 2 | nm | float32
TCS2.20MBP03DU003_1FEGVB_GV | 30760 | ~PREMIX FUEL MASS FLOW GAS REQ | Kg/s | float32
TCS2.20MBP03DU003_COMB_LOAD_VAR_NG_JVAREGG | 30761 | ~COMB_LOAD_VAR_NG | % | float32
TCS2.20MBP03DU003_FEGDB | 30762 | ~DIFF FUEL GAS REQ | Kg/sec | float32
TCS2.20MBP03DU003_FMIGD | 30763 | ~DIFF MIN FLOW GAS REQ | Kg/sec | float32
TCS2.20MBP03DU003_FMIGV | 30764 | ~PREMIX MIN FLOW GAS REQ | Kg/s | float32
TCS2.20MBP03DU003_FP | 30765 | ~COMB_LOAD_VAR_NG | Kg/s | float32
TCS2.20MBP03DU003_GD | 30766 | ~DIFF MASS FLOW FUEL GAS REQ | Kg/sec | float32
TCS2.20MBP03DU003_GV | 30767 | ~PREMIX FUEL MASS FLOW GAS REQ | Kg/s | float32
TCS2.20MBP03DU003_OUT | 30768 | ~FUEL CONTROLLER NG STEP |  | float32
TCS2.20MBP03DU003_UAGV | 30769 | ~FG PREMIX PROPORTION | % | float32
TCS2.20MBP13CP101_XQ01 | 30770 | FG PRESS UPST STOP VLV - PREMIX LINE 1 | bar | float32
TCS2.20MBP13CP102_XQ01 | 30771 | FG PRESS UPST STOP VLV - PREMIX LINE 2 | bar | float32
TCS2.20MBP13CT101A_XQ01 | 30772 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS2.20MBP13CT101B_XQ01 | 30773 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS2.20MBP13CT102A_XQ01 | 30774 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS2.20MBP13CT102B_XQ01 | 30775 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS2.20MBP13CT103A_XQ01 | 30776 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS2.20MBP13CT103B_XQ01 | 30777 | FG TEMP UPST ESV PREMIX VLV 1 | °C | float32
TCS2.20MBP13EU010_193350_OUT | 30778 | \ |  | float32
TCS2.20MBP13FQ101_XQ01 | 30779 | DENSITY/HUMIDITY GAS | kg/m? | float32
TCS2.20MBP13FQ101_XQ02 | 30780 | DENSITY/HUMIDITY GAS | MJ/m? | float32
TCS2.20MBP13FT901_ZQ01 | 30781 | \ |  | float32
TCS2.20MBP14CP101_XQ01 | 30782 | FG PRESS DOWNST STOP VLV - PREMIX LINE | bar | float32
TCS2.20MBP22DG151_XQ01 | 30783 | NG PREMIX CTRL POSN |  | float32
TCS2.20MBP23DG151_XQ01 | 30784 | PILOT 1 CTRL POSN |  | float32
TCS2.20MBP23DU071_PGSTRT_PGSTRT | 30785 | MASS-F SETP CV PILOT GAS | Kg/s | float32
TCS2.20MBP23DU071_XQ01 | 30786 | MASS-F SETP CV PILOT GAS | Kg/s | float32
TCS2.20MBP24DG151_XQ01HW | 30787 | NG PILOT 2 CTRL POSN |  | float32
TCS2.20MBP24DU070_FP | 30788 | ~COMB_LOAD_VAR_NG | Kg/s | float32
TCS2.20MBP24DU070_PGSTRT | 30789 | ~LIFTING CALC CV PILOT 2 GAS | Kg/s | float32
TCS2.20MBP24DU070_XQ01 | 30790 | ~LIFTING CALC CV PILOT 2 GAS | Kg/s | float32
TCS2.20MBP32CP101_XQ01 | 30791 | FUEL GAS PRESSURE PREMIX HEADER | bar | float32
TCS2.20MBP32CT101_XQ01 | 30792 | TEMP GAS PREMIX LINE | °C | float32
TCS2.20MBP32CT102_XQ01 | 30793 | TEMP GAS PREMIX LINE | ?C | float32
TCS2.20MBP32CT901_XQ01 | 30794 | \ |  | float32
TCS2.20MBP34CF101_XQ01 | 30795 | PILOT 2 FLOW GAS | kg/s | float32
TCS2.20MBP34CF101_ZQ01 | 30796 | PILOT 2 FLOW GAS | kg/s | float32
TCS2.20MBP34CP101_XQ01 | 30797 | FUEL GAS PRESSURE PILOT 2 HEADER | bar | float32
TCS2.20MBP34CT101_XQ01 | 30798 | TEMP GAS PILOT 2 LINE | % | float32
TCS2.20MBP34CT102_XQ01 | 30799 | TEMP GAS PILOT 2 LINE | C | float32
TCS2.20MBP34CT901_XQ01 | 30800 | \ |  | float32
TCS2.20MBR20CP101_XQ01 | 30801 | DP EXHAUST GAS 1 | mbar | float32
TCS2.20MBR20CP102_XQ01 | 30802 | DP EXHAUST GAS 2 | mbar | float32
TCS2.20MBR20CP103_XQ01 | 30803 | DP EXHAUST GAS 3 | mbar | float32
TCS2.20MBR20CT101_XQ01 | 30804 | EXHAUST DIFFUSOR TEMP 1 | °C | float32
TCS2.20MBR20CT102_XQ01 | 30805 | EXHAUST DIFFUSOR TEMP 2 | °C | float32
TCS2.20MBR20CT103_XQ01 | 30806 | EXHAUST DIFFUSOR TEMP 3 | °C | float32
TCS2.20MBR20CT104_XQ01 | 30807 | EXHAUST DIFFUSOR TEMP 4 | °C | float32
TCS2.20MBR20CT105_XQ01 | 30808 | EXHAUST DIFFUSOR TEMP 5 | °C | float32
TCS2.20MBR20CT106_XQ01 | 30809 | EXHAUST DIFFUSOR TEMP 6 | °C | float32
TCS2.20MBR20CT901_OUT | 30810 | EXHAUST DIFFUSOR TEMP | °C | float32
TCS2.20MBR20CT901_XQ01 | 30811 | EXHAUST DIFFUSOR TEMP |  | float32
TCS2.20MBV10CL101_XQ01 | 30812 | LUBE OIL TANK LVL | mm | float32
TCS2.20MBV10CP101_XQ01 | 30813 | PRESSURE LUBE OIL TANK | kPa | float32
TCS2.20MBV10CT101_XQ01 | 30814 | LUBE OIL TANK TEMP | °C | float32
TCS2.20MBV21AP001_XQ01 | 30815 | MAIN LUBE OIL PUMP CURRENT | A | float32
TCS2.20MBV21AP002_DCO | 30816 | AUX LUBE OIL PUMP |  | float32
TCS2.20MBV21AP002_XQ01 | 30817 | AUX LUBE OIL PUMP CURRENT | A | float32
TCS2.20MBV21AP003_XQ05 | 30818 | EMERG LUBE OIL PUMP |  | float32
TCS2.20MBV26CP101_XQ01 | 30819 | LUBE OIL PRESS DWNSTR. FILTERS | bar | float32
TCS2.20MBV26CT101_XQ01 | 30820 | LUBE OIL TEMP DWNSTR. FILTERS | °C | float32
TCS2.20MBV30AP001_XQ01 | 30821 | LIFT OIL PUMP 1 CURRENT | A | float32
TCS2.20MBV30AP002_XQ01 | 30822 | AUX LIFT OIL PUMP 2 CURRENT | A | float32
TCS2.20MBV31CP101_XQ01 | 30823 | LIFT OIL PRESSURE DWNSTR LIFTING OIL FILTER | bar | float32
TCS2.20MBV31CP102_XQ01 | 30824 | LIFT OIL PRESSURE DWNSTR LIFTING OIL FILTER | bar | float32
TCS2.20MBV50AN001_DCO | 30825 | LUBE OIL TANK VENT FAN 1 |  | float32
TCS2.20MBV50AN002_DCO | 30826 | LUBE OIL TANK VENT FAN 2 |  | float32
TCS2.20MBV90CT071_XQ01 | 30827 | GEN LUBE OIL TEMP OCE BEARING | C | float32
TCS2.20MBV90CT081_XQ01 | 30828 | GEN LUBE OIL TEMP CE BEARING | °C | float32
TCS2.20MBX01CL101_XQ01 | 30829 | HYD OIL TANK LEVEL 1 | mm | float32
TCS2.20MBX01CT101A_XQ01 | 30830 | HYD OIL TANK TEMP 1 | °C | float32
TCS2.20MBX01CT101B_XQ02 | 30831 | HYD OIL TANK TEMP 2 | °C | float32
TCS2.20MBX01EZ001_912688_OUT | 30832 |  |  | float32
TCS2.20MBX02AP001_DCO | 30833 | HYD OIL PUMP 1 |  | float32
TCS2.20MBX02AP002_DCO | 30834 | HYD OIL PUMP 2 |  | float32
TCS2.20MBX03CP101_XQ01 | 30835 | HYD OIL DELIVERY LINE PRESSURE | bar | float32
TCS2.20MBY01DU001_BAGVAR | 30836 | ~PROPN FUEL OIL | % | float32
TCS2.20MBY01DU001_BAOVAR | 30837 | ~PROPN FUEL OIL | % | float32
TCS2.20MBY10CE901_XQ01 | 30838 | ACTIVE POWER |  | float32
TCS2.20MBY10CE901_XQ03 | 30839 | ACTIVE POWER | MW | float32
TCS2.20MBY10CE901_XQ91 | 30840 | ACTIVE POWER | MW | float32
TCS2.20MBY10CS901_XQ01 | 30841 | TURBINE SPEED | Hz | float32
TCS2.20MBY10CS901_ZQ01 | 30842 | TURBINE SPEED | s-1 | float32
TCS2.20MBY10CS901_ZQ11 | 30843 | TURBINE SPEED | Hz | float32
TCS2.20MBY10CS901_ZQ12 | 30844 | TURBINE SPEED | rpm | float32
TCS2.20MBY10DE010_134646_OUT | 30845 | \ |  | float32
TCS2.20MBY10DE010_134681_OUT | 30846 | \ |  | float32
TCS2.20MBY10DE010_134682_OUT | 30847 | \ |  | float32
TCS2.20MBY10DE010_94330_OUT | 30848 | \ |  | float32
TCS2.20MBY10DE010_94339_OUT | 30849 | \ |  | float32
TCS2.20MBY10DE010_MARGIN_XQ01 | 30850 | LOAD SETPOINT | MW | float32
TCS2.20MBY10DE010_PSV | 30851 | ~LOAD SETP DELAYED | MW | float32
TCS2.20MBY10DE010_XQ01 | 30852 | LOAD SETPOINT | MW | float32
TCS2.20MBY10DE010_XQ03 | 30853 | LOAD SETPOINT | MW/min | float32
TCS2.20MBY10DE010_XQ04 | 30854 | LOAD SETPOINT | MW/min | float32
TCS2.20MBY10DE010_XQ05 | 30855 | LOAD SETPOINT | MW/min | float32
TCS2.20MBY10DE010_XQ51 | 30856 | ~INPUT LOAD SETPOINT | MW | float32
TCS2.20MBY10DE010_YN | 30857 | LOAD SETPOINT | MW | float32
TCS2.20MBY10DE010_ZQ02 | 30858 | LOAD SETPOINT | MW | float32
TCS2.20MBY10DE020_XQ01 | 30859 | ~LOAD SET POINT REF FROM AGC | MW | float32
TCS2.20MBY10DE051_XQ01 | 30860 | CALC GT LOAD | MW | float32
TCS2.20MBY10DP080_XQ01 | 30861 | ~COMPRESSOR MASS FLOW | % | float32
TCS2.20MBY10DS010_OM_XQ52 | 30862 | ~EXT TARG FREQ SETP | s-1 | float32
TCS2.20MBY10DS010_XQ51 | 30863 | \ |  | float32
TCS2.20MBY10DS010_ZQ01 | 30864 | SPEED SETPOINT | s-1 | float32
TCS2.20MBY10DS010_ZQ02 | 30865 | ~SPEED SETP DELAYED | s-1 | float32
TCS2.20MBY10DT010_XQ01 | 30866 | ~EFFECTIVE TEMPERATURE SETPOINT FOR IGV | °C | float32
TCS2.20MBY10DT010_XQ02 | 30867 | ~TEMPERATURE SETPOINT AT BASE LOAD | °C | float32
TCS2.20MBY10DT010_XQ03 | 30868 | ~SETPOINT DELAYED OTC-CONTROL | °C | float32
TCS2.20MBY10DT010_XQ04 | 30869 | ~DELTA ON SETPOINT OTC-CONTROLLER | °C | float32
TCS2.20MBY10DT010_XQ05 | 30870 | ~SETPOINT OTC-CONTROLLER | °C | float32
TCS2.20MBY10DT040_1_XQ51 | 30871 | ~IGV TEMP CONTROLLER | % | float32
TCS2.20MBY10DT040_1YLTR | 30872 | ~IGV TEMP CONTROLLER | % | float32
TCS2.20MBY10DT040_XQ01 | 30873 | ~IGV POS SETPOINT | % | float32
TCS2.20MBY10DT040_XQ02 | 30874 | ~ACTUAL POSN IGV |  | float32
TCS2.20MBY10DT040_XQ03 | 30875 | ACTUAL POSN CV | % | float32
TCS2.20MBY10DT040_XQ51 | 30876 | ~INPUT IGV POSN SETP | % | float32
TCS2.20MBY10DU050_DF_XQ53 | 30877 | ~DELTA F PER TEST | Hz | float32
TCS2.20MBY10DU050_PSF_XQ01 | 30878 | ~KDELTAF FROM FUEL CONTROLLER |  | float32
TCS2.20MBY10DU050_XQ07_OUT | 30879 | \ |  | float32
TCS2.20MBY10DU050_XQ08_OUT | 30880 | \ |  | float32
TCS2.20MBY10DU050_XQ02 | 30881 | ~DELTA FREQ | Hz | float32
TCS2.20MBY10DU050_XQ03 | 30882 | ~FREQUENCY DEVIATION | Hz | float32
TCS2.20MBY10DU060_1PIVMAX_OUT | 30883 | \ |  | float32
TCS2.20MBY10DU060_1PIVMXL_OUT | 30884 |  |  | float32
TCS2.20MBY10DU060_1PIV_YKLGR | 30885 | ~COOLING AIR LIMIT CTRL (KLGR) | % | float32
TCS2.20MBY10DU060_1WPGR_OUT | 30886 | \ |  | float32
TCS2.20MBY10DU060_1YNPR_OUT | 30887 | \ |  | float32
TCS2.20MBY10DU060_IGV FF | 30888 | ~TEMP CONTROLLER FEED FORWARD | % | float32
TCS2.20MBY10DU060_LTRY | 30889 | ~OUTPUT OID TEMP CONTROLLER | % | float32
TCS2.20MBY10DU060_WLTR | 30890 | ~SETPOINT IGV POSITION CONTROLLER | °C | float32
TCS2.20MBY10DU060_YATK | 30891 | ~OTC CONTROLLER (ATKR) | % | float32
TCS2.20MBY10DU060_YHLG | 30892 | ~RUN UP FUNCTION (HLG) | % | float32
TCS2.20MBY10DU060_YKLGR | 30893 | ~COOLING AIR LIMIT CTRL (KLGR) | % | float32
TCS2.20MBY10DU060_YMIN | 30894 | ~THERMANL LOAD REQUEST |  | float32
TCS2.20MBY10DU060_YPG | 30895 | ~LIMIT LOAD CONTROLLER (PGR) | % | float32
TCS2.20MBY10DU060_YVPVR | 30896 | ~COMPR PRES RATIO LMT CTRL (VPVR) | % | float32
TCS2.20MBY10EP801_1XQ15 | 30897 | EQUIV OP HOURS | h | float32
TCS2.20MBY10EP801_XQ04 | 30898 | ~COMPTEUR DEMARRAGE NORMAL TG |  | float32
TCS2.20MBY10EP801_XQ10 | 30899 | ~TOTALE HEURES FONCTIONNEMENT TG |  | float32
TCS2.20MBY10EP801_XQ11 | 30900 | EQUIV OP HOURS |  | float32
TCS2.20MBY10EP801_XQ12 | 30901 | EQUIV OP HOURS |  | float32
TCS2.20MBY10EP801_XQ13 | 30902 | ~OP HOURS <= BASE LOAD | h | float32
TCS2.20MBY10EP801_XQ14 | 30903 | ~OP HOURS > BASE LOAD | h | float32
TCS2.20MBY10EP801_XQ15 | 30904 | ~DYN OP HOURS | h | float32
TCS2.20MBY10EP801_XQ21 | 30905 | EQUIV OP HOURS | h | float32
TCS2.20MBY10EP802_XQ01 | 30906 | OVER-/UNDERFREQUENCY | s | float32
TCS2.20MBY10EP803_XQ01 | 30907 | ~FO PREM CHANGEOVER |  | float32
TCS2.20MBY10EP804_XQ01 | 30908 |  |  | float32
TCS2.20MBY10EP804_XQ03 | 30909 | GT START UP MONITORING |  | float32
TCS2.20MBY10EP811_XQ01 | 30910 | ~EQUIV OP HOURS | h | float32
TCS2.20MBY10EP811_XQ02 | 30911 | ~EQUIV OP HOURS | h | float32
TCS2.20MBY10EP811_XQ03 | 30912 | ~EQUIV OP HOURS | h | float32
TCS2.20MBY10EP811_XQ04 | 30913 | ~EQUIV OP HOURS | h | float32
TCS2.20MBY10EP811_XQ10 | 30914 | ~EQUIV OP HOURS | h | float32
TCS2.20MBY10EP811_XQ20 | 30915 | ~EQUIV OP HOURS | h | float32
TCS2.20MBY10EP813_XQ01 | 30916 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ02 | 30917 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ03 | 30918 | ~TOTAL TRIP NG |  | float32
TCS2.20MBY10EP813_XQ04 | 30919 | ~COMPTEUR DECL A GASOIL TG |  | float32
TCS2.20MBY10EP813_XQ05 | 30920 | ~COMPTEUR SYNCHRONISATION TG AVEC RESEAU |  | float32
TCS2.20MBY10EP813_XQ11 | 30921 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ12 | 30922 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ13 | 30923 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ14 | 30924 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ15 | 30925 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ16 | 30926 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ17 | 30927 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ18 | 30928 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ19 | 30929 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ20 | 30930 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ21 | 30931 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ22 | 30932 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ23 | 30933 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ24 | 30934 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ25 | 30935 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ26 | 30936 | EQUIV STARTS |  | float32
TCS2.20MBY10EP813_XQ27 | 30937 | ~NG LOAD REJ |  | float32
TCS2.20MBY10EP813_XQ28 | 30938 | ~FO LOAD REJ |  | float32
TCS2.20MBY10FE901_XQ05 | 30939 | ~NORMALIZED LOAD | % | float32
TCS2.20PGT_CO_XQ01 | 30940 | MISURE TEMPORANEA CO | ppm | float32
TCS2.20PGT_NOX_XQ01 | 30941 | MISURE TEMPORANEA NOX | ppm | float32
TCS2.20PGT_O2_XQ01 | 30942 | MISURE TEMPORANEA O2 | vol% | float32
TCS2.20SAM10AN001_XQ01 | 30943 | GT ENC VENT FAN 1 | A | float32
TCS2.20SAM10AN002_XQ01 | 30944 | GT ENC VENT FAN 2 | A | float32
TCS2.20SAM10AN003_XQ01 | 30945 | GT ENC VENT FAN 3 | A | float32
TCS2.20SAM10CT101_XQ01 | 30946 | TEMP GT ENCLOSURE 1 | C | float32
TCS2.20SAM10CT102_XQ01 | 30947 | TEMP GT ENCLOSURE 2 | C | float32
TCS2.21BFA01CE004_XQ02 | 30948 | BFA01 VOLTAGE MEASURE | V | float32
TCS2.21BFA02CE004_XQ02 | 30949 | BFA02 VOLTAGE MEASURE | V | float32
TCS2.21BNA01CE004_XQ02 | 30950 | EMCC BUS BAR VOLATGE | V | float32
TCS2.21BNA01GS001A_XQ01 | 30951 | EMCC INC CB A CURRENT | A | float32
TCS2.21BNA01GS001A_XQ02 | 30952 | EMCC INC CB A VOLTAGE | V | float32
TCS2.21BNA01GS001B_XQ01 | 30953 | EMCC INC CB B CURRENT | V | float32
TCS2.21BNA01GS001B_XQ02 | 30954 | EMCC INC CB B VOLTAGE | A | float32
TCS2.21BRA01EG001_XQ01 | 30955 | 1XBRA 220Vac BUS BAR VOLTAGE | V | float32
TCS2.21BUA01CE001_XQ01 | 30956 | 110 VDC BUA BUS BAR VOLTAGE | V | float32
TCS2.21MBR20CP101_XQ01B | 30957 | AI FROM SIL3 SYSTEM | mbar | float32
TCS2.21MBR20CP102_XQ01B | 30958 | AI FROM SIL3 SYSTEM | mbar | float32
TCS2.21MBR20CP103_XQ01B | 30959 | AI FROM SIL3 SYSTEM | mbar | float32
TCS2.21MBY10EP801A_XQ01 | 30960 | ~DYN OP HOURS | h | float32
TCS2.21MKA01CE001_XQ01 | 30961 | GEN VOLTAGE | KV | float32
TCS2.21MKA01CE001_XQ02 | 30962 | GEN VOLTAGE | KV | float32
TCS2.21MKA01CE001_XQ03 | 30963 | GEN VOLTAGE | KV | float32
TCS2.21MKA01CE002_XQ01 | 30964 | GEN CURRENT | A | float32
TCS2.21MKA01CE002_XQ02 | 30965 | GEN CURRENT | A | float32
TCS2.21MKA01CE002_XQ03 | 30966 | GEN CURRENT | A | float32
TCS2.21MKA01CE003_XQ02 | 30967 | GENERATOR ACTIVE POWER | MW | float32
TCS2.21MKA01CE004_XQ01 | 30968 | GEN REACTIVE POWER | MVAR | float32
TCS2.21MKA01CE006_XQ01 | 30969 | GENERATOR FREQUENCY | Hz | float32
TCS2.21MKA01CE011_XQ01 | 30970 | GENERATOR STATOR NEC CURRENT | kV | float32
TCS2.21MKA01CE013_XQ01 | 30971 | GENERATOR STATOR ZERO VOLTAGE | A | float32
TCS2.21MKA01GH001_XQ01 | 30972 | GEN SHAFT VOLTAGE MONITORING | V | float32
TCS2.21MKA01GH001_XQ02 | 30973 | GEN SHAFT CURRENT MONITORING | A | float32
TCS2.21MKA20CT301_XQ01 | 30974 | STR CO END SHID TEMP EE 01 | C | float32
TCS2.21MKA20CT302_XQ01 | 30975 | STR CO END SHID TEMP EE 02 | C | float32
TCS2.21MKA20CT303_XQ01 | 30976 | STR CO END SHID TEMP EE 03 | C | float32
TCS2.21MKA20CT304_XQ01 | 30977 | STR CO END SHID TEMP EE 04 | C | float32
TCS2.21MKA20CT311_XQ01 | 30978 | STR CO END SHID TEMP GTE 01 | C | float32
TCS2.21MKA20CT312_XQ01 | 30979 | STR CO END SHID TEMP GTE 02 | C | float32
TCS2.21MKA20CT313_XQ01 | 30980 | STR CO END SHID TEMP GTE 03 | C | float32
TCS2.21MKA20CT314_XQ01 | 30981 | STR CO END SHID TEMP GTE 04 | C | float32
TCS2.21MKA21CT301_XQ01 | 30982 | STR END SHID TEMP EE 01 | C | float32
TCS2.21MKA21CT302_XQ01 | 30983 | STR END SHID TEMP EE 02 | C | float32
TCS2.21MKA21CT303_XQ01 | 30984 | STR END SHID TEMP EE 03 | C | float32
TCS2.21MKA21CT304_XQ01 | 30985 | STR END SHID TEMP EE 04 | C | float32
TCS2.21MKA21CT311_XQ01 | 30986 | STR END SHID TEMP GTE 01 | C | float32
TCS2.21MKA21CT312_XQ01 | 30987 | STR END SHID TEMP GTE 02 | C | float32
TCS2.21MKA21CT313_XQ01 | 30988 | STR END SHID TEMP GTE 03 | C | float32
TCS2.21MKA21CT314_XQ01 | 30989 | STR END SHID TEMP GTE 04 | C | float32
TCS2.21MKA22CT301_XQ01 | 30990 | STR FINGER PL EE 01 | C | float32
TCS2.21MKA22CT302_XQ01 | 30991 | STR FINGER PL EE 02 | C | float32
TCS2.21MKA22CT303_XQ01 | 30992 | STR FINGER PL EE 03 | C | float32
TCS2.21MKA22CT304_XQ01 | 30993 | STR FINGER PL EE 04 | C | float32
TCS2.21MKA22CT311_XQ01 | 30994 | STR FINGER PL TE 01 | C | float32
TCS2.21MKA22CT312_XQ01 | 30995 | STR FINGER PL TE 02 | C | float32
TCS2.21MKA22CT313_XQ01 | 30996 | STR FINGER PL TE 03 | C | float32
TCS2.21MKA22CT314_XQ01 | 30997 | STR FINGER PL TE 04 | C | float32
TCS2.21MKA23CT301_XQ01 | 30998 | STR CORE TEMP EE 01 | C | float32
TCS2.21MKA23CT302_XQ01 | 30999 | STR CORE TEMP EE 02 | C | float32
TCS2.21MKA23CT303_XQ01 | 31000 | STR CORE TEMP EE 03 | C | float32
TCS2.21MKA23CT304_XQ01 | 31001 | STR CORE TEMP EE 04 | C | float32
TCS2.21MKA23CT305_XQ01 | 31002 | STR CORE TEMP EE 05 | C | float32
TCS2.21MKA23CT306_XQ01 | 31003 | STR CORE TEMP EE 06 | C | float32
TCS2.21MKA23CT307_XQ01 | 31004 | STR CORE TEMP EE 07 | C | float32
TCS2.21MKA23CT308_XQ01 | 31005 | STR CORE TEMP EE 08 | C | float32
TCS2.21MKA23CT309_XQ01 | 31006 | STR CORE TEMP MID 01 | C | float32
TCS2.21MKA23CT310_XQ01 | 31007 | STR CORE TEMP MID 02 | C | float32
TCS2.21MKA23CT311_XQ01 | 31008 | STR CORE TEMP MID 03 | C | float32
TCS2.21MKA23CT312_XQ01 | 31009 | STR CORE TEMP MID 04 | C | float32
TCS2.21MKA23CT313_XQ01 | 31010 | STR CORE TEMP MID 05 | C | float32
TCS2.21MKA23CT314_XQ01 | 31011 | STR CORE TEMP MID 06 | C | float32
TCS2.21MKA23CT315_XQ01 | 31012 | STR CORE TEMP MID 07 | C | float32
TCS2.21MKA23CT316_XQ01 | 31013 | STR CORE TEMP MID 08 | C | float32
TCS2.21MKA23CT317_XQ01 | 31014 | STR CORE TEMP MID 09 | C | float32
TCS2.21MKA23CT318_XQ01 | 31015 | STR CORE TEMP MID 10 | C | float32
TCS2.21MKA23CT319_XQ01 | 31016 | STR CORE TEMP MID 11 | C | float32
TCS2.21MKA23CT320_XQ01 | 31017 | STR CORE TEMP MID 12 | C | float32
TCS2.21MKA24CT301_XQ01 | 31018 | STR WINDG SLOT TEMP 01 | C | float32
TCS2.21MKA24CT302_XQ01 | 31019 | STR WINDG SLOT TEMP 02 | C | float32
TCS2.21MKA24CT303_XQ01 | 31020 | STR WINDG SLOT TEMP 03 | C | float32
TCS2.21MKA24CT304_XQ01 | 31021 | STR WINDG SLOT TEMP 04 | C | float32
TCS2.21MKA24CT305_XQ01 | 31022 | STR WINDG SLOT TEMP 05 | C | float32
TCS2.21MKA24CT306_XQ01 | 31023 | STR WINDG SLOT TEMP 06 | C | float32
TCS2.21MKA24CT307_XQ01 | 31024 | STR WINDG SLOT TEMP 07 | C | float32
TCS2.21MKA24CT308_XQ01 | 31025 | STR WINDG SLOT TEMP 08 | C | float32
TCS2.21MKA24CT309_XQ01 | 31026 | STR WINDG SLOT TEMP 09 | C | float32
TCS2.21MKA24CT310_XQ01 | 31027 | STR WINDG SLOT TEMP 10 | C | float32
TCS2.21MKA24CT311_XQ01 | 31028 | STR WINDG SLOT TEMP 11 | C | float32
TCS2.21MKA24CT312_XQ01 | 31029 | STR WINDG SLOT TEMP 12 | C | float32
TCS2.21MKA24CT313_XQ01 | 31030 | STR WINDG SLOT TEMP 13 | C | float32
TCS2.21MKA24CT314_XQ01 | 31031 | STR WINDG SLOT TEMP 14 | C | float32
TCS2.21MKA24CT315_XQ01 | 31032 | STR WINDG SLOT TEMP 15 | C | float32
TCS2.21MKA24CT316_XQ01 | 31033 | STR WINDG SLOT TEMP 16 | C | float32
TCS2.21MKA24CT317_XQ01 | 31034 | STR WINDG SLOT TEMP 17 | C | float32
TCS2.21MKA24CT318_XQ01 | 31035 | STR WINDG SLOT TEMP 18 | C | float32
TCS2.21MKA24CT319_XQ01 | 31036 | STR WINDG SLOT TEMP 19 | C | float32
TCS2.21MKA24CT320_XQ01 | 31037 | STR WINDG SLOT TEMP 20 | C | float32
TCS2.21MKA24CT321_XQ01 | 31038 | STR WINDG SLOT TEMP 21 | C | float32
TCS2.21MKA24CT322_XQ01 | 31039 | STR WINDG SLOT TEMP 22 | C | float32
TCS2.21MKA24CT323_XQ01 | 31040 | STR WINDG SLOT TEMP 23 | C | float32
TCS2.21MKA24CT324_XQ01 | 31041 | STR WINDG SLOT TEMP 24 | C | float32
TCS2.21MKA24CT325_XQ01 | 31042 | STR WINDG SLOT TEMP 25 | C | float32
TCS2.21MKA24CT326_XQ01 | 31043 | STR WINDG SLOT TEMP 26 | C | float32
TCS2.21MKA24CT327_XQ01 | 31044 | STR WINDG SLOT TEMP 27 | C | float32
TCS2.21MKA24CT328_XQ01 | 31045 | STR WINDG SLOT TEMP 28 | C | float32
TCS2.21MKA24CT329_XQ01 | 31046 | STR WINDG SLOT TEMP 29 | C | float32
TCS2.21MKA24CT330_XQ01 | 31047 | STR WINDG SLOT TEMP 30 | C | float32
TCS2.21MKA24CT331_XQ01 | 31048 | STR WINDG SLOT TEMP 31 | C | float32
TCS2.21MKA24CT332_XQ01 | 31049 | STR WINDG SLOT TEMP 32 | C | float32
TCS2.21MKA24CT333_XQ01 | 31050 | STR WINDG SLOT TEMP 33 | C | float32
TCS2.21MKA24CT334_XQ01 | 31051 | STR WINDG SLOT TEMP 34 | C | float32
TCS2.21MKA24CT335_XQ01 | 31052 | STR WINDG SLOT TEMP 35 | C | float32
TCS2.21MKA24CT336_XQ01 | 31053 | STR WINDG SLOT TEMP 36 | C | float32
TCS2.21MKA24CT337_XQ01 | 31054 | STR WINDG SLOT TEMP 37 | C | float32
TCS2.21MKA24CT338_XQ01 | 31055 | STR WINDG SLOT TEMP 38 | C | float32
TCS2.21MKA24CT339_XQ01 | 31056 | STR WINDG SLOT TEMP 39 | C | float32
TCS2.21MKA24CT340_XQ01 | 31057 | STR WINDG SLOT TEMP 40 | C | float32
TCS2.21MKA24CT341_XQ01 | 31058 | STR WINDG SLOT TEMP 41 | C | float32
TCS2.21MKA24CT342_XQ01 | 31059 | STR WINDG SLOT TEMP 42 | C | float32
TCS2.21MKA24CT343_XQ01 | 31060 | STR WINDG SLOT TEMP 43 | C | float32
TCS2.21MKA24CT344_XQ01 | 31061 | STR WINDG SLOT TEMP 44 | C | float32
TCS2.21MKA24CT345_XQ01 | 31062 | STR WINDG SLOT TEMP 45 | C | float32
TCS2.21MKA24CT346_XQ01 | 31063 | STR WINDG SLOT TEMP 46 | C | float32
TCS2.21MKA24CT347_XQ01 | 31064 | STR WINDG SLOT TEMP 47 | C | float32
TCS2.21MKA24CT348_XQ01 | 31065 | STR WINDG SLOT TEMP 48 | C | float32
TCS2.21MKA24CT349_XQ01 | 31066 | STR WINDG SLOT TEMP 49 | C | float32
TCS2.21MKA24CT350_XQ01 | 31067 | STR WINDG SLOT TEMP 50 | C | float32
TCS2.21MKA24CT351_XQ01 | 31068 | STR WINDG SLOT TEMP 51 | C | float32
TCS2.21MKA24CT352_XQ01 | 31069 | STR WINDG SLOT TEMP 52 | C | float32
TCS2.21MKA24CT353_XQ01 | 31070 | STR WINDG SLOT TEMP 53 | C | float32
TCS2.21MKA24CT354_XQ01 | 31071 | STR WINDG SLOT TEMP 54 | C | float32
TCS2.21MKA25CT301_XQ01 | 31072 | STR COIL WTR OUT TEMP 01 | C | float32
TCS2.21MKA25CT302_XQ01 | 31073 | STR COIL WTR OUT TEMP 02 | C | float32
TCS2.21MKA25CT303_XQ01 | 31074 | STR COIL WTR OUT TEMP 03 | C | float32
TCS2.21MKA25CT304_XQ01 | 31075 | STR COIL WTR OUT TEMP 04 | C | float32
TCS2.21MKA25CT305_XQ01 | 31076 | STR COIL WTR OUT TEMP 05 | C | float32
TCS2.21MKA25CT306_XQ01 | 31077 | STR COIL WTR OUT TEMP 06 | C | float32
TCS2.21MKA25CT307_XQ01 | 31078 | STR COIL WTR OUT TEMP 07 | C | float32
TCS2.21MKA25CT308_XQ01 | 31079 | STR COIL WTR OUT TEMP 08 | C | float32
TCS2.21MKA25CT309_XQ01 | 31080 | STR COIL WTR OUT TEMP 09 | C | float32
TCS2.21MKA25CT310_XQ01 | 31081 | STR COIL WTR OUT TEMP 10 | C | float32
TCS2.21MKA25CT311_XQ01 | 31082 | STR COIL WTR OUT TEMP 11 | C | float32
TCS2.21MKA25CT312_XQ01 | 31083 | STR COIL WTR OUT TEMP 12 | C | float32
TCS2.21MKA25CT313_XQ01 | 31084 | STR COIL WTR OUT TEMP 13 | C | float32
TCS2.21MKA25CT314_XQ01 | 31085 | STR COIL WTR OUT TEMP 14 | C | float32
TCS2.21MKA25CT315_XQ01 | 31086 | STR COIL WTR OUT TEMP 15 | C | float32
TCS2.21MKA25CT316_XQ01 | 31087 | STR COIL WTR OUT TEMP 16 | C | float32
TCS2.21MKA25CT317_XQ01 | 31088 | STR COIL WTR OUT TEMP 17 | C | float32
TCS2.21MKA25CT318_XQ01 | 31089 | STR COIL WTR OUT TEMP18 | C | float32
TCS2.21MKA25CT319_XQ01 | 31090 | STR COIL WTR OUT TEMP 19 | C | float32
TCS2.21MKA25CT320_XQ01 | 31091 | STR COIL WTR OUT TEMP 20 | C | float32
TCS2.21MKA25CT321_XQ01 | 31092 | STR COIL WTR OUT TEMP 21 | C | float32
TCS2.21MKA25CT322_XQ01 | 31093 | STR COIL WTR OUT TEMP 22 | C | float32
TCS2.21MKA25CT323_XQ01 | 31094 | STR COIL WTR OUT TEMP 23 | C | float32
TCS2.21MKA25CT324_XQ01 | 31095 | STR COIL WTR OUT TEMP 24 | C | float32
TCS2.21MKA25CT325_XQ01 | 31096 | STR COIL WTR OUT TEMP 25 | C | float32
TCS2.21MKA25CT326_XQ01 | 31097 | STR COIL WTR OUT TEMP 26 | C | float32
TCS2.21MKA25CT327_XQ01 | 31098 | STR COIL WTR OUT TEMP 27 | C | float32
TCS2.21MKA25CT328_XQ01 | 31099 | STR COIL WTR OUT TEMP 28 | C | float32
TCS2.21MKA25CT329_XQ01 | 31100 | STR COIL WTR OUT TEMP 29 | C | float32
TCS2.21MKA25CT330_XQ01 | 31101 | STR COIL WTR OUT TEMP 30 | C | float32
TCS2.21MKA25CT331_XQ01 | 31102 | STR COIL WTR OUT TEMP 31 | C | float32
TCS2.21MKA25CT332_XQ01 | 31103 | STR COIL WTR OUT TEMP 32 | C | float32
TCS2.21MKA25CT333_XQ01 | 31104 | STR COIL WTR OUT TEMP 33 | C | float32
TCS2.21MKA25CT334_XQ01 | 31105 | STR COIL WTR OUT TEMP 34 | C | float32
TCS2.21MKA25CT335_XQ01 | 31106 | STR COIL WTR OUT TEMP 35 | C | float32
TCS2.21MKA25CT336_XQ01 | 31107 | STR COIL WTR OUT TEMP 36 | C | float32
TCS2.21MKA25CT337_XQ01 | 31108 | STR COIL WTR OUT TEMP 37 | C | float32
TCS2.21MKA25CT338_XQ01 | 31109 | STR COIL WTR OUT TEMP 38 | C | float32
TCS2.21MKA25CT339_XQ01 | 31110 | STR COIL WTR OUT TEMP 39 | C | float32
TCS2.21MKA25CT340_XQ01 | 31111 | STR COIL WTR OUT TEMP 40 | C | float32
TCS2.21MKA25CT341_XQ01 | 31112 | STR COIL WTR OUT TEMP 41 | C | float32
TCS2.21MKA25CT342_XQ01 | 31113 | STR COIL WTR OUT TEMP 42 | C | float32
TCS2.21MKA25CT343_XQ01 | 31114 | STR COIL WTR OUT TEMP 43 | C | float32
TCS2.21MKA25CT344_XQ01 | 31115 | STR COIL WTR OUT TEMP 44 | C | float32
TCS2.21MKA25CT345_XQ01 | 31116 | STR COIL WTR OUT TEMP 45 | C | float32
TCS2.21MKA25CT346_XQ01 | 31117 | STR COIL WTR OUT TEMP 46 | C | float32
TCS2.21MKA25CT347_XQ01 | 31118 | STR COIL WTR OUT TEMP 47 | C | float32
TCS2.21MKA25CT348_XQ01 | 31119 | STR COIL WTR OUT TEMP 48 | C | float32
TCS2.21MKA25CT349_XQ01 | 31120 | STR COIL WTR OUT TEMP 49 | C | float32
TCS2.21MKA25CT350_XQ01 | 31121 | STR COIL WTR OUT TEMP 50 | C | float32
TCS2.21MKA25CT351_XQ01 | 31122 | STR COIL WTR OUT TEMP 51 | C | float32
TCS2.21MKA25CT352_XQ01 | 31123 | STR COIL WTR OUT TEMP 52 | C | float32
TCS2.21MKA25CT353_XQ01 | 31124 | STR COIL WTR OUT TEMP 53 | C | float32
TCS2.21MKA25CT354_XQ01 | 31125 | STR COIL WTR OUT TEMP 54 | C | float32
TCS2.21MKA26CT301_XQ01 | 31126 | MAIN BSHG AIR TEMP 1 | C | float32
TCS2.21MKA26CT302_XQ01 | 31127 | MAIN BSHG AIR TEMP 2 | C | float32
TCS2.21MKA30CT301A_XQ01 | 31128 | GEN COLD GAS TEMP EE | C | float32
TCS2.21MKA30CT302A_XQ01 | 31129 | GEN COLD GAS TEMP EE | C | float32
TCS2.21MKA30CT303A_XQ01 | 31130 | GEN COLD GAS TEMP EE | C | float32
TCS2.21MKA30CT304A_XQ01 | 31131 | GEN COLD GAS TEMP EE | C | float32
TCS2.21MKA30CT311A_XQ01 | 31132 | GEN COLD GAS TEMP GTE | C | float32
TCS2.21MKA30CT312A_XQ01 | 31133 | GEN COLD GAS TEMP GTE | C | float32
TCS2.21MKA30CT313A_XQ01 | 31134 | GEN COLD GAS TEMP GTE | C | float32
TCS2.21MKA30CT314A_XQ01 | 31135 | GEN COLD GAS TEMP GTE | C | float32
TCS2.21MKA31CT301_XQ01 | 31136 | GEN WARM GAS TEMP EE | C | float32
TCS2.21MKA31CT311_XQ01 | 31137 | GEN WARM GAS TEMP TE | C | float32
TCS2.21MKA31CT901_ZQ01 | 31138 | \ |  | float32
TCS2.21MKC10CE002_XQ01 | 31139 | EXC TRASNF CURRENT | A | float32
TCS2.21MKC10CE003_XQ01 | 31140 | EXC TRASNF ACTIVE POWER | MW | float32
TCS2.21MKC10CE004_XQ01 | 31141 | EXC TRASNF REACTIVE POWER | KVAR | float32
TCS2.21MKC10CT001_XQ01 | 31142 | LV WINDINGS TEMP PH R | °C | float32
TCS2.21MKC10CT002_XQ01 | 31143 | LV WINDINGS TEMP PH S | °C | float32
TCS2.21MKC10CT003_XQ01 | 31144 | LV WINDINGS TEMP PH T | °C | float32
TCS2.21MKC10FT002_XQ01 | 31145 | ROTOR EARTH RESISTANCE | M? | float32
TCS2.21MKC20CE001_XQ01 | 31146 | EXCITATION CURRENT | A | float32
TCS2.21MKC20CE002_XQ01 | 31147 | EXCITATION VOLTAGE | V | float32
TCS2.21MKD11CT601_XQ01 | 31148 | BRG OIL OUTLET TEMP GTE | C | float32
TCS2.21MKD11CT602_XQ01 | 31149 | GEN GTE SIDE BEARING TEMP | °C | float32
TCS2.21MKD11CT602_XQ11 | 31150 | GEN GTE SIDE BEARING TEMP | °C | float32
TCS2.21MKD11CY021_XQ01 | 31151 | GEN GTE SIDE BEARING ABS VIBR CH. A | mm/s | float32
TCS2.21MKD11CY022_XQ01 | 31152 | GEN GTE SIDE BEARING ABS VIBR CH. B | mm/s | float32
TCS2.21MKD11CY940_XQ01 | 31153 | GEN GTE SIDE BEARING REL VIBR Smax VALUE | um | float32
TCS2.21MKD12CT601_XQ01 | 31154 | BRG OIL OUTLET TEMP EE | C | float32
TCS2.21MKD12CT602_XQ01 | 31155 | GEN EE SIDE BEARING TEMP | °C | float32
TCS2.21MKD12CT602_XQ11 | 31156 | GEN EE SIDE BEARING TEMP | °C | float32
TCS2.21MKD12CY021_XQ01 | 31157 | GEN ABS VIBR CE BEARING CH. A | mm/s | float32
TCS2.21MKD12CY022_XQ01 | 31158 | GEN ABS VIBR CE BEARING CH. B | mm/s | float32
TCS2.21MKD12CY940_XQ01 | 31159 | GEN CE SIDE BEARING REL VIBR Smax VALUE | um | float32
TCS2.21MKD13CT601_XQ01 | 31160 | BRG OIL OUTLET TEMP COLLECTOR | C | float32
TCS2.21MKD13CT602_XQ01 | 31161 | BRG TEMP COLLECTOR | °C | float32
TCS2.21MKD13CT602_XQ11 | 31162 | BRG TEMP COLLECTOR | °C | float32
TCS2.21MKD13CY021_XQ01 | 31163 | GEN COLLECTOR SIDE BEARING ABS VIBR CH. A | mm/s | float32
TCS2.21MKD13CY022_XQ01 | 31164 | GEN COLLECTOR SIDE BEARING ABS VIBR CH. B | mm/s | float32
TCS2.21MKD13CY940_XQ01 | 31165 | GEN COLLECTOR SIDE BEARING REL VIBR Smax | um | float32
TCS2.21MKF05CL101_XQ01 | 31166 | STATOR WTR PRIMARY TANK | mm | float32
TCS2.21MKF11AP001_DCO | 31167 | PRIMARY WTR PUMP 1 |  | float32
TCS2.21MKF11AP001_XQ01 | 31168 | PRIMARY WTR PUMP 1 CURRENT | A | float32
TCS2.21MKF12AP001_DCO | 31169 | PRIMARY WTR PUMP 2 |  | float32
TCS2.21MKF12AP001_XQ01 | 31170 | PRIMARY WTR PUMP 2 CURRENT | A | float32
TCS2.21MKF18CQ101_XQ01 | 31171 | CONDUCT MAIL LOOP | ?S/cm | float32
TCS2.21MKF19CF101_XQ01 | 31172 | F STATOR WATER | m?/h | float32
TCS2.21MKF20CT301_XQ01 | 31173 | T U/S STATOR WATER | C | float32
TCS2.21MKF20CT302_XQ01 | 31174 | T D/S STATOR WATER | C | float32
TCS2.21MKF23CQ101_XQ01 | 31175 | CONDUCT TREATMENT LOOP | ?S/cm | float32
TCS2.21MKF30CP101_XQ01 | 31176 | DP STATOR WINDING | kPa | float32
TCS2.21MKG21CP101_XQ01 | 31177 | PRES HYDROGEN SUPPLY | MPa | float32
TCS2.21MKG24CF101_XQ01 | 31178 | M/U H2 FLOW | m?/h | float32
TCS2.21MKG26CP101_XQ01 | 31179 | PRES H2 GEN CASING | kPa | float32
TCS2.21MKG30CQ901_XQ01 | 31180 | H2 GAS ANALYZER 1 | % H2 | float32
TCS2.21MKG30CQ901_XQ01_MULTIPLY | 31181 | H2 GAS ANALYZER 1 | %H2 | float32
TCS2.21MKG35CQ401_XQ01 | 31182 | H2 LEAKAGE DETECTOR 1 | % | float32
TCS2.21MKG35CQ401_XQ02 | 31183 | H2 LEAKAGE DETECTOR 2 | % | float32
TCS2.21MKG35CQ401_XQ03 | 31184 | LEAKAGE DETECTOR 3 | % | float32
TCS2.21MKG35CQ401_XQ04 | 31185 | LEAKAGE DETECTOR 4 | % | float32
TCS2.21MKG35CQ401_XQ05 | 31186 | LEAKAGE DETECTOR 5 | % | float32
TCS2.21MKG35CQ401_XQ06 | 31187 | LEAKAGE DETECTOR 6 | % | float32
TCS2.21MKG35CQ401_XQ07 | 31188 | LEAKAGE DETECTOR 7 | % | float32
TCS2.21MKG51CM101_XQ01 | 31189 | DEW POINT D/STR DRY | Td | float32
TCS2.21MKG52CM102_XQ01 | 31190 | DEW POINT D/STR DRY | Td | float32
TCS2.21MKW06CL101_XQ01 | 31191 | LEVEL TANK HYDROGEN | mm | float32
TCS2.21MKW11AP001_DCO | 31192 | ~AIR SEAL OIL PUMP 1 |  | float32
TCS2.21MKW11AP001_XQ01 | 31193 | SEAL OIL PUMP 1 CURRENT | A | float32
TCS2.21MKW12AP001_DCO | 31194 | ~AIR SEAL OIL PUMP 2 |  | float32
TCS2.21MKW12AP001_XQ01 | 31195 | SEAL OIL PUMP 2 CURRENT | A | float32
TCS2.21MKW13AP001_XQ01 | 31196 | DC SEAL OIL PUMP CURRENT | A | float32
TCS2.21MKW14CT301_XQ01 | 31197 | TEMP D/S COOLER AIR SIDE | C | float32
TCS2.21MKW19CP101_XQ01 | 31198 | PRES SEAL OIL TE REG A/S | kPa | float32
TCS2.21MKW25AP001_DCO | 31199 | ~H2 GAS SEAL OIL PUMP 1 |  | float32
TCS2.21MKW25AP001_XQ01 | 31200 | ~SEAL OIL PUMP 1#(H2) | A | float32
TCS2.21MKW26AP001_DCO | 31201 | ~H2 GAS SEAL OIL PUMP 2 |  | float32
TCS2.21MKW26AP001_XQ01 | 31202 | H2 GAS SEAL OIL PUMP 5 | A | float32
TCS2.21MKW27CT301_XQ01 | 31203 | TEMP D/S COOLER GAS SIDE | C | float32
TCS2.21MKW51AN001_DCO | 31204 | GEN EXH BLWR 1 |  | float32
TCS2.21MKW51CP101_XQ01 | 31205 | PRES U/S EXH BLWR 1 | kPa | float32
TCS2.21MKW52AN001_DCO | 31206 | GEN EXH BLWR 2 |  | float32
TCS2.21MKW52CP101_XQ01 | 31207 | PRES U/S EXH BLWR 2 | kPa | float32
TCS2.20EKG60FF001_COUNT_ZV10 | 31208 |  | Nm3 | float32
TCS2.20CJQ02GS001_XM11 | 31209 | \ |  | digital
TCS2.20CJQ02GW001_XM31 | 31210 | \ |  | digital
TCS2.20CYE01EG001_XB01 | 31211 | ENCLOSURE TG/GAS | \ | digital
TCS2.20CYE01EG001_XB02 | 31212 | ENCLOSURE TG/GAS | \ | digital
TCS2.20CYE01EG001_XB11 | 31213 | ENCLOSURE TG/GAS | \ | digital
TCS2.20EKE31CL081_XB01 | 31214 | FILTER 1 STAGE 2 | \ | digital
TCS2.20EKE31CL083_XB01 | 31215 | FILTER 1 STAGE 1 | \ | digital
TCS2.20EKE31CP081_XB01 | 31216 | DIFF PRESSURE GAS FINAL FILTER 1 | \ | digital
TCS2.20EKE31CQ501_XB03HW | 31217 | \ |  | digital
TCS2.20EKE32CL081_XB01 | 31218 | FILTER 2 STAGE 2 | \ | digital
TCS2.20EKE32CL083_XB01 | 31219 | FILTER 2 STAGE 1 | \ | digital
TCS2.20EKE32CP081_XB01 | 31220 | DIFF PRESSURE GAS FINAL FILTER 2 | \ | digital
TCS2.20EKE32CQ501_XH01 | 31221 | \ |  | digital
TCS2.20EKG60CQ501_XH01 | 31222 | LEAKAGE ALARM 1 HIGH & HIGH | \ | digital
TCS2.20EKG60FF001_XB03 | 31223 | \ |  | digital
TCS2.20EKG60FF101_COUNT_ZV10 | 31224 | \ |  | digital
TCS2.20EKG60FF101_XQ01 | 31225 | \ |  | digital
TCS2.20EKG70AA001_XG01 | 31226 | BLOCK VLV AA001 | \ | digital
TCS2.20EKG70CQ501_XH01 | 31227 | LEAK ALARM H | \ | digital
TCS2.20MBA10AT001_XB01 | 31228 | AIR DRYER | \ | digital
TCS2.20MBA10CG001_XG02 | 31229 | SAFETY SWITCH FOR INTERM. SHAFT | \ | digital
TCS2.20MBA10CG002_XG02 | 31230 | SAFETY SWITCH FOR INTERM. SHAFT | \ | digital
TCS2.20MBA10CG003_XG02 | 31231 | SAFETY SWITCH FOR INTERM. SHAFT | \ | digital
TCS2.20MBA10EU010_ZV51 | 31232 | SAFETY SWITCH FOR INTERM. SHAFT | \ | digital
TCS2.20MBA10EZ001_ZV01 | 31233 | OVER-/UNDERFREQUENCY | \ | digital
TCS2.20MBA10EZ001_ZV13 | 31234 | OVER-/UNDERFREQUENCY | \ | digital
TCS2.20MBA10FG100_ZV01 | 31235 | ROTOR AXIAL DISPLACEMENT | \ | digital
TCS2.20MBA10FG100_ZV02 | 31236 | ROTOR AXIAL DISPLACEMENT | \ | digital
TCS2.20MBA10FS010_XK01 | 31237 | HW TRIP (BRAUN) | \ | digital
TCS2.20MBA11AS001_XG01 | 31238 | IGV MAX LIMIT POSITION ON ACTUATOR | \ | digital
TCS2.20MBA11AS002_XG01 | 31239 | CV MAX LIMIT POSITION ON ACTUATOR | \ | digital
TCS2.20MBA11CG001_XG01 | 31240 | IGV MAX LIMIT POSITION ON RING | \ | digital
TCS2.20MBA11CG002_XG01 | 31241 | IGV MIN LIMIT POSITION ON RING | \ | digital
TCS2.20MBA11CG011_XG01 | 31242 | CV MAX LIMIT POSITION ON RING | \ | digital
TCS2.20MBA11CG012_XG01 | 31243 | CV MIN LIMIT POSITION ON RING | \ | digital
TCS2.20MBA11CT901_ZV02 | 31244 | COMPRESSOR AIR INLET TEMP | \ | digital
TCS2.20MBA11DG012_804189_OUT | 31245 | \ |  | digital
TCS2.20MBA26EZ001_B1 | 31246 | \ |  | digital
TCS2.20MBA26EZ001_B24 | 31247 | \ |  | digital
TCS2.20MBA26EZ001_B24_1 | 31248 | \ |  | digital
TCS2.20MBA26EZ001_ZV01 | 31249 | TURBINE EXHAUST GAS TEMP ANALYSIS | \ | digital
TCS2.20MBA26EZ001_ZV02 | 31250 | TURBINE EXHAUST GAS TEMP ANALYSIS | \ | digital
TCS2.20MBA26EZ001_ZV91 | 31251 | TURBINE EXHAUST GAS TEMP ANALYSIS | \ | digital
TCS2.20MBA40EZ001_ZV01 | 31252 | COMPR BLOWOFF PROT | \ | digital
TCS2.20MBA41AA051_XB02 | 31253 | COMP BLOWOFF VLV 1.1 | \ | digital
TCS2.20MBA42AA051_XB02 | 31254 | COMP BLOWOFF VLV 1.2 | \ | digital
TCS2.20MBA43AA051_XB02 | 31255 | COMP BLOWOFF VLV 2 | \ | digital
TCS2.20MBA44AA051_XB02 | 31256 | COMP BLOWOFF VLV 3 | \ | digital
TCS2.20MBA50EC001_REG_TIME_OUT | 31257 | \ |  | digital
TCS2.20MBA50EC001_ON | 31258 | SGC RDS | \ | digital
TCS2.20MBA50EC001_XA01 | 31259 | SGC RDS | \ | digital
TCS2.20MBA50EC001_ZV03 | 31260 | SGC RDS | \ | digital
TCS2.20MBA50EC001_ZV04 | 31261 | SGC RDS | \ | digital
TCS2.20MBA50EC001_ZV12 | 31262 | \ |  | digital
TCS2.20MBA50EC001_ZV21 | 31263 | \ |  | digital
TCS2.20MBA50EU003_ZV20 | 31264 | \ |  | digital
TCS2.20MBA50EU005_ON | 31265 | \ |  | digital
TCS2.20MBA50EU005_RUN2 | 31266 | \ |  | digital
TCS2.20MBA51AA251_XG02 | 31267 | RDS PUMP 1 FEED VLV | \ | digital
TCS2.20MBA51AA252_XG02 | 31268 | RDS PUMP 2 FEED VLV | \ | digital
TCS2.20MBA51AP001_XB01 | 31269 | RDS PUMP 1 | \ | digital
TCS2.20MBA51AP002_XB01 | 31270 | RDS PUMP 2 | \ | digital
TCS2.20MBA51CP001_XB01 | 31271 | RDS DOWSTR PUMP 1 PRESSURE | \ | digital
TCS2.20MBA51CP002_XB01 | 31272 | RDS DOWSTR PUMP 2 PRESSURE | \ | digital
TCS2.20MBA51CP003_XB01 | 31273 | RDS FEED LINE 1 DP FILTER | \ | digital
TCS2.20MBA51CP004_XB01 | 31274 | RDS FEED LINE 2 DP FILTER | \ | digital
TCS2.20MBA52CP001_XB01 | 31275 | RDS LUBE OIL DP FILTER | \ | digital
TCS2.20MBA53AA001_XG52 | 31276 | RDS MAIN CH RETURN VLV | \ | digital
TCS2.20MBA53AA002_XG01 | 31277 | RDS MAIN CH SUPPLY VLV | \ | digital
TCS2.20MBA53AA003_XG01 | 31278 | RDS MAIN CH SUPPLY VLV | \ | digital
TCS2.20MBA53AA004_XG52 | 31279 | RDS SECOND CH FEED VLV | \ | digital
TCS2.20MBA53AA005_XG01 | 31280 | RDS SECOND CH RETURN VLV | \ | digital
TCS2.20MBA53AA006_XG01 | 31281 | RDS MAIN CH SUPPLY VLV | \ | digital
TCS2.20MBA53FP101_ZV11 | 31282 | MAIN RETURN LINE PRESS | \ | digital
TCS2.20MBA53FP102_ZV11 | 31283 | SEC RETURN LINE PRESS | \ | digital
TCS2.20MBD11EZ110_XK01 | 31284 | TURBINE BEARING TEMP CH.1 | \ | digital
TCS2.20MBD11EZ120_XK01 | 31285 | TURBINE BEARING TEMP CH.2 | \ | digital
TCS2.20MBD11EZ210_XK01 | 31286 | TURBINE BEARING VIBR | \ | digital
TCS2.20MBD12EZ110_XK01 | 31287 | COMP. BEARINGS TEMP | \ | digital
TCS2.20MBD12EZ120_XK01 | 31288 | THRUST BEARINGS TEMP GEN PART | \ | digital
TCS2.20MBD12EZ130_XK01 | 31289 | COMP. THRUST BEARING UPPER PART | \ | digital
TCS2.20MBD12EZ210_XK01 | 31290 | ~COMP. BEARINGS VIBR. | \ | digital
TCS2.20MBH22AA101_XG01 | 31291 | COOL AIR DAMPER 1 STAGE 2 | \ | digital
TCS2.20MBH22AA102_XG01 | 31292 | COOL AIR DAMPER 2 STAGE 2 | \ | digital
TCS2.20MBH22FP100_ZQ01 | 31293 | \ |  | digital
TCS2.20MBH23AA101_XG01 | 31294 | COOL AIR DAMPER 1 STAGE 3 | \ | digital
TCS2.20MBH23AA102_XG01 | 31295 | COOL AIR DAMPER 2 STAGE 3 | \ | digital
TCS2.20MBH23FP100_ZQ01 | 31296 | \ |  | digital
TCS2.20MBJ01EC001_XA03 | 31297 |  |  | digital
TCS2.20MBJ01EU003_89901_OUT | 31298 | \ |  | digital
TCS2.20MBJ01EU003_963297_OUT | 31299 | \ |  | digital
TCS2.20MBJ01EZ001_SLC_ON | 31300 |  |  | digital
TCS2.20MBJ20EA008_RESET_ON | 31301 |  |  | digital
TCS2.20MBJ20EU001_PRESEL_SEL2 | 31302 |  |  | digital
TCS2.20MBJ20EU001_XT42 | 31303 | SFC MODE | \ | digital
TCS2.20MBJ20EU005_EN_ON | 31304 | SFC START/STOP | \ | digital
TCS2.20MBJ20EU006_239237_SEL3 | 31305 |  |  | digital
TCS2.20MBK21EU001_ZV55 | 31306 | TURNING GEAR LIMIT SWITCH | \ | digital
TCS2.20MBK21EU001_ZV56 | 31307 | TURNING GEAR LIMIT SWITCH | \ | digital
TCS2.20MBK21EU001_ZV62 | 31308 | TURNING GEAR LIMIT SWITCH | \ | digital
TCS2.20MBL10CG101_XG01 | 31309 | INSPECTION DOOR 1 | \ | digital
TCS2.20MBL10CG102_XG01 | 31310 | INSPECTION DOOR 2 | \ | digital
TCS2.20MBL10CG103_XG01 | 31311 | INSPECTION DOOR 3 | \ | digital
TCS2.20MBL10CG104_XG01 | 31312 | INSPECTION DOOR 4 | \ | digital
TCS2.20MBL10CU00X_XB01 | 31313 | GT INLET AIR FILTRATION SYSTEM | \ | digital
TCS2.20MBL14CP001_XG01 | 31314 | INTAKE TOTAL FILTER DP 1 | \ | digital
TCS2.20MBL14CP002_XG01 | 31315 | INTAKE TOTAL FILTER DP 2 | \ | digital
TCS2.20MBL17EU001_ZV52 | 31316 | ANTI IMPLOSION DOOR 1 | \ | digital
TCS2.20MBL17EU002_ZV52 | 31317 | ANTI IMPLOSION DOOR 2 | \ | digital
TCS2.20MBL17EU003_ZV52 | 31318 | ANTI IMPLOSION DOOR 3 | \ | digital
TCS2.20MBL17EU004_ZV52 | 31319 | ANTI IMPLOSION DOOR 4 | \ | digital
TCS2.20MBL20AA001_XB01 | 31320 | AIR DAMPER | \ | digital
TCS2.20MBL20CG011_XG01 | 31321 | INSPECTION DOOR 1 | \ | digital
TCS2.20MBL20CG012_XG01 | 31322 | INSPECTION DOOR 2 | \ | digital
TCS2.20MBL20CG013_XG01 | 31323 | INSPECTION DOOR 3 | \ | digital
TCS2.20MBL20CG014_XG01 | 31324 | INSPECTION DOOR 4 | \ | digital
TCS2.20MBL20EU001_ZV01 | 31325 | ~INSPECTION DOORS PERM. | \ | digital
TCS2.20MBL21CQ101_XB01 | 31326 | ICE DETECTOR | \ | digital
TCS2.20MBL30CP001_XG01 | 31327 | ~INLET AIR FILTR PRESS FROM AUX COMPR | \ | digital
TCS2.20MBM00EU006_XT51 | 31328 | \ |  | digital
TCS2.20MBM00EU007_ZV01 | 31329 | \ |  | digital
TCS2.20MBM12GT001_XB01 | 31330 | IGN TRF | \ | digital
TCS2.20MBM13CR101_XB12 | 31331 | FLAME 1 | \ | digital
TCS2.20MBM13CR102_XB12 | 31332 | FLAME 2 | \ | digital
TCS2.20MBM13EU010_ZV01 | 31333 | FLAME | \ | digital
TCS2.20MBM13EU010_ZV01HW | 31334 | FLAME |  | digital
TCS2.20MBM13EU011_ZV09 | 31335 | FLAME MONITORING | \ | digital
TCS2.20MBP00EU001_XV01 | 31336 | \ |  | digital
TCS2.20MBP01EC001_ON | 31337 |  |  | digital
TCS2.20MBP01EC001_ZA01 | 31338 | \ |  | digital
TCS2.20MBP03DU001_ZV01 | 31339 | NG CONTROLLER TRIP | \ | digital
TCS2.20MBP03DU003_1FEGVB_OUT | 31340 | \ |  | digital
TCS2.20MBP03DU003_COMB_LOAD_VAR_NG_OUT | 31341 |  |  | digital
TCS2.20MBP03DU003_STEP_OUT | 31342 |  |  | digital
TCS2.20MBP13AA051_ZG01 | 31343 | FG STOP VALVE | \ | digital
TCS2.20MBP13AA051_ZV01 | 31344 | \ |  | digital
TCS2.20MBP13AA501_ZG01 | 31345 | \ |  | digital
TCS2.20MBP22AA151_ZV01HW | 31346 | \ |  | digital
TCS2.20MBP22DG151_XG01 | 31347 | ~PILOT 1 CTRL POSN | \ | digital
TCS2.20MBP24AA151_ZV01HW | 31348 | \ |  | digital
TCS2.20MBP24DG151_XG01 | 31349 | NG PILOT 2 CTRL POSN | \ | digital
TCS2.20MBP32AH001_XT01 | 31350 | FG PREMIX HEAT. | \ | digital
TCS2.20MBP34AH001_XT01 | 31351 | FG PILOT 2 HEAT. | \ | digital
TCS2.20MBV00EE010_XA01 | 31352 | LUBE OIL HEATING | \ | digital
TCS2.20MBV01EC001_XA41 | 31353 | \ |  | digital
TCS2.20MBV02EC001_XA03 | 31354 | \ |  | digital
TCS2.20MBV10CL001_XG01 | 31355 | LUBE OIL TANK LEVEL | \ | digital
TCS2.20MBV10CL001_XG02 | 31356 | LUBE OIL TANK LEVEL | \ | digital
TCS2.20MBV10CL001_XG03 | 31357 | LUBE OIL TANK LEVEL | \ | digital
TCS2.20MBV10CL001_XG04 | 31358 | LUBE OIL TANK LEVEL | \ | digital
TCS2.20MBV10CL002_XG01 | 31359 | LUBE OIL TANK LEVEL | \ | digital
TCS2.20MBV10CL002_XG02 | 31360 | LUBE OIL TANK LEVEL | \ | digital
TCS2.20MBV10CL002_XG03 | 31361 | LUBE OIL TANK LEVEL | \ | digital
TCS2.20MBV10CL002_XG04 | 31362 | LUBE OIL TANK LEVEL | \ | digital
TCS2.20MBV10EZ001_ZK51 | 31363 | LUBE OIL TANK LVL | \ | digital
TCS2.20MBV21AP001_EN_START | 31364 | MAIN LUBE OIL PUMP | \ | digital
TCS2.20MBV21AP001_XB01 | 31365 | MAIN LUBE OIL PUMP | \ | digital
TCS2.20MBV21AP002_EN_START | 31366 | AUX LUBE OIL PUMP | \ | digital
TCS2.20MBV21AP002_XB01 | 31367 | AUX LUBE OIL PUMP | \ | digital
TCS2.20MBV21AP003_696654_ON | 31368 | \ |  | digital
TCS2.20MBV21AP003_EN_START | 31369 | EMERG LUBE OIL PUMP | \ | digital
TCS2.20MBV21AP003_XB01 | 31370 | EMERG LUBE OIL PUMP | \ | digital
TCS2.20MBV21AP003_XB04 | 31371 | EMERG LUBE OIL PUMP | \ | digital
TCS2.20MBV21CP001_XG51 | 31372 | LUBE OIL PUMP PRESS | \ | digital
TCS2.20MBV21EU007_ZV01 | 31373 | ~STARTUP FROM SPEED ZERO | \ | digital
TCS2.20MBV21EU008_291005_OUT | 31374 | \ |  | digital
TCS2.20MBV21EU009_240332_ON | 31375 | \ |  | digital
TCS2.20MBV21EZ001_ZV01 | 31376 | LUBE OIL PUMP OFF | \ | digital
TCS2.20MBV25CP001_XG51 | 31377 | OIL FILTER DIFF PRESS | \ | digital
TCS2.20MBV26AA510_YB11HW | 31378 | EMERG LUBE OIL PUMP VLV |  | digital
TCS2.20MBV26CP002_XG11 | 31379 | LUBE OIL PRESS DOWNSTR. FILTERS | \ | digital
TCS2.20MBV26CP003_XG02 | 31380 | LUBE OIL PRESS DOWNSTR. FILTERS | \ | digital
TCS2.20MBV26EZ001_XK52 | 31381 | LUBE OIL SYSTEM PRESS. | \ | digital
TCS2.20MBV30AP001_XB01 | 31382 | LIFT OIL PUMP | \ | digital
TCS2.20MBV30AP002_XB01 | 31383 | AUX LIFT OIL PUMP | \ | digital
TCS2.20MBV30CP001_XG01 | 31384 | LIFT OIL FILTER | \ | digital
TCS2.20MBV35AA001_XB01 | 31385 | TURNING GEAR CLUTCH A001 VLV | \ | digital
TCS2.20MBV35AA002_XB01 | 31386 | TURNING GEAR CLUTCH A002 VLV | \ | digital
TCS2.20MBV35AA003_XB01 | 31387 | TURNING GEAR A003 VLV | \ | digital
TCS2.20MBV35AA101_YB01HW | 31388 | \ |  | digital
TCS2.20MBV35AA101_YB21HW | 31389 | \ |  | digital
TCS2.20MBV50AN001_XB01 | 31390 | LUBE OIL TANK VENT FAN 1 | \ | digital
TCS2.20MBV50AN002_XB01 | 31391 | LUBE OIL TANK VENT FAN 2 | \ | digital
TCS2.20MBV50EE010_309391_ON | 31392 | \ |  | digital
TCS2.20MBX01CL001_XG02 | 31393 | HYD OIL TANK LEVEL | \ | digital
TCS2.20MBX01CL002_XG02 | 31394 | HYD OIL TANK LEVEL | \ | digital
TCS2.20MBX01CL002_XG12 | 31395 | HYD OIL TANK LEVEL | \ | digital
TCS2.20MBX01EE001_309616_RUN2 | 31396 |  |  | digital
TCS2.20MBX01EE001_309844_RUN2 | 31397 |  |  | digital
TCS2.20MBX01EZ001_XQ01 | 31398 | \ |  | digital
TCS2.20MBX02AP001_XB01 | 31399 | HYD OIL PUMP 1 | \ | digital
TCS2.20MBX02AP002_XB01 | 31400 | HYD OIL PUMP 2 | \ | digital
TCS2.20MBX03CP002_XG52 | 31401 | HYD OIL FILTER 2 | \ | digital
TCS2.20MBX03CP005_XG11 | 31402 | HYD OIL DELIVERY LINE PRESSURE | \ | digital
TCS2.20MBX03CP006_XG02 | 31403 | HYD OIL DELIVERY LINE PRESSURE | \ | digital
TCS2.20MBX03CP101_XH54 | 31404 | HYD OIL DELIVERY LINE PRESSURE | \ | digital
TCS2.20MBX03CQ001_XG01 | 31405 | HYD OIL CONTAMINATION DEGREE (OIL PURITY) | \ | digital
TCS2.20MBX03CQ001_XG11 | 31406 | HYD OIL CONTAMINATION DEGREE (OIL PURITY) | \ | digital
TCS2.20MBX03EZ001_ZV02 | 31407 | HYD OIL LINE STATUS | \ | digital
TCS2.20MBX06AH001_YB01HW | 31408 | HYD OIL COOLER FAN |  | digital
TCS2.20MBX06CP001_XG51 | 31409 | HYD OIL FILTRATION LINE PRESSURE | \ | digital
TCS2.20MBX08CP001_XG52 | 31410 | HYD OIL COOLING LINE FILTER | \ | digital
TCS2.20MBX70CP001_XG01 | 31411 | HYD OIL FILTER STOP VLV ACTUATOR (PREMIX LINE) | \ | digital
TCS2.20MBX81CP001_XG01 | 31412 | HYD OIL FILTER PREMIX CV ACTUATOR | \ | digital
TCS2.20MBX90AA002A_YB11HW | 31413 | SOV A MBA41AA051 |  | digital
TCS2.20MBX90AA002A_ZV03 | 31414 | SOV A MBA41AA051 | \ | digital
TCS2.20MBX90AA002B_YB11HW | 31415 | SOV B MBA41AA051 |  | digital
TCS2.20MBX90AA002B_ZV03 | 31416 | SOV B MBA41AA051 | \ | digital
TCS2.20MBX91AA002A_YB11HW | 31417 | SOV A MBA42AA051 |  | digital
TCS2.20MBX91AA002A_ZV03 | 31418 | SOV A MBA42AA051 | \ | digital
TCS2.20MBX91AA002B_YB11HW | 31419 | SOV B MBA42AA051 |  | digital
TCS2.20MBX91AA002B_ZV03 | 31420 | SOV B MBA42AA051 | \ | digital
TCS2.20MBX92AA002A_YB11HW | 31421 | SOV A MBA43AA051 |  | digital
TCS2.20MBX92AA002A_ZV03 | 31422 | SOV A MBA43AA051 | \ | digital
TCS2.20MBX92AA002B_ZV03 | 31423 | SOV B MBA43AA051 | \ | digital
TCS2.20MBX93AA002A_YB11HW | 31424 | SOV A MBA44AA051 |  | digital
TCS2.20MBX93AA002A_ZV03 | 31425 | SOV A MBA44AA051 | \ | digital
TCS2.20MBX93AA002B_YB11HW | 31426 | SOV B MBA44AA051 |  | digital
TCS2.20MBX93AA002B_ZV03 | 31427 | SOV B MBA44AA051 | \ | digital
TCS2.20MBY00DU100_XK01 | 31428 | ~GT CONTROLLER | \ | digital
TCS2.20MBY00EY010_ZV01 | 31429 | FIRE PROTECTION GT | \ | digital
TCS2.20MBY10DE010_134664_OUT | 31430 | \ |  | digital
TCS2.20MBY10DE010_134666_ON | 31431 | \ |  | digital
TCS2.20MBY10DE010_711763_ON | 31432 | \ |  | digital
TCS2.20MBY10DE010_XA01 | 31433 | LOAD SETPOINT | \ | digital
TCS2.20MBY10DE010_XT61 | 31434 | \ |  | digital
TCS2.20MBY10DE050_PSFE_XT03 | 31435 | \ |  | digital
TCS2.20MBY10DT040_XT04 | 31436 | ~COMPR RA-C ON IGV | \ | digital
TCS2.20MBY10DT040_XT05 | 31437 | ~COOL AIR LMT CTRL ON IGV | \ | digital
TCS2.20MBY10DT040_ZV01 | 31438 | \ |  | digital
TCS2.20MBY10DT060_1PIV_OUT | 31439 | \ |  | digital
TCS2.20MBY10DU010_ZV01 | 31440 | \ |  | digital
TCS2.20MBY10DU050_128725_ON | 31441 | \ |  | digital
TCS2.20MBY10DU050_PSFE_XT03 | 31442 | ~PRIM FREQ INFL | \ | digital
TCS2.20MBY10DU050_XA01 | 31443 | SPEED/LOAD CTRL | \ | digital
TCS2.20MBY10DU050_XQ04 | 31444 | \ |  | digital
TCS2.20MBY10DU050_XQ05 | 31445 | \ |  | digital
TCS2.20MBY10DU050_XQ06 | 31446 | \ |  | digital
TCS2.20MBY10DU050_XT01 | 31447 | ~LOAD OP SPEED CTRL | \ | digital
TCS2.20MBY10DU050_XT02 | 31448 | ~LOAD OP LOAD CTRL | \ | digital
TCS2.20MBY10DU050_XT03 | 31449 | \ |  | digital
TCS2.20MBY10DU050_XT04 | 31450 | \ |  | digital
TCS2.20MBY10DU050_XT05 | 31451 | \ |  | digital
TCS2.20MBY10DU050_XT06 | 31452 | \ |  | digital
TCS2.20MBY10DU050_XT07 | 31453 | \ |  | digital
TCS2.20MBY10DU050_XT13 | 31454 | \ |  | digital
TCS2.20MBY10DU050_XT14 | 31455 | \ |  | digital
TCS2.20MBY10DU050_XT52 | 31456 | \ |  | digital
TCS2.20MBY10DU050_XT53 | 31457 | \ |  | digital
TCS2.20MBY10DU050_XT54 | 31458 | \ |  | digital
TCS2.20MBY10DU050_ZV02 | 31459 | SPEED/LOAD CTRL | \ | digital
TCS2.20MBY10DU060_1PIVVMXL_OUT | 31460 | \ |  | digital
TCS2.20MBY10DU060_1PIVMAX | 31461 |  |  | digital
TCS2.20MBY10DU060_1PIVMXL | 31462 |  |  | digital
TCS2.20MBY10DU060_1WPGR | 31463 |  |  | digital
TCS2.20MBY10DU060_XA03 | 31464 | \ |  | digital
TCS2.20MBY10DU060_XT03 | 31465 | COMBUSTION LOAD SETPOINT | \ | digital
TCS2.20MBY10DU060_XT04 | 31466 | COMBUSTION LOAD SETPOINT | \ | digital
TCS2.20MBY10DU060_XT05 | 31467 | ~RUN UP FUNCTION | \ | digital
TCS2.20MBY10DU060_XT06 | 31468 | COMBUSTION LOAD SETPOINT | \ | digital
TCS2.20MBY10DU060_XT07 | 31469 | ~OTC CONTROLLER | \ | digital
TCS2.20MBY10DU060_XT13 | 31470 | ~COMPR PRES RATIO LMT CTRL | \ | digital
TCS2.20MBY10DU060_XT14 | 31471 | ~COOLING AIR LMT CTRL | \ | digital
TCS2.20MBY10DU060_ZV03 | 31472 | COMBUSTION LOAD SETPOINT | \ | digital
TCS2.20MBY10DU090_XM63 | 31473 | \ |  | digital
TCS2.20MBY10EP801_ZV01 | 31474 | EQUIV OP HOURS | \ | digital
TCS2.20MBY10EU001_ZV99 | 31475 | GT UNLOAD | \ | digital
TCS2.20MYB00EU103_ZV13 | 31476 | MONIT COMM. AP2-AP1 | \ | digital
TCS2.20MYB00EU120_XA41 | 31477 | GT FAIL SAFE FUNCTIONS | \ | digital
TCS2.20MYB00EU120_ZV01 | 31478 | \ |  | digital
TCS2.20MYB01EC001_XA01 | 31479 | \ |  | digital
TCS2.20MYB01EC001_XA03 | 31480 | SGC GAS TURBINE | \ | digital
TCS2.20MYB01EC001_ZV01 | 31481 | SGC GAS TURBINE | \ | digital
TCS2.20MYB01EC001_ZV02 | 31482 | \ |  | digital
TCS2.20MYB01EC001_ZV20 | 31483 | \ |  | digital
TCS2.20MYB01EZ002_ZV01 | 31484 | GT TRIP CIRCUIT | \ | digital
TCS2.20MYB01EZ002_ZV10 | 31485 |  |  | digital
TCS2.20MYB01EZ141_XK01 | 31486 | TURB EXHAUST GAS TEMP HH | \ | digital
TCS2.20MYB01EZ201_COM | 31487 | HMI TRIP | \ | digital
TCS2.20MYB01EZ201_XA41 | 31488 | HMI TRIP | \ | digital
TCS2.20MYB01EZ201_ZV04A | 31489 | \ |  | digital
TCS2.20MYB01EZ201_ZV05A | 31490 | \ |  | digital
TCS2.20MYB01EZ201_ZV08A | 31491 | \ |  | digital
TCS2.20MYB01EZ201_ZV11A | 31492 | \ |  | digital
TCS2.20MYB01EZ201_ZV13A | 31493 | \ |  | digital
TCS2.20MYB01EZ201_ZV15A | 31494 | \ |  | digital
TCS2.20MYB01EZ201_ZV16A | 31495 | \ |  | digital
TCS2.20MYB01EZ201_ZV18A | 31496 | \ |  | digital
TCS2.20MYB01EZ201_ZV22A | 31497 | \ |  | digital
TCS2.20MYB01EZ902_ZV02 | 31498 | \ |  | digital
TCS2.20MYB01EZ902_ZV03 | 31499 | \ |  | digital
TCS2.20MYB01EZ902_ZV05 | 31500 | \ |  | digital
TCS2.20MYB01EZ902_ZV06 | 31501 | \ |  | digital
TCS2.20MYB01EZ902_ZV09 | 31502 | \ |  | digital
TCS2.20MYB01EZ902_ZV10 | 31503 | \ |  | digital
TCS2.20MYB01EZ902_ZV100 | 31504 | \ |  | digital
TCS2.20MYB01EZ902_ZV11 | 31505 | \ |  | digital
TCS2.20MYB01EZ902_ZV12 | 31506 | \ |  | digital
TCS2.20MYB01EZ902_ZV14 | 31507 | \ |  | digital
TCS2.20MYB01EZ902_ZV15 | 31508 | \ |  | digital
TCS2.20MYB01EZ902_ZV17 | 31509 | \ |  | digital
TCS2.20MYB01EZ902_ZV19 | 31510 | \ |  | digital
TCS2.20MYB01EZ902_ZV21 | 31511 | \ |  | digital
TCS2.20MYB01EZ902_ZV22 | 31512 | \ |  | digital
TCS2.20MYB01EZ902_ZV24 | 31513 | \ |  | digital
TCS2.20MYB01EZ902_ZV26 | 31514 | \ |  | digital
TCS2.20MYB01EZ902_ZV27 | 31515 | \ |  | digital
TCS2.20MYB01EZ902_ZV28 | 31516 | \ |  | digital
TCS2.20MYB01EZ902_ZV29 | 31517 | \ |  | digital
TCS2.20MYB01EZ902_ZV30 | 31518 | \ |  | digital
TCS2.20MYB01EZ902_ZV32 | 31519 | \ |  | digital
TCS2.20MYB01EZ902_ZV33 | 31520 | \ |  | digital
TCS2.20MYB01EZ902_ZV36 | 31521 | \ |  | digital
TCS2.20MYB01EZ902_ZV37 | 31522 | \ |  | digital
TCS2.20MYB01EZ902_ZV39 | 31523 | \ |  | digital
TCS2.20MYB01EZ902_ZV40 | 31524 | \ |  | digital
TCS2.20MYB01EZ902_ZV41 | 31525 | \ |  | digital
TCS2.20MYB01EZ902_ZV44 | 31526 | \ |  | digital
TCS2.20MYB01EZ902_ZV45 | 31527 | \ |  | digital
TCS2.20MYB01EZ902_ZV46 | 31528 | \ |  | digital
TCS2.20MYB01EZ902_ZV47 | 31529 | \ |  | digital
TCS2.20MYB01EZ902_ZV48 | 31530 | \ |  | digital
TCS2.20MYB01EZ902_ZV53 | 31531 | \ |  | digital
TCS2.20MYB01EZ902_ZV54 | 31532 | \ |  | digital
TCS2.20MYB01EZ902_ZV55 | 31533 | \ |  | digital
TCS2.20MYB01EZ902_ZV58 | 31534 | \ |  | digital
TCS2.20MYB01EZ902_ZV59 | 31535 | \ |  | digital
TCS2.20MYB01EZ902_ZV66 | 31536 | \ |  | digital
TCS2.20MYB01EZ902_ZV68 | 31537 | \ |  | digital
TCS2.20MYB01EZ902_ZV69 | 31538 | \ |  | digital
TCS2.20MYB01EZ902_ZV71 | 31539 | \ |  | digital
TCS2.20MYB01EZ902_ZV72 | 31540 | \ |  | digital
TCS2.20MYB01EZ902_ZV77 | 31541 | \ |  | digital
TCS2.20MYB01EZ902_ZV90 | 31542 | \ |  | digital
TCS2.20MYB01EZ902_ZV95 | 31543 | \ |  | digital
TCS2.20MYB01EZ902_ZV98 | 31544 | \ |  | digital
TCS2.20MYB01EZ902_ZV99 | 31545 | \ |  | digital
TCS2.20MYB10EU006_XA02 | 31546 | \ |  | digital
TCS2.20MYB10EU006_XT02 | 31547 | ~EXT LOAD SETPOINT ENABLED | \ | digital
TCS2.20SAM10AA001_XG01 | 31548 | GT ENC INLET FLAP 1 | \ | digital
TCS2.20SAM10AA002_XG01 | 31549 | GT ENC INLET FLAP 2 | \ | digital
TCS2.20SAM10AA003_XG01 | 31550 | GT ENC INLET FLAP 3 | \ | digital
TCS2.20SAM10AA004_XG01 | 31551 | GT ENC INLET FLAP 4 | \ | digital
TCS2.20SAM10AA005_XG01 | 31552 | GT ENC OUTLET FLAP 1 | \ | digital
TCS2.20SAM10AA006_XG01 | 31553 | GT ENC OUTLET FLAP 2 | \ | digital
TCS2.20SAM10AN001_XB01 | 31554 | GT ENC VENT FAN 1 | \ | digital
TCS2.20SAM10AN002_XB01 | 31555 | GT ENC VENT FAN 2 | \ | digital
TCS2.20SAM10AN003_XB01 | 31556 | GT ENC VENT FAN 3 | \ | digital
TCS2.20SAM10CF001_XG02 | 31557 | AIR FLOW ENC VENT | \ | digital
TCS2.20SAM10CF002_XG02 | 31558 | AIR FLOW ENC VENT | \ | digital
TCS2.20SAM10CF003_XG02 | 31559 | AIR FLOW ENC VENT | \ | digital
TCS2.20SAM10CP001_XG02 | 31560 | DP GT ENC VENT FAN 1 | \ | digital
TCS2.20SAM10CP002_XG02 | 31561 | DP GT ENC VENT FAN 2 | \ | digital
TCS2.20SAM10CP003_XG02 | 31562 | DP GT ENC VENT FAN 3 | \ | digital
TCS2.20SAM10EE010_SLC_ON | 31563 | \ |  | digital
TCS2.20SAM10EE010_PRESEL | 31564 | \ |  | digital
TCS2.20SAM10EE010_XA01 | 31565 | SLC GT ENC VENT M/A FLAP | \ | digital
TCS2.210MBP13EU010_193350_OUT | 31566 | \ |  | digital
TCS2.21AEA01GS001_XB02 | 31567 | HVCB | \ | digital
TCS2.21AYG02GT001_728751_ON | 31568 |  |  | digital
TCS2.21BAC01GS001_XB02 | 31569 | G.C.B. | \ | digital
TCS2.21BAC01GS002_XB02 | 31570 | EARTH DISC. SW. TRANSF. SIDE | \ | digital
TCS2.21BAC01GS003_XB02 | 31571 | EARTH DISC. SW. GEN. SIDE | \ | digital
TCS2.21BAC01GS004_MOTOR_XB02 | 31572 | SFC DISC SW MBM | \ | digital
TCS2.21BAC01GS008_XB02 | 31573 | LINE DISC. | \ | digital
TCS2.21BAW20GS301_MOTOR_RUNNING | 31574 | \ |  | digital
TCS2.21BAW20GS301_XB02 | 31575 | G.T.G. DISCONNECTOR | \ | digital
TCS2.21BBA10GS001_MOTOR_RUNNING | 31576 | \ |  | digital
TCS2.21BFA01EA001_453390_XB02 | 31577 | AUTO TRANSFER SWITCH | \ | digital
TCS2.21BFA01EA001_XB01 | 31578 | AUTO TRANSFER SWITCH | \ | digital
TCS2.21BFA01EA001_XB02 | 31579 | AUTO TRANSFER SWITCH | \ | digital
TCS2.21BFA01EG001_XB27 | 31580 | 380 BUS BAR | \ | digital
TCS2.21BFA02EA001_453390_XB02 | 31581 | AUTO TRANSFER SWITCH | \ | digital
TCS2.21BFA02EA001_XB01 | 31582 | AUTO TRANSFER SWITCH | \ | digital
TCS2.21BFA02EA001_XB02 | 31583 | AUTO TRANSFER SWITCH | \ | digital
TCS2.21BFA02EG001_XB27 | 31584 | 380 BUS BAR | \ | digital
TCS2.21BNA01EA001_XB01 | 31585 | ATD ACTION | \ | digital
TCS2.21BNA01EG003_453470_XB01 | 31586 | VT DISCONNECTOR | \ | digital
TCS2.21BNA01EG003_453471_XB01 | 31587 | DEVICE BLOCK OR ALARM SIGNAL | \ | digital
TCS2.21BNA01EG003_453472_XB01 | 31588 | LOSS OF DEVICE SUPPLY DC POWER | \ | digital
TCS2.21BNA01GS001A_XB02 | 31589 | EMCC INC CB A | \ | digital
TCS2.21BNA01GS001A_XB07 | 31590 | EMCC INC CB A | \ | digital
TCS2.21BNA01GS001B_XB02 | 31591 | EMCC INC CB B | \ | digital
TCS2.21BNA01GS001B_XB07 | 31592 | EMCC INC CB B | \ | digital
TCS2.21BRA01EG003_XB01 | 31593 | 220VAC 11BRA FEEDER | \ | digital
TCS2.21BUA01EG002_XB02 | 31594 | 110Vdc BUA INC. LINE BKR | \ | digital
TCS2.21MBA10EU010_ZV51 | 31595 | \ |  | digital
TCS2.21MBA10FS010_XT23A | 31596 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBA11CP001_XG01A | 31597 | \ |  | digital
TCS2.21MBA11CP002_XG01A | 31598 | \ |  | digital
TCS2.21MBA11CP003_XG01A | 31599 | \ |  | digital
TCS2.21MBJ10GT001_XB02 | 31600 | SFC FEEDER BKR | \ | digital
TCS2.21MBJ20EA001_XB01 | 31601 | SFC 1 IS ON | \ | digital
TCS2.21MBJ20EA001_XB02 | 31602 | SFC 1 IS OFF | \ | digital
TCS2.21MBJ20EA004_XB01 | 31603 | SFC 1 | \ | digital
TCS2.21MBJ20EA006_XB01 | 31604 | SFC X IS SELECTED BY UNIT X | \ | digital
TCS2.21MBJ20EA006_XB02 | 31605 | SFC X IS SELECTED BY OTHER UNIT | \ | digital
TCS2.21MBJ20EA007_XB01 | 31606 | SFC 1 STATUS | \ | digital
TCS2.21MBJ20EA007_XB02 | 31607 | SFC 1 STATUS | \ | digital
TCS2.21MBJ20EA011_XB01 | 31608 | SFC SPEED 2100 RPM REACHED | \ | digital
TCS2.21MBJ20EA013_XB01 | 31609 | SFC IS READY FOR OPERATION | \ | digital
TCS2.21MBJ20EA020_XB01 | 31610 | SFC MODE DIRECT STARTUP SELECTED | \ | digital
TCS2.21MBJ20EA021_XB01 | 31611 | SFC MODE PURGING SELECTED | \ | digital
TCS2.21MBJ20EA022_XB01 | 31612 | SFC MODE WASHING SELECTED | \ | digital
TCS2.21MBJ20EG001_XB01 | 31613 | SFC CUMULATIVE ALARM | \ | digital
TCS2.21MBJ20EZ001_XB01 | 31614 | SFC X | \ | digital
TCS2.21MBJ20GS002_XB02 | 31615 | SFC SW CROSS MBM03 | \ | digital
TCS2.21MBJ20GS003_XB02 | 31616 | SFC SW DIRECT MBM01 | \ | digital
TCS2.21MBM13CR900_ZV01 | 31617 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBN04DU001_ZV51A | 31618 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBN04DU001_ZV52A | 31619 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBN04DU001_ZV53A | 31620 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBP03DU001_ZV01A | 31621 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBP03DU001_ZV02A | 31622 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBP03DU001_ZV03A | 31623 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBP03DU900_ZV01 | 31624 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBR20CP001_XH03 | 31625 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBR20CP002_XH03 | 31626 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBR20CP003_XH03 | 31627 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBR20CP900_ZV01 | 31628 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MBX70AA001_ZV32FS | 31629 | \ |  | digital
TCS2.21MBX70AA001_ZV33FS | 31630 | \ |  | digital
TCS2.21MBX70AA031_ZV32FS | 31631 | \ |  | digital
TCS2.21MBX70AA031_ZV33FS | 31632 | \ |  | digital
TCS2.21MBX81AA002_ZV32FS | 31633 | \ |  | digital
TCS2.21MBX81AA002_ZV33FS | 31634 | \ |  | digital
TCS2.21MBX84AA001_ZV32FS | 31635 | \ |  | digital
TCS2.21MBX84AA001_ZV33FS | 31636 | \ |  | digital
TCS2.21MKA01CE005_XQ01 | 31637 | \ |  | digital
TCS2.21MKA01DE020_187610_COM | 31638 | BAC SELECTION | \ | digital
TCS2.21MKA01DE020_EN_SEL2 | 31639 | SEL BAC / AEA | \ | digital
TCS2.21MKA01DE020_XT01 | 31640 | AEA SELECTION | \ | digital
TCS2.21MKC10EA032_XB02 | 31641 | DE-EXC SWITCH | \ | digital
TCS2.21MKC10GT001_XB02 | 31642 | EXC FEEDER S201 BKR | \ | digital
TCS2.21MKC20EA001_453931_XB01 | 31643 | EXCITATION STATUS | \ | digital
TCS2.21MKC20EA001_XB01 | 31644 | EXCITATION STATUS | \ | digital
TCS2.21MKC20EA001_XB02 | 31645 | EXCITATION STATUS | \ | digital
TCS2.21MKC20EA014_XB01 | 31646 | EXCITATION MODE REG | \ | digital
TCS2.21MKC20EA014_XB02 | 31647 | EXCITATION MODE REG | \ | digital
TCS2.21MKC20EA014_XB03 | 31648 | EXCITATION MODE REG | \ | digital
TCS2.21MKC20EA020_XB01 | 31649 | ROTOR CURRENT LIMIT OPERATING | \ | digital
TCS2.21MKC20EA021_XB01 | 31650 | UNDER EXCIT LIMIT | \ | digital
TCS2.21MKC20EA023_XB01 | 31651 | V/Hz LIMIT | \ | digital
TCS2.21MKC20EA026_XB01 | 31652 | EXC LOC/REM | \ | digital
TCS2.21MKC20EA029_452005_ON | 31653 |  |  | digital
TCS2.21MKC20EA029_XB01 | 31654 | POWER SYSTEM STABILIZER | \ | digital
TCS2.21MKC20EA029_XB02 | 31655 | POWER SYSTEM STABILIZER | \ | digital
TCS2.21MKC20EA033_XB01 | 31656 | EXCITATION SELECTED BY SFC | \ | digital
TCS2.21MKC20EU001_ZV01 | 31657 | EXCITATION ON/OFF CMD | \ | digital
TCS2.21MKC20EU002_PRESEL_SEL3 | 31658 |  |  | digital
TCS2.21MKC20EU002_XQ01 | 31659 | \ |  | digital
TCS2.21MKC20EU005_ZV01 | 31660 | AVR REF. UP-DOWN | \ | digital
TCS2.21MKC20EU005_ZV02 | 31661 | AVR REF. UP-DOWN | \ | digital
TCS2.21MKC20EU007_117650_ON | 31662 |  |  | digital
TCS2.21MKC20EU007_COM | 31663 | ZERO REACTIVE POWER REQUEST | \ | digital
TCS2.21MKC20EZ001_XB01 | 31664 | EXCITATION TRIP | \ | digital
TCS2.21MKC20GT001_XB01 | 31665 | EXC FEEDER S102 BKR (STARTUP EXC) | \ | digital
TCS2.21MKC20GT002_XB28 | 31666 | ESC FEEDER S103 CLOSED | \ | digital
TCS2.21MKC30GT001_XB01HW | 31667 | EXC FEEDER BRK CLOSED S104 (FILED FLUSHING EXC |  | digital
TCS2.21MKD12CY021A_XQ01 | 31668 | \ |  | digital
TCS2.21MKD13EZ002_XK01 | 31669 | GEN COLLECTOR SIDE BEARING TEMP | \ | digital
TCS2.21MKF00EU001_ZV01 | 31670 | \ |  | digital
TCS2.21MKF05CL101_XG52 | 31671 | \ |  | digital
TCS2.21MKF05CP001_XG02 | 31672 | P WATER TANK | \ | digital
TCS2.21MKF10EE001_XA01 | 31673 | \ |  | digital
TCS2.21MKF11AP001_XB01 | 31674 | PRIMARY WTR PUMP 1 | \ | digital
TCS2.21MKF11CP001_XG02 | 31675 | P D/STR PRIM WTR PUMP1 | \ | digital
TCS2.21MKF12AP001_XB01 | 31676 | PRIMARY WTR PUMP 2 | \ | digital
TCS2.21MKF12CP001_XG02 | 31677 | P D/STR PRIM WTR PUMP2 | \ | digital
TCS2.21MKF16CP001_XG02 | 31678 | DP U/S FILTER | \ | digital
TCS2.21MKF23CQ101_XH01 | 31679 | CONDUCT TREATMENT LOOP | \ | digital
TCS2.21MKF30CP101_XH01 | 31680 | DP STATOR WINDING | \ | digital
TCS2.21MKF30EU001_XA01 | 31681 | STATOR COIL DIFF PRESSURE | \ | digital
TCS2.21MKF30EU001_XA02 | 31682 | STATOR COIL DIFF PRESSURE | \ | digital
TCS2.21MKF30EU001_XA03 | 31683 | STATOR COIL DIFF PRESSURE | \ | digital
TCS2.21MKF30EU001_XK01 | 31684 | STATOR COIL DIFF PRESSURE | \ | digital
TCS2.21MKF31CP001_XG02_XG02 | 31685 | P H2 TO WATER | \ | digital
TCS2.21MKG24CF101_XH01 | 31686 | M/U H2 FLOW | \ | digital
TCS2.21MKG24CF101_XH02 | 31687 | \ |  | digital
TCS2.21MKG26CP101_ZV01 | 31688 | PRES H2 GEN CASING | \ | digital
TCS2.21MKG30CQ901_XH01 | 31689 | H2 GAS PURITY ANALYZER | \ | digital
TCS2.21MKG30CQ901_ZV01 | 31690 |  |  | digital
TCS2.21MKG32CQ401_XG51 | 31691 | OVERHEATING MONITOR | \ | digital
TCS2.21MKG41CL001_XG01 | 31692 | \ |  | digital
TCS2.21MKG42CL001_XG01 | 31693 | \ |  | digital
TCS2.21MKG43CL001_XG01 | 31694 | \ |  | digital
TCS2.21MKG44CL001_XG01 | 31695 | \ |  | digital
TCS2.21MKG51AN001_47935_OUT | 31696 |  |  | digital
TCS2.21MKG51AN001_MOTOR_RUNNING | 31697 |  |  | digital
TCS2.21MKG51AN001_47935 | 31698 | \ |  | digital
TCS2.21MKG52AT001_MOTOR_RUNNING | 31699 |  |  | digital
TCS2.21MKW01CL001_XG52 | 31700 | \ |  | digital
TCS2.21MKW06CL001_XG52 | 31701 | \ |  | digital
TCS2.21MKW07CL001_XG02 | 31702 | L DEFOAMING TANK EE | \ | digital
TCS2.21MKW08CL001_XG02 | 31703 | L DEFOAMING TANK TE | \ | digital
TCS2.21MKW11AP001_XB01 | 31704 | ~AIR SEAL OIL PUMP 1 | \ | digital
TCS2.21MKW11CP001_XG01 | 31705 | PRES D/STR SO PUMP 1 | \ | digital
TCS2.21MKW11EE001_XA01 | 31706 | \ |  | digital
TCS2.21MKW11EU001_ZV01 | 31707 | \ |  | digital
TCS2.21MKW12AP001_XB01 | 31708 | ~AIR SEAL OIL PUMP 2 | \ | digital
TCS2.21MKW12CP001_XG01 | 31709 | PRES D/STR SO PUMP 2 | \ | digital
TCS2.21MKW13AP001_XB01 | 31710 | SEAL OIL PUMP 3 | \ | digital
TCS2.21MKW13AP001_ZV02 | 31711 | \ |  | digital
TCS2.21MKW13CP001_XG01 | 31712 | PRES D/STR SEAL OIL PUMP 3 | \ | digital
TCS2.21MKW17CP001_XG01 | 31713 | DP SEAL OIL FILTER AIR SIDE | \ | digital
TCS2.21MKW19CP001_XG51 | 31714 | PRES SEAL OIL FOR DC PUMP | \ | digital
TCS2.21MKW21EE001_XA01 | 31715 | \ |  | digital
TCS2.21MKW25AP001_XB01 | 31716 | ~H2 GAS SEAL OIL PUMP 1 | \ | digital
TCS2.21MKW25CP001_XG01 | 31717 | PRES D/STR SO PUMP 4 | \ | digital
TCS2.21MKW26AP001_XB01 | 31718 | ~H2 GAS SEAL OIL PUMP 2 | \ | digital
TCS2.21MKW26CP001_XG01 | 31719 | PRES D/STR SO PUMP 5 | \ | digital
TCS2.21MKW30CP001_XG01 | 31720 | DP SEAL OIL FILTER GAS SIDE | \ | digital
TCS2.21MKW30CQ901_XM71 | 31721 | \ |  | digital
TCS2.21MKW50EE001_DCO_SEL1 | 31722 | \ |  | digital
TCS2.21MKW50EE001_XA01 | 31723 | SLC BRG CHMB EXH BLWR | \ | digital
TCS2.21MKW51AN001_MOTOR_RUNNING | 31724 | \ |  | digital
TCS2.21MKW51AN001_XB01 | 31725 | GEN EXH BLWR 1 | \ | digital
TCS2.21MKW52AN001_XB01 | 31726 | GEN EXH BLWR 2 | \ | digital
TCS2.21MKW52AT001_MOTOR_RUNNING | 31727 | \ |  | digital
TCS2.21MKY01EU003_ZV01 | 31728 | RESYNCH SELECT | \ | digital
TCS2.21MKY01EZ112_XB01A | 31729 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MKY01EZ212_XB01A | 31730 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MKY01EZ900_ZV01 | 31731 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYA01EA001_SEL2 | 31732 | SYNCH MODE SELECT | \ | digital
TCS2.21MYA01EA001_YB01 | 31733 | \ |  | digital
TCS2.21MYA01EA001_ZV01 | 31734 | SEMI-AUTO SYNCH | \ | digital
TCS2.21MYA01EA001_ZV03 | 31735 |  |  | digital
TCS2.21MYA01EA001_ZV04 | 31736 | \ |  | digital
TCS2.21MYA01EA001_ZV11 | 31737 | SYNCHRO AUTOSTOP P31CBP01 | \ | digital
TCS2.21MYA01EA002_XB01 | 31738 | INPUT FROM SYNCHRO. | \ | digital
TCS2.21MYA01EA020_XB02 | 31739 | INPUT FROM SYNCHRO. | \ | digital
TCS2.21MYA01EA099_XB01 | 31740 | INPUT FROM SYNCHRO. | \ | digital
TCS2.21MYA02EA001_COM | 31741 | SYNCHRO AUTOSTOP P31CBP01 | \ | digital
TCS2.21MYB00EU110_ZV90A | 31742 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB00EU110_ZV92A | 31743 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB00EU110_ZV99A | 31744 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB00EU902_ZV01 | 31745 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB00EY011_XG01A | 31746 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB00EY013_XG01A | 31747 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB00EY202_XG02A | 31748 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB00EY900_ZV01 | 31749 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB01EE200_ZV02 | 31750 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB01EU002_ZV10 | 31751 | OVERSPEED MANUAL TEST TO BRAUN | \ | digital
TCS2.21MYB01EU002_ZV90 | 31752 | RESET PASSIVATION TRIP DO | \ | digital
TCS2.21MYB01EU002_ZV91 | 31753 | RESET PASSIVATION | \ | digital
TCS2.21MYB01EU002_ZV99 | 31754 | RESET BRAUN | \ | digital
TCS2.21MYB10CS902_ZV01 | 31755 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21MYB10CS902_ZV02 | 31756 | DI FROM SIL3 SYSTEM | \ | digital
TCS2.21SAM10EE005_ZV51 | 31757 | ENCLOSURE VENT TRIP CIRCUIT | \ | digital
TCS2.21MBJ10GT001_XB12 | 31758 | FEEDER BKR | \ | digital
TCS2.21MBJ20GS002_XB12 | 31759 | SFC SW CROSS MBM02 | \ | digital
TCS2.21MBJ20GS003_XB12 | 31760 | SFC SW DIRECT MBM04 | \ | digital
TCS2.21MBJ20EA006_XB11 | 31761 |  | \ | digital
TCS2.21MBJ20EA006_XB12 | 31762 |  | \ | digital
TCS2.21MBJ20EA020_XB11 | 31763 |  | \ | digital
TCS2.21MBJ20EA021_XB11 | 31764 |  | \ | digital
TCS2.21MBJ20EA022_XB11 | 31765 |  | \ | digital
TCS2.21MBJ20EA007_XB11 | 31766 |  | \ | digital
TCS2.21MBJ20EA007_XB12 | 31767 |  | \ | digital
TCS2.21MBJ20EA011_XB11 | 31768 |  | \ | digital
TCS2.21MBJ20EA004_XB11 | 31769 |  | \ | digital
TCS2.21MBJ20EA001_XB11 | 31770 |  | \ | digital
TCS2.21MBJ20EA001_XB12 | 31771 |  | \ | digital
TCS2.21MBJ20EZ001_XB11 | 31772 |  | \ | digital
TCS2.21MBJ20EG001_XB11 | 31773 |  | \ | digital
TCS2.21MBJ20EA013_XB11 | 31774 |  | \ | digital
TCS1.10MBH22DP100_48026_OUT | 31775 |  |  | float32
TCS1.10MBP01EC001_STEP_A | 31776 |  |  | float32
TCS2.20MBH22DP100_48026_OUT | 31777 |  |  | float32
TCS2.20MBP01EC001_STEP_A | 31778 |  |  | float32